## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-08-2025 | [28 empty] | Date: | 04-08-2025 | [28 empty] | Date: | 04-08-2025 | [28 empty] | Date: | 04-08-2025 | [28 empty] | Date: | 04-08-2025 | [12 empty] | Date: | 04-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [12 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.7 | 18 | 67 | 62 | 0 | 0 | 0 | 67 | 0 | 450 | 303 | 390 | 0 | 0 | 335 | 198 | 0 | 0 | 90 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 13 | 65 | 22 | 0 | 12 | 25 | 0 | 219 | 0 | 26 | 741 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 51 | 24 | 63 | 0 | 355 | 330 | 50 | 172 | 39 | 86 | 70 | 160 | 72 | 20 | 100 | 42 | 8 | 0 | 44 | 0 | 275 | 385 | 0 | 60 | 156 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 100 | 112 | 0 | 0 | 12 | 7567.2 | 886 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 17 | 1352.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 175 | 0 | 174 | 0 | 414 | 0 | 0 | 176 | 0 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 304 | 1100 | 0 | 7047.88 | 14615.08 | 107.21
01:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 67 | 15 | 0 | 0 | 0 | 61 | 0 | 450 | 301 | 390 | 0 | 0 | 335 | 198 | 0 | 0 | 90 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 15 | 65 | 22 | 0 | 12 | 25 | 0 | 219 | 0 | 32 | 745 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 51 | 0 | 63 | 0 | 354 | 330 | 50 | 172 | 39 | 82 | 50 | 160 | 67 | 20 | 98 | 40 | 8 | 0 | 44 | 0 | 275 | 355 | 0 | 60 | 149 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 65 | 111 | 0 | 0 | 12 | 7270.4 | 880 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1069 | 0 | 1307.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 166 | 0 | 165 | 0 | 334 | 0 | 0 | 176 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 120 | 220 | 0 | 305 | 1090 | 0 | 6740.58 | 14010.98 | 107.25
02:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 67 | 0 | 0 | 0 | 0 | 33 | 0 | 450 | 304 | 400 | 0 | 0 | 335 | 195 | 0 | 0 | 70 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 12 | 65 | 22 | 0 | 12 | 25 | 0 | 219 | 0 | 32 | 747 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 62 | 0 | 353 | 330 | 50 | 172 | 39 | 84 | 50 | 160 | 64 | 20 | 102 | 38 | 8 | 0 | 44 | 0 | 275 | 385 | 0 | 60 | 153 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 14 | 75 | 45 | 112 | 0 | 0 | 8 | 7140.8 | 880 | 346 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 0 | 1205.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 171 | 0 | 170 | 0 | 348 | 0 | 0 | 176 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 305 | 1095 | 0 | 6478.91 | 13619.71 | 107.29
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 305 | 400 | 0 | 0 | 335 | 195 | 0 | 0 | 35 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 65 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 33 | 743 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 63 | 0 | 354 | 330 | 50 | 176 | 39 | 85 | 50 | 168 | 70 | 20 | 62 | 38 | 0 | 0 | 44 | 0 | 275 | 385 | 0 | 60 | 153 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 75 | 45 | 111 | 0 | 0 | 12 | 6871.8 | 881 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 1107.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 172 | 0 | 171 | 0 | 350 | 0 | 0 | 176 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 306 | 1000 | 0 | 6261.12 | 13132.92 | 107.33
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 302 | 395 | 0 | 0 | 332 | 195 | 0 | 0 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 50 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 28 | 746 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 895 | 0 | 43 | 0 | 63 | 0 | 352 | 330 | 50 | 181 | 39 | 68 | 50 | 177 | 72 | 20 | 36 | 38 | 0 | 0 | 44 | 0 | 275 | 385 | 0 | 60 | 152 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 55 | 45 | 111 | 0 | 0 | 12 | 6744.5 | 881 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 882 | 0 | 1003.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 171 | 0 | 171 | 0 | 350 | 0 | 0 | 176 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 180 | 0 | 306 | 900 | 0 | 5913.13 | 12657.63 | 107.37
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 410 | 0 | 0 | 335 | 200 | 0 | 0 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 50 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 33 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 5 | 0 | 8 | 0 | 326 | 330 | 51 | 202 | 39 | 62 | 50 | 180 | 73 | 20 | 31 | 38 | 0 | 0 | 0 | 0 | 275 | 380 | 0 | 60 | 151 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 55 | 35 | 111 | 0 | 0 | 12 | 6492.8 | 882 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 809 | 0 | 863.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 170 | 0 | 170 | 0 | 350 | 0 | 0 | 176 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 180 | 0 | 306 | 602 | 0 | 5384.19 | 11876.99 | 107.4
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 300 | 400 | 0 | 0 | 335 | 133 | 0 | 0 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 50 | 0 | 0 | 12 | 25 | 0.06 | 220 | 0 | 35 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 1 | 5 | 0 | 8 | 0 | 300 | 310 | 51 | 198 | 39 | 63 | 70 | 180 | 71 | 20 | 32 | 36 | 0 | 1 | 0 | 0 | 275 | 375 | 0 | 60 | 147 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 55 | 35 | 111 | 0 | 0.6 | 12 | 6309.16 | 881 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.77 | 795 | 0 | 867.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 170 | 0 | 173 | 0 | 173 | 0 | 345 | 0 | 0 | 175 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1 | 0 | 0 | 170 | 120 | 180 | 0 | 306 | 600 | 0 | 5331.88 | 11641.04 | 107.43
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 309 | 410 | 0 | 0 | 335 | 135 | 0 | 1 | 17 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 50 | 0 | 0 | 12 | 25 | 0.41 | 220 | 0 | 33 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 845 | 3 | 5 | 0 | 8 | 0 | 300 | 280 | 50 | 202 | 36 | 67 | 70 | 182 | 67 | 8 | 32 | 34 | 0 | 5 | 0 | 0 | 275 | 330 | 0 | 60 | 141 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 35 | 111 | 0 | 0.86 | 12 | 6273.27 | 881 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 800 | 0 | 872.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 5 | 0 | 3.11 | 174 | 0 | 178 | 0 | 178 | 0 | 365 | 0 | 0.25 | 175 | 0 | 0 | 0 | 34 | 0 | 0 | 0.9 | 18 | 0.05 | 0 | 172 | 120 | 180 | 0 | 306 | 600 | 0 | 5413.27 | 11686.54 | 107.46
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 1 | 0 | 0 | 350 | 315 | 410 | 0 | 0 | 335 | 134 | 0 | 3 | 17 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 3 | 34 | 0 | 0 | 12 | 25 | 2.03 | 219 | 0 | 8 | 742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 7 | 5 | 0 | 8 | 0 | 300 | 280 | 50 | 204 | 37 | 60 | 70 | 180 | 71 | 8 | 33 | 30 | 0 | 9 | 0 | 0 | 275 | 335 | 0 | 60 | 143 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 35 | 102 | 0 | 8.63 | 12 | 6236.66 | 881 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 816 | 0 | 873.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.21 | 14 | 0 | 5.38 | 177 | 0 | 179 | 0 | 180 | 0 | 377 | 0 | 0 | 177 | 0 | 17 | 2 | 50 | 0 | 0 | 2 | 19 | 0.17 | 0 | 173 | 120 | 180 | 0 | 306 | 600 | 0 | 5518.77 | 11755.43 | 107.49
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 35 | 24 | 0 | 350 | 310 | 420 | 0 | 0 | 332 | 134 | 0 | 5 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 4 | 17 | 0 | 0 | 12 | 25 | 2.46 | 218 | 0 | 2 | 742 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 13 | 18 | 0 | 25 | 0 | 300 | 280 | 51 | 213 | 38 | 35 | 70 | 180 | 73 | 8 | 17 | 28 | 0 | 31 | 0 | 0 | 275 | 340 | 0 | 60 | 149 | 6 | 0 | 81 | 0 | 0 | 18 | 0 | 17 | 86 | 35 | 103 | 0 | 6.85 | 12 | 6343.81 | 889 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 842 | 0 | 909.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.79 | 17 | 0 | 9.58 | 181 | 0 | 186 | 0 | 185 | 0 | 396 | 0 | 1.07 | 173 | 0 | 35 | 6 | 56 | 0 | 0 | 0.7 | 24 | 0.28 | 0 | 179 | 120 | 180 | 0 | 306 | 600 | 0 | 5727.96 | 12071.77 | 107.52
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 | 35 | 0 | 350 | 309 | 450 | 0 | 0 | 330 | 195 | 0 | 11 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 15 | 33 | 0 | 0 | 25 | 25 | 3.4 | 218 | 0 | 4 | 748 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 844 | 6 | 51 | 0 | 26 | 0 | 312 | 280 | 50 | 213 | 38 | 34 | 30 | 180 | 73 | 8 | 17 | 18 | 0 | 35 | 0 | 0 | 275 | 352 | 0 | 60 | 158 | 6 | 0 | 81 | 0 | 0 | 18 | 0 | 17 | 86 | 35 | 103 | 1 | 5.86 | 12 | 6522.76 | 889 | 327 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 845 | 0 | 910.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.59 | 2 | 0 | 13.01 | 185 | 0 | 189 | 0 | 190 | 0 | 399 | 0 | 1.41 | 173 | 0 | 35 | 13 | 49 | 0 | 0 | 0.2 | 29 | 0.36 | 0 | 177 | 120 | 220 | 0 | 306 | 615 | 0 | 5812.02 | 12334.78 | 107.55
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 | 34 | 0 | 350 | 304 | 450 | 0 | 0 | 330 | 193 | 0 | 9 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 33 | 0 | 0 | 25 | 25 | 1.75 | 217 | 0 | 3 | 762 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 845 | 14 | 51 | 0 | 26 | 0 | 344 | 280 | 50 | 208 | 38 | 34 | 31 | 181 | 68 | 12 | 16 | 16 | 0 | 47 | 0 | 0 | 275 | 390 | 0 | 60 | 159 | 6 | 0 | 79 | 0 | 0 | 18 | 0 | 17 | 86 | 45 | 100 | 1 | 16.22 | 12 | 6635.47 | 890 | 322 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 918 | 0 | 978.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.31 | 18 | 0 | 20.06 | 180 | 0 | 199 | 0 | 199 | 0 | 415 | 0 | 1.58 | 169 | 0 | 35 | 7 | 49 | 0 | 0 | 1 | 11 | 0.45 | 0 | 174 | 120 | 220 | 0 | 304 | 740 | 0 | 6051.56 | 12687.03 | 107.58
12:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 41 | 109 | 0 | 350 | 306 | 500 | 0 | 0 | 329 | 191 | 0 | 13 | 35 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 23 | 33 | 0 | 0 | 25 | 25 | 2.29 | 218 | 0 | 2 | 762 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 858 | 16 | 43 | 0 | 51 | 0 | 342 | 280 | 47 | 205 | 40 | 49 | 51 | 180 | 47 | 12 | 16 | 26 | 0 | 45 | 0 | 0 | 275 | 375 | 0 | 60 | 159 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 50 | 99 | 1 | 6.31 | 12 | 6830.1 | 890 | 314 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 941 | 0 | 1001.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.77 | 11 | 0 | 14.45 | 181 | 0 | 196 | 0 | 199 | 0 | 414 | 0 | 1.16 | 170 | 0 | 35 | 1 | 34 | 0 | 0 | 3.6 | 39 | 0.14 | 0 | 194 | 120 | 220 | 0 | 304 | 995 | 0 | 6352.79 | 13182.89 | 107.61
13:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 50 | 0 | 0 | 0 | 55 | 132 | 0 | 350 | 295 | 500 | 0 | 0 | 330 | 193 | 0 | 14 | 35 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 150 | 31 | 33 | 0 | 0 | 25 | 25 | 0.16 | 218 | 0 | 15 | 762 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 933 | 13 | 51 | 33 | 53 | 0 | 343 | 280 | 48 | 195 | 40 | 66 | 50 | 179 | 52 | 12 | 17 | 26 | 0 | 32 | 0 | 0 | 275 | 367 | 0 | 60 | 157 | 6 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 87 | 65 | 67 | 0 | 18.53 | 6 | 6939.19 | 899 | 303 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1040 | 0 | 1006.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.13 | 23 | 0 | 14.77 | 174 | 0 | 190 | 0 | 191 | 0 | 410 | 0 | 1.23 | 170 | 0 | 70 | 2 | 34 | 0 | 0 | 3.4 | 43 | 0.2 | 0 | 219 | 120 | 220 | 0 | 305 | 1120 | 0 | 6645.82 | 13585.01 | 107.71
14:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 50 | 0 | 0 | 0 | 55 | 127 | 0 | 350 | 299 | 450 | 0 | 0 | 330 | 132 | 0 | 15 | 35 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 22 | 33 | 0 | 0 | 25 | 25 | 0.06 | 219 | 0 | 7 | 767 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 937 | 17 | 51 | 50 | 53 | 0 | 344 | 280 | 49 | 197 | 40 | 62 | 50 | 180 | 53 | 12 | 15 | 24 | 0 | 36 | 0 | 0 | 270 | 370 | 0 | 60 | 149 | 6 | 0 | 60 | 0 | 0 | 18 | 0 | 17 | 94 | 65 | 68 | 1 | 10.14 | 2 | 6907.4 | 900 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 1025 | 0 | 1023.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.01 | 38 | 0 | 7.56 | 165 | 0 | 181 | 0 | 181 | 0 | 355 | 0 | 0.89 | 169 | 0 | 70 | 1 | 34 | 0 | 0 | 2.8 | 97 | 0.13 | 0 | 221 | 120 | 220 | 0 | 305 | 1120 | 0 | 6618.65 | 13526.05 | 107.8
15:00 | 0 | 41 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 50 | 31 | 0 | 0 | 55 | 139 | 0 | 350 | 295 | 450 | 0 | 0 | 335 | 197 | 0 | 5 | 35 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 22 | 33 | 0 | 0 | 25 | 25 | 0.62 | 219 | 0 | 3 | 768 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 15 | 51 | 50 | 53 | 0 | 350 | 330 | 49 | 191 | 37 | 71 | 50 | 186 | 53 | 18 | 14 | 16 | 0 | 19 | 0 | 0 | 270 | 318 | 0 | 60 | 143 | 6 | 0 | 81 | 20 | 0 | 18 | 0 | 0 | 84 | 120 | 72 | 1 | 11.24 | 6 | 7070.06 | 883 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1059 | 0 | 1004.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.64 | 29 | 0 | 16.12 | 176 | 0 | 174 | 0 | 173 | 0 | 341 | 0 | 1.42 | 169 | 0 | 70 | 6 | 34 | 0 | 0 | 5.8 | 2 | 0.03 | 0 | 215 | 120 | 220 | 0 | 305 | 1120 | 0 | 6496.66 | 13566.72 | 107.82
16:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 67 | 31 | 0 | 0 | 55 | 126 | 0 | 400 | 293 | 500 | 0 | 0 | 333 | 130 | 0 | 4 | 35 | 21.2 | 15 | 0 | 0 | 0 | 0 | 0 | 150 | 13 | 33 | 0 | 0 | 37 | 25 | 0.96 | 221 | 0 | 4 | 768 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 10 | 51 | 12 | 53 | 0 | 357 | 330 | 49 | 190 | 37 | 67 | 30 | 155 | 55 | 20 | 30 | 36 | 0 | 8 | 0 | 0 | 270 | 314 | 0 | 60 | 131 | 6 | 0 | 81 | 20 | 0 | 18 | 0 | 0 | 85 | 120 | 82 | 1 | 13.62 | 6 | 7040.78 | 882 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1019 | 0 | 1012.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.38 | 30 | 0 | 17.72 | 165 | 0 | 162 | 0 | 161 | 0 | 334 | 0 | 1.8 | 171 | 0 | 35 | 9 | 34 | 0 | 0 | 2 | 10 | 0.04 | 0 | 213 | 120 | 220 | 0 | 305 | 1070 | 0 | 6324.55 | 13365.33 | 107.84
17:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 17 | 17 | 67 | 15 | 0 | 0 | 55 | 72 | 0 | 360 | 288 | 500 | 0 | 0 | 335 | 133 | 0 | 2 | 35 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 150 | 15 | 33 | 0 | 0 | 37 | 25 | 1.15 | 221 | 0 | 14 | 766 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 3 | 51 | 12 | 53 | 0 | 356 | 330 | 50 | 192 | 37 | 65 | 30 | 139 | 58 | 20 | 14 | 20 | 0 | 3 | 7 | 0 | 270 | 308 | 0 | 60 | 133 | 6 | 0 | 82 | 20 | 0 | 18 | 0 | 0 | 85 | 120 | 94 | 0 | 7.23 | 6 | 6877.88 | 883 | 292 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 994 | 0 | 1008.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 9 | 0 | 4.82 | 169 | 0 | 166 | 0 | 164 | 0 | 342 | 0 | 0.24 | 174 | 0 | 35 | 8 | 34 | 0 | 0 | 2 | 11 | 0.02 | 0 | 217 | 120 | 220 | 0 | 304 | 1042 | 0 | 6249.1 | 13126.98 | 107.87
18:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 17 | 17 | 67 | 15 | 0 | 0 | 55 | 64 | 0 | 320 | 302 | 400 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 21.5 | 14 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 33 | 0 | 0 | 37 | 25 | 0.06 | 217 | 0 | 15 | 763 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 851 | 0 | 51 | 12 | 53 | 0 | 320 | 330 | 49 | 201 | 40 | 65 | 50 | 140 | 59 | 20 | 15 | 22 | 0 | 1 | 13 | 0 | 270 | 334 | 0 | 60 | 134 | 6 | 0 | 82 | 20 | 0 | 18 | 0 | 0 | 103 | 120 | 94 | 0 | 1.47 | 6 | 6864.03 | 882 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 888 | 0 | 1110.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 3 | 0 | 1.1 | 168 | 0 | 166 | 0 | 165 | 0 | 369 | 0 | 0.11 | 172 | 0 | 35 | 2 | 32 | 0 | 0 | 0.3 | 3 | 0.01 | 0 | 220 | 120 | 180 | 0 | 305 | 955 | 0 | 6110.2 | 12974.23 | 107.9
19:00 | 7 | 73 | 25 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 23 | 17 | 67 | 45 | 45 | 4 | 55 | 145 | 0 | 320 | 303 | 400 | 0 | 35 | 332 | 0 | 0 | 0 | 125 | 21.5 | 18 | 0 | 0 | 0 | 15 | 1 | 150 | 6 | 66 | 21 | 0 | 37 | 25 | 0 | 217 | 4 | 25 | 760 | 17 | 0 | 33 | 1 | 14 | 0 | 0 | 0 | 0 | 947 | 0 | 51 | 26 | 70 | 0 | 351 | 330 | 51 | 201 | 40 | 75 | 50 | 156 | 68 | 20 | 68 | 26 | 25 | 0 | 37 | 0 | 270 | 366 | 0 | 60 | 141 | 6 | 0 | 82 | 20 | 0 | 18 | 0 | 0 | 103 | 127 | 102 | 0 | 0 | 6 | 7631.5 | 883 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1079 | 12 | 1324.8 | 0 | 14 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 0 | 175 | 0 | 172 | 0 | 171 | 0 | 406 | 0 | 0 | 171 | 0 | 92 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 180 | 0 | 304 | 1015 | 0 | 6858.8 | 14490.3 | 107.93
19:30 | 7 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 44 | 17 | 80 | 62 | 30 | 15 | 35 | 112 | 5 | 320 | 290 | 400 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 26.5 | 23 | 0 | 0 | 0 | 15 | 41 | 150 | 3 | 66 | 28 | 0 | 37 | 25 | 0 | 216 | 16 | 24 | 766 | 0 | 0 | 33 | 8 | 39 | 0 | 0 | 0 | 0 | 967 | 0 | 51 | 50 | 78 | 0 | 356 | 330 | 51 | 189 | 40 | 115 | 50 | 200 | 54 | 20 | 98 | 26 | 52.2 | 0 | 37 | 0 | 255 | 358 | 0 | 60 | 135 | 6 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 94 | 180 | 102 | 0 | 0 | 6 | 7906.7 | 883 | 290 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1189 | 17 | 1417.25 | 0 | 37 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 27 | 0 | 182 | 0 | 163 | 0 | 165 | 0 | 343 | 0 | 0 | 169 | 0 | 94 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 304 | 1120 | 0 | 7201.25 | 15107.95 | 107.93
20:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 42 | 17 | 85 | 46 | 15 | 0 | 42 | 108 | 16 | 320 | 291 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 34 | 150 | 3 | 66 | 30 | 0 | 37 | 25 | 0 | 212 | 17 | 22 | 770 | 0 | 0 | 33 | 13 | 17 | 0 | 0 | 0 | 0 | 960 | 0 | 51 | 24 | 100 | 0 | 356 | 330 | 48 | 191 | 40 | 107 | 70 | 198 | 57 | 20 | 88 | 24 | 34 | 0 | 37 | 0 | 255 | 357 | 0 | 60 | 130 | 6 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 93 | 178 | 102 | 0 | 0 | 6 | 7768 | 882 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 17 | 1411.61 | 0 | 37 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 27 | 0 | 177 | 0 | 162 | 0 | 163 | 0 | 345 | 0 | 0 | 170 | 0 | 94 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 305 | 1125 | 0 | 7213.61 | 14981.61 | 107.96
21:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 29 | 17 | 62 | 15 | 0 | 0 | 27 | 72 | 16 | 320 | 285 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 33 | 150 | 1 | 66 | 52 | 0 | 37 | 25 | 0 | 212 | 0 | 24 | 771 | 0 | 0 | 33 | 20 | 15 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 12 | 130 | 0 | 356 | 330 | 49 | 182 | 40 | 109 | 70 | 199 | 54 | 20 | 88 | 26 | 34 | 0 | 37 | 0 | 255 | 351 | 0 | 60 | 137 | 5 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 94 | 182 | 102 | 0 | 0 | 6 | 7645 | 883 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 17 | 1412 | 0 | 32 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 27 | 0 | 169 | 0 | 167 | 0 | 164 | 0 | 383 | 0 | 0 | 173 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 120 | 220 | 0 | 303 | 1121 | 0 | 7241 | 14886 | 107.99
22:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 22 | 17 | 55 | 31 | 0 | 0 | 17 | 53 | 16 | 320 | 295 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 66 | 52 | 0 | 37 | 25 | 0 | 209 | 0 | 26 | 775 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 968 | 0 | 51 | 0 | 68 | 0 | 356 | 330 | 50 | 210 | 41 | 108 | 70 | 199 | 54 | 20 | 88 | 42 | 34 | 0 | 37 | 0 | 255 | 362 | 0 | 60 | 150 | 5 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 94 | 181 | 102 | 0 | 0 | 6 | 7548 | 883 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 17 | 1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 180 | 0 | 168 | 0 | 343 | 0 | 0 | 174 | 0 | 94 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 303 | 1122 | 0 | 7126 | 14674 | 108.02
23:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 17 | 50 | 31 | 0 | 0 | 0 | 17 | 0 | 320 | 307 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 66 | 53 | 0 | 37 | 25 | 0 | 208 | 0 | 28 | 774 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 985 | 0 | 51 | 0 | 45 | 0 | 352 | 330 | 50 | 190 | 41 | 93 | 70 | 197 | 55 | 20 | 88 | 44 | 34 | 0 | 37 | 0 | 255 | 388 | 0 | 60 | 155 | 5 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 94 | 181 | 102 | 0 | 0 | 6 | 7443 | 896 | 286 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 187 | 0 | 177 | 0 | 378 | 0 | 0 | 175 | 0 | 94 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 302 | 1110 | 0 | 7009 | 14452 | 108.04
Total KWH | 5166 | 1120320 | 498240 | 0 | 0 | 0 | 0 | 0 | 1990800 | 0 | 0 | 308160 | 219960 | 1320624 | 281280 | 53695 | 16982 | 651745 | 1350720 | 48960 | 8821500 | 7230196 | 10209545 | 0 | 77604 | 7981003 | 3192000 | 0 | 80391 | 1191600 | 507000 | 485640 | 0 | 0 | 0 | 10036 | 82560 | 3800000 | 280320 | 1151994 | 286896 | 0 | 577920 | 593280 | 15719 | 5210625 | 28440 | 462720 | 18283636.36 | 5018 | 0 | 612000 | 89103.6 | 84472 | 0 | 0 | 0 | 0 | 21927270 | 115425 | 1015467 | 327854 | 1221091 | 0 | 8507400 | 7604000 | 1194240 | 4720000 | 931608 | 1752000 | 1277580 | 4276800 | 1484280 | 370580 | 1112640 | 716160 | 213514 | 314891 | 432176 | 0 | 6453500 | 8946000 | 0 | 1424040 | 3545345.5 | 152496 | 0 | 1841280 | 232608 | 0 | 446000 | 0 | 249120 | 2017200 | 2133600 | 2311680 | 5200 | 99220 | 213600 | 168803736.46 | 21425455 | 7655904 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 300240 | 23483630 | 87360 | 26241209.76 | 0 | 73142 | 0 | 0 | 20256 | 0 | 99392 | 0 | 0 | 136208 | 198110 | 64637 | 129752 | 4296818 | 0 | 4474173 | 0 | 4447818 | 0 | 8883854 | 0 | 10320 | 4240000 | 0 | 1100395 | 61760 | 1433068 | 0 | 0 | 25816.8 | 321120 | 0 | 0 | 5150000 | 2858000 | 5214000 | 0 | 7352727 | 23288727.27 | 0 | 153985892.83 | 322789629.29

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-08-2025 | during | 05-08-2025 | during | 05-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 294 | 400.75 | 400.75 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 320 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 290 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 191 | 0 | 208.13 | 208.13 | 198 | 198 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 44 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 62 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 41 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 26.5 | 33 | 33 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 23 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 25 | 52.19 | 52.19 | 25 | 25 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 80 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 86 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 5 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 109 | 112 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 17 | 0 | 17 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 500 | 400 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2016.5 | 2349.5 | 5795.7 | 5778.7 | 3778.47 | 3761.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 216 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 39 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 28 | 64 | 72 | 64 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 66 | 0 | 0 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 37 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 24 | 35 | 42 | 35 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 41 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.29 | 0 | 3.3 | 0 | 3.3 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 858 | 967 | 1052 | 1052 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 23 | 3 | 5 | 0 | 5 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 762 | 766 | 755 | 755 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2133.29 | 2434 | 3521.02 | 3509.72 | 3630.02 | 3618.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 205 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 342 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 46.7 | 46.7 | 39 | 39 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 51 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 51 | 78 | 195 | 195 | 182 | 182 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 200 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 16 | 98 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 54 | 113 | 113 | 73 | 73 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 115 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 45 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1434 | 1797.2 | 2429.56 | 2379.56 | 2217.36 | 2167.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-08-2025 | during | 05-08-2025 | during | 05-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 99 | 102 | 157.5 | 157.5 | 153 | 153 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1 | 0 | 1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 50 | 180 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 86 | 94 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 6.31 | 0 | 37 | 0 | 37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 6 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 18 | 18 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 271.31 | 382 | 587 | 549 | 491.2 | 453.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 0 | 0 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 135 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 30 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 82 | 82 | 84 | 84 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 6 | 25 | 25 | 7 | 7 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 358 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 275 | 255 | 300 | 300 | 300 | 300 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 975 | 944 | 1000 | 1000 | 984 | 984
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 890 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 314 | 290 | 410 | 410 | 348 | 348 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 941 | 1189 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2203 | 2417 | 3493.2 | 3443.2 | 3394.2 | 3344.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 304 | 304 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 995 | 1120 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 194 | 275 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.14 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1833.14 | 2039 | 2162 | 2161 | 2102 | 2101
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 15.77 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 182 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 163 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 165 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 343 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.16 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1001.67 | 1417.25 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 14.45 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 11 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2034.05 | 2376.25 | 3180.37 | 3028.87 | 3095.59 | 2944.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 169 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 94 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 22 | 0 | 22 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 39 | 0 | 71.6 | 0 | 71.6 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 282.6 | 369 | 502.2 | 402 | 502.2 | 402
System Total |  |  |  |  | 28671.2 | 27843.665 | 13182.89 | 15107.95 | 22671.05 | 22252.05 | 20195.04 | 19776.04
Forecast Scenario (05-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14580 |  | 0 |  | 14580
|  |  |  | 1:00 | 14160 |  | 0 |  | 14160
|  |  |  | 2:00 | 13730 |  | 0 |  | 13730
|  |  |  | 3:00 | 13380 |  | 0 |  | 13380
|  |  |  | 4:00 | 13090 |  | 0 |  | 13090
|  |  |  | 5:00 | 12730 |  | 0 |  | 12730
|  |  |  | 6:00 | 12020 |  | 0 |  | 12020
|  |  |  | 7:00 | 11700 |  | 0 |  | 11700
|  |  |  | 8:00 | 11580 |  | 0 |  | 11580
|  |  |  | 9:00 | 11350 |  | 0 |  | 11350
|  |  |  | 10:00 | 10730 |  | 0 |  | 10730
|  |  |  | 11:00 | 10840 |  | 0 |  | 10840
|  |  |  | 12:00 | 11460 |  | 0 |  | 11460
|  |  |  | 13:00 | 12090 |  | 0 |  | 12090
|  |  |  | 14:00 | 11610 |  | 0 |  | 11610
|  |  |  | 15:00 | 11310 |  | 0 |  | 11310
|  |  |  | 16:00 | 11090 |  | 0 |  | 11090
|  |  |  | 17:00 | 10720 |  | 0 |  | 10720
|  |  |  | 18:00 | 10630 |  | 0 |  | 10630
|  |  |  | 18:30 | 11900 |  | 0 |  | 11900
|  |  |  | 19:00 | 12550 |  | 0 |  | 12550
|  |  |  | 19:30 | 13370 |  | 0 |  | 13370
|  |  |  | 20:00 | 13190 |  | 0 |  | 13190
|  |  |  | 21:00 | 13420 |  | 0 |  | 13420
|  |  |  | 22:00 | 13480 |  | 0 |  | 13480
|  |  |  | 23:00 | 13560 |  | 0 |  | 13560
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 11460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13420.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14020.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 303.40 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:22 hrs on 05-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13182.89 | MW | 12:00 Hr. | Energy Generated |  |  | 322.7896 |  | MKWHr.
| Day Peak Demand |  |  | 13182.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 15107.95 | MW | 19:30 Hr. | Energy Demand |  |  | 322.7896 |  | MKWHr.
| Evening Peak Demand |  |  | 15107.95 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 11641.04 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1001.34 |  | MMCFD
| Maximum Generation of the Day |  |  | 15107.95 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9026 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.4177 | 0 | 7.1451 | 0 | 0 | 0.080391 | 0 | 0 | 47.6431 | Gas | 134.7059 | Gas | 500442588.805
| Chattogram Zone |  |  | 4.2627 | 40.2109 | 3.5217 | 0 | 5.2106 | 0.13114 | 0 | 0.28032 | 53.6174 | Coal | 103.726 | Coal | 619361539.3463
| Cumilla Zone |  |  | 26.842 | 0 | 9.5993 | 0 | 0 | 0.31489 | 0.71616 | 0 | 37.4723 | HFO | 27.7578 | HFO | 507539470.902
| Mymensingh Zone |  |  | 2.3117 | 0 | 4.6135 | 0 | 0 | 0.10442 | 0 | 0 | 7.0296 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.0413 | Hydro | 5.2106 | Hydro | 521062.5
| Khulna Zone |  |  | 7.6559 | 23.4836 | 0.08736 | 0 | 0 | 0.30024 | 22.3375 | 0 | 53.8646 | Solar | 1.8142 | Solar | 26290963.398
| Barishal Zone |  |  | 8.072 | 35.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8635 | Import | 49.2948 | Import | 247032694.4684
| Rajshahi Zone |  |  | 22.1027 | 0 | 0.25743 | 0 | 0 | 0.47439 | 26.2412 | 0 | 49.0757 | Wind | 0.28032 | Wind | 4103884.8
| Rangpur Zone |  |  | 0 | 4.24 | 2.5335 | 0 | 0 | 0.4087 | 0 | 0 | 7.1822
| Total |  |  | 134.7059 | 103.726 | 27.7578 | 0 | 5.2106 | 1.8142 | 49.2948 | 0.28032 | 322.7896
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 500442588.805 |  | Hydro | 521062.5
|  |  |  | Coal | 619361539.3463 |  | Solar | 26290963.398
|  |  |  | HFO | 507539470.902 |  | Import | 247032694.4684
|  |  |  | HSD | 0 |  | Wind | 4103884.8
[5 empty] | Total: | 190,52,92,204 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4255 | Peak Hr Flow | 883.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47727418.29 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.2412 | Peak Hr Flow | 1417.25 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 956 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.71616 | Peak Hr Flow | 26.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1080 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.3828 | Peak Hr Flow | 2326.25 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5198
|  |  |  | Chattogram |  | 0 |  | 1446
|  |  |  | Cumilla |  | 0 |  | 1381
|  |  |  | Mymensingh |  | 0 |  | 1236
|  |  |  | Sylhet |  | 0 |  | 509
|  |  |  | Khulna |  | 0 |  | 1810
|  |  |  | Barishal |  | 0 |  | 466
|  |  |  | Rajshahi |  | 0 |  | 1457
|  |  |  | Rangpur |  | 0 |  | 929
|  |  |  | Total |  | 0 |  | 14432
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:25 | Haripur-Madanganj 132kV Ckt-1 is restored.
|  | 08:38 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 08:39 | Khulna (C) S/S TR-1 425T LT is restored.
|  | 09:45 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
|  | 09:46 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 09:49 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 09:50 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 10:15 | 12:08 | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D Due to To cheak and rectify the
33kv CSE insulation & transformer oil leakage
| 10:16 | 12:07 | Bhandaria 132/33kV S/S Transformer-2 HT Project Work S/D Due to To cheak and rectify the
33 kv CSE insulation & transformer oil leakage
|  | 10:20 | Hasnabad 132/33kV S/S 33kv Reserve Bus is restored.
| 10:42 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- As per NLDC demand
| 11:12 |  | Rooppur 400/230KV 522MVA Auto Tx 00ATT10 was shutdown for maintenance.
|  | 12:14 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 is restored.
| 12:22 | 13:22 | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to To check and rectify the
33kv cse insulation and Transformer oil leakage.
| 12:23 | 13:21 | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to Project work
| 12:33 | 13:32 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Over Current Earth Fault Relay, Lockout
Relay relays Due to 33 KV CT Blast in B phase
| 12:33 |  | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockoyt Relay relays Due to 33 KV CT
Blast
| 12:33 | 13:30 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing Over Current Earth Fault Relay, relays
Due to 33 KV CT Blast in B phase
| 12:33 | 13:33 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip Relay relays Due to 33 Kv CT Blast
| 12:33 | 13:29 | Shahjibazar 132/33kV S/S TR-06 HT Tripped showing Over Current Earth Fault Relay, Diff
Relay relays Due to 33 KV CT Blast in B Phase
| 12:33 |  | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Over Current Earth Fault Relay, Lockout
Relay, Siemens Relay relays Due to 33 KV CT Blast
|  | 16:48 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 16:53 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 17:35 |  | Siddhirganj 2x120 MW GT-1 and GT-2 was shutdown at 17:35 and 17:40 hrs. respectively.
| 18:40 |  | Raozan 25 MW PP Synchronized
| 19:30 |  | Evening Peak Generation: 15107 MW.
| 01:29 | 02:48 | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing General
trip Dist. trip Tph relays.
| 01:41 |  | Raozan 25 MW PP Shutdown
| 02:23 | 06:38 | Ghorashal 230kV S/S TARFO-2 HT Tripped showing SIEMENS relays Due to 33kv outgoing-1 PBS | [7 empty] | 35.0MW load
|  |  | Earth fault | [7 empty] | interrup.
| 02:23 | 07:03 | Ghorashal 230kV S/S TARFO-2 LT Tripped showing mikro relays Due to 33kv outgoing-1 PBS | [7 empty] | 35.0MW load
|  |  | Earth fault. | [7 empty] | interrup.
| 04:40 |  | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to Y-phase red hot maintenance | [7 empty] | 40.0MW load
interrup.
| 04:40 |  | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to Y-phase red hot maintenance | [7 empty] | 40.0MW load
interrup.
| 07:00 |  | Minimum Generation 10493 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 294 | 1990800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8821500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7230196 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 16982 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 3192000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7981003 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 5166 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 308160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 281280 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 651745 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 77604 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.5 | 507000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 23 | 485640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 498240 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 53695 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 80 | 1320624 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 86 | 1120320 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 5 | 48960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 112 | 1350720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 80391 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 219960 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 400 | 10209545 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1191600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2349.5 | 47643131
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3800000 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 89103.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115425 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 612000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 216 | 5210625 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 39 | 84472 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 28 | 286896 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1151994 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 577920 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 462720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 41 | 82560 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 10036 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 28440 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 593280 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 5018 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 967 | 21927270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 280320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 766 | 18283636.36 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2434 | 53617434.96
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4720000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8507400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7604000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 931608 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1194240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 78 | 1221091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1015467 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 327854 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 432176 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1277580 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4276800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 26 | 716160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 213514 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 370580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1112640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 54 | 1484280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1752000 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 314891 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1797.2 | 37472281
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 102 | 2311680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 2133600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 2017200 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 99220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 213600 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 249120 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 382 | 7029620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1424040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 135 | 3545345.5 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 232608 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1841280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 446000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 152496 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 358 | 8946000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 255 | 6453500 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 944 | 23041269.5
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 21425455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 290 | 7655904 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 87360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 300240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1189 | 23483630 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2417 | 53864589
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7352727 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2858000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 23288727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5214000 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 5150000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2236 | 2039 | 43863454.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 136208 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 73142 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4296818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4474173 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 165 | 4447818 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 343 | 8883854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 64637 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 99392 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 20256 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 10320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1417.25 | 26241209.76 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 129752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 198110 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2376.25 | 49075689.76
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 169 | 4240000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1433068 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25816.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 1100395 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 61760 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 321120 | -
Rangpur Area Total |  |  |  |  | 950 | 369 | 7182159.8
Eastern Grid Total |  |  |  |  | 17401.505 | 7906.7 | 168803736.46
Western Grid Total |  |  |  |  | 10442.16 | 7201.25 | 153985892.83
National Grid Total |  |  |  |  | 27843.665 | 15107.95 | 322789629.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9769.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4662.6 | MW
i) Dhaka area |  |  | 5198.04 |  | MW | i) Khulna area |  |  |  | 1810.2 | MW
ii) Chattogram area |  |  | 1445.5 |  | MW | ii) Barishal area |  |  |  | 466 | MW
iii) Cumilla area |  |  | 1380.62 |  | MW | iii) Rajshahi area |  |  |  | 1457.4 | MW
iv) Mymensingh area |  |  | 1236 |  | MW | iv) Rangpur area |  |  |  | 929 | MW
v) Sylhet area |  |  | 509 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14431.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 23 | 06:00 | 67 | Hathazari | 77 | 00:00 | 133 | PHP | 9 | 17:00
2 | AKSML | 133 | 10:00 | 68 | Ishurdi | 78 | 19:00 | 134 | Pabna | 116 | 20:00
3 | Aftabnagar | 46 | 00:00 | 69 | Jaldhaka | 78 | 21:00 | 135 | Palashbari | 100 | 21:00
4 | Agargaon | 133 | 14:00 | 70 | Jamalpur | 138 | 23:00 | 136 | Panchagarh | 53 | 19:30
5 | Agrabad | 92 | 13:00 | 71 | Jashore | 141 | 21:00 | 137 | Patuakhali | 73 | 22:00
6 | Amnura | 25 | 00:00 | 72 | Jhenaidah | 119 | 00:00 | 138 | Payra | 36 | 00:00
7 | Ashuganj | 103 | 01:00 | 73 | Joydebpur | 154 | 15:00 | 139 | Postogola | 54 | 00:00
8 | BSRM | 203 | 16:00 | 74 | Joypurhat | 62 | 19:30 | 140 | Purbachal | 21 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 15 | 00:00 | 141 | Purbasadipur | 121 | 19:30
10 | Bajitpur | 84 | 22:00 | 76 | KSRM | 25 | 16:00 | 142 | Rahanpur | 39 | 23:00
11 | Bakulia | 94 | 19:30 | 77 | Kabirpur | 244 | 15:00 | 143 | Rahim | 23 | 23:00
12 | Banani | 52.6 | 13:00 | 78 | Kachua | 90 | 21:00 | 144 | Rajbari | 81 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rajendrapur | 135 | 19:00
14 | Barapukuria | 59 | 19:00 | 80 | Kalurghat | 40 | 10:00 | 146 | Rajshahi | 110 | 19:30
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi-230 | 88 | 20:00
16 | Barishal | 111 | 20:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 120 | 22:00
17 | Barishal-230 | 102 | 20:00 | 83 | Kasba | 35 | 22:00 | 149 | Rampur | 40 | 21:00
18 | Baroaulia | 65 | 09:00 | 84 | Kazla | 96 | 16:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 75 | 19:00 | 85 | Keranigonj | 84 | 19:00 | 151 | Rangpur | 144 | 21:00
20 | Bashundhara | 198 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Ruppur | 6.6 | 16:00
21 | BashundharaCement | 9 | 12:00 | 87 | Khulna | 76 | 13:00 | 153 | SSM | 2 | 23:00
22 | Beanibazar | 66 | 00:00 | 88 | Khulshi | 179 | 19:30 | 154 | Saidpur | 106 | 19:00
23 | Benapole | 68 | 20:00 | 89 | Kishoreganj | 134 | 21:00 | 155 | Satkhira | 132 | 00:00
24 | Bhaluka | 150 | 23:00 | 90 | Kodda | 301 | 14:00 | 156 | Satmasjid | 98 | 13:00
25 | Bhandaria | 57 | 00:00 | 91 | Kulaura | 46 | 00:00 | 157 | Savar | 227 | 12:00
26 | Bhangura | 36 | 19:00 | 92 | Kurigram | 68 | 19:30 | 158 | SevenRings | 5.18 | 16:00
27 | Bheramara(GK) | 65 | 19:30 | 93 | Kushtia | 152 | 19:30 | 159 | ShahCement | 17 | 19:30
28 | Bhulta | 231 | 00:00 | 94 | Laksam | 22 | 13:00 | 160 | Shahjadpur | 86 | 19:30
29 | Bog-Sherpur | 76 | 22:00 | 95 | Lakshmipur | 21 | 21:00 | 161 | Shahjibazar | 114 | 00:00
30 | Bogura | 169 | 21:00 | 96 | Lalbag | 56 | 16:00 | 162 | Shahmirpur | 60 | 15:00
31 | Borhanuddin | 93 | 20:00 | 97 | Lalmonirhat | 67 | 19:30 | 163 | Shariatpur | 92 | 22:00
32 | Brahmanbaria | 125 | 00:00 | 98 | MI_Cement | 12.5 | 14:00 | 164 | Sherpur | 156 | 19:30
33 | Cantonment | 145 | 13:00 | 99 | Madanganj | 40 | 12:00 | 165 | Shikalbaha | 8 | 00:00
34 | Chandina | 16.17 | 09:00 | 100 | Madaripur | 118 | 23:00 | 166 | Shitalakhya | 82.7 | 15:00
35 | Chandpur | 81 | 21:00 | 101 | Madartek | 93 | 23:00 | 167 | Sholosohor | 43 | 15:00
36 | Chandraghona | 36 | 19:00 | 102 | Madunaghat | 54 | 00:00 | 168 | Shyampur | 88 | 00:00
37 | Chapai | 62 | 19:30 | 103 | Magura | 70 | 19:30 | 169 | Siddhirganj | 120 | 12:00
38 | Charsaidpur | 42 | 02:00 | 104 | Mahasthangarh | 86 | 20:00 | 170 | Sirajganj | 116 | 21:00
39 | Chauddagram | 67 | 00:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sonargaon | 110 | 19:00
40 | Chhatak | 32 | 00:00 | 106 | Manikganj | 126 | 21:00 | 172 | Sreemongol | 78 | 00:00
41 | Chowmuhani | 195 | 20:00 | 107 | Maniknagar | 82 | 13:00 | 173 | Sreepur | 99 | 15:00
42 | Chuadanga | 108 | 19:00 | 108 | Matarbari | 53 | 19:30 | 174 | Srinagar | 48.6 | 22:00
43 | Coxsbazar | 138 | 21:00 | 109 | Matuail | 60 | 00:00 | 175 | Sunamganj | 54 | 00:00
44 | Cumilla(N) | 138 | 19:00 | 110 | Millgate | 133 | 15:00 | 176 | Sylhet | 45 | 00:00
45 | Cumilla(S) | 143 | 16:00 | 111 | Mirpur | 124 | 19:00 | 177 | Sylhet-132 | 105 | 14:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 09:00 | 178 | TK | 34 | 00:00
47 | Daudkandi | 153 | 19:30 | 113 | Mirzapur | 45 | 21:00 | 179 | Tangail | 188 | 19:30
48 | Dhaka | 78 | 13:00 | 114 | Mithapukur | 64 | 19:30 | 180 | Taraganj | 22 | 19:00
49 | Dhamrai | 116 | 15:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 99 | 20:00
50 | Dhanmondi | 148 | 13:00 | 116 | Mogbazar | 154.8 | 13:00 | 182 | Tongi | 110 | 15:00
51 | Dohazari | 109 | 19:00 | 117 | Mongla | 31 | 10:00 | 183 | Ullahpara | 40 | 20:00
52 | Faridpur | 175 | 20:00 | 118 | Motijheel | 43 | 12:00 | 184 | Ullon | 42 | 00:00
53 | Fatullah | 99 | 15:00 | 119 | Muktagacha | 37 | 19:00 | 185 | Uttara | 83 | 13:00
54 | Fenchuganj | 40 | 21:00 | 120 | Munshiganj | 112 | 23:00 | 186 | UttaraNew | 61 | 00:00
55 | Feni | 111 | 19:30 | 121 | Muradnagar | 41 | 22:00 | 187 | Zigatola | 72 | 19:00
56 | GPH | 90 | 05:00 | 122 | Mymensingh | 204 | 19:00
57 | Ghatail | 90 | 19:00 | 123 | Naogaon | 130 | 21:00
58 | Ghorashal | 13 | 00:00 | 124 | Narail | 59.5 | 23:00
59 | Ghorashal-230 | 84 | 22:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 39 | 19:30 | 126 | Narshingdi | 178 | 00:00
61 | Gollamari | 96 | 00:00 | 127 | Natore | 145 | 19:30
62 | Gopalganj | 112.1 | 21:00 | 128 | Nawabganj | 60.6 | 22:00
63 | Gulshan | 126 | 13:00 | 129 | Netrakona | 126 | 19:30
64 | Halishahar | 68 | 12:00 | 130 | New | 62.2 | 12:00
65 | HaripurSBU | 152 | 09:00 | 131 | Niamatpur | 66 | 00:00
66 | Hasnabad | 78 | 00:00 | 132 | Noapara | 46 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14615.08 | 0 |  | 14615.08
1:00 | 14010.98 | 0 |  | 14010.98
2:00 | 13619.71 | 0 |  | 13619.71
3:00 | 13132.92 | 0 |  | 13132.92
4:00 | 12657.63 | 0 |  | 12657.63
5:00 | 11876.99 | 0 |  | 11876.99
6:00 | 11641.04 | 0 |  | 11641.04
7:00 | 11686.54 | 0 |  | 11686.54
8:00 | 11755.43 | 0 |  | 11755.43
9:00 | 12071.77 | 0 |  | 12071.77
10:00 | 12334.78 | 0 |  | 12334.78
11:00 | 12687.03 | 0 |  | 12687.03
12:00 | 13182.89 | 0 |  | 13182.89
13:00 | 13585.01 | 0 |  | 13585.01
14:00 | 13526.05 | 0 |  | 13526.05
15:00 | 13566.72 | 0 |  | 13566.72
16:00 | 13365.33 | 0 |  | 13365.33
17:00 | 13126.98 | 0 |  | 13126.98
18:00 | 12974.23 | 0 |  | 12974.23
19:00 | 14490.3 | 0 |  | 14490.3
19:30 | 15107.95 | 0 |  | 15107.95
20:00 | 14981.61 | 0 |  | 14981.61
21:00 | 14886 | 0 |  | 14886
22:00 | 14674 | 0 |  | 14674
23:00 | 14452 | 0 |  | 14452
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7567.2 | 7047.88 | 14615.08 | DAILY GENERATION CURVE
00:30 | 7418.8 | 6894.23 | 14313.03
01:00 | 7270.4 | 6740.58 | 14010.98 | 04-08-2025
01:30 | 7205.6 | 6609.745 | 13815.345
02:00 | 7140.8 | 6478.91 | 13619.71
02:30 | 7006.3 | 6370.015 | 13376.315
03:00 | 6871.8 | 6261.12 | 13132.92
03:30 | 6808.15 | 6087.125 | 12895.275
04:00 | 6744.5 | 5913.13 | 12657.63
04:30 | 6618.65 | 5648.66 | 12267.31
05:00 | 6492.8 | 5384.19 | 11876.99
05:30 | 6400.98 | 5358.035 | 11759.015
06:00 | 6309.16 | 5331.88 | 11641.04
06:30 | 6291.215 | 5372.575 | 11663.79
07:00 | 6273.27 | 5413.27 | 11686.54
07:30 | 6254.965 | 5466.02 | 11720.985
08:00 | 6236.66 | 5518.77 | 11755.43
08:30 | 6290.235 | 5623.365 | 11913.6
09:00 | 6343.81 | 5727.96 | 12071.77
09:30 | 6433.285 | 5769.99 | 12203.275
10:00 | 6522.76 | 5812.02 | 12334.78
10:30 | 6579.115 | 5931.79 | 12510.905
11:00 | 6635.47 | 6051.56 | 12687.03
11:30 | 6732.785 | 6202.175 | 12934.96
12:00 | 6830.1 | 6352.79 | 13182.89
12:30 | 6884.645 | 6499.305 | 13383.95
13:00 | 6939.19 | 6645.82 | 13585.01
13:30 | 6923.295 | 6632.235 | 13555.53
14:00 | 6907.4 | 6618.65 | 13526.05
14:30 | 6988.73 | 6557.655 | 13546.385
15:00 | 7070.06 | 6496.66 | 13566.72
15:30 | 7055.42 | 6410.605 | 13466.025
16:00 | 7040.78 | 6324.55 | 13365.33
16:30 | 6959.33 | 6286.825 | 13246.155
17:00 | 6877.88 | 6249.1 | 13126.98
17:30 | 6870.955 | 6179.65 | 13050.605
18:00 | 6864.03 | 6110.2 | 12974.23
18:30 | 7247.765 | 6484.5 | 13732.265
19:00 | 7631.5 | 6858.8 | 14490.3
19:30 | 7906.7 | 7201.25 | 15107.95
20:00 | 7768 | 7213.61 | 14981.61
20:30 | 7706.5 | 7227.305 | 14933.805 |  | Executive Engineer
21:00 | 7645 | 7241 | 14886 |  | Network Operation Division
21:30 | 7596.5 | 7183.5 | 14780
22:00 | 7548 | 7126 | 14674
22:30 | 7495.5 | 7067.5 | 14563
23:00 | 7443 | 7009 | 14452

## En-Curve
QF-LDC-12
Date | 04-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3920 | 1859.5 | 886 | 38 | 42 | 1352.88 | 219 | 4834 | 0 | 377 | 1073.7 | 0 | 0 | 13 | 0 | DAILY ENERGY CURVE
00:30 | 3839.5 | 1858 | 883 | 38 | 41 | 1330.23 | 219 | 4756 | 0 | 344 | 990.3 | 0 | 0 | 14 | 0 | 04-08-2025
01:00 | 3759 | 1856.5 | 880 | 38 | 40 | 1307.58 | 219 | 4678 | 0 | 311 | 906.9 | 0 | 0 | 15 | 0
01:30 | 3779 | 1864.5 | 880 | 38 | 39 | 1256.745 | 219 | 4582.5 | 0 | 285 | 858.1 | 0 | 0 | 13.5 | 0 | Energy Generated | 322.7896 |  | MKWHr
02:00 | 3799 | 1872.5 | 880 | 38 | 38 | 1205.91 | 219 | 4487 | 0 | 259 | 809.3 | 0 | 0 | 12 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3803.5 | 1870 | 880.5 | 38 | 38 | 1156.515 | 219 | 4372.5 | 0 | 214 | 773.3 | 0 | 0 | 11 | 0 | Total Energy Requirement | 322.7896 |  | MKWHr
03:00 | 3808 | 1867.5 | 881 | 38 | 38 | 1107.12 | 219 | 4258 | 0 | 169 | 737.3 | 0 | 0 | 10 | 0
03:30 | 3806 | 1840.5 | 881 | 38 | 38 | 1055.125 | 219 | 4167.5 | 0 | 152.5 | 687.15 | 0 | 0 | 10.5 | 0
04:00 | 3804 | 1813.5 | 881 | 38 | 38 | 1003.13 | 219 | 4077 | 0 | 136 | 637 | 0 | 0 | 11 | 0
04:30 | 3802 | 1728 | 881.5 | 38 | 38 | 933.16 | 219.5 | 3893 | 0 | 114 | 610.15 | 0 | 0 | 10 | 0
05:00 | 3800 | 1642.5 | 882 | 38 | 38 | 863.19 | 220 | 3709 | 0 | 92 | 583.3 | 0 | 0 | 9 | 0
05:30 | 3727.5 | 1634.5 | 881.5 | 38 | 37 | 865.32 | 220 | 3670.5 | 3.545 | 92 | 575.65 | 0 | 0 | 13.5 | 0
06:00 | 3655 | 1626.5 | 881 | 38 | 36 | 867.45 | 220 | 3632 | 7.09 | 92 | 568 | 0 | 0 | 18 | 0
06:30 | 3636 | 1625.25 | 881 | 38 | 35 | 870.1 | 220 | 3640 | 28.44 | 92 | 584.5 | 0 | 0 | 13.5 | 0
07:00 | 3617 | 1624 | 881 | 38 | 34 | 872.75 | 220 | 3648 | 49.79 | 92 | 601 | 0 | 0 | 9 | 0
07:30 | 3625 | 1615.5 | 881 | 38 | 32 | 872.88 | 219.5 | 3654 | 77.105 | 84 | 616 | 0 | 0 | 6 | 0
08:00 | 3633 | 1607 | 881 | 38 | 30 | 873.01 | 219 | 3660 | 104.42 | 76 | 631 | 0 | 0 | 3 | 0
08:30 | 3677 | 1624.75 | 885 | 38 | 29 | 891.275 | 218.5 | 3676 | 137.575 | 71.5 | 661.5 | 0 | 0 | 3.5 | 0
09:00 | 3721 | 1642.5 | 889 | 38 | 28 | 909.54 | 218 | 3692 | 170.73 | 67 | 692 | 0 | 0 | 4 | 0
09:30 | 3743.5 | 1699 | 889 | 38 | 23 | 909.995 | 218 | 3700 | 188.78 | 75 | 709.5 | 0 | 0 | 9.5 | 0
10:00 | 3766 | 1755.5 | 889 | 38 | 18 | 910.45 | 218 | 3708 | 206.83 | 83 | 727 | 0 | 0 | 15 | 0
10:30 | 3809 | 1754 | 889.5 | 38 | 17 | 944.305 | 217.5 | 3810 | 198.6 | 87.5 | 729 | 0 | 0 | 16.5 | 0
11:00 | 3852 | 1752.5 | 890 | 38 | 16 | 978.16 | 217 | 3912 | 190.37 | 92 | 731 | 0 | 0 | 18 | 0
11:30 | 3845.5 | 1786.5 | 890 | 38 | 21 | 989.915 | 217.5 | 4068 | 190.045 | 105 | 763 | 0 | 0 | 20.5 | 0
12:00 | 3839 | 1820.5 | 890 | 38 | 26 | 1001.67 | 218 | 4224 | 189.72 | 118 | 795 | 0 | 0 | 23 | 0
12:30 | 3797.5 | 1782 | 894.5 | 38 | 26 | 1003.88 | 218 | 4386.5 | 202.07 | 126.5 | 882 | 0 | 0 | 27 | 0
13:00 | 3756 | 1743.5 | 899 | 38 | 26 | 1006.09 | 218 | 4549 | 214.42 | 135 | 969 | 0 | 0 | 31 | 0
13:30 | 3683.5 | 1746.35 | 899.5 | 38 | 25 | 1014.675 | 218.5 | 4546.5 | 242.505 | 135 | 979.5 | 0 | 0 | 26.5 | 0
14:00 | 3611 | 1749.2 | 900 | 38 | 24 | 1023.26 | 219 | 4544 | 270.59 | 135 | 990 | 0 | 0 | 22 | 0
14:30 | 3642 | 1755.7 | 891.5 | 38 | 20 | 1013.955 | 219 | 4560 | 213.23 | 150 | 1021 | 0 | 0 | 22 | 0
15:00 | 3673 | 1762.2 | 883 | 38 | 16 | 1004.65 | 219 | 4576 | 155.87 | 165 | 1052 | 0 | 0 | 22 | 0
15:30 | 3613.5 | 1803.2 | 882.5 | 38 | 26 | 1008.63 | 220 | 4513 | 142.695 | 178.5 | 1022.5 | 0 | 0 | 17.5 | 0
16:00 | 3554 | 1844.2 | 882 | 38 | 36 | 1012.61 | 221 | 4450 | 129.52 | 192 | 993 | 0 | 0 | 13 | 0
16:30 | 3595.5 | 1828.85 | 882.5 | 38 | 28 | 1010.75 | 221 | 4393.5 | 96.055 | 187.5 | 950.5 | 0 | 0 | 14 | 0
17:00 | 3637 | 1813.5 | 883 | 38 | 20 | 1008.89 | 221 | 4337 | 62.59 | 183 | 908 | 0 | 0 | 15 | 0
17:30 | 3694 | 1730.5 | 882.5 | 38 | 21 | 1059.675 | 219 | 4245.5 | 39.43 | 186 | 922 | 0 | 0 | 13 | 0
18:00 | 3751 | 1647.5 | 882 | 38 | 22 | 1110.46 | 217 | 4154 | 16.27 | 189 | 936 | 0 | 0 | 11 | 0
18:30 | 3831 | 1668 | 882.5 | 38 | 24 | 1217.63 | 217 | 4355 | 8.135 | 328.5 | 1154 | 0 | 0 | 8.5 | 0
19:00 | 3911 | 1688.5 | 883 | 38 | 26 | 1324.8 | 217 | 4556 | 0 | 468 | 1372 | 0 | 0 | 6 | 0
19:30 | 3830 | 1726.5 | 883 | 38 | 26 | 1417.25 | 216 | 4790 | 0 | 518 | 1660.2 | 0 | 0 | 3 | 0
20:00 | 3837 | 1736 | 882 | 38 | 24 | 1411.61 | 212 | 4814 | 0 | 504 | 1520 | 0 | 0 | 3 | 0
20:30 | 3847 | 1752.5 | 882.5 | 38 | 25 | 1411.805 | 212 | 4803.5 | 0 | 497 | 1462.5 | 0 | 0 | 2 | 0
21:00 | 3857 | 1769 | 883 | 38 | 26 | 1412 | 212 | 4793 | 0 | 490 | 1405 | 0 | 0 | 1 | 0
21:30 | 3874 | 1751 | 883 | 38 | 34 | 1413 | 210.5 | 4811 | 0 | 438.5 | 1326.5 | 0 | 0 | 0.5 | 0
22:00 | 3891 | 1733 | 883 | 38 | 42 | 1414 | 209 | 4829 | 0 | 387 | 1248 | 0 | 0 | 0 | 0
22:30 | 3920 | 1731 | 889.5 | 38 | 43 | 1364 | 208.5 | 4802 | 0 | 387.5 | 1176.5 | 0 | 0 | 3 | 0
23:00 | 3949 | 1729 | 896 | 38 | 44 | 1314 | 208 | 4775 | 0 | 388 | 1105 | 0 | 0 | 6 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 06:00 | 339 | 19:00 | Payra | 418 | 06:00 | 410 | 23:00
Ashuganj | 406 | 4:00 | 378 | 12:00 | Rahanpur | 402 | 06:00 | 387 | 19:30
Bhulta | 404 | 04:00 | 373 | 11:00 | Rampal | 411 | 06:00 | 394 | 00:00
Bibiana | 389 | 06:00 | 380 | 12:00
BIPTC | 401 | 06:00 | 395 | 00:00
Bogura | 385 | 06:00 | 366 | 21:00
Gopalganj | 405 | 06:00 | 388 | 00:00
Kaliakoir | 380 | 05:00 | 363 | 14:00
Madunaghat | 394 | 07:00 | 385 | 00:00
Meghnaghat | 395 | 06:00 | 378 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 217 | 12:00 | Keranigonj | 227 | 05:00 | 215 | 00:00
AKSML | 232 | 19:30 | 223 | 00:00 | Khulna(S) | 236 | 06:00 | 221 | 00:00
Aminbazar | 230 | 05:00 | 218 | 12:00 | Madunaghat | 231 | 07:00 | 228 | 00:00
Ashuganj | 234 | 03:00 | 222 | 13:00 | Madunaghat-400 | 233 | 07:00 | 226 | 00:00
Ashuganj-400 | 234 | 03:00 | 222 | 13:00 | Maniknagar | 223 | 06:00 | 212 | 12:00
Baghabari | 236 | 06:00 | 227 | 21:00 | Meghnaghat | 231 | 08:00 | 221 | 13:00
Barapukuria | 225 | 15:00 | 219 | 19:30 | Meghnaghat-400 | 228 | 05:00 | 218 | 00:00
Barapukuria-230 | 225 | 15:00 | 219 | 19:30 | Mirsorai | 228 | 07:00 | 221 | 18:30
Barishal | 231 | 06:00 | 220 | 23:00 | Rajshahi | 233 | 05:00 | 219 | 21:00
Bheramara | 233 | 04:00 | 223 | 21:00 | Rampal | 234 | 05:00 | 220 | 00:00
Bhulta | 233 | 04:00 | 212 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 06:00 | 222 | 14:00 | Rampura | 231 | 04:00 | 211 | 11:00
BIPTC | 237 | 06:00 | 224 | 00:00 | Shikalbaha | 230 | 06:00 | 224 | 00:00
Bogura | 237 | 06:00 | 228 | 19:30 | Shyampur | 227 | 05:00 | 215 | 00:00
Bogura-400 | 238 | 06:00 | 228 | 21:00 | Siddhirganj | 222 | 02:00 | 216 | 00:00
Borhanuddin | 235 | 08:00 | 228 | 00:00 | Sirajgonj | 241 | 05:00 | 234 | 12:00
BSRM | 228 | 07:00 | 220 | 00:00 | Sreepur | 229 | 04:00 | 220 | 12:00
Cumilla(N) | 226 | 07:00 | 216 | 00:00 | Tongi | 226 | 07:00 | 215 | 12:00
Faridpur | 231 | 06:00 | 217 | 00:00
Fenchuganj | 231 | 09:00 | 223 | 00:00
Ghorashal | 235 | 01:00 | 220 | 18:30
Ghorashal-230 | 230 | 04:00 | 213 | 12:00
Gopalganj | 231 | 06:00 | 219 | 00:00
GPH | 230 | 07:00 | 223 | 00:00
Haripur | 226 | 06:00 | 214 | 12:00
Hasnabad | 222 | 09:00 | 215 | 12:00
Hathazari | 229 | 04:00 | 221 | 12:00
Ishurdi | 237 | 06:00 | 225 | 22:00
Jhenaidah | 234 | 06:00 | 219 | 00:00
Kaliakoir | 234 | 05:00 | 221 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 04:00 | 123 | 11:00 | Lalmonirhat | 128 | 00:00 | 123 | 16:00
Agargaon | 135 | 06:00 | 126 | 12:00 | Madanganj | 132 | 04:00 | 123 | 12:00
Agrabad | 131 | 06:00 | 126 | 13:00 | Madaripur | 135 | 05:00 | 129 | 00:00
AKS | 128 | 07:00 | 125 | 12:00 | Madartek | 139 | 04:00 | 124 | 11:00
Aminbazar | 135 | 05:00 | 128 | 00:00 | Madunaghat | 132 | 06:00 | 128 | 00:00
Amnura | 136 | 05:00 | 128 | 00:00 | Magura | 138 | 06:00 | 126 | 00:00
Ashuganj | 143 | 07:00 | 136 | 12:00 | Mahasthangarh | 137 | 06:00 | 128 | 21:00
Bagerhat | 135 | 05:00 | 120 | 23:00 | Maijdee | 124 | 07:00 | 113 | 01:00
Bajitpur | 133 | 05:00 | 126 | 23:00 | Manikganj | 130 | 04:00 | 121 | 11:00
Bakulia | 132 | 07:00 | 128 | 00:00 | Maniknagar | 136 | 05:00 | 127 | 12:00
Banani | 139 | 03:00 | 125 | 11:00 | Matarbari | 117 | 08:00 | 109 | 00:00
Bangabhaban | 136 | 05:00 | 127 | 12:00 | Matuail | 132 | 05:00 | 124 | 12:00
Barapukuria | 137 | 18:30 | 128 | 07:00 | Millgate | 134 | 03:00 | 124 | 11:00
Barguna | 134 | 06:00 | 129 | 00:00 | Mirpur | 133 | 05:00 | 126 | 00:00
Barishal | 135 | 07:00 | 126 | 00:00 | Mirzapur | 132 | 08:00 | 124 | 12:00
Barishal-230 | 136 | 07:00 | 127 | 00:00 | Mithapukur | 131 | 16:00 | 119 | 21:00
Baroaulia | 130 | 04:00 | 127 | 12:00 | MI_Cement | 132.4 | 05:00 | 124 | 12:00
Baroirhat | 125 | 07:00 | 119 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 140 | 04:00 | 123 | 15:00 | Mogbazar | 140 | 05:00 | 125 | 11:00
BashundharaCement | 132 | 04:00 | 123 | 12:00 | Mongla | 136 | 08:00 | 123 | 00:00
Beanibazar | 130 | 08:00 | 120 | 00:00 | Motijheel | 136 | 05:00 | 127 | 12:00
Benapole | 135 | 06:00 | 121 | 00:00 | Muktagacha | 136 | 08:00 | 132 | 14:00
Bhaluka | 131 | 05:00 | 124 | 12:00 | Munshiganj | 131 | 06:00 | 123 | 12:00
Bhandaria | 130 | 06:00 | 118 | 00:00 | Muradnagar | 127 | 06:00 | 119 | 00:00
Bhangura | 135 | 06:00 | 129 | 21:00 | Mymensingh | 138 | 08:00 | 120 | 11:00
Bheramara | 137 | 04:00 | 133 | 00:00 | Naogaon | 135 | 08:00 | 126 | 00:00
Bheramara(GK) | 137 | 05:00 | 132 | 21:00 | Narail | 138 | 05:00 | 126 | 00:00
Bhulta | 124 | 06:00 | 117 | 02:00 | Narinda | 136 | 05:00 | 127 | 12:00
Bog-Sherpur | 137 | 06:00 | 129 | 21:00 | Narshingdi | 137 | 05:00 | 120 | 00:00
Bogura | 140 | 06:00 | 132 | 00:00 | Natore | 135 | 08:00 | 128 | 19:30
Bogura-230 | 140 | 06:00 | 133 | 00:00 | Nawabganj | 136 | 06:00 | 127 | 00:00
Brahmanbaria | 139 | 07:00 | 130 | 00:00 | Netrakona | 126 | 17:00 | 118 | 14:00
Cantonment | 134 | 05:00 | 125 | 12:00 | New | 134 | 05:00 | 125 | 11:00
Chandina | 130 | 07:00 | 122 | 13:00 | Niamatpur | 137 | 05:00 | 130 | 19:30
Chandpur | 133 | 07:00 | 122 | 00:00 | Noapara | 138 | 08:00 | 125 | 00:00
Chandraghona | 133 | 07:00 | 129 | 00:00 | Pabna | 135 | 06:00 | 129 | 22:00
Chapai | 136 | 07:00 | 131 | 00:00 | Palashbari | 129 | 06:00 | 116 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 04:00 | 124 | 12:00 | Panchagarh | 132 | 00:00 | 121 | 07:00
Chauddagram | 126 | 07:00 | 118 | 00:00 | Patuakhali | 135 | 04:00 | 131 | 19:00
Chhatak | 129 | 06:00 | 116 | 00:00 | Payra | 137 | 06:00 | 134 | 00:00
Chowmuhani | 125 | 08:00 | 113 | 00:00 | PHP | 125 | 08:00 | 117 | 13:00
Chuadanga | 136 | 06:00 | 124 | 23:00 | Postogola | 134 | 06:00 | 126 | 12:00
Coxsbazar | 118 | 07:00 | 110 | 00:00 | Purbachal | 140 | 03:00 | 124 | 11:00
Cumilla(N) | 129 | 07:00 | 122 | 00:00 | Purbasadipur | 130 | 00:00 | 122 | 07:00
Cumilla(S) | 133 | 05:00 | 121 | 00:00 | Rahanpur | 138 | 06:00 | 132 | 21:00
Daganbhuiyan | 125 | 08:00 | 114 | 13:00 | Rahanpur-400 | 138 | 06:00 | 133 | 00:00
Daudkandi | 125 | 06:00 | 116 | 12:00 | Rahim | 132 | 06:00 | 123 | 12:00
Dhaka | 140 | 04:00 | 124 | 11:00 | Rajbari | 136 | 06:00 | 126 | 00:00
Dhamrai | 133 | 05:00 | 125 | 11:00 | Rajendrapur | 132 | 06:00 | 120 | 12:00
Dhanmondi | 140 | 04:00 | 124 | 11:00 | Rajshahi | 134 | 05:00 | 126 | 21:00
Dohazari | 127 | 07:00 | 121 | 00:00 | Rajshahi-230 | 134 | 05:00 | 127 | 00:00
Faridpur | 136 | 05:00 | 128 | 23:00 | Ramganj | 126 | 08:00 | 117 | 23:00
Fatullah | 134 | 06:00 | 125 | 12:00 | Rampur | 131 | 07:00 | 126 | 12:00
Fenchuganj | 136 | 07:00 | 130 | 00:00 | Rampura | 140 | 04:00 | 124 | 11:00
Feni | 123 | 07:00 | 114 | 13:00 | Rangamati | 131 | 06:00 | 128 | 00:00
Ghatail | 132 | 08:00 | 125 | 19:00 | Rangpur | 132 | 19:00 | 126 | 07:00
Ghorashal | 137 | 01:00 | 128 | 12:00 | Ruppur | 137 | 04:00 | 132 | 00:00
Goalpara | 140 | 08:00 | 128 | 00:00 | Saidpur | 132 | 18:30 | 124 | 03:00
Gollamari | 139 | 05:00 | 129 | 00:00 | Satkhira | 136 | 04:00 | 122 | 00:00
Gopalganj | 138 | 06:00 | 128 | 00:00 | Satmasjid | 135 | 06:00 | 125 | 12:00
Gopalganj-400 | 139 | 06:00 | 131 | 00:00 | Savar | 132 | 05:00 | 125 | 11:00
Gulshan | 137 | 05:00 | 124 | 11:00 | SevenRings | 138 | 05:00 | 128 | 12:00
Halishahar | 132 | 06:00 | 126 | 12:00 | ShahCement | 132 | 04:00 | 124 | 12:00
Haripur | 132 | 05:00 | 124 | 12:00 | Shahjadpur | 138 | 05:00 | 133 | 22:00
HaripurSBU | 132 | 05:00 | 124 | 12:00 | Shahjibazar | 139 | 07:00 | 129 | 00:00
Hasnabad | 134 | 06:00 | 127 | 00:00 | Shahmirpur | 132 | 07:00 | 128 | 00:00
Hathazari | 133 | 04:00 | 128 | 12:00 | Shariatpur | 136 | 06:00 | 126 | 00:00
Ishurdi | 139 | 06:00 | 132 | 21:00 | Sherpur | 138 | 10:00 | 124 | 3:00
Jaldhaka | 130 | 18:30 | 119 | 07:00 | Shikalbaha | 122 | 06:00 | 117 | 00:00
Jamalpur | 139 | 15:00 | 134 | 14:00 | Shikalbaha-230 | 133 | 08:00 | 128 | 00:00
Jashore | 138 | 06:00 | 123 | 00:00 | Shitalakhya | 132.4 | 05:00 | 124 | 12:00
Jhenaidah | 138 | 04:00 | 123 | 00:00 | Sholosohor | 132 | 07:00 | 128 | 00:00
Jhenaidah-230 | 140 | 06:00 | 129 | 00:00 | Shyampur | 133 | 05:00 | 126 | 00:00
Joydebpur | 134 | 04:00 | 122 | 14:00 | Shyampur-230 | 133 | 05:00 | 126 | 00:00
Joypurhat | 133 | 08:00 | 124 | 00:00 | Siddhirganj | 131 | 07:00 | 124 | 12:00
Juldah | 132 | 07:00 | 128 | 0:00 | Sirajganj | 135 | 06:00 | 127 | 20:00
Kabirpur | 131 | 07:00 | 121 | 11:00 | Sonargaon | 129 | 08:00 | 122 | 00:00
Kachua | 129 | 07:00 | 120 | 00:00 | Sreemongol | 136 | 07:00 | 127 | 00:00
Kaliakoir | 136 | 06:00 | 127 | 14:00 | Sreepur | 133 | 06:00 | 127 | 11:00
Kallyanpur | 131 | 02:00 | 127 | 11:00 | Srinagar | 136 | 04:00 | 127 | 00:00
Kalurghat | 131 | 19:30 | 128 | 00:00 | SSM | 132 | 09:00 | 130 | 00:00
Kamrangirchar | 136 | 05:00 | 127 | 00:00 | Sunamganj | 128 | 09:00 | 117 | 00:00
Kaptai | 135 | 20:00 | 132 | 9:00 | Sylhet | 130 | 07:00 | 122 | 00:00
Kasba | 127 | 06:00 | 118 | 12:00 | Sylhet-132 | 131 | 05:00 | 122 | 00:00
Kazla | 135 | 05:00 | 126 | 13:00 | Tangail | 129 | 01:00 | 122 | 19:00
Keranigonj | 137 | 05:00 | 127 | 12:00 | Taraganj | 133 | 19:00 | 123 | 07:00
Khagrachori | 131 | 06:00 | 127 | 00:00 | Thakurgaon | 131 | 00:00 | 119 | 07:00
Khulna | 138 | 05:00 | 127 | 00:00 | TK | 132 | 07:00 | 128 | 00:00
Khulna(S) | 141 | 06:00 | 129 | 00:00 | Tongi | 135 | 07:00 | 127 | 12:00
Khulshi | 130 | 06:00 | 126 | 00:00 | Ullahpara | 136 | 05:00 | 129 | 19:30
Kishoreganj | 132 | 05:00 | 124 | 14:00 | Ullon | 140 | 04:00 | 124 | 11:00
Kodda | 132 | 19:30 | 120 | 12:00 | Uttara | 133 | 05:00 | 126 | 11:00
KSRM | 131 | 03:00 | 127 | 11:00 | UttaraNew | 133 | 05:00 | 126 | 12:00
Kulaura | 135 | 07:00 | 129 | 00:00 | Zigatola | 137 | 05:00 | 128 | 00:00
Kurigram | 131 | 20:00 | 121 | 07:00
Kushtia | 134 | 06:00 | 127 | 00:00
Laksam | 129 | 07:00 | 119 | 00:00
Lakshmipur | 125 | 07:00 | 114 | 00:00
Lalbag | 132 | 09:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division