## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-08-2025 | during | 08-08-2025 | during | 08-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 368 | 341 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450 | 450 | 450 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 298 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | 335 | machine problem
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 44 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 46 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28.2 | 26 | 33 | 33 | 25 | 25 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 34 | 52.19 | 52.19 | 25.01 | 25.01 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 86 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 51 | 135 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 385 | 330 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 70 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2178.2 | 2325 | 5822.9 | 5794.9 | 3341.79 | 3313.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 205 | 204 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 36 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 31 | 80 | 80 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 37 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 25 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.25 | 0 | 1.13 | 0 | 1.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 20 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 38 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 7 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 830 | 585 | 1224 | 1224 | 809 | 1006 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 8 | 26 | 18 | 26 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 770 | 780 | 775 | 775 | 775 | 775 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1913.25 | 1922 | 3622.85 | 3626.72 | 3033.85 | 3275.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 215 | 0 | 221 | 0 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 347 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 36 | 46.7 | 46.7 | 40 | 40 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 103 | 16 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 80 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 44 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 150 | 164 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 19 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 70 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 53 | 63 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 65 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 33 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1534 | 1667 | 2203.56 | 2379.56 | 2006.36 | 2166.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-08-2025 | during | 08-08-2025 | during | 08-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 142 | 130 | 157.5 | 157.5 | 140 | 140 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 170 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 85 | 93 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 20.18 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 5 | 54.5 | 54.5 | 18 | 18 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 313.18 | 398 | 585.2 | 549 | 476.4 | 440.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 60 | 60 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 83 | 83 | 80 | 80 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 6 | 6 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 240 | 341 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 272 | 246 | 265 | 265 | 265 | 265 | ST shutdown due to maitenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 280 | 290 | 270 | 270 | 270 | 270 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1067 | 1187 | 1255 | 1255 | 1123 | 1123
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 910 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 392 | 375 | 410 | 410 | 380 | 380 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 10 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 27.04 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 856 | 1150 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2223.04 | 2483 | 3586.2 | 3546.2 | 3414.2 | 3374.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 305 | 298 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 946 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 175 | 270 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1766.24 | 2088 | 2162 | 2161 | 2162 | 2161
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 46.98 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 187 | 193 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 196 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 195 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 390 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 27 | 27 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 25 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.47 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1044 | 1304 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 17.35 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 47 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2109.8 | 2303 | 3171.47 | 3022.87 | 3066.69 | 2918.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 172 | 174 | 170 | 170 | 170 | 173 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 110 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 111.05 | 0 | 111.05 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 422.7 | 379 | 579.65 | 432 | 559.65 | 415
System Total |  |  |  |  | 28671.2 | 27843.665 | 13527.41 | 14752 | 22988.83 | 22767.25 | 19183.94 | 19187.36
Forecast Scenario (08-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14280 |  | 0 |  | 14280
|  |  |  | 1:00 | 13860 |  | 0 |  | 13860
|  |  |  | 2:00 | 13430 |  | 0 |  | 13430
|  |  |  | 3:00 | 13080 |  | 0 |  | 13080
|  |  |  | 4:00 | 12790 |  | 0 |  | 12790
|  |  |  | 5:00 | 12430 |  | 0 |  | 12430
|  |  |  | 6:00 | 11720 |  | 0 |  | 11720
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11280 |  | 0 |  | 11280
|  |  |  | 9:00 | 11050 |  | 0 |  | 11050
|  |  |  | 10:00 | 11030 |  | 0 |  | 11030
|  |  |  | 11:00 | 11140 |  | 0 |  | 11140
|  |  |  | 12:00 | 11760 |  | 0 |  | 11760
|  |  |  | 13:00 | 12390 |  | 0 |  | 12390
|  |  |  | 14:00 | 11910 |  | 0 |  | 11910
|  |  |  | 15:00 | 11610 |  | 0 |  | 11610
|  |  |  | 16:00 | 11390 |  | 0 |  | 11390
|  |  |  | 17:00 | 11020 |  | 0 |  | 11020
|  |  |  | 18:00 | 10930 |  | 0 |  | 10930
|  |  |  | 18:30 | 11700 |  | 0 |  | 11700
|  |  |  | 19:00 | 12850 |  | 0 |  | 12850
|  |  |  | 19:30 | 13670 |  | 0 |  | 13670
|  |  |  | 20:00 | 13490 |  | 0 |  | 13490
|  |  |  | 21:00 | 13720 |  | 0 |  | 13720
|  |  |  | 22:00 | 13780 |  | 0 |  | 13780
|  |  |  | 23:00 | 13860 |  | 0 |  | 13860
Probable Maximum Temperature: |  |  | 30.30°C
Probable Maximum Demand at Day Peak: |  |  | 12060.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14020.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13720.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 296.20 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:15 hrs on 08-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-08-2025 | [28 empty] | Date: | 07-08-2025 | [28 empty] | Date: | 07-08-2025 | [28 empty] | Date: | 07-08-2025 | [28 empty] | Date: | 07-08-2025 | [12 empty] | Date: | 07-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 0 | 350 | 294 | 360 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 66 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 30 | 741 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 61 | 0 | 355 | 330 | 51 | 192 | 37 | 84 | 70 | 177 | 57 | 19 | 60 | 42 | 0 | 0 | 37 | 175 | 280 | 365 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 94 | 150 | 155 | 0 | 0 | 5 | 7213 | 903 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 188 | 0 | 187 | 0 | 414 | 0 | 0 | 166 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 305 | 1110 | 0 | 7298.6 | 14511.6 | 108.79
01:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 291 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 66 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 37 | 740 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 51 | 0 | 61 | 0 | 354 | 330 | 48 | 187 | 37 | 80 | 70 | 170 | 58 | 19 | 62 | 40 | 0 | 0 | 37 | 175 | 280 | 352 | 0 | 0 | 151 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 95 | 95 | 154 | 0 | 0 | 5 | 7079 | 903 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 1305.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 184 | 0 | 183 | 0 | 400 | 0 | 0 | 168 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 120 | 220 | 0 | 305 | 1100 | 0 | 7069.48 | 14148.48 | 108.79
02:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 298 | 364 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 25.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 38 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 63 | 0 | 354 | 330 | 48 | 199 | 37 | 81 | 70 | 170 | 63 | 19 | 62 | 38 | 0 | 0 | 37 | 175 | 280 | 367 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 95 | 95 | 154 | 0 | 0 | 5 | 6939.9 | 903 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1021 | 0 | 1220.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 186 | 0 | 184 | 0 | 358 | 0 | 0 | 169 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 305 | 1100 | 0 | 6771.29 | 13711.19 | 108.79
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 293 | 367 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 33 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 38 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 51 | 0 | 63 | 0 | 354 | 330 | 47 | 200 | 37 | 82 | 50 | 174 | 58 | 19 | 46 | 38 | 0 | 0 | 37 | 175 | 280 | 378 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 95 | 45 | 154 | 0 | 0 | 5 | 6790 | 903 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 919 | 0 | 1139.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 188 | 0 | 186 | 0 | 352 | 0 | 0 | 170 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 120 | 220 | 0 | 304 | 1110 | 0 | 6537.2 | 13327.2 | 108.79
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 292 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 38 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 0 | 51 | 0 | 63 | 0 | 353 | 330 | 48 | 198 | 37 | 83 | 50 | 175 | 63 | 19 | 0 | 36 | 0 | 0 | 37 | 175 | 280 | 361 | 0 | 0 | 155 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 45 | 154 | 0 | 0 | 5 | 6696 | 903 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 825 | 0 | 1126.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 188 | 0 | 187 | 0 | 350 | 0 | 0 | 170 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 304 | 1050 | 0 | 6368.71 | 13064.71 | 108.79
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 296 | 360 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 206 | 0 | 38 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 835 | 0 | 51 | 0 | 63 | 0 | 355 | 330 | 48 | 197 | 36 | 81 | 50 | 173 | 64 | 19 | 0 | 36 | 0 | 0 | 37 | 175 | 280 | 195 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 45 | 154 | 0 | 0 | 5 | 6508 | 903 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 798 | 0 | 1124.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 187 | 0 | 186 | 0 | 349 | 0 | 0 | 169 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 305 | 1045 | 0 | 6318.86 | 12826.86 | 108.79
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 365 | 0 | 0 | 290 | 0 | 0 | 1 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 205 | 0 | 40 | 649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 0 | 51 | 0 | 63 | 0 | 320 | 330 | 47 | 206 | 36 | 50 | 50 | 172 | 63 | 9 | 0 | 32 | 0 | 0 | 37 | 175 | 270 | 215 | 0 | 0 | 149 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 45 | 154 | 0 | 0.28 | 5 | 6330.28 | 903 | 387 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.54 | 796 | 0 | 1023.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 1 | 0 | 0.3 | 184 | 0 | 183 | 0 | 182 | 0 | 375 | 0 | 0 | 168 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 173 | 120 | 220 | 0 | 305 | 800 | 0 | 5969.35 | 12299.63 | 108.79
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 370 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | 0 | 0 | 12 | 12 | 0 | 205 | 0 | 36 | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 1 | 51 | 0 | 63 | 0 | 320 | 330 | 46 | 203 | 37 | 16 | 50 | 183 | 63 | 16 | 0 | 32 | 0 | 1 | 37 | 175 | 280 | 285 | 0 | 0 | 144 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 45 | 154 | 0 | 4.18 | 5 | 6352.18 | 903 | 387 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.51 | 817 | 0 | 1027.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.99 | 11 | 0 | 2.45 | 164 | 0 | 174 | 0 | 173 | 0 | 377 | 0 | 0.28 | 169 | 0 | 35 | 3 | 70 | 0 | 0 | 0.6 | 17 | 0.03 | 0 | 173 | 120 | 220 | 0 | 305 | 801 | 0 | 5998.65 | 12350.83 | 108.79
08:00 | 0 | 2 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 6 | 0 | 0 | 350 | 298 | 370 | 0 | 0 | 280 | 0 | 0 | 14 | 17 | 23.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | 0 | 0 | 12 | 12 | 0 | 204 | 0 | 15 | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 3 | 51 | 0 | 61 | 0 | 320 | 330 | 45 | 198 | 37 | 16 | 70 | 183 | 64 | 19 | 0 | 32 | 0 | 8 | 37 | 175 | 280 | 273 | 0 | 0 | 142 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 86 | 45 | 151 | 0 | 8.8 | 5 | 6403.3 | 903 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 813 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.07 | 27 | 0 | 5.44 | 163 | 0 | 173 | 0 | 172 | 0 | 358 | 0 | 0.59 | 170 | 0 | 35 | 7 | 70 | 0 | 0 | 1 | 59 | 0.01 | 0 | 173 | 120 | 220 | 0 | 305 | 801 | 0 | 6029.11 | 12432.41 | 108.79
09:00 | 0 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 52 | 15 | 0 | 0 | 20 | 0 | 0 | 350 | 295 | 370 | 0 | 0 | 280 | 0 | 0 | 22 | 17 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 12 | 12 | 0 | 213 | 0 | 7 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 833 | 7 | 51 | 0 | 63 | 0 | 320 | 330 | 47 | 196 | 38 | 16 | 70 | 179 | 63 | 19 | 0 | 32 | 0 | 4 | 37 | 175 | 275 | 258 | 0 | 0 | 139 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 85 | 75 | 153 | 0 | 4.47 | 5 | 6471.97 | 903 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 806 | 0 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.98 | 40 | 0 | 15.94 | 160 | 0 | 171 | 0 | 169 | 0 | 351 | 0 | 1.48 | 171 | 0 | 35 | 16 | 70 | 0 | 0 | 1.1 | 60 | 0 | 0 | 172 | 120 | 220 | 0 | 305 | 802 | 0 | 6066.5 | 12538.47 | 108.8
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 85 | 15 | 0 | 0 | 35 | 0 | 0 | 350 | 298 | 375 | 0 | 0 | 310 | 0 | 0 | 24 | 17 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 36 | 0.55 | 213 | 0 | 6 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 13 | 51 | 0 | 63 | 0 | 320 | 330 | 47 | 200 | 38 | 15 | 70 | 177 | 63 | 19 | 0 | 34 | 0 | 30 | 37 | 175 | 280 | 268 | 0 | 0 | 139 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 78 | 65 | 153 | 0 | 10.09 | 0 | 6614.64 | 910 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.49 | 804 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.34 | 55 | 0 | 26.66 | 161 | 0 | 171 | 0 | 170 | 0 | 366 | 0 | 1.75 | 172 | 0 | 35 | 29 | 34 | 0 | 0 | 4.2 | 106 | 0.02 | 0 | 171 | 120 | 220 | 0 | 305 | 803 | 0 | 6163.46 | 12778.1 | 108.82
11:00 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 149 | 15 | 0 | 0 | 35 | 15 | 0 | 350 | 298 | 375 | 0 | 0 | 335 | 0 | 0 | 22 | 30 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 36 | 2.52 | 207 | 0 | 7 | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 12 | 51 | 0 | 73 | 0 | 352 | 330 | 47 | 198 | 38 | 16 | 50 | 155 | 55 | 19 | 17 | 34 | 0 | 41 | 37 | 190 | 280 | 268 | 0 | 0 | 139 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 76 | 65 | 143 | 1 | 16.18 | 0 | 6810.2 | 910 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46.6 | 804 | 0 | 963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.65 | 44 | 0 | 11.88 | 161 | 0 | 171 | 0 | 190 | 0 | 414 | 0 | 1.53 | 172 | 0 | 35 | 27 | 34 | 0 | 0 | 2.5 | 85 | 0.21 | 0 | 172 | 120 | 220 | 0 | 305 | 835 | 0 | 6163.37 | 12973.57 | 108.82
12:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 149 | 15 | 0 | 0 | 35 | 51 | 0 | 350 | 298 | 385 | 0 | 0 | 333 | 0 | 0 | 25 | 35 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 25 | 36 | 2.25 | 205 | 0 | 8 | 770 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 11 | 51 | 0 | 103 | 0 | 347 | 330 | 47 | 210 | 38 | 15 | 50 | 150 | 53 | 16 | 17 | 38 | 0 | 33 | 36 | 240 | 280 | 272 | 0 | 0 | 141 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 85 | 65 | 142 | 1 | 20.18 | 0 | 7005.63 | 910 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27.04 | 856 | 0 | 1044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.98 | 47 | 0 | 17.35 | 187 | 0 | 173 | 0 | 179 | 0 | 414 | 0 | 1.47 | 172 | 0 | 35 | 30 | 34 | 0 | 0 | 5.7 | 146 | 0.24 | 0 | 175 | 120 | 220 | 0 | 305 | 946 | 0 | 6521.78 | 13527.41 | 108.82
13:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 10 | 5 | 149 | 15 | 0 | 0 | 35 | 84 | 0 | 350 | 296 | 370 | 0 | 0 | 333 | 0 | 0 | 15 | 42 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 36 | 0.48 | 204 | 0 | 7 | 779 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 0 | 51 | 1 | 122 | 0 | 348 | 330 | 48 | 204 | 38 | 44 | 50 | 167 | 57 | 20 | 49 | 40 | 0 | 8 | 36 | 240 | 280 | 265 | 0 | 0 | 140 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 84 | 65 | 128 | 1 | 27.79 | 0 | 6994.27 | 910 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.62 | 1023 | 0 | 1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.05 | 72 | 0 | 17.48 | 176 | 0 | 191 | 0 | 171 | 0 | 372 | 0 | 2 | 171 | 0 | 35 | 21 | 34 | 0 | 0 | 1.8 | 140 | 0.17 | 0 | 202 | 120 | 220 | 0 | 305 | 1006 | 0 | 6700.12 | 13694.39 | 108.82
14:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 15.5 | 17 | 149 | 15 | 0 | 0 | 35 | 82 | 0 | 350 | 296 | 365 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 25 | 36 | 0.91 | 203 | 0 | 2 | 777 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 7 | 51 | 24 | 137 | 0 | 353 | 330 | 49 | 196 | 38 | 62 | 50 | 175 | 57 | 20 | 47 | 40 | 0 | 8 | 36 | 235 | 280 | 252 | 0 | 0 | 134 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 84 | 85 | 117 | 1 | 27.81 | 0 | 6935.22 | 910 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38.36 | 1042 | 0 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.81 | 90 | 0 | 12.35 | 171 | 0 | 170 | 0 | 167 | 0 | 350 | 0 | 1.45 | 168 | 0 | 35 | 20 | 34 | 0 | 0 | 2.6 | 151 | 0.18 | 0 | 199 | 120 | 180 | 0 | 305 | 1090 | 0 | 6673.75 | 13608.97 | 108.82
15:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 15.4 | 17 | 149 | 15 | 0 | 0 | 35 | 81 | 0 | 350 | 300 | 365 | 0 | 0 | 335 | 0 | 0 | 11 | 52 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 25 | 36 | 1.31 | 203 | 0 | 2 | 780 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 7 | 51 | 24 | 137 | 0 | 355 | 330 | 49 | 197 | 37 | 66 | 50 | 171 | 52 | 20 | 17 | 38 | 0 | 4 | 36 | 250 | 280 | 270 | 0 | 0 | 134 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 84 | 85 | 121 | 1 | 21.58 | 0 | 6943.29 | 910 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.19 | 1041 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.19 | 82 | 0 | 16.35 | 171 | 0 | 170 | 0 | 166 | 0 | 354 | 0 | 1.94 | 170 | 0 | 35 | 19 | 34 | 0 | 0 | 0.8 | 144 | 0.3 | 0 | 201 | 120 | 180 | 0 | 302 | 1080 | 0 | 6633.77 | 13577.06 | 108.83
16:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 149 | 15 | 0 | 0 | 35 | 78 | 0 | 350 | 300 | 365 | 0 | 0 | 332 | 0 | 0 | 3 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 0.84 | 203 | 0 | 3 | 780 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 4 | 51 | 0 | 137 | 0 | 356 | 330 | 47 | 202 | 35 | 48 | 70 | 155 | 47 | 19 | 17 | 38 | 0 | 8 | 44 | 280 | 280 | 268 | 0 | 0 | 134 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 84 | 85 | 122 | 1 | 11.04 | 0 | 6799.88 | 910 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11.29 | 1039 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 33 | 0 | 33.76 | 170 | 0 | 170 | 0 | 167 | 0 | 367 | 0 | 2.62 | 171 | 0 | 35 | 4 | 34 | 0 | 0 | 3.5 | 90 | 0.1 | 0 | 201 | 120 | 180 | 0 | 305 | 1080 | 0 | 6543 | 13342.88 | 108.83
17:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 149 | 15 | 0 | 0 | 35 | 35 | 0 | 350 | 298 | 320 | 0 | 0 | 332 | 0 | 0 | 1 | 66 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 25 | 0.48 | 204 | 0 | 12 | 715 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 1 | 51 | 0 | 85 | 0 | 355 | 300 | 47 | 187 | 39 | 29 | 70 | 134 | 49 | 19 | 17 | 36 | 0 | 7 | 36 | 310 | 280 | 261 | 0 | 0 | 132 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 93 | 85 | 122 | 0 | 9.01 | 0 | 6559.49 | 910 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.44 | 972 | 0 | 1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 11 | 0 | 12.28 | 168 | 0 | 170 | 0 | 163 | 0 | 356 | 0 | 1.06 | 173 | 0 | 35 | 6 | 34 | 0 | 0 | 1.2 | 28 | 0.03 | 0 | 201 | 120 | 180 | 0 | 305 | 998 | 0 | 6274.81 | 12834.3 | 108.83
18:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 94 | 15 | 0 | 0 | 17 | 17 | 0 | 350 | 306 | 340 | 0 | 0 | 329 | 0 | 0 | 1 | 35 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 25 | 0.18 | 204 | 0 | 10 | 717 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 51 | 0 | 50 | 0 | 349 | 330 | 48 | 176 | 39 | 31 | 50 | 120 | 53 | 19 | 17 | 36 | 0 | 1 | 44 | 320 | 280 | 265 | 0 | 20 | 138 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 85 | 122 | 0 | 0.55 | 0 | 6474.73 | 910 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.87 | 978 | 0 | 979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 5 | 0 | 2.79 | 173 | 0 | 172 | 0 | 169 | 0 | 393 | 0 | 0.35 | 172 | 0 | 35 | 1 | 34 | 0 | 0 | 0 | 10 | 0.01 | 0 | 175 | 120 | 180 | 0 | 307 | 950 | 0 | 6156.39 | 12631.12 | 108.83
19:00 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17.5 | 17 | 68 | 46 | 0 | 0 | 26 | 73 | 0 | 350 | 307 | 355 | 0 | 17 | 332 | 0 | 0 | 0 | 70 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65 | 31 | 0 | 37 | 38 | 0 | 204 | 5 | 16 | 780 | 17 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 0 | 587 | 0 | 51 | 20 | 16 | 0 | 348 | 330 | 49 | 198 | 36 | 56 | 50 | 129 | 55 | 19 | 67 | 42 | 25 | 0 | 44 | 341 | 290 | 272 | 0 | 20 | 154 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 78 | 96 | 120 | 0 | 0 | 0 | 7083.5 | 909 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 2 | 1187 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 193 | 0 | 191 | 0 | 409 | 0 | 0 | 174 | 0 | 90 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 120 | 220 | 0 | 300 | 1020 | 0 | 6807 | 13890.5 | 108.83
19:30 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 44 | 17 | 70 | 46 | 15 | 0 | 35 | 135 | 16 | 350 | 298 | 330 | 0 | 55 | 335 | 0 | 0 | 0 | 70 | 26 | 22 | 0 | 0 | 7 | 30 | 0 | 0 | 8 | 65 | 31 | 0 | 37 | 38 | 0 | 204 | 20 | 25 | 780 | 17 | 0 | 39 | 0 | 36 | 0 | 0 | 0 | 0 | 585 | 0 | 51 | 80 | 16 | 0 | 348 | 330 | 49 | 215 | 36 | 65 | 50 | 164 | 63 | 19 | 70 | 42 | 25 | 0 | 44 | 341 | 290 | 246 | 0 | 20 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 5 | 93 | 170 | 130 | 0 | 0 | 0 | 7499 | 910 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 10 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 196 | 0 | 195 | 0 | 390 | 0 | 0 | 174 | 0 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 120 | 220 | 0 | 298 | 1180 | 0 | 7253 | 14752
20:00 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 44.5 | 17 | 76 | 46 | 30 | 0 | 44 | 142 | 16 | 320 | 295 | 340 | 0 | 55 | 280 | 0 | 0 | 0 | 90 | 28 | 22 | 0 | 0 | 8 | 30 | 0 | 0 | 18 | 65 | 30 | 0 | 37 | 38 | 0 | 204 | 24 | 26 | 780 | 17 | 0 | 34 | 0 | 37 | 0 | 0 | 0 | 0 | 586 | 0 | 51 | 80 | 16 | 0 | 300 | 330 | 50 | 184 | 39 | 66 | 50 | 174 | 63 | 19 | 75 | 42 | 52.2 | 0 | 44 | 341 | 290 | 240 | 0 | 20 | 151 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 11 | 93 | 170 | 129 | 0 | 0 | 0 | 7464.7 | 910 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1143 | 14 | 1367 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 183 | 0 | 183 | 0 | 332 | 0 | 0 | 176 | 0 | 95 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 120 | 220 | 0 | 298 | 1190 | 0 | 7226 | 14690.7 | 108.83
21:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 23.2 | 17 | 66 | 15 | 0 | 0 | 17 | 72 | 16 | 350 | 301 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 65 | 0 | 0 | 12 | 36 | 0 | 204 | 0 | 30 | 780 | 17 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 586 | 0 | 51 | 0 | 16 | 0 | 354 | 330 | 51 | 201 | 39 | 68 | 50 | 174 | 63 | 19 | 78 | 42 | 52.2 | 0 | 45 | 341 | 290 | 268 | 0 | 20 | 155 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 129 | 0 | 0 | 0 | 7200.4 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1198 | 0 | 1415.18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 168 | 0 | 170 | 0 | 414 | 0 | 0 | 178 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 296 | 1180 | 0 | 7347.18 | 14547.58 | 108.83
22:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 16.3 | 17 | 51 | 15 | 0 | 0 | 17 | 69 | 16 | 350 | 308 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 65 | 0 | 0 | 12 | 36 | 0 | 204 | 0 | 30 | 780 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 588 | 0 | 51 | 0 | 16 | 0 | 353 | 330 | 51 | 204 | 36 | 70 | 70 | 180 | 64 | 19 | 79 | 44 | 52.2 | 0 | 45 | 280 | 280 | 269 | 0 | 20 | 159 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 129 | 0 | 0 | 0 | 7165.5 | 890 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 1415.15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 175 | 0 | 177 | 0 | 414 | 0 | 0 | 180 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 297 | 1162 | 0 | 7357.15 | 14522.65 | 108.83
23:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 14.9 | 17 | 51 | 15 | 0 | 0 | 17 | 63 | 0 | 350 | 305 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 65 | 0 | 0 | 12 | 36 | 0 | 204 | 0 | 38 | 775 | 0 | 0 | 0 | 0 | 48 | 0 | 145 | 0 | 0 | 588 | 0 | 51 | 0 | 16 | 0 | 356 | 330 | 51 | 199 | 39 | 68 | 70 | 174 | 64 | 19 | 76 | 46 | 52.2 | 0 | 44 | 280 | 270 | 265 | 0 | 30 | 153 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 94 | 170 | 132 | 0 | 0 | 0 | 7242.1 | 891 | 369 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 1420.55 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 194 | 0 | 188 | 0 | 414 | 0 | 0 | 180 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 298 | 1162 | 0 | 7381.55 | 14623.65 | 108.83
Total KWH | 0 | 987840 | 648960 | 0 | 0 | 0 | 0 | 0 | 9295200 | 0 | 0 | 178560 | 203760 | 2084976 | 284640 | 17815 | 0 | 476094 | 918720 | 47040 | 8526000 | 7224844 | 8707372 | 0 | 74443 | 7783412 | 0 | 0 | 150601 | 981600 | 569400 | 506160 | 0 | 0 | 13800 | 32618 | 0 | 0 | 207360 | 726199 | 41032 | 0 | 417600 | 587520 | 9703 | 4919995 | 47672 | 551040 | 17752727.27 | 48509 | 0 | 282240 | 8796.6 | 250072 | 0 | 228098 | 0 | 0 | 17678180 | 57105 | 1231030 | 199054 | 1639273 | 0 | 8666800 | 7956000 | 1152960 | 4833000 | 905328 | 1275840 | 1441200 | 4026240 | 1436400 | 422030 | 825360 | 899520 | 255523 | 148245 | 932736 | 5811500 | 6689200 | 7013000 | 0 | 110640 | 3513355 | 168168 | 0 | 1909440 | 719040 | 0 | 449000 | 0 | 87120 | 2044800 | 2220000 | 3245760 | 6350 | 165340 | 52320 | 165979275.87 | 21890909 | 9036000 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 215280 | 23396370 | 31200 | 27334606 | 0 | 0 | 0 | 0 | 0 | 0 | 124528 | 0 | 0 | 253048 | 544680 | 0 | 165744 | 4376273 | 0 | 4507964 | 0 | 4538509 | 0 | 9066181 | 0 | 15840 | 4191000 | 0 | 1346914 | 191695 | 1857004 | 0 | 0 | 26894.76 | 110160 | 1423 | 0 | 5018000 | 2885000 | 5329120 | 0 | 7293816 | 25239272.73 | 0 | 159899431.49 | 325878707.36

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13527.41 | MW | 12:00 Hr. | Energy Generated |  |  | 325.8787 |  | MKWHr.
| Day Peak Demand |  |  | 13527.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.56 |  | MKWHr.
| Evening Peak Generation |  |  | 14752 | MW | 19:30 Hr. | Energy Demand |  |  | 326.4387 |  | MKWHr.
| Evening Peak Demand |  |  | 14782 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.7 |  | °C
| Minimum Generation of the Day |  |  | 12299.63 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1034.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 14752 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.7335 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.6124 | 0 | 6.9044 | 0 | 0 | 0.1506 | 0 | 0 | 49.6674 | Gas | 140.7792 | Gas | 503353496.43
| Chattogram Zone |  |  | 0.55104 | 35.4309 | 2.4561 | 0.2281 | 4.92 | 0.066808 | 0 | 0.20736 | 43.8603 | Coal | 100.5694 | Coal | 596748919.9365
| Cumilla Zone |  |  | 28.2476 | 0 | 8.9512 | 0 | 0 | 0.14824 | 0.89952 | 0 | 38.2465 | HFO | 26.0755 | HFO | 477796666.652
| Mymensingh Zone |  |  | 3.2458 | 0 | 4.4042 | 0 | 0 | 0.17169 | 0 | 0 | 7.8217 | HSD | 0.2281 | HSD | 796062.02
| Sylhet Zone |  |  | 26.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3833 | Hydro | 4.92 | Hydro | 491999.5
| Khulna Zone |  |  | 9.036 | 23.3964 | 0.0312 | 0 | 0 | 0.21528 | 22.8029 | 0 | 55.4818 | Solar | 2.0621 | Solar | 28906239.1936
| Barishal Zone |  |  | 8.2141 | 37.5511 | 0 | 0 | 0 | 0.001423 | 0 | 0 | 45.7666 | Import | 51.037 | Import | 257280687.03
| Rajshahi Zone |  |  | 22.4889 | 0 | 0.12453 | 0 | 0 | 0.97931 | 27.3346 | 0 | 50.9274 | Wind | 0.20736 | Wind | 3035750.4
| Rangpur Zone |  |  | 0 | 4.191 | 3.2039 | 0 | 0 | 0.32875 | 0 | 0 | 7.7237
| Total |  |  | 140.7792 | 100.5694 | 26.0755 | 0.2281 | 4.92 | 2.0621 | 51.037 | 0.20736 | 325.8787
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 503353496.43 |  | Hydro | 491999.5
|  |  |  | Coal | 596748919.9365 |  | Solar | 28906239.1936
|  |  |  | HFO | 477796666.652 |  | Import | 257280687.03
|  |  |  | HSD | 796062.02 |  | Wind | 3035750.4
[5 empty] | Total: | 186,84,09,821 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8909 | Peak Hr Flow | 910.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50294636.47 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.3346 | Peak Hr Flow | 1304.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 882 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.89952 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1130 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.125 | Peak Hr Flow | 2256.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 7 |  | 5211
|  |  |  | Chattogram |  | 0 |  | 1386
|  |  |  | Cumilla |  | 0 |  | 1348
|  |  |  | Mymensingh |  | 0 |  | 1127
|  |  |  | Sylhet |  | 0 |  | 570
|  |  |  | Khulna |  | 0 |  | 1732
|  |  |  | Barishal |  | 0 |  | 442
|  |  |  | Rajshahi |  | 0 |  | 1436
|  |  |  | Rangpur |  | 22 |  | 986
|  |  |  | Total |  | 29 |  | 14238
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 08:26 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Lockout relays Due to Polaspur 33 kv | [7 empty] | 46.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 08:32 | 08:55 | Mongla 132/33kV S/S T-1 LT Tripped showing Lockout Relay relays Due to Over current fault | [7 empty] | 12.0MW load
interrup.
| 08:34 | 11:12 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Due to Red Hot Maintanence work at | [7 empty] | 95.0MW load
|  |  | 33kV IFAD Bus DS. | [7 empty] | interrup.
| 08:35 | 11:12 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to Due to Red Hot Maintanence Work at | [7 empty] | 95.0MW load
|  |  | 33 kV Ifad feeder. | [7 empty] | interrup.
| 09:27 | 16:56 | Bogura-Rahanpur 400kV Ckt-2 Scheduled S/D from Bogura 400/230kV end Due to Relay changing
work and from Rahanpur 400/132kV end Due to Bogura End Relay work
| 09:36 | 14:26 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Scheduled S/D Due to High
Temperature Maintenance.
| 09:37 |  | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end.
| 09:37 | 14:26 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to High
Temperature Maintenance.
| 09:40 | 11:04 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to water spray system testing
| 09:40 | 11:05 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to water spray system testing
| 10:10 | 17:05 | Madunaghat 400/230kV S/S Madunaghat-Old Madunaghat 230kV Ckt.-2 Project Work S/D Due to
S/D is taken by Madunaghat230 KV S/S
| 10:44 |  | Sylhet 222 MW CCPP unit transformers T-1, T-2, and T-3 were switched ON.
| 11:14 | 14:24 | Bogura 400/230kV S/S ATR-03 HT Scheduled S/D Due to Fire fighting water spray testing.
| 11:15 | 14:24 | Bogura 400/230kV S/S ATR-03 LT Scheduled S/D Due to Fire fighting water spray testing
| 11:24 | 14:24 | Sholosohor 132/33kV S/S TRAFO-02 HT Forced S/D Due to Shutdown for BPDB Feeder Bus
Isolator Replacement Works.
| 12:00 |  | Day Peak Generation 13524 MW.
| 12:15 | 12:25 | Madunaghat 400/230kV S/S Madunaghat-Old Madunaghat 230kV Ckt.-1 Tripped showing REL670
relays Due to None
| 12:24 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO is off at 11:58 hrs as fuel gas
pressure decreases
| 12:30 | 14:03 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Scheduled S/D Due to Oil leakage check in Unit
Transformer
| 13:08 | 13:29 | Kaliakoir-Tangail 132kV Ckt-2 Tripped from Kaliakoir 400/230/132kV end showing REL 670
relays.
| 14:38 | 16:29 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to
Maintenance work at Payra end. and from Payra 400/132/33kV end Due to High Temperature
Maintenance.
| 15:02 | 19:27 | Sholosohor 132/33kV S/S TRAFO-02 HT Forced S/D Due to Red Hot on Secondary Side of TR-02.
| 15:20 | 15:39 | BIPTC S/S 10CF15 Scheduled S/D Due to Tripped by C1 unbalance 60/61 stage-1 L1 trip.
| 18:46 |  | Sathkhira 132/33 KV T3 Transformer Breaker Closed.
| 20:28 |  | Gopalganj(N)-Payra 400KV Ckt-1 Forced S/D from Payra 400kV end Due to Due to the Red Hot
in Payra Ckt-1 of Amtoli 400KV Switching station
| 20:50 | 22:12 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Remove 33kv incoming braker red hot
| 20:52 | 22:09 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D
| 22:01 |  | Sikalbaha 225 MW GT was sync.
| 01:29 |  | Payra 1320 MW record a general event:- Line-1 has been charged from Payra Power Plant
side.
| 02:57 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 03:14 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 07:00 |  | Minimum Generation is 11261 MW
| 07:17 |  | Bhulta 132/33kV S/S GT1 LT Tripped showing No signal relays Due to 33 KV incomer Breaker
trip
| 07:17 |  | Bhulta 132/33kV S/S GT1 LT Tripped showing No signal relays Due to 33 KV incomer Breaker
trip
| 07:23 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Scheduled S/D Due to Red hot Maintenance work.
| 07:23 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Scheduled S/D Due to Red hot Maintenance work.
| 07:52 |  | Amtoli - Payra P/S 400 KV Ckt-2 S/D due to SAS Testing Work at Amtoli S/S.
| 07:52 |  | Payra 1320 MW record a general event:- Payra-Amtali Line-2 has been taken shutdown from
Amtali end at 07:52 hrs.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 341 | 9295200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8526000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 7224844 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7783412 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 178560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 46 | 284640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 476094 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 74443 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 569400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 506160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 648960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 17815 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 2084976 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 86 | 987840 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 47040 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 135 | 918720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 150601 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 203760 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 8707372 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 981600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2325 | 49667437
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 180MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 8796.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 57105 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 282240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 204 | 4919995 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 228098 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 36 | 250072 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 41032 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 726199 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 417600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 551040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9703 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 32618 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 20 | 47672 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 587520 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 7 | 13800 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 48509 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 585 | 17678180 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 207360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 780 | 17752727.27 | -
Chattogram Area Total |  |  |  |  | 5120.72 | 1922 | 43860266.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 215 | 4833000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8666800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7956000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 905328 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1152960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 1639273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1231030 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 199054 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 932736 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1441200 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 164 | 4026240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 42 | 899520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 255523 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 422030 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 825360 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 1436400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 65 | 1275840 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 148245 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1667 | 38246539
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 130 | 3245760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2220000 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 2044800 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 165340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 52320 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 5 | 87120 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 398 | 7821690
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 110640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3513355 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719040 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1909440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 449000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 168168 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 341 | 5811500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 246 | 7013000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 290 | 6689200 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1187 | 26383343
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 910 | 21890909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 375 | 9036000 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 10 | 31200 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 215280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1150 | 23396370 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2483 | 55481759
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 298 | 7293816 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2885000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 25239272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5329120 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 270 | 5018000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1423 | -
Barishal Area Total |  |  |  |  | 2236 | 2088 | 45766631.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 253048 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 193 | 4376273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4507964 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 195 | 4538509 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 390 | 9066181 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 124528 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1304 | 27334606 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 165744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 544680 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2303 | 50927373
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 174 | 4191000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 1857004 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26894.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1346914 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 191695 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 110160 | -
Rangpur Area Total |  |  |  |  | 950 | 379 | 7723667.76
Eastern Grid Total |  |  |  |  | 17626.505 | 7499 | 165979275.87
Western Grid Total |  |  |  |  | 10442.16 | 7253 | 159899431.49
National Grid Total |  |  |  |  | 28068.665 | 14752 | 325878707.36
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9634.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4574.9 | MW
i) Dhaka area |  |  | 5204 |  | MW | i) Khulna area |  |  |  | 1732 | MW
ii) Chattogram area |  |  | 1386 |  | MW | ii) Barishal area |  |  |  | 442.5 | MW
iii) Cumilla area |  |  | 1347.59 |  | MW | iii) Rajshahi area |  |  |  | 1436.4 | MW
iv) Mymensingh area |  |  | 1127 |  | MW | iv) Rangpur area |  |  |  | 964 | MW
v) Sylhet area |  |  | 570 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14209.49 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 14:00 | 133 | PHP | 9 | 00:00
2 | AKSML | 112 | 15:00 | 68 | Ishurdi | 78 | 19:30 | 134 | Pabna | 125 | 19:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 93 | 00:00 | 135 | Palashbari | 102 | 19:30
4 | Agargaon | 131 | 13:00 | 70 | Jamalpur | 128 | 21:00 | 136 | Panchagarh | 55 | 01:00
5 | Agrabad | 90 | 19:00 | 71 | Jashore | 131 | 19:30 | 137 | Patiya | 0 | 08:00
6 | Amnura | 27 | 00:00 | 72 | Jhenaidah | 127 | 19:30 | 138 | Patuakhali | 67 | 00:00
7 | Ashuganj | 78 | 01:00 | 73 | Joydebpur | 144 | 15:00 | 139 | Payra | 34 | 00:00
8 | BSRM | 206 | 17:00 | 74 | Joypurhat | 60 | 22:00 | 140 | Postogola | 55 | 13:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 15 | 14:00 | 141 | Purbachal | 21 | 00:00
10 | Bajitpur | 84 | 19:00 | 76 | KSRM | 25 | 00:00 | 142 | Purbasadipur | 127 | 19:30
11 | Bakulia | 89 | 19:00 | 77 | Kabirpur | 240 | 18:30 | 143 | Rahanpur | 37 | 00:00
12 | Banani | 50 | 11:00 | 78 | Kachua | 90 | 22:00 | 144 | Rahim | 48 | 17:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 99 | 00:00 | 145 | Rajbari | 80 | 19:30
14 | Barapukuria | 67 | 21:00 | 80 | Kalurghat | 38 | 12:00 | 146 | Rajendrapur | 124 | 19:30
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi | 104 | 21:00
16 | Barishal | 104 | 19:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 84 | 14:00
17 | Barishal-230 | 90 | 00:00 | 83 | Kasba | 34 | 19:30 | 149 | Ramganj | 112 | 20:00
18 | Baroaulia | 59 | 12:00 | 84 | Kazla | 96 | 13:00 | 150 | Rampur | 38 | 00:00
19 | Baroirhat | 68 | 19:30 | 85 | Keranigonj | 93 | 19:00 | 151 | Rangamati | 15 | 18:30
20 | Bashundhara | 195 | 13:00 | 86 | Khagrachori | 28 | 19:00 | 152 | Rangpur | 154 | 21:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulna | 63 | 00:00 | 153 | Ruppur | 6.6 | 15:00
22 | Beanibazar | 71 | 22:00 | 88 | Khulshi | 173 | 13:00 | 154 | SSM | 13 | 00:00
23 | Benapole | 60 | 19:00 | 89 | Kishoreganj | 126 | 19:30 | 155 | Saidpur | 112 | 19:00
24 | Bhaluka | 146 | 16:00 | 90 | Kodda | 305 | 14:00 | 156 | Satkhira | 123 | 01:00
25 | Bhandaria | 54 | 00:00 | 91 | Kulaura | 48 | 19:00 | 157 | Satmasjid | 97 | 13:00
26 | Bhangura | 38 | 23:00 | 92 | Kurigram | 76 | 19:00 | 158 | Savar | 228 | 16:00
27 | Bheramara(GK) | 64 | 19:30 | 93 | Kushtia | 144 | 19:00 | 159 | SevenRings | 19.17 | 00:00
28 | Bhulta | 227 | 14:00 | 94 | Laksam | 21 | 23:00 | 160 | ShahCement | 22 | 12:00
29 | Bog-Sherpur | 74 | 00:00 | 95 | Lakshmipur | 19 | 00:00 | 161 | Shahjadpur | 83 | 21:00
30 | Bogura | 145 | 19:30 | 96 | Lalbag | 41 | 13:00 | 162 | Shahjibazar | 115 | 22:00
31 | Borhanuddin | 93 | 01:00 | 97 | Lalmonirhat | 60 | 19:00 | 163 | Shahmirpur | 58 | 17:00
32 | Brahmanbaria | 120 | 22:00 | 98 | MI_Cement | 16.8 | 15:00 | 164 | Shariatpur | 88 | 22:00
33 | Cantonment | 136 | 14:00 | 99 | Madanganj | 42 | 00:00 | 165 | Sherpur | 156 | 00:00
34 | Chandina | 20.02 | 03:00 | 100 | Madaripur | 112 | 00:00 | 166 | Shikalbaha | 8 | 12:00
35 | Chandpur | 81 | 23:00 | 101 | Madartek | 88 | 00:00 | 167 | Shitalakhya | 87.3 | 12:00
36 | Chandraghona | 33 | 19:30 | 102 | Madunaghat | 52 | 19:30 | 168 | Sholosohor | 44 | 16:00
37 | Chapai | 64 | 00:00 | 103 | Magura | 65 | 19:30 | 169 | Shyampur | 170 | 02:00
38 | Charsaidpur | 32 | 00:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 117 | 12:00
39 | Chauddagram | 65 | 22:00 | 105 | Maijdee | 14 | 00:00 | 171 | Sirajganj | 106 | 20:00
40 | Chhatak | 37 | 01:00 | 106 | Manikganj | 128 | 20:00 | 172 | Sonargaon | 118 | 19:00
41 | Chowmuhani | 193 | 19:30 | 107 | Maniknagar | 82 | 13:00 | 173 | Sreemongol | 78 | 21:00
42 | Chuadanga | 108 | 00:00 | 108 | Matarbari | 52 | 01:00 | 174 | Sreepur | 111 | 15:00
43 | Coxsbazar | 126 | 21:00 | 109 | Matuail | 60 | 10:00 | 175 | Srinagar | 47.92 | 22:00
44 | Cumilla(N) | 137 | 00:00 | 110 | Millgate | 128 | 12:00 | 176 | Sunamganj | 56 | 00:00
45 | Cumilla(S) | 159 | 18:30 | 111 | Mirpur | 134 | 12:00 | 177 | Sylhet | 45 | 23:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 12:00 | 178 | Sylhet-132 | 108 | 20:00
47 | Daudkandi | 149 | 00:00 | 113 | Mirzapur | 46 | 19:30 | 179 | TK | 32 | 00:00
48 | Dhaka | 76 | 13:00 | 114 | Mithapukur | 68 | 19:30 | 180 | Tangail | 182 | 19:00
49 | Dhamrai | 120 | 15:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 22 | 23:00
50 | Dhanmondi | 144 | 13:00 | 116 | Mogbazar | 146.8 | 13:00 | 182 | Thakurgaon | 107 | 00:00
51 | Dohazari | 105 | 00:00 | 117 | Mongla | 40 | 16:00 | 183 | Tongi | 113 | 11:00
52 | Faridpur | 170 | 22:00 | 118 | Motijheel | 42 | 12:00 | 184 | Ullahpara | 39 | 19:00
53 | Fatullah | 101 | 15:00 | 119 | Muktagacha | 34 | 23:00 | 185 | Ullon | 39 | 00:00
54 | Fenchuganj | 39 | 19:00 | 120 | Munshiganj | 114 | 00:00 | 186 | Uttara | 83 | 13:00
55 | Feni | 103 | 19:00 | 121 | Muradnagar | 40 | 19:00 | 187 | UttaraNew | 58 | 00:00
56 | GPH | 77 | 04:00 | 122 | Mymensingh | 190 | 19:00 | 188 | Zigatola | 70 | 14:00
57 | Ghatail | 80 | 19:00 | 123 | Naogaon | 125 | 21:00
58 | Ghorashal | 14 | 14:00 | 124 | Narail | 58 | 19:30
59 | Ghorashal-230 | 84 | 23:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 176 | 23:00
61 | Gollamari | 90 | 00:00 | 127 | Natore | 143 | 19:30
62 | Gopalganj | 105 | 19:00 | 128 | Nawabganj | 59.8 | 22:00
63 | Gulshan | 120 | 13:00 | 129 | Netrakona | 130 | 21:00
64 | Halishahar | 71.5 | 15:00 | 130 | New | 68 | 12:00
65 | HaripurSBU | 156 | 08:00 | 131 | Niamatpur | 70 | 22:00
66 | Hasnabad | 69 | 00:00 | 132 | Noapara | 48 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14511.6 | 104 |  | 14620.28
1:00 | 14148.48 | 97 |  | 14249.85
2:00 | 13711.19 | 96 |  | 13811.51
3:00 | 13327.2 | 89 |  | 13420.21
4:00 | 13064.71 | 63 |  | 13130.55
5:00 | 12826.86 | 42 |  | 12870.75
6:00 | 12299.63 | 31 |  | 12332.03
7:00 | 12350.83 | 0 |  | 12350.83
8:00 | 12432.41 | 0 |  | 12432.41
9:00 | 12538.47 | 0 |  | 12538.47
10:00 | 12778.1 | 0 |  | 12778.1
11:00 | 12973.57 | 0 |  | 12973.57
12:00 | 13527.41 | 0 |  | 13527.41
13:00 | 13694.39 | 0 |  | 13694.39
14:00 | 13608.97 | 0 |  | 13608.97
15:00 | 13577.06 | 0 |  | 13577.06
16:00 | 13342.88 | 0 |  | 13342.88
17:00 | 12834.3 | 0 |  | 12834.3
18:00 | 12631.12 | 0 |  | 12631.12
19:00 | 13890.5 | 0 |  | 13890.5
19:30 | 14752 | 29 |  | 14782
20:00 | 14690.7 | 38 |  | 14730.7
21:00 | 14547.58 | 0 |  | 14547.58
22:00 | 14522.65 | 0 |  | 14522.65
23:00 | 14623.65 | 0 |  | 14623.65
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7213 | 7298.6 | 14511.6 | DAILY GENERATION CURVE
00:30 | 7146 | 7184.04 | 14330.04
01:00 | 7079 | 7069.48 | 14148.48 | 07-08-2025
01:30 | 7009.45 | 6920.385 | 13929.835
02:00 | 6939.9 | 6771.29 | 13711.19
02:30 | 6864.95 | 6654.245 | 13519.195
03:00 | 6790 | 6537.2 | 13327.2
03:30 | 6743 | 6452.955 | 13195.955
04:00 | 6696 | 6368.71 | 13064.71
04:30 | 6602 | 6343.785 | 12945.785
05:00 | 6508 | 6318.86 | 12826.86
05:30 | 6419.14 | 6144.105 | 12563.245
06:00 | 6330.28 | 5969.35 | 12299.63
06:30 | 6341.23 | 5984 | 12325.23
07:00 | 6352.18 | 5998.65 | 12350.83
07:30 | 6377.74 | 6013.88 | 12391.62
08:00 | 6403.3 | 6029.11 | 12432.41
08:30 | 6437.635 | 6047.805 | 12485.44
09:00 | 6471.97 | 6066.5 | 12538.47
09:30 | 6543.305 | 6114.98 | 12658.285
10:00 | 6614.64 | 6163.46 | 12778.1
10:30 | 6712.42 | 6163.415 | 12875.835
11:00 | 6810.2 | 6163.37 | 12973.57
11:30 | 6907.915 | 6342.575 | 13250.49
12:00 | 7005.63 | 6521.78 | 13527.41
12:30 | 6999.95 | 6610.95 | 13610.9
13:00 | 6994.27 | 6700.12 | 13694.39
13:30 | 6964.745 | 6686.935 | 13651.68
14:00 | 6935.22 | 6673.75 | 13608.97
14:30 | 6939.255 | 6653.76 | 13593.015
15:00 | 6943.29 | 6633.77 | 13577.06
15:30 | 6871.585 | 6588.385 | 13459.97
16:00 | 6799.88 | 6543 | 13342.88
16:30 | 6679.685 | 6408.905 | 13088.59
17:00 | 6559.49 | 6274.81 | 12834.3
17:30 | 6517.11 | 6215.6 | 12732.71
18:00 | 6474.73 | 6156.39 | 12631.12
18:30 | 6779.115 | 6481.695 | 13260.81
19:00 | 7083.5 | 6807 | 13890.5
19:30 | 7499 | 7253 | 14752
20:00 | 7464.7 | 7226 | 14690.7
20:30 | 7332.55 | 7286.59 | 14619.14 |  | Executive Engineer
21:00 | 7200.4 | 7347.18 | 14547.58 |  | Network Operation Division
21:30 | 7182.95 | 7352.165 | 14535.115
22:00 | 7165.5 | 7357.15 | 14522.65
22:30 | 7203.8 | 7369.35 | 14573.15
23:00 | 7242.1 | 7381.55 | 14623.65

## En-Curve
QF-LDC-12
Date | 07-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4035 | 1902 | 903 | 38 | 42 | 1421.6 | 206 | 4794 | 0 | 214 | 950 | 0 | 0 | 6 | 104 | DAILY ENERGY CURVE
00:30 | 4008.5 | 1900.5 | 903 | 38 | 41 | 1363.54 | 206 | 4765.5 | 0 | 188 | 902.5 | 0 | 0 | 13.5 | 100.5 | 07-08-2025
01:00 | 3982 | 1899 | 903 | 38 | 40 | 1305.48 | 206 | 4737 | 0 | 162 | 855 | 0 | 0 | 21 | 97
01:30 | 3990 | 1907.45 | 903 | 38 | 39 | 1262.885 | 206 | 4582 | 0 | 132.5 | 854 | 0 | 0 | 15 | 96.5 | Energy Generated | 325.8787 |  | MKWHr
02:00 | 3998 | 1915.9 | 903 | 38 | 38 | 1220.29 | 206 | 4427 | 0 | 103 | 853 | 0 | 0 | 9 | 96 | Energy not Served | 0.56 |  | MKWHr
02:30 | 3992 | 1912.95 | 903 | 38 | 38 | 1179.745 | 206 | 4346.5 | 0 | 99 | 790 | 0 | 0 | 14 | 92.5 | Total Energy Requirement | 326.4387 |  | MKWHr
03:00 | 3986 | 1910 | 903 | 38 | 38 | 1139.2 | 206 | 4266 | 0 | 95 | 727 | 0 | 0 | 19 | 89
03:30 | 3978 | 1909 | 903 | 38 | 37 | 1132.955 | 206 | 4189 | 0 | 95 | 697.5 | 0 | 0 | 10.5 | 76
04:00 | 3970 | 1908 | 903 | 38 | 36 | 1126.71 | 206 | 4112 | 0 | 95 | 668 | 0 | 0 | 2 | 63
04:30 | 3877 | 1907.5 | 903 | 38 | 36 | 1125.785 | 206 | 4090 | 0 | 95 | 666.5 | 0 | 0 | 1 | 52.5
05:00 | 3784 | 1907 | 903 | 38 | 36 | 1124.86 | 206 | 4068 | 0 | 95 | 665 | 0 | 0 | 0 | 42
05:30 | 3770.5 | 1905.5 | 903 | 38 | 34 | 1074.15 | 205.5 | 3906.5 | 4.095 | 95 | 627 | 0 | 0 | 0 | 36.5
06:00 | 3757 | 1904 | 903 | 38 | 32 | 1023.44 | 205 | 3745 | 8.19 | 95 | 589 | 0 | 0 | 0 | 31
06:30 | 3773 | 1894 | 903 | 38 | 32 | 1025.615 | 205 | 3747 | 32.115 | 95 | 577.5 | 0 | 0 | 3 | 15.5
07:00 | 3789 | 1884 | 903 | 38 | 32 | 1027.79 | 205 | 3749 | 56.04 | 95 | 566 | 0 | 0 | 6 | 0
07:30 | 3772 | 1878.75 | 903 | 38 | 32 | 1019.895 | 204.5 | 3749 | 108.975 | 104.5 | 575 | 0 | 0 | 6 | 0
08:00 | 3755 | 1873.5 | 903 | 38 | 32 | 1012 | 204 | 3749 | 161.91 | 114 | 584 | 0 | 0 | 6 | 0
08:30 | 3736.5 | 1872.5 | 903 | 38 | 32 | 1017 | 208.5 | 3748 | 189.44 | 131 | 604 | 0 | 0 | 5.5 | 0
09:00 | 3718 | 1871.5 | 903 | 38 | 32 | 1022 | 213 | 3747 | 216.97 | 148 | 624 | 0 | 0 | 5 | 0
09:30 | 3751 | 1875.25 | 906.5 | 38 | 33 | 1023.5 | 213 | 3744 | 287.535 | 154.5 | 629.5 | 0 | 0 | 2.5 | 0
10:00 | 3784 | 1879 | 910 | 38 | 34 | 1025 | 213 | 3741 | 358.1 | 161 | 635 | 0 | 0 | 0 | 0
10:30 | 3820.5 | 1892.25 | 910 | 38 | 34 | 994 | 210 | 3792 | 349.585 | 161.5 | 674 | 0 | 0 | 0 | 0
11:00 | 3857 | 1905.5 | 910 | 38 | 34 | 963 | 207 | 3843 | 341.07 | 162 | 713 | 0 | 0 | 0 | 0
11:30 | 3870 | 1950.35 | 910 | 38 | 36 | 1003.5 | 206 | 3948.5 | 377.64 | 166 | 741 | 0 | 0 | 3.5 | 0
12:00 | 3883 | 1995.2 | 910 | 38 | 38 | 1044 | 205 | 4054 | 414.21 | 170 | 769 | 0 | 0 | 7 | 0
12:30 | 3847.5 | 1995.6 | 910 | 38 | 39 | 1035 | 204.5 | 4132.5 | 388.3 | 173.5 | 843.5 | 0 | 0 | 3.5 | 0
13:00 | 3812 | 1996 | 910 | 38 | 40 | 1026 | 204 | 4211 | 362.39 | 177 | 918 | 0 | 0 | 0 | 0
13:30 | 3747.5 | 1971.5 | 910 | 38 | 40 | 1017.5 | 203.5 | 4209.5 | 371.43 | 182 | 959.75 | 0 | 0 | 1 | 0
14:00 | 3683 | 1947 | 910 | 38 | 40 | 1009 | 203 | 4208 | 380.47 | 187 | 1001.5 | 0 | 0 | 2 | 0
14:30 | 3697 | 1954.5 | 910 | 38 | 39 | 1012 | 203 | 4185 | 361.565 | 187 | 982.95 | 0 | 0 | 23 | 0
15:00 | 3711 | 1962 | 910 | 38 | 38 | 1015 | 203 | 4162 | 342.66 | 187 | 964.4 | 0 | 0 | 44 | 0
15:30 | 3728 | 1968 | 910 | 38 | 38 | 1019.5 | 203 | 4164 | 276.27 | 191 | 902.2 | 0 | 0 | 22 | 0
16:00 | 3745 | 1974 | 910 | 38 | 38 | 1024 | 203 | 4166 | 209.88 | 195 | 840 | 0 | 0 | 0 | 0
16:30 | 3707.5 | 1952.5 | 910 | 38 | 37 | 1025 | 203.5 | 4060 | 152.09 | 198 | 804 | 0 | 0 | 1 | 0
17:00 | 3670 | 1931 | 910 | 38 | 36 | 1026 | 204 | 3954 | 94.3 | 201 | 768 | 0 | 0 | 2 | 0
17:30 | 3719.5 | 1939 | 910 | 38 | 36 | 1002.5 | 204 | 3922.5 | 59.21 | 189.5 | 709.5 | 0 | 0 | 3 | 0
18:00 | 3769 | 1947 | 910 | 38 | 36 | 979 | 204 | 3891 | 24.12 | 178 | 651 | 0 | 0 | 4 | 0
18:30 | 3832 | 1980 | 909.5 | 38 | 39 | 1083 | 204 | 4035.5 | 12.06 | 279 | 841.75 | 0 | 0 | 7 | 0
19:00 | 3895 | 2013 | 909 | 38 | 42 | 1187 | 204 | 4180 | 0 | 380 | 1032.5 | 0 | 0 | 10 | 0
19:30 | 3858 | 1989 | 910 | 38 | 42 | 1304 | 204 | 4437 | 0 | 401 | 1561 | 0 | 0 | 8 | 29
20:00 | 3633 | 1967 | 910 | 38 | 42 | 1367 | 204 | 4440 | 0 | 420 | 1651.7 | 0 | 0 | 18 | 38
20:30 | 3736 | 1990 | 900 | 38 | 42 | 1391.09 | 204 | 4468.5 | 0 | 382 | 1451.05 | 0 | 0 | 16.5 | 19
21:00 | 3839 | 2013 | 890 | 38 | 42 | 1415.18 | 204 | 4497 | 0 | 344 | 1250.4 | 0 | 0 | 15 | 0
21:30 | 3863.5 | 1996 | 890 | 38 | 43 | 1415.165 | 204 | 4489 | 0 | 344 | 1234.45 | 0 | 0 | 18 | 0
22:00 | 3888 | 1979 | 890 | 38 | 44 | 1415.15 | 204 | 4481 | 0 | 344 | 1218.5 | 0 | 0 | 21 | 0
22:30 | 3896.5 | 1981 | 890.5 | 38 | 45 | 1417.85 | 204 | 4474.5 | 0 | 333.5 | 1200.3 | 72.5 | 0 | 19.5 | 0
23:00 | 3905 | 1983 | 891 | 38 | 46 | 1420.55 | 204 | 4468 | 0 | 323 | 1182.1 | 145 | 0 | 18 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 06:00 | 376 | 00:00 | Payra | 416 | 06:00 | 410 | 00:00
Ashuganj | 401 | 06:00 | 387 | 00:00 | Rahanpur | 402 | 08:00 | 386 | 00:00
Bhulta | 405 | 06:00 | 380 | 12:00 | Rampal | 407 | 08:00 | 393 | 00:00
Bibiana | 387 | 06:00 | 381 | 12:00
BIPTC | 403 | 06:00 | 395 | 20:00
Bogura | 383 | 06:00 | 364 | 21:00
Gopalganj | 401 | 06:00 | 387 | 00:00
Kaliakoir | 378 | 06:00 | 365 | 12:00
Madunaghat | 398 | 04:00 | 386 | 00:00
Meghnaghat | 391 | 06:00 | 378 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 218 | 12:00 | Keranigonj | 225 | 06:00 | 216 | 12:00
AKSML | 234 | 19:30 | 224 | 12:00 | Khulna(S) | 233 | 08:00 | 220 | 00:00
Aminbazar | 228 | 06:00 | 218 | 12:00 | Madunaghat | 235 | 19:00 | 227 | 00:00
Ashuganj | 234 | 05:00 | 224 | 23:00 | Madunaghat-400 | 234 | 20:00 | 226 | 00:00
Ashuganj-400 | 234 | 05:00 | 224 | 23:00 | Maniknagar | 222 | 05:00 | 216 | 00:00
Baghabari | 235 | 05:00 | 225 | 22:00 | Meghnaghat | 230 | 06:00 | 223 | 00:00
Barapukuria | 224 | 05:00 | 216 | 21:00 | Meghnaghat-400 | 227 | 06:00 | 219 | 12:00
Barapukuria-230 | 224 | 05:00 | 216 | 21:00 | Mirsorai | 230 | 19:30 | 219 | 00:00
Barishal | 229 | 08:00 | 221 | 00:00 | Rajshahi | 232 | 04:00 | 218 | 23:00
Bheramara | 234 | 04:00 | 221 | 21:00 | Rampal | 232 | 06:00 | 220 | 23:00
Bhulta | 233 | 06:00 | 214 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 08:00 | 221 | 00:00 | Rampura | 232 | 05:00 | 216 | 12:00
BIPTC | 236 | 03:00 | 222 | 21:00 | Shikalbaha | 233 | 20:00 | 224 | 00:00
Bogura | 237 | 06:00 | 225 | 21:00 | Shyampur | 225 | 06:00 | 216 | 12:00
Bogura-400 | 237 | 06:00 | 226 | 21:00 | Siddhirganj | 224 | 06:00 | 216 | 12:00
Borhanuddin | 233 | 04:00 | 228 | 00:00 | Sirajgonj | 241 | 05:00 | 235 | 21:00
BSRM | 229 | 19:30 | 220 | 00:00 | Sreepur | 229 | 06:00 | 221 | 12:00
Cumilla(N) | 226 | 08:00 | 217 | 00:00 | Tongi | 227 | 07:00 | 217 | 11:00
Faridpur | 227 | 07:00 | 18 | 06:00
Fenchuganj | 230 | 09:00 | 223 | 00:00
Ghorashal | 230 | 08:00 | 225 | 00:00
Ghorashal-230 | 230 | 06:00 | 218 | 12:00
Gopalganj | 229 | 08:00 | 220 | 00:00
GPH | 231 | 19:30 | 223 | 00:00
Haripur | 224 | 06:00 | 216 | 12:00
Hasnabad | 223 | 04:00 | 217 | 13:00
Hathazari | 231 | 08:00 | 222 | 00:00
Ishurdi | 236 | 04:00 | 224 | 21:00
Jhenaidah | 230 | 05:00 | 217 | 21:00
Kaliakoir | 233 | 05:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 148 | 04:00 | 128 | 12:00 | Lalmonirhat | 130 | 20:00 | 121 | 00:00
Agargaon | 134 | 06:00 | 126 | 13:00 | Madanganj | 130 | 05:00 | 124 | 12:00
Agrabad | 133 | 19:30 | 126 | 00:00 | Madaripur | 135 | 04:00 | 129 | 00:00
AKS | 130 | 19:00 | 124 | 00:00 | Madartek | 140 | 06:00 | 127 | 12:00
Aminbazar | 133 | 05:00 | 127 | 12:00 | Madunaghat | 134 | 20:00 | 128 | 00:00
Amnura | 136 | 08:00 | 128 | 23:00 | Magura | 134 | 09:00 | 124 | 21:00
Ashuganj | 144 | 08:00 | 136 | 21:00 | Mahasthangarh | 136 | 08:00 | 126 | 21:00
Bagerhat | 135 | 09:00 | 121 | 00:00 | Maijdee | 122 | 09:00 | 111 | 00:00
Bajitpur | 132 | 04:00 | 126 | 21:00 | Manikganj | 130 | 05:00 | 120 | 00:00
Bakulia | 135 | 20:00 | 126 | 00:00 | Maniknagar | 135 | 06:00 | 128 | 12:00
Banani | 140 | 04:00 | 127 | 12:00 | Matarbari | 121 | 09:00 | 110 | 00:00
Bangabhaban | 134 | 05:00 | 127 | 12:00 | Matuail | 130 | 05:00 | 125 | 12:00
Barapukuria | 135 | 09:00 | 128 | 12:00 | Millgate | 134 | 03:00 | 125 | 12:00
Barguna | 135 | 08:00 | 131 | 00:00 | Mirpur | 132 | 05:00 | 125 | 12:00
Barishal | 135 | 08:00 | 126 | 00:00 | Mirzapur | 131 | 09:00 | 126 | 12:00
Barishal-230 | 134 | 08:00 | 127 | 00:00 | Mithapukur | 129 | 09:00 | 114 | 23:00
Baroaulia | 132 | 19:00 | 127 | 12:00 | MI_Cement | 131 | 06:00 | 124.6 | 12:00
Baroirhat | 125 | 05:00 | 118 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 140 | 04:00 | 126 | 12:00 | Mogbazar | 140 | 03:00 | 129 | 12:00
BashundharaCement | 1127 | 09:00 | 124 | 12:00 | Mongla | 135 | 09:00 | 123 | 00:00
Beanibazar | 129 | 07:00 | 120 | 22:00 | Motijheel | 134 | 05:00 | 127 | 12:00
Benapole | 135 | 09:00 | 122 | 00:00 | Muktagacha | 136 | 19:30 | 131 | 04:00
Bhaluka | 131 | 06:00 | 124 | 00:00 | Munshiganj | 129 | 06:00 | 123 | 12:00
Bhandaria | 130 | 08:00 | 120 | 00:00 | Muradnagar | 126 | 06:00 | 120 | 00:00
Bhangura | 132 | 17:00 | 128 | 23:00 | Mymensingh | 137 | 11:00 | 117 | 23:00
Bheramara | 137 | 03:00 | 132 | 21:00 | Naogaon | 135 | 09:00 | 124 | 21:00
Bheramara(GK) | 137 | 04:00 | 132 | 21:00 | Narail | 134 | 08:00 | 123 | 23:00
Bhulta | 124 | 09:00 | 120 | 01:00 | Narinda | 135 | 06:00 | 128 | 12:00
Bog-Sherpur | 137 | 08:00 | 128 | 21:00 | Narshingdi | 136 | 06:00 | 121 | 12:00
Bogura | 139 | 09:00 | 131 | 21:00 | Natore | 135 | 09:00 | 127 | 21:00
Bogura-230 | 140 | 09:00 | 131 | 21:00 | Nawabganj | 135 | 06:00 | 128 | 00:00
Brahmanbaria | 139 | 07:00 | 129 | 23:00 | Netrakona | 127 | 17:00 | 116 | 01:00
Cantonment | 133 | 04:00 | 126 | 12:00 | New | 135 | 04:00 | 126 | 11:00
Chandina | 128 | 06:00 | 123 | 00:00 | Niamatpur | 138 | 09:00 | 130 | 00:00
Chandpur | 130 | 08:00 | 122 | 00:00 | Noapara | 137 | 09:00 | 126 | 00:00
Chandraghona | 133 | 08:00 | 128 | 00:00 | Pabna | 135 | 04:00 | 128 | 21:00
Chapai | 136 | 09:00 | 130 | 21:00 | Palashbari | 128 | 09:00 | 113 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 07:00 | 125 | 12:00 | Panchagarh | 133 | 02:00 | 124 | 11:00
Chauddagram | 125 | 08:00 | 117 | 00:00 | Patiya | 133 | 19:00 | 127 | 12:00
Chhatak | 129 | 08:00 | 115 | 00:00 | Patuakhali | 135 | 07:00 | 132 | 00:00
Chowmuhani | 122 | 08:00 | 112 | 00:00 | Payra | 137 | 07:00 | 135 | 00:00
Chuadanga | 132 | 05:00 | 120 | 23:00 | PHP | 124 | 09:00 | 116 | 00:00
Coxsbazar | 124 | 19:00 | 111 | 00:00 | Postogola | 132 | 04:00 | 127 | 12:00
Cumilla(N) | 129 | 05:00 | 123 | 00:00 | Purbachal | 140 | 04:00 | 125 | 12:00
Cumilla(S) | 133 | 04:00 | 121 | 00:00 | Purbasadipur | 131 | 19:00 | 119 | 21:00
Daganbhuiyan | 122 | 08:00 | 114 | 00:00 | Rahanpur | 138 | 08:00 | 131 | 22:00
Daudkandi | 124 | 08:00 | 117 | 00:00 | Rahanpur-400 | 138 | 06:00 | 132 | 00:00
Dhaka | 138 | 03:00 | 128 | 12:00 | Rahim | 130 | 05:00 | 125 | 12:00
Dhamrai | 133 | 08:00 | 126 | 12:00 | Rajbari | 134 | 08:00 | 127 | 00:00
Dhanmondi | 141 | 06:00 | 128 | 12:00 | Rajendrapur | 131 | 06:00 | 123 | 12:00
Dohazari | 131 | 19:00 | 121 | 00:00 | Rajshahi | 134 | 05:00 | 126 | 21:00
Faridpur | 135 | 06:00 | 129 | 00:00 | Rajshahi-230 | 133 | 04:00 | 126 | 21:00
Fatullah | 132 | 06:00 | 126 | 12:00 | Ramganj | 124 | 00:00 | 10 | 06:00
Fenchuganj | 136 | 07:00 | 129 | 00:00 | Rampur | 132 | 19:00 | 125 | 00:00
Feni | 124 | 22:00 | 118 | 00:00 | Rampura | 140 | 04:00 | 129 | 12:00
Ghatail | 131 | 09:00 | 126 | 13:00 | Rangamati | 132 | 08:00 | 128 | 00:00
Ghorashal | 139 | 06:00 | 131 | 00:00 | Rangpur | 130 | 03:00 | 123 | 12:00
Goalpara | 140 | 09:00 | 128 | 00:00 | Ruppur | 137 | 04:00 | 131 | 22:00
Gollamari | 139 | 09:00 | 129 | 00:00 | Saidpur | 132 | 18:30 | 121 | 12:00
Gopalganj | 137 | 09:00 | 128 | 00:00 | Satkhira | 136 | 09:00 | 123 | 00:00
Gopalganj-400 | 139 | 11:00 | 131 | 00:00 | Satmasjid | 133 | 06:00 | 126 | 12:00
Gulshan | 140 | 05:00 | 128 | 12:00 | Savar | 132 | 19:00 | 125 | 12:00
Halishahar | 134 | 19:00 | 127 | 00:00 | SevenRings | 138 | 07:00 | 131 | 00:00
Haripur | 131 | 06:00 | 126 | 12:00 | ShahCement | 131 | 06:00 | 125 | 12:00
HaripurSBU | 131 | 06:00 | 126 | 12:00 | Shahjadpur | 137 | 02:00 | 132 | 21:00
Hasnabad | 132 | 04:00 | 126 | 11:00 | Shahjibazar | 138 | 07:00 | 129 | 22:00
Hathazari | 133 | 06:00 | 129 | 00:00 | Shahmirpur | 133 | 19:00 | 127 | 00:00
Ishurdi | 138 | 04:00 | 132 | 21:00 | Shariatpur | 135 | 09:00 | 126 | 00:00
Jaldhaka | 129 | 19:00 | 117 | 21:00 | Sherpur | 136 | 11:00 | 128 | 05:00
Jamalpur | 139 | 00:00 | 132 | 07:00 | Shikalbaha | 122 | 20:00 | 116 | 00:00
Jashore | 133 | 18:00 | 121 | 21:00 | Shikalbaha-230 | 135 | 19:00 | 129 | 00:00
Jhenaidah | 135 | 04:00 | 123 | 19:30 | Shitalakhya | 131 | 06:00 | 124.6 | 12:00
Jhenaidah-230 | 136 | 08:00 | 126 | 23:00 | Sholosohor | 133 | 20:00 | 127 | 00:00
Joydebpur | 140 | 14:00 | 131 | 00:00 | Shyampur | 131 | 07:00 | 125 | 00:00
Joypurhat | 133 | 08:00 | 121 | 23:00 | Shyampur-230 | 131 | 06:00 | 126 | 12:00
Juldah | 134 | 18:30 | 126 | 00:00 | Siddhirganj | 131 | 05:00 | 125 | 12:00
Kabirpur | 132 | 09:00 | 123 | 12:00 | Sirajganj | 135 | 04:00 | 126 | 21:00
Kachua | 129 | 14:00 | 120 | 00:00 | Sonargaon | 129 | 03:00 | 124 | 13:00
Kaliakoir | 135 | 07:00 | 128 | 12:00 | Sreemongol | 136 | 07:00 | 127 | 22:00
Kallyanpur | 134 | 05:00 | 127 | 00:00 | Sreepur | 132 | 06:00 | 127 | 00:00
Kalurghat | 133 | 19:00 | 127 | 00:00 | Srinagar | 134 | 05:00 | 128 | 00:00
Kamrangirchar | 136 | 05:00 | 128 | 12:00 | SSM | 134 | 18:30 | 130 | 07:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 09:00 | 113 | 00:00
Kasba | 125 | 06:00 | 119 | 00:00 | Sylhet | 130 | 08:00 | 121 | 00:00
Kazla | 134 | 08:00 | 127 | 13:00 | Sylhet-132 | 130 | 07:00 | 122 | 00:00
Keranigonj | 135 | 06:00 | 128 | 12:00 | Tangail | 129 | 03:00 | 124 | 12:00
Khagrachori | 131 | 07:00 | 127 | 00:00 | Taraganj | 131 | 19:00 | 122 | 11:00
Khulna | 138 | 09:00 | 128 | 00:00 | Thakurgaon | 131 | 02:00 | 121 | 12:00
Khulna(S) | 139 | 09:00 | 129 | 00:00 | TK | 133 | 19:00 | 127 | 00:00
Khulshi | 132 | 20:00 | 125 | 00:00 | Tongi | 134 | 04:00 | 128 | 11:00
Kishoreganj | 130 | 05:00 | 124 | 21:00 | Ullahpara | 135 | 06:00 | 128 | 21:00
Kodda | 133 | 07:00 | 122 | 00:00 | Ullon | 140 | 05:00 | 128 | 12:00
KSRM | 133 | 19:00 | 128 | 00:00 | Uttara | 133 | 06:00 | 125 | 12:00
Kulaura | 135 | 07:00 | 128 | 00:00 | UttaraNew | 132 | 05:00 | 125 | 12:00
Kurigram | 128 | 05:00 | 121 | 12:00 | Zigatola | 135 | 06:00 | 128 | 12:00
Kushtia | 134 | 09:00 | 127 | 23:00
Laksam | 128 | 08:00 | 120 | 00:00
Lakshmipur | 123 | 09:00 | 112 | 00:00
Lalbag | 135 | 06:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division