## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-08-2025 | during | 09-08-2025 | during | 09-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 367 | 336 | 400.75 | 400.75 | 370.8 | 370.8 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 330 | 450 | 450 | 450 | 450
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 284 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 14 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 13 | 33 | 33 | 25 | 25 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 23 | 23 | 23 | 23 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 25.01 | 25.01 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 13 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 15 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 14 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 375 | 380 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 70 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 1814 | 1863 | 5805.7 | 5779.7 | 3310.84 | 3284.84
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 3 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 174 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 151 | 150 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 80 | 80 | 56 | 72 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 37 | 42 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.72 | 0 | 2.25 | 0 | 2.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 560 | 655 | 1224 | 1224 | 809 | 1006 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 11 | 13 | 6 | 13 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 640 | 667 | 780 | 780 | 775 | 775 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1571.72 | 1770 | 3770.97 | 3769.72 | 3176.97 | 3413.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 30 | 113 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 350 | 320 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 41 | 41 | 46.7 | 46.7 | 41 | 41 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 50 | 48 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 107 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 138 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 24 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 4 | 29 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 55 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 23 | 101 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1012 | 1478 | 2424.56 | 2379.56 | 2236.36 | 2191.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-08-2025 | during | 09-08-2025 | during | 09-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 146 | 154 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 65 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 90 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.3 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 18 | 18 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 245.3 | 315 | 585.2 | 549 | 493.9 | 457.7
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 60 | 60 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 130 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 67 | 370 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 290 | 280 | 270 | 270 | 270 | 270 | Air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1001 | 1264 | 1375 | 1375 | 1250 | 1250
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 895 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 357 | 345 | 410 | 410 | 380 | 380 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 7 | 0 | 42 | 0 | 42 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 796 | 971 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2086 | 2249 | 3588.2 | 3546.2 | 3386 | 3344
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 298 | 330 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 640 | 800 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 269 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.12 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1411.12 | 1739 | 2162 | 2161 | 2072 | 2071
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 15.29 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 180 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | -
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 174 | 184 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 368 | 385 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.86 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 813.95 | 1003 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 8.89 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 19 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1576.99 | 1752 | 2964.47 | 2804.87 | 2798.4 | 2638.8
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 175 | 168 | 150 | 150 | 170 | 173 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 114 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 26 | 0 | 26 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 117 | 0 | 111.05 | 0 | 111.05 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 436.4 | 395 | 555.65 | 412 | 555.65 | 415
System Total |  |  |  |  | 28671.2 | 27843.665 | 11154.53 | 12825 | 23231.75 | 22777.05 | 19280.12 | 19066.42
Forecast Scenario (09-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12700 |  | 0 |  | 12700
|  |  |  | 1:00 | 12410 |  | 0 |  | 12410
|  |  |  | 2:00 | 11960 |  | 0 |  | 11960
|  |  |  | 3:00 | 11740 |  | 0 |  | 11740
|  |  |  | 4:00 | 11390 |  | 0 |  | 11390
|  |  |  | 5:00 | 11220 |  | 0 |  | 11220
|  |  |  | 6:00 | 10930 |  | 0 |  | 10930
|  |  |  | 7:00 | 11020 |  | 0 |  | 11020
|  |  |  | 8:00 | 11070 |  | 0 |  | 11070
|  |  |  | 9:00 | 11420 |  | 0 |  | 11420
|  |  |  | 10:00 | 11260 |  | 0 |  | 11260
|  |  |  | 11:00 | 11630 |  | 0 |  | 11630
|  |  |  | 12:00 | 12000 |  | 0 |  | 12000
|  |  |  | 13:00 | 12480 |  | 0 |  | 12480
|  |  |  | 14:00 | 12600 |  | 0 |  | 12600
|  |  |  | 15:00 | 12570 |  | 0 |  | 12570
|  |  |  | 16:00 | 12300 |  | 0 |  | 12300
|  |  |  | 17:00 | 11790 |  | 0 |  | 11790
|  |  |  | 18:00 | 11600 |  | 0 |  | 11600
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13140 |  | 0 |  | 13140
|  |  |  | 19:30 | 13910 |  | 0 |  | 13910
|  |  |  | 20:00 | 14110 |  | 0 |  | 14110
|  |  |  | 21:00 | 14150 |  | 0 |  | 14150
|  |  |  | 22:00 | 13940 |  | 0 |  | 13940
|  |  |  | 23:00 | 13850 |  | 0 |  | 13850
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 293.28 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:12 hrs on 09-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-08-2025 | [28 empty] | Date: | 08-08-2025 | [28 empty] | Date: | 08-08-2025 | [28 empty] | Date: | 08-08-2025 | [28 empty] | Date: | 08-08-2025 | [12 empty] | Date: | 08-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 40 | 17 | 51 | 15 | 0 | 0 | 17 | 130 | 0 | 350 | 302 | 370 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 65 | 0 | 0 | 25 | 12 | 0 | 204 | 0 | 40 | 770 | 0 | 0 | 0 | 0 | 50 | 130 | 0 | 0 | 0 | 580 | 0 | 51 | 2 | 16 | 0 | 357 | 330 | 51 | 199 | 39 | 68 | 70 | 180 | 59 | 19 | 76 | 44 | 52.2 | 0 | 44 | 315 | 270 | 260 | 0 | 30 | 157 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 94 | 170 | 131 | 0 | 0 | 0 | 7344.2 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 1311.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 198 | 0 | 198 | 0 | 414 | 0 | 0 | 178 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 298 | 1162 | 0 | 7268.22 | 14612.42 | 108.83
01:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 46 | 17 | 51 | 0 | 0 | 0 | 0 | 90 | 0 | 350 | 303 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 0 | 0 | 25 | 12 | 0 | 203 | 0 | 40 | 769 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 551 | 0 | 51 | 0 | 16 | 0 | 356 | 330 | 51 | 200 | 39 | 66 | 70 | 171 | 63 | 17 | 78 | 42 | 52.2 | 0 | 44 | 310 | 270 | 98 | 0 | 30 | 153 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 94 | 130 | 135 | 0 | 0 | 0 | 6893.2 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1177 | 0 | 1223.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 192 | 0 | 192 | 0 | 414 | 0 | 0 | 174 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 296 | 1156 | 0 | 7135.59 | 14028.79 | 108.82
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 24.5 | 17 | 51 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 303 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 25 | 12 | 0 | 203 | 0 | 40 | 770 | 0 | 0 | 0 | 0 | 51 | 150 | 0 | 0 | 0 | 566 | 0 | 51 | 0 | 16 | 0 | 356 | 330 | 51 | 197 | 39 | 68 | 70 | 175 | 65 | 14 | 78 | 40 | 52.2 | 0 | 44 | 310 | 270 | 11 | 0 | 30 | 153 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 94 | 100 | 137 | 0 | 0 | 0 | 6709.7 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1181 | 0 | 1210.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 193 | 0 | 193 | 0 | 402 | 0 | 0 | 171 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 296 | 1156 | 0 | 7044.42 | 13754.12 | 108.81
03:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 14.5 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 311 | 365 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 25 | 12 | 0 | 203 | 0 | 40 | 772 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 567 | 0 | 51 | 0 | 16 | 0 | 356 | 330 | 51 | 65 | 39 | 65 | 70 | 168 | 65 | 17 | 52 | 40 | 52.2 | 0 | 44 | 305 | 270 | 63 | 0 | 30 | 150 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 94 | 95 | 139 | 0 | 0 | 0 | 6500.2 | 891 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 1218.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 189 | 0 | 188 | 0 | 398 | 0 | 0 | 172 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 298 | 1103 | 0 | 6928.98 | 13429.18 | 108.8
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 307 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 41 | 760 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 562 | 0 | 51 | 0 | 80 | 0 | 356 | 330 | 51 | 0 | 39 | 51 | 50 | 177 | 65 | 17 | 14 | 38 | 52.2 | 0 | 44 | 315 | 270 | 3 | 0 | 30 | 157 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 94 | 95 | 152 | 0 | 0 | 0 | 6370.7 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 957 | 0 | 1229.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 198 | 0 | 197 | 0 | 414 | 0 | 0 | 171 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 120 | 220 | 0 | 298 | 1000 | 0 | 6620.88 | 12991.58 | 108.79
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 306 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 41 | 763 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 556 | 0 | 51 | 0 | 81 | 0 | 357 | 330 | 51 | 0 | 39 | 49 | 50 | 175 | 65 | 17 | 15 | 38 | 16 | 0 | 44 | 310 | 270 | 68 | 0 | 30 | 154 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 84 | 95 | 145 | 0 | 0 | 0 | 6362.5 | 890 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 0 | 1046.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 195 | 0 | 194 | 0 | 414 | 0 | 0 | 171 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 120 | 220 | 0 | 298 | 1000 | 0 | 6368.45 | 12730.95 | 108.78
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 365 | 0 | 0 | 280 | 0 | 0 | 1 | 70 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.22 | 163 | 0 | 42 | 762 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 560 | 1 | 51 | 0 | 81 | 0 | 357 | 330 | 51 | 0 | 40 | 48 | 50 | 170 | 64 | 17 | 14 | 34 | 0 | 1 | 0 | 305 | 270 | 66 | 0 | 30 | 145 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 95 | 145 | 0 | 0.5 | 0 | 6114.22 | 891 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 791 | 0 | 863.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0.54 | 185 | 0 | 180 | 0 | 185 | 0 | 341 | 0 | 0.1 | 173 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 3 | 0 | 0 | 218 | 120 | 220 | 0 | 298 | 800 | 0 | 5782.83 | 11897.05 | 108.77
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 312 | 370 | 0 | 0 | 280 | 0 | 0 | 4 | 52 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 1.42 | 163 | 0 | 31 | 638 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 565 | 5 | 5 | 0 | 8 | 0 | 300 | 330 | 51 | 0 | 40 | 16 | 50 | 136 | 66 | 19 | 16 | 34 | 0 | 2 | 0 | 320 | 270 | 67 | 0 | 30 | 142 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 75 | 150 | 0 | 3.14 | 0 | 5766.56 | 890 | 282 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 818 | 0 | 883.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.09 | 8 | 0 | 0.77 | 188 | 0 | 129 | 0 | 174 | 0 | 393 | 0 | 0.09 | 171 | 0 | 35 | 2 | 70 | 0 | 0 | 0.5 | 12 | 0.01 | 0 | 175 | 120 | 180 | 0 | 299 | 620 | 0 | 5496.74 | 11263.3 | 108.76
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 370 | 0 | 0 | 280 | 0 | 0 | 4 | 52 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 2.36 | 165 | 0 | 37 | 635 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 565 | 4 | 5 | 0 | 8 | 0 | 300 | 310 | 51 | 0 | 40 | 16 | 50 | 100 | 35 | 7 | 14 | 32 | 0 | 5 | 0 | 310 | 270 | 67 | 0 | 30 | 156 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 75 | 152 | 0 | 9.46 | 0 | 5636.82 | 883 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 807 | 0 | 862.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 36 | 0 | 12.41 | 175 | 0 | 125 | 0 | 172 | 0 | 408 | 0 | 2.32 | 171 | 0 | 35 | 4 | 70 | 0 | 0 | 0.4 | 52 | 0.01 | 0 | 172 | 120 | 180 | 0 | 298 | 607 | 0 | 5507 | 11143.82 | 108.74
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 370 | 0 | 0 | 280 | 0 | 0 | 2 | 17 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 1.12 | 205 | 0 | 37 | 635 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 570 | 7 | 5 | 0 | 8 | 0 | 300 | 280 | 51 | 0 | 41 | 15 | 50 | 51 | 8 | 7 | 0 | 30 | 0 | 12 | 0 | 300 | 270 | 67 | 0 | 30 | 134 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 75 | 55 | 152 | 1 | 21.63 | 0 | 5479.75 | 889 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 793 | 0 | 859.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.02 | 31 | 0 | 14.8 | 168 | 0 | 0 | 0 | 165 | 0 | 335 | 0 | 1.11 | 175 | 0 | 90 | 8 | 86 | 0 | 0 | 0.9 | 63 | 0.05 | 0 | 162 | 120 | 180 | 0 | 298 | 600 | 0 | 5364.11 | 10843.86 | 108.72
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 373 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 37 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 560 | 3 | 5 | 0 | 8 | 0 | 300 | 280 | 51 | 0 | 41 | 14 | 50 | 17 | 8 | 7 | 0 | 32 | 0 | 21 | 0 | 341 | 270 | 67 | 0 | 30 | 131 | 6 | 0 | 21 | 20 | 0 | 18 | 0 | 0 | 45 | 45 | 151 | 2 | 16.24 | 0 | 5182.24 | 888 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 775 | 0 | 822.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.61 | 15 | 0 | 9.14 | 165 | 0 | 0 | 0 | 161 | 0 | 348 | 0 | 0.68 | 175 | 0 | 50 | 9 | 105 | 0 | 0 | 4.9 | 86 | 0.14 | 0 | 172 | 120 | 180 | 0 | 298 | 596 | 0 | 5277.58 | 10459.82 | 108.7
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 370 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 37 | 579 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 570 | 4 | 5 | 0 | 8 | 0 | 300 | 280 | 50 | 0 | 41 | 15 | 50 | 16 | 13 | 11 | 0 | 34 | 0 | 21 | 0 | 341 | 290 | 67 | 0 | 30 | 135 | 6 | 0 | 21 | 20 | 0 | 18 | 0 | 0 | 45 | 45 | 146 | 0 | 7.53 | 0 | 5259.53 | 889 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.72 | 770 | 0 | 818.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 10 | 0 | 0.52 | 171 | 0 | 0 | 0 | 168 | 0 | 383 | 0 | 0.03 | 173 | 0 | 50 | 20 | 70 | 0 | 0 | 2.2 | 80 | 0.16 | 0 | 172 | 120 | 180 | 0 | 298 | 600 | 0 | 5255.15 | 10514.68 | 108.68
12:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 307 | 375 | 0 | 0 | 335 | 0 | 0 | 14 | 52 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.72 | 166 | 0 | 37 | 640 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 560 | 3 | 10 | 0 | 8 | 0 | 350 | 280 | 50 | 30 | 41 | 23 | 50 | 52 | 28 | 11 | 4 | 36 | 0 | 39 | 0 | 341 | 290 | 67 | 0 | 30 | 143 | 6 | 0 | 76 | 30 | 0 | 18 | 0 | 0 | 45 | 45 | 146 | 1 | 8.3 | 0 | 5644.02 | 888 | 357 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 796 | 0 | 813.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.29 | 19 | 0 | 8.89 | 177 | 0 | 0 | 0 | 174 | 0 | 368 | 0 | 0.86 | 175 | 0 | 70 | 0 | 70 | 0 | 0 | 4.4 | 117 | 0.12 | 0 | 173 | 120 | 180 | 0 | 298 | 640 | 0 | 5510.51 | 11154.53 | 108.67
13:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 400 | 0 | 0 | 333 | 0 | 0 | 13 | 32 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1.18 | 214 | 0 | 40 | 700 | 0 | 0 | 0 | 1 | 0 | 151 | 0 | 0 | 0 | 535 | 6 | 39 | 0 | 36 | 0 | 344 | 330 | 50 | 44 | 41 | 42 | 50 | 74 | 53 | 13 | 16 | 38 | 0 | 49 | 16 | 341 | 300 | 160 | 0 | 30 | 149 | 6 | 0 | 76 | 30 | 0 | 18 | 0 | 0 | 45 | 45 | 147 | 1 | 20.52 | 0 | 6076.7 | 895 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 790 | 0 | 862.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.24 | 14 | 0 | 13.26 | 185 | 0 | 0 | 0 | 183 | 0 | 373 | 0 | 0.89 | 172 | 0 | 90 | 35 | 88 | 0 | 0 | 4.8 | 76 | 0.11 | 0 | 173 | 120 | 180 | 0 | 298 | 760 | 0 | 5697.83 | 11774.53 | 108.65
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 12.9 | 2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 365 | 0 | 0 | 280 | 0 | 0 | 11 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.24 | 213 | 0 | 40 | 631 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 540 | 10 | 10 | 0 | 16 | 0 | 320 | 290 | 50 | 61 | 41 | 16 | 50 | 51 | 55 | 13 | 0 | 36 | 0 | 29 | 22 | 310 | 300 | 334 | 0 | 30 | 139 | 6 | 0 | 76 | 20 | 0 | 18 | 0 | 0 | 24 | 16 | 151 | 1 | 25.41 | 0 | 5800.55 | 895 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 760 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.06 | 36 | 0 | 20.3 | 173 | 0 | 0 | 0 | 176 | 0 | 380 | 0 | 1.14 | 172 | 0 | 50 | 4 | 105 | 0 | 0 | 0.6 | 34 | 0.36 | 0 | 173 | 100 | 180 | 0 | 257 | 620 | 0 | 5251.46 | 11052.01 | 108.63
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 300 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.49 | 213 | 0 | 40 | 590 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 560 | 14 | 10 | 0 | 8 | 0 | 295 | 280 | 50 | 61 | 40 | 16 | 70 | 34 | 35 | 13 | 0 | 34 | 0 | 47 | 23 | 310 | 280 | 334 | 0 | 30 | 134 | 6 | 0 | 76 | 20 | 0 | 18 | 0 | 0 | 24 | 16 | 152 | 1 | 7.54 | 3 | 5600.03 | 895 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 774 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.26 | 43 | 0 | 15.21 | 170 | 0 | 0 | 0 | 168 | 0 | 331 | 0 | 1.23 | 170 | 0 | 50 | 15 | 105 | 0 | 0 | 0.2 | 112 | 0.36 | 0 | 158 | 100 | 180 | 0 | 258 | 595 | 0 | 5265.26 | 10865.29 | 108.61
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 275 | 0 | 0 | 250 | 0 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.53 | 173 | 0 | 40 | 580 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 610 | 5 | 10 | 0 | 8 | 0 | 280 | 270 | 26 | 61 | 10 | 14 | 50 | 17 | 25 | 13 | 0 | 30 | 0 | 11 | 0 | 280 | 280 | 310 | 0 | 30 | 133 | 6 | 0 | 7 | 20 | 0 | 18 | 0 | 0 | 8 | 0 | 152 | 1 | 13.42 | 6 | 5139.95 | 895 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 749 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.15 | 40 | 0 | 14.76 | 130 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 1.54 | 170 | 0 | 43 | 13 | 34 | 0 | 0 | 0.9 | 39 | 0.19 | 0 | 175 | 100 | 180 | 0 | 264 | 500 | 0 | 5000.54 | 10140.49 | 108.6
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 293 | 260 | 0 | 0 | 250 | 0 | 0 | 4 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 173 | 0 | 40 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 580 | 3 | 10 | 0 | 8 | 0 | 280 | 270 | 5 | 39 | 10 | 16 | 50 | 16 | 25 | 13 | 0 | 30 | 0 | 2 | 0 | 240 | 280 | 310 | 0 | 30 | 140 | 6 | 0 | 7 | 20 | 0 | 18 | 0 | 0 | 8 | 0 | 153 | 0 | 4.13 | 6 | 4973.05 | 895 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 742 | 0 | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.99 | 14 | 0 | 5.99 | 130 | 0 | 0 | 0 | 140 | 0 | 358 | 0 | 0.46 | 171 | 0 | 35 | 2 | 70 | 0 | 0 | 1.1 | 20 | 0.15 | 0 | 172 | 100 | 180 | 0 | 262 | 500 | 0 | 4892.69 | 9865.74 | 108.59
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 304 | 265 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 174 | 0 | 40 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 580 | 1 | 10 | 0 | 8 | 0 | 280 | 270 | 10 | 52 | 41 | 15 | 70 | 16 | 25 | 13 | 0 | 32 | 0 | 3 | 0 | 240 | 280 | 310 | 0 | 30 | 140 | 6 | 0 | 7 | 20 | 0 | 18 | 0 | 0 | 8 | 0 | 153 | 0 | 0.25 | 6 | 5115.44 | 895 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.24 | 742 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 3 | 0 | 1.75 | 135 | 0 | 0 | 0 | 150 | 0 | 394 | 0 | 0 | 170 | 0 | 34 | 1 | 70 | 0 | 0 | 0.2 | 1 | 0.02 | 0 | 178 | 100 | 180 | 0 | 262 | 500 | 0 | 4921.08 | 10036.52 | 108.58
19:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 5 | 0 | 25 | 0 | 0 | 0 | 3 | 15 | 0 | 330 | 283 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 24 | 0 | 174 | 0 | 42 | 665 | 17 | 0 | 3 | 0 | 0 | 150 | 0 | 0 | 0 | 590 | 0 | 36 | 0 | 93 | 0 | 315 | 325 | 36 | 65 | 41 | 27 | 70 | 21 | 55 | 13 | 12 | 38 | 1 | 0 | 0 | 240 | 280 | 366 | 0 | 30 | 150 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 45 | 46 | 153 | 0 | 0 | 6 | 6163 | 895 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 180 | 0 | 414 | 0 | 0 | 170 | 0 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 120 | 220 | 0 | 330 | 565 | 0 | 5723 | 11886 | 108.57
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 14 | 0 | 34 | 0 | 0 | 0 | 0 | 15 | 13 | 330 | 284 | 380 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 24 | 0 | 174 | 0 | 42 | 667 | 17 | 0 | 18 | 0 | 0 | 150 | 0 | 0 | 0 | 655 | 0 | 51 | 0 | 107 | 0 | 320 | 330 | 48 | 113 | 41 | 101 | 70 | 138 | 55 | 13 | 29 | 38 | 24 | 0 | 0 | 320 | 280 | 370 | 0 | 30 | 130 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 90 | 65 | 154 | 0 | 0 | 6 | 6690 | 895 | 345 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 971 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 184 | 0 | 385 | 0 | 0 | 168 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 120 | 220 | 0 | 330 | 800 | 0 | 6135 | 12825
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 330 | 291 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0 | 174 | 0 | 42 | 668 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 656 | 0 | 51 | 0 | 108 | 0 | 320 | 330 | 47 | 127 | 41 | 93 | 70 | 132 | 55 | 19 | 32 | 38 | 25 | 0 | 0 | 310 | 280 | 371 | 0 | 30 | 130 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 90 | 45 | 154 | 0 | 0 | 6 | 6630 | 898 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 925 | 0 | 969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 177 | 0 | 363 | 0 | 0 | 174 | 0 | 114 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 120 | 220 | 0 | 331 | 785 | 0 | 5977 | 12607 | 108.56
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 330 | 309 | 415 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 13 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 24 | 0 | 221 | 0 | 36 | 671 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 678 | 0 | 51 | 0 | 108 | 0 | 320 | 330 | 50 | 211 | 41 | 106 | 70 | 142 | 56 | 19 | 34 | 40 | 25 | 0 | 0 | 320 | 280 | 385 | 0 | 30 | 145 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 94 | 45 | 153 | 0 | 0 | 6 | 6924 | 901 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 184 | 0 | 390 | 0 | 0 | 178 | 0 | 114 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 120 | 220 | 0 | 331 | 800 | 0 | 5768 | 12692 | 108.55
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 330 | 309 | 420 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 221 | 0 | 36 | 668 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 620 | 0 | 51 | 0 | 108 | 0 | 320 | 330 | 50 | 212 | 41 | 110 | 70 | 155 | 63 | 19 | 33 | 40 | 25 | 0 | 0 | 325 | 280 | 387 | 0 | 30 | 149 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 94 | 45 | 154 | 0 | 0 | 6 | 6909 | 902 | 395 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 826 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 187 | 0 | 414 | 0 | 0 | 178 | 0 | 114 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 120 | 220 | 0 | 331 | 800 | 0 | 5819 | 12728 | 108.54
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 309 | 400 | 0 | 0 | 260 | 0 | 0 | 0 | 70 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 221 | 0 | 42 | 716 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 155 | 0 | 355 | 330 | 50 | 197 | 41 | 107 | 50 | 154 | 64 | 19 | 32 | 42 | 25 | 0 | 0 | 315 | 280 | 385 | 0 | 30 | 159 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 94 | 45 | 156 | 0 | 0 | 6 | 6882.5 | 901 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 856 | 0 | 962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 208 | 0 | 414 | 0 | 0 | 180 | 0 | 114 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 120 | 220 | 0 | 332 | 887 | 0 | 6067 | 12949.5 | 108.53
Total KWH | 0 | 253440 | 216163 | 0 | 0 | 0 | 0 | 0 | 8582400 | 0 | 0 | 115920 | 165240 | 1161504 | 0 | 0 | 0 | 24438 | 247680 | 45120 | 8043500 | 7275695 | 8581335 | 0 | 0 | 7288076 | 0 | 0 | 75568 | 1137600 | 371400 | 293040 | 0 | 0 | 0 | 0 | 0 | 0 | 377760 | 75397 | 0 | 0 | 89280 | 163200 | 14578 | 4621895 | 27600 | 956640 | 16160000 | 48509 | 0 | 15360 | 10657.8 | 175636 | 3345771 | 145000 | 0 | 0 | 13881817 | 62775 | 826862 | 26763 | 1104000 | 0 | 8150000 | 7550000 | 1088160 | 1865000 | 910584 | 1152960 | 1356690 | 2480160 | 1168440 | 334880 | 506160 | 868800 | 393864 | 235855 | 0 | 7476500 | 6668000 | 5055000 | 0 | 675960 | 3487009 | 157584 | 0 | 1530240 | 649152 | 0 | 432000 | 0 | 38520 | 1521600 | 1406400 | 3475200 | 7950 | 136780 | 58320 | 146845387.8 | 21624000 | 7802496 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 126720 | 20530910 | 0 | 21942909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126617 | 249110 | 0 | 144752 | 4355364 | 0 | 0 | 0 | 4504527 | 0 | 9221745 | 0 | 12840 | 4255000 | 0 | 1683320 | 123281 | 1989264 | 0 | 0 | 19518.48 | 712080 | 1749 | 0 | 4800000 | 2765000 | 5172190 | 0 | 7184736 | 19121454.55 | 0 | 139381583.03 | 286226970.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11154.53 | MW | 12:00 Hr. | Energy Generated |  |  | 286.227 |  | MKWHr.
| Day Peak Demand |  |  | 11154.53 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12825 | MW | 19:30 Hr. | Energy Demand |  |  | 286.227 |  | MKWHr.
| Evening Peak Demand |  |  | 12825 | MW | 19:30 Hr. | Maximum Temperature |  |  | 29.6 |  | °C
| Minimum Generation of the Day |  |  | 9865.74 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 949.76 |  | MMCFD
| Maximum Generation of the Day |  |  | 14612.42 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.3639 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.4354 | 0 | 3.3671 | 0 | 0 | 0.075568 | 0 | 0 | 43.8781 | Gas | 131.352 | Gas | 469909053.57
| Chattogram Zone |  |  | 4.3024 | 30.0418 | 0.60564 | 0.145 | 4.6219 | 0.077353 | 0 | 0.37776 | 40.1719 | Coal | 85.9339 | Coal | 505240590.6755
| Cumilla Zone |  |  | 23.1862 | 0 | 5.7283 | 0 | 0 | 0.23586 | 0.8688 | 0 | 30.0192 | HFO | 16.3985 | HFO | 301301198.806
| Mymensingh Zone |  |  | 3.4752 | 0 | 3.0248 | 0 | 0 | 0.14473 | 0 | 0 | 6.6448 | HSD | 0.145 | HSD | 506050
| Sylhet Zone |  |  | 26.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1314 | Hydro | 4.6219 | Hydro | 462189.5
| Khulna Zone |  |  | 7.8025 | 20.5309 | 0 | 0 | 0 | 0.12672 | 22.536 | 0 | 50.9961 | Solar | 2.0502 | Solar | 31633102.7828
| Barishal Zone |  |  | 7.9372 | 31.1062 | 0 | 0 | 0 | 0.001749 | 0 | 0 | 39.0451 | Import | 45.3477 | Import | 220708778.31
| Rajshahi Zone |  |  | 18.0816 | 0 | 0 | 0 | 0 | 0.53332 | 21.9429 | 0 | 40.5579 | Wind | 0.37776 | Wind | 5530406.4
| Rangpur Zone |  |  | 0 | 4.255 | 3.6726 | 0 | 0 | 0.85488 | 0 | 0 | 8.7825
| Total |  |  | 131.352 | 85.9339 | 16.3985 | 0.145 | 4.6219 | 2.0502 | 45.3477 | 0.37776 | 286.227
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 469909053.57 |  | Hydro | 462189.5
|  |  |  | Coal | 505240590.6755 |  | Solar | 31633102.7828
|  |  |  | HFO | 301301198.806 |  | Import | 220708778.31
|  |  |  | HSD | 506050 |  | Wind | 5530406.4
[5 empty] | Total: | 153,52,91,370 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.624 | Peak Hr Flow | 895.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45090691.01 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.9429 | Peak Hr Flow | 1003.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 882 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8688 | Peak Hr Flow | 38.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1130 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.4357 | Peak Hr Flow | 1936.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3958
|  |  |  | Chattogram |  | 0 |  | 1326
|  |  |  | Cumilla |  | 0 |  | 1205
|  |  |  | Mymensingh |  | 0 |  | 1108
|  |  |  | Sylhet |  | 0 |  | 530
|  |  |  | Khulna |  | 0 |  | 1489
|  |  |  | Barishal |  | 0 |  | 414
|  |  |  | Rajshahi |  | 0 |  | 1313
|  |  |  | Rangpur |  | 0 |  | 920
|  |  |  | Total |  | 0 |  | 12263
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 08:13 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 08:13 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 08:17 | 17:20 | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end Due to
Project work S/D and from Mahasthangarh 132/33kV end Due to Re conductoring purpose.
|  | 08:30 | Bhulta 132/33kV S/S GT1 LT is restored.
| 09:29 | 12:50 | Bhulta 132/33kV S/S GT1 LT Tripped showing No relays Due to 33 KV incomer breaker Trip | [7 empty] | 58.0MW load
interrup.
| 09:29 | 20:21 | Bhulta 132/33kV S/S GT2 LT Tripped showing No relays Due to 33 KV incomer breaker Trip | [7 empty] | 58.0MW load
interrup.
| 09:39 | 12:16 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Instruction by NLDC
| 10:14 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 11:37 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 12:00 |  | Day Peak Generation: 11150 MW.
| 12:04 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
|  | 12:19 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 12:20 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
| 12:35 |  | Raozan 25 MW PP Synchronized
| 14:21 |  | Raozan 25 MW PP Shutdown
| 15:30 | 20:21 | Bhulta 132/33kV S/S GT1 LT Tripped showing No relays Due to 33 KV incomer of GT-1 CB Trip | [7 empty] | 80.0MW load
interrup.
| 16:30 |  | Rooppur 230kV Bus-1 and Bus-2 were energized for the first time by 400/230kV 522MVA
ATT-10 transformer, without prior permission from NLDC.
| 18:55 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 19:03 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO ON @ 18:45 as per NLDC demand.
| 19:30 |  | Evening Peak Generation 12825 MW.
| 20:25 |  | Rooppur 230kV Bus-1 and Bus-2 were de-energized, without prior permission from NLDC.
| 21:00 |  | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to 33 KV Bus at PBS Area Maintenance | [7 empty] | 80.0MW load
interrup.
| 21:02 |  | Bhulta 132/33kV S/S GT1 LT Scheduled S/D Due to 33 KV Bus at PBS Area Maintenance | [7 empty] | 80.0MW load
interrup.
| 00:59 | 01:26 | Barapukuria-Saidpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing ABB | [7 empty] | and 165.0MW load
|  |  | REL 511 relays. and from Saidpur 132/33kV end showing No relay. relays Due to Over Load | [7 empty] | interrup. Saidpur
132/33kV end
| 00:59 | 01:33 | Barapukuria-Saidpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing ABB
REL 511 relays.
| 01:01 | 01:37 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing 67 Direct Over | [7 empty] | 165.0MW load
|  |  | Current. relays Due to Over Current. | [7 empty] | interrup. Saidpur
132/33kV end
| 03:20 |  | Daudkandi-Sonargaon 132 kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to Haripur
circuit over current
| 04:35 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- None
| 04:35 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1 SD & GT-2 Running.
| 04:35 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
| 06:03 | 07:32 | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end.
| 06:11 | 06:25 | Noapara 132/33kV S/S T-1 LT Tripped showing O/C relays Due to REB-2 (O/C ins: & E/F ins:) | [7 empty] | 30.0MW load
|  |  | REB-4 (O/C ins: & E/F ins:) 33Kv feeder Fault. | [7 empty] | interrup.
| 06:11 | 06:25 | Noapara 132/33kV S/S T-2 LT Tripped showing O/C relays Due to REB-2 (O/C ins: & E/F ins:) | [7 empty] | 30.0MW load
|  |  | REB-4 (O/C ins: & E/F ins:) 33Kv feeder Fault. | [7 empty] | interrup.
| 06:14 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Pbs
33kV bus working.
| 06:15 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Pbs
33kV bus working
| 06:19 | 07:55 | Natore 132/33kV S/S TR-1 (405 T) LT Forced S/D | [7 empty] | 29.0MW load
interrup.
| 06:19 | 07:54 | Natore 132/33kV S/S TR-2 (415 T) LT Forced S/D | [7 empty] | 29.0MW load
interrup.
| 06:20 | 07:52 | Natore 132/33kV S/S TR-1 (405 T) HT Forced S/D Due to Red hot maintainanc | [7 empty] | 29.0MW load
interrup.
| 06:20 | 07:53 | Natore 132/33kV S/S TR-2 (415 T) HT Forced S/D Due to Red hot maintainance | [7 empty] | 29.0MW load
interrup.
| 07:12 |  | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to To fix red hot in
incomer -02 D/S
| 07:13 |  | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to To fix red hot in
incomer -02 D/S
| 07:27 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Mahasthangarh 132/33kV end Due
to Reconducting
| 07:32 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Hot Spot Maintenance | [7 empty] | 50.0MW load
interrup.
| 07:32 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Hot Spot Maintenance | [7 empty] | 50.0MW load
interrup.
| 07:40 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end.
| 07:40 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end.
| 07:40 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end.
| 07:41 |  | Cumilla(S) 132/33kV S/S Cumilla North-2 Scheduled S/D
| 07:44 |  | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to T1 Transformer S/D due to PDB division 01 | [7 empty] | 35.0MW load
|  |  | maintenance work . | [7 empty] | interrup.
| 07:44 |  | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to T1 Transformer S/D due to PDB division 01 | [7 empty] | 35.0MW load
|  |  | maintenance work . | [7 empty] | interrup.
| 07:46 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken for spmd works
|  | 07:53 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
| 07:54 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33kv Korapur feeder bus DS maintenance | [7 empty] | 10.0MW load
interrup.
| 07:55 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33kv Korapur feeder bus ds maintenance | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 336 | 8582400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 8043500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 284 | 7275695 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7288076 | machine problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 14 | 115920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 24438 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 371400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 293040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 216163 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 1161504 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 253440 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 13 | 45120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 15 | 247680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 75568 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 165240 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 380 | 8581335 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1137600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 1863 | 43878119
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 10657.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 62775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 15360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 174 | 4621895 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3345771 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 145000 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 175636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 75397 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 89280 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 956640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14578 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 27600 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 163200 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 48509 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 655 | 13881817 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 377760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 667 | 16160000 | Machine Problem
Chattogram Area Total |  |  |  |  | 5120.72 | 1920 | 40171875.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 113 | 1865000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 8150000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7550000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 41 | 910584 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1088160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 107 | 1104000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 826862 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 26763 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1356690 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 138 | 2480160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 38 | 868800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 24 | 393864 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 334880 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 29 | 506160 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 1168440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1152960 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 235855 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1478 | 30019178
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 154 | 3475200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 1406400 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 90 | 1521600 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 136780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 58320 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 38520 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 315 | 6644770
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 675960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3487009 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 649152 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1530240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 157584 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7476500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 5055000 | ST shutdown due to maitenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 280 | 6668000 | -
Sylhet Area Total |  |  |  |  | 2325 | 1264 | 26131445
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 895 | 21624000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 345 | 7802496 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 126720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 971 | 20530910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2249 | 50996126
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 330 | 7184736 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2765000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 19121454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5172190 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 269 | 4800000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1749 | -
Barishal Area Total |  |  |  |  | 2236 | 1739 | 39045129.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 126617 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4355364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 184 | 4504527 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 385 | 9221745 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 12840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1003 | 21942909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 144752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 249110 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 1752 | 40557864
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 4255000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1989264 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19518.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1683320 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 123281 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 712080 | -
Rangpur Area Total |  |  |  |  | 950 | 395 | 8782463.48
Eastern Grid Total |  |  |  |  | 17626.505 | 6840 | 146845387.8
Western Grid Total |  |  |  |  | 10442.16 | 6135 | 139381583.03
National Grid Total |  |  |  |  | 28068.665 | 12975 | 286226970.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8127.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4135.5 | MW
i) Dhaka area |  |  | 3958.16 |  | MW | i) Khulna area |  |  |  | 1489 | MW
ii) Chattogram area |  |  | 1326.3 |  | MW | ii) Barishal area |  |  |  | 413.5 | MW
iii) Cumilla area |  |  | 1205.07 |  | MW | iii) Rajshahi area |  |  |  | 1313 | MW
iv) Mymensingh area |  |  | 1108 |  | MW | iv) Rangpur area |  |  |  | 920 | MW
v) Sylhet area |  |  | 530 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12263.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 74 | 00:00 | 133 | PHP | 9 | 09:00
2 | AKSML | 147 | 05:00 | 68 | Ishurdi | 74 | 00:00 | 134 | Pabna | 115 | 00:00
3 | Aftabnagar | 34 | 01:00 | 69 | Jaldhaka | 86 | 00:00 | 135 | Palashbari | 98 | 00:00
4 | Agargaon | 111 | 00:00 | 70 | Jamalpur | 130 | 19:30 | 136 | Panchagarh | 49 | 00:00
5 | Agrabad | 72 | 00:00 | 71 | Jashore | 118 | 00:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 25 | 00:00 | 72 | Jhenaidah | 116 | 00:00 | 138 | Patuakhali | 63 | 23:00
7 | Ashuganj | 85 | 02:00 | 73 | Joydebpur | 125 | 00:00 | 139 | Payra | 32 | 00:00
8 | BSRM | 201 | 01:00 | 74 | Joypurhat | 61 | 00:00 | 140 | Postogola | 54 | 00:00
9 | Bagerhat | 77 | 00:00 | 75 | Juldah | 14.5 | 00:00 | 141 | Purbachal | 20 | 00:00
10 | Bajitpur | 76 | 00:00 | 76 | KSRM | 22 | 15:00 | 142 | Purbasadipur | 126 | 01:00
11 | Bakulia | 76 | 00:00 | 77 | Kabirpur | 222 | 00:00 | 143 | Rahanpur | 38 | 21:00
12 | Banani | 30 | 12:00 | 78 | Kachua | 86 | 00:00 | 144 | Rahim | 32 | 00:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 93 | 01:00 | 145 | Rajbari | 78 | 00:00
14 | Barapukuria | 65 | 01:00 | 80 | Kalurghat | 28 | 00:00 | 146 | Rajendrapur | 127 | 01:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 68 | 00:00 | 147 | Rajshahi | 109 | 21:00
16 | Barishal | 100 | 23:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 82 | 13:00
17 | Barishal-230 | 86 | 00:00 | 83 | Kasba | 32 | 00:00 | 149 | Ramganj | 114 | 23:00
18 | Baroaulia | 54 | 23:00 | 84 | Kazla | 88 | 00:00 | 150 | Rampur | 37 | 00:00
19 | Baroirhat | 63 | 01:00 | 85 | Keranigonj | 88 | 00:00 | 151 | Rangamati | 15 | 19:30
20 | Bashundhara | 167 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Rangpur | 146 | 00:00
21 | BashundharaCement | 6 | 00:00 | 87 | Khulna | 58 | 00:00 | 153 | Ruppur | 6.2 | 11:00
22 | Beanibazar | 70 | 00:00 | 88 | Khulshi | 154 | 20:00 | 154 | SSM | 13 | 00:00
23 | Benapole | 57 | 00:00 | 89 | Kishoreganj | 120 | 00:00 | 155 | Saidpur | 101 | 00:00
24 | Bhaluka | 145 | 00:00 | 90 | Kodda | 263 | 00:00 | 156 | Satkhira | 118 | 19:30
25 | Bhandaria | 51 | 01:00 | 91 | Kulaura | 46 | 00:00 | 157 | Satmasjid | 87 | 13:00
26 | Bhangura | 34 | 00:00 | 92 | Kurigram | 66 | 00:00 | 158 | Savar | 186 | 00:00
27 | Bheramara(GK) | 60 | 00:00 | 93 | Kushtia | 140 | 00:00 | 159 | SevenRings | 4.78 | 01:00
28 | Bhulta | 229 | 00:00 | 94 | Laksam | 21 | 00:00 | 160 | ShahCement | 21 | 00:00
29 | Bog-Sherpur | 74 | 00:00 | 95 | Lakshmipur | 19 | 00:00 | 161 | Shahjadpur | 75 | 00:00
30 | Bogura | 140 | 05:00 | 96 | Lalbag | 37 | 00:00 | 162 | Shahjibazar | 112 | 00:00
31 | Borhanuddin | 92 | 00:00 | 97 | Lalmonirhat | 63 | 19:30 | 163 | Shahmirpur | 51 | 00:00
32 | Brahmanbaria | 116 | 21:00 | 98 | MI_Cement | 15.8 | 01:00 | 164 | Shariatpur | 84 | 01:00
33 | Cantonment | 120 | 13:00 | 99 | Madanganj | 38 | 13:00 | 165 | Sherpur | 146 | 00:00
34 | Chandina | 17.77 | 19:00 | 100 | Madaripur | 104 | 00:00 | 166 | Shikalbaha | 8 | 00:00
35 | Chandpur | 78 | 01:00 | 101 | Madartek | 86.33 | 00:00 | 167 | Shitalakhya | 61.3 | 00:00
36 | Chandraghona | 33 | 19:00 | 102 | Madunaghat | 48 | 13:00 | 168 | Sholosohor | 39 | 00:00
37 | Chapai | 61 | 21:00 | 103 | Magura | 61 | 00:00 | 169 | Shyampur | 178 | 00:00
38 | Charsaidpur | 38 | 10:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Siddhirganj | 97 | 00:00
39 | Chauddagram | 62 | 01:00 | 105 | Maijdee | 14 | 00:00 | 171 | Sirajganj | 98 | 00:00
40 | Chhatak | 33 | 22:00 | 106 | Manikganj | 125 | 00:00 | 172 | Sonargaon | 103 | 00:00
41 | Chowmuhani | 179 | 00:00 | 107 | Maniknagar | 68 | 13:00 | 173 | Sreemongol | 76 | 00:00
42 | Chuadanga | 100 | 00:00 | 108 | Matarbari | 45 | 00:00 | 174 | Sreepur | 91 | 00:00
43 | Coxsbazar | 125 | 00:00 | 109 | Matuail | 58 | 00:00 | 175 | Srinagar | 46.72 | 00:00
44 | Cumilla(N) | 132 | 00:00 | 110 | Millgate | 106 | 00:00 | 176 | Sunamganj | 52 | 01:00
45 | Cumilla(S) | 140 | 00:00 | 111 | Mirpur | 106 | 13:00 | 177 | Sylhet | 45 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 9 | 00:00 | 178 | Sylhet-132 | 101 | 00:00
47 | Daudkandi | 142 | 00:00 | 113 | Mirzapur | 46 | 00:00 | 179 | TK | 31 | 00:00
48 | Dhaka | 34 | 00:00 | 114 | Mithapukur | 66 | 00:00 | 180 | Tangail | 172 | 00:00
49 | Dhamrai | 114 | 00:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 22 | 00:00
50 | Dhanmondi | 100 | 13:00 | 116 | Mogbazar | 111.6 | 13:00 | 182 | Thakurgaon | 102 | 22:00
51 | Dohazari | 101 | 00:00 | 117 | Mongla | 36 | 00:00 | 183 | Tongi | 98 | 00:00
52 | Faridpur | 159 | 01:00 | 118 | Motijheel | 35 | 13:00 | 184 | Ullahpara | 36 | 00:00
53 | Fatullah | 77 | 00:00 | 119 | Muktagacha | 34 | 00:00 | 185 | Ullon | 38 | 00:00
54 | Fenchuganj | 39 | 00:00 | 120 | Munshiganj | 104 | 00:00 | 186 | Uttara | 64 | 19:00
55 | Feni | 98 | 00:00 | 121 | Muradnagar | 37 | 00:00 | 187 | UttaraNew | 56 | 00:00
56 | GPH | 77 | 03:00 | 122 | Mymensingh | 182 | 00:00 | 188 | Zigatola | 66 | 13:00
57 | Ghatail | 78 | 00:00 | 123 | Naogaon | 124 | 00:00
58 | Ghorashal | 12 | 00:00 | 124 | Narail | 54.5 | 00:00
59 | Ghorashal-230 | 98 | 21:00 | 125 | Narinda | 54 | 00:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 174 | 00:00
61 | Gollamari | 86 | 00:00 | 127 | Natore | 136 | 23:00
62 | Gopalganj | 98.4 | 00:00 | 128 | Nawabganj | 56.8 | 00:00
63 | Gulshan | 78 | 12:00 | 129 | Netrakona | 136 | 19:30
64 | Halishahar | 38 | 00:00 | 130 | New | 55 | 00:00
65 | HaripurSBU | 143 | 04:00 | 131 | Niamatpur | 70 | 22:00
66 | Hasnabad | 67 | 00:00 | 132 | Noapara | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14612.42 | 0 |  | 14612.42
1:00 | 14028.79 | 0 |  | 14028.79
2:00 | 13754.12 | 0 |  | 13754.12
3:00 | 13429.18 | 0 |  | 13429.18
4:00 | 12991.58 | 0 |  | 12991.58
5:00 | 12730.95 | 0 |  | 12730.95
6:00 | 11897.05 | 0 |  | 11897.05
7:00 | 11263.3 | 0 |  | 11263.3
8:00 | 11143.82 | 0 |  | 11143.82
9:00 | 10843.86 | 0 |  | 10843.86
10:00 | 10459.82 | 0 |  | 10459.82
11:00 | 10514.68 | 0 |  | 10514.68
12:00 | 11154.53 | 0 |  | 11154.53
13:00 | 11774.53 | 0 |  | 11774.53
14:00 | 11052.01 | 0 |  | 11052.01
15:00 | 10865.29 | 0 |  | 10865.29
16:00 | 10140.49 | 0 |  | 10140.49
17:00 | 9865.74 | 0 |  | 9865.74
18:00 | 10036.52 | 0 |  | 10036.52
19:00 | 11886 | 0 |  | 11886
19:30 | 12825 | 0 |  | 12825
20:00 | 12607 | 0 |  | 12607
21:00 | 12692 | 0 |  | 12692
22:00 | 12728 | 0 |  | 12728
23:00 | 12949.5 | 0 |  | 12949.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7344.2 | 7268.22 | 14612.42 | DAILY GENERATION CURVE
00:30 | 7118.7 | 7201.905 | 14320.605
01:00 | 6893.2 | 7135.59 | 14028.79 | 08-08-2025
01:30 | 6801.45 | 7090.005 | 13891.455
02:00 | 6709.7 | 7044.42 | 13754.12
02:30 | 6604.95 | 6986.7 | 13591.65
03:00 | 6500.2 | 6928.98 | 13429.18
03:30 | 6435.45 | 6774.93 | 13210.38
04:00 | 6370.7 | 6620.88 | 12991.58
04:30 | 6366.6 | 6494.665 | 12861.265
05:00 | 6362.5 | 6368.45 | 12730.95
05:30 | 6238.36 | 6075.64 | 12314
06:00 | 6114.22 | 5782.83 | 11897.05
06:30 | 5940.39 | 5639.785 | 11580.175
07:00 | 5766.56 | 5496.74 | 11263.3
07:30 | 5701.69 | 5501.87 | 11203.56
08:00 | 5636.82 | 5507 | 11143.82
08:30 | 5558.285 | 5435.555 | 10993.84
09:00 | 5479.75 | 5364.11 | 10843.86
09:30 | 5330.995 | 5320.845 | 10651.84
10:00 | 5182.24 | 5277.58 | 10459.82
10:30 | 5220.885 | 5266.365 | 10487.25
11:00 | 5259.53 | 5255.15 | 10514.68
11:30 | 5451.775 | 5382.83 | 10834.605
12:00 | 5644.02 | 5510.51 | 11154.53
12:30 | 5860.36 | 5604.17 | 11464.53
13:00 | 6076.7 | 5697.83 | 11774.53
13:30 | 5938.625 | 5474.645 | 11413.27
14:00 | 5800.55 | 5251.46 | 11052.01
14:30 | 5700.29 | 5258.36 | 10958.65
15:00 | 5600.03 | 5265.26 | 10865.29
15:30 | 5369.99 | 5132.9 | 10502.89
16:00 | 5139.95 | 5000.54 | 10140.49
16:30 | 5056.5 | 4946.615 | 10003.115
17:00 | 4973.05 | 4892.69 | 9865.74
17:30 | 5044.245 | 4906.885 | 9951.13
18:00 | 5115.44 | 4921.08 | 10036.52
18:30 | 5639.22 | 5322.04 | 10961.26
19:00 | 6163 | 5723 | 11886
19:30 | 6690 | 6135 | 12825
20:00 | 6630 | 5977 | 12607
20:30 | 6777 | 5872.5 | 12649.5 |  | Executive Engineer
21:00 | 6924 | 5768 | 12692 |  | Network Operation Division
21:30 | 6916.5 | 5793.5 | 12710
22:00 | 6909 | 5819 | 12728
22:30 | 6895.75 | 5943 | 12838.75
23:00 | 6882.5 | 6067 | 12949.5

## En-Curve
QF-LDC-12
Date | 08-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4057 | 2025 | 890 | 38 | 44 | 1311.22 | 204 | 4458 | 0 | 298 | 1268.2 | 0 | 0 | 19 | 0 | DAILY ENERGY CURVE
00:30 | 3898 | 2015.5 | 890 | 38 | 43 | 1267.405 | 203.5 | 4429.5 | 0 | 286 | 1232.2 | 0 | 0 | 17.5 | 0 | 08-08-2025
01:00 | 3739 | 2006 | 890 | 38 | 42 | 1223.59 | 203 | 4401 | 0 | 274 | 1196.2 | 0 | 0 | 16 | 0
01:30 | 3767 | 2001 | 890 | 38 | 41 | 1217.005 | 203 | 4408 | 0 | 219 | 1091.45 | 0 | 0 | 16 | 0 | Energy Generated | 286.227 |  | MKWHr
02:00 | 3795 | 1996 | 890 | 38 | 40 | 1210.42 | 203 | 4415 | 0 | 164 | 986.7 | 0 | 0 | 16 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3740.5 | 2000.25 | 890.5 | 38 | 40 | 1214.7 | 203 | 4381 | 0 | 155.5 | 907.7 | 0 | 0 | 20.5 | 0 | Total Energy Requirement | 286.227 |  | MKWHr
03:00 | 3686 | 2004.5 | 891 | 38 | 40 | 1218.98 | 203 | 4347 | 0 | 147 | 828.7 | 0 | 0 | 25 | 0
03:30 | 3652.5 | 2040 | 890.5 | 38 | 39 | 1224.43 | 203 | 4157.5 | 0 | 138.5 | 799.95 | 0 | 0 | 27 | 0
04:00 | 3619 | 2075.5 | 890 | 38 | 38 | 1229.88 | 203 | 3968 | 0 | 130 | 771.2 | 0 | 0 | 29 | 0
04:30 | 3647 | 2071.5 | 890 | 38 | 38 | 1138.165 | 203 | 3932 | 0 | 130 | 746.6 | 0 | 0 | 27 | 0
05:00 | 3675 | 2067.5 | 890 | 38 | 38 | 1046.45 | 203 | 3896 | 0 | 130 | 722 | 0 | 0 | 25 | 0
05:30 | 3585 | 2035.5 | 890.5 | 38 | 36 | 955.155 | 183 | 3749 | 3.845 | 108 | 705 | 0 | 0 | 25 | 0
06:00 | 3495 | 2003.5 | 891 | 38 | 34 | 863.86 | 163 | 3602 | 7.69 | 86 | 688 | 0 | 0 | 25 | 0
06:30 | 3430.5 | 1933.75 | 890.5 | 38 | 34 | 873.57 | 163 | 3444 | 27.355 | 73 | 647 | 0 | 0 | 25.5 | 0
07:00 | 3366 | 1864 | 890 | 38 | 34 | 883.28 | 163 | 3286 | 47.02 | 60 | 606 | 0 | 0 | 26 | 0
07:30 | 3346.5 | 1858 | 886.5 | 38 | 33 | 872.815 | 164 | 3270.5 | 92.745 | 60 | 561.5 | 0 | 0 | 20 | 0
08:00 | 3327 | 1852 | 883 | 38 | 32 | 862.35 | 165 | 3255 | 138.47 | 60 | 517 | 0 | 0 | 14 | 0
08:30 | 3200 | 1828.5 | 886 | 38 | 31 | 860.79 | 185 | 3244 | 159.55 | 42.5 | 483 | 0 | 0 | 35.5 | 0
09:00 | 3073 | 1805 | 889 | 38 | 30 | 859.23 | 205 | 3233 | 180.63 | 25 | 449 | 0 | 0 | 57 | 0
09:30 | 3047 | 1787.5 | 888.5 | 38 | 31 | 840.67 | 180.5 | 3192 | 190.67 | 25 | 383.5 | 0 | 0 | 47.5 | 0
10:00 | 3021 | 1770 | 888 | 38 | 32 | 822.11 | 156 | 3151 | 200.71 | 25 | 318 | 0 | 0 | 38 | 0
10:30 | 3060 | 1776.5 | 888.5 | 38 | 33 | 820.445 | 185.5 | 3156.5 | 181.305 | 25 | 303 | 0 | 0 | 19.5 | 0
11:00 | 3099 | 1783 | 889 | 38 | 34 | 818.78 | 215 | 3162 | 161.9 | 25 | 288 | 0 | 0 | 1 | 0
11:30 | 3240 | 1820.5 | 888.5 | 38 | 35 | 816.365 | 190.5 | 3222 | 200.74 | 46.5 | 329.5 | 0 | 0 | 7 | 0
12:00 | 3381 | 1858 | 888 | 38 | 36 | 813.95 | 166 | 3282 | 239.58 | 68 | 371 | 0 | 0 | 13 | 0
12:30 | 3444 | 1901 | 891.5 | 38 | 37 | 838.24 | 190 | 3355 | 260.29 | 62 | 438 | 0 | 0 | 9.5 | 0
13:00 | 3507 | 1944 | 895 | 38 | 38 | 862.53 | 214 | 3428 | 281 | 56 | 505 | 0 | 0 | 6 | 0
13:30 | 3478 | 1881.5 | 895 | 38 | 37 | 840.265 | 213.5 | 3290.5 | 242.055 | 51.5 | 438.95 | 0 | 0 | 7 | 0
14:00 | 3449 | 1819 | 895 | 38 | 36 | 818 | 213 | 3153 | 203.11 | 47 | 372.9 | 0 | 0 | 8 | 0
14:30 | 3405.5 | 1777 | 895 | 38 | 35 | 822 | 213 | 3129 | 247.7 | 43.5 | 343.95 | 0 | 0 | 9 | 0
15:00 | 3362 | 1735 | 895 | 38 | 34 | 826 | 213 | 3105 | 292.29 | 40 | 315 | 0 | 0 | 10 | 0
15:30 | 3283 | 1665.5 | 895 | 38 | 32 | 827.5 | 193 | 3076.5 | 235.39 | 20 | 231 | 0 | 0 | 6 | 0
16:00 | 3204 | 1596 | 895 | 38 | 30 | 829 | 173 | 3048 | 178.49 | 0 | 147 | 0 | 0 | 2 | 0
16:30 | 3163 | 1571 | 895 | 38 | 30 | 821.5 | 173 | 3025 | 124.115 | 0 | 161.5 | 0 | 0 | 1 | 0
17:00 | 3122 | 1546 | 895 | 38 | 30 | 814 | 173 | 3002 | 69.74 | 0 | 176 | 0 | 0 | 0 | 0
17:30 | 3205 | 1563 | 895 | 38 | 31 | 822 | 173.5 | 3004.5 | 44.13 | 0 | 175 | 0 | 0 | 0 | 0
18:00 | 3288 | 1580 | 895 | 38 | 32 | 830 | 174 | 3007 | 18.52 | 0 | 174 | 0 | 0 | 0 | 0
18:30 | 3554 | 1768 | 895 | 38 | 35 | 877 | 174 | 3210.5 | 9.26 | 41.5 | 354.5 | 0 | 0 | 4.5 | 0
19:00 | 3820 | 1956 | 895 | 38 | 38 | 924 | 174 | 3414 | 0 | 83 | 535 | 0 | 0 | 9 | 0
19:30 | 3791 | 2038 | 895 | 38 | 38 | 1003 | 174 | 3860 | 0 | 95 | 882 | 0 | 0 | 11 | 0
20:00 | 3796 | 2056 | 898 | 38 | 38 | 969 | 174 | 3774 | 0 | 87 | 773 | 0 | 0 | 4 | 0
20:30 | 3901.5 | 2080.5 | 899.5 | 38 | 39 | 906.5 | 197.5 | 3713 | 0 | 87 | 778 | 0 | 0 | 9 | 0
21:00 | 4007 | 2105 | 901 | 38 | 40 | 844 | 221 | 3652 | 0 | 87 | 783 | 0 | 0 | 14 | 0
21:30 | 4031 | 2121.5 | 901.5 | 38 | 40 | 847 | 221 | 3625.5 | 0 | 87 | 786.5 | 0 | 0 | 11 | 0
22:00 | 4055 | 2138 | 902 | 38 | 40 | 850 | 221 | 3599 | 0 | 87 | 790 | 0 | 0 | 8 | 0
22:30 | 4006 | 2179.75 | 901.5 | 38 | 41 | 906 | 221 | 3671 | 0 | 87 | 779.5 | 0 | 0 | 8 | 0
23:00 | 3957 | 2221.5 | 901 | 38 | 42 | 962 | 221 | 3743 | 0 | 87 | 769 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 09:00 | 380 | 00:00 | Payra | 421 | 16:00 | 412 | 00:00
Ashuganj | 406 | 8:00 | 385 | 23:00 | Rahanpur | 407 | 09:00 | 389 | 00:00
Bhulta | 404 | 06:00 | 391 | 00:00 | Rampal | 412 | 16:00 | 394 | 00:00
Bibiana | 392 | 16:00 | 382 | 00:00
BIPTC | 405 | 06:00 | 397 | 21:00
Bogura | 391 | 09:00 | 367 | 00:00
Gopalganj | 407 | 09:00 | 390 | 00:00
Kaliakoir | 384 | 17:00 | 372 | 00:00
Madunaghat | 398 | 10:00 | 391 | 23:00
Meghnaghat | 396 | 09:00 | 384 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 08:00 | 222 | 00:00 | Keranigonj | 228 | 08:00 | 219 | 00:00
AKSML | 234 | 08:00 | 223 | 00:00 | Khulna(S) | 236 | 08:00 | 222 | 00:00
Aminbazar | 231 | 18:00 | 218 | 22:00 | Madunaghat | 236 | 09:00 | 230 | 00:00
Ashuganj | 237 | 06:00 | 226 | 00:00 | Madunaghat-400 | 235 | 09:00 | 231 | 00:00
Ashuganj-400 | 234 | 6:00 | 225 | 23:00 | Maniknagar | 226 | 08:00 | 218 | 00:00
Baghabari | 237 | 09:00 | 228 | 00:00 | Meghnaghat | 233 | 09:00 | 225 | 01:00
Barapukuria | 229 | 09:00 | 217 | 00:00 | Meghnaghat-400 | 230 | 09:00 | 222 | 00:00
Barapukuria-230 | 229 | 9:00 | 218 | 23:00 | Mirsorai | 231 | 09:00 | 222 | 00:00
Barishal | 233 | 17:00 | 222 | 00:00 | Rajshahi | 233 | 06:00 | 220 | 00:00
Bheramara | 234 | 06:00 | 223 | 00:00 | Rampal | 236 | 09:00 | 222 | 00:00
Bhulta | 233 | 06:00 | 218 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 07:00 | 223 | 00:00 | Rampura | 232 | 05:00 | 223 | 00:00
BIPTC | 237 | 06:00 | 224 | 00:00 | Shikalbaha | 232 | 07:00 | 226 | 23:00
Bogura | 242 | 09:00 | 227 | 00:00 | Shyampur | 228 | 08:00 | 220 | 00:00
Bogura-400 | 242 | 09:00 | 227 | 00:00 | Siddhirganj | 228 | 05:00 | 222 | 01:00
Borhanuddin | 237 | 10:00 | 229 | 00:00 | Sirajgonj | 242 | 08:00 | 235 | 00:00
BSRM | 231 | 09:00 | 224 | 01:00 | Sreepur | 232 | 06:00 | 223 | 00:00
Cumilla(N) | 228 | 06:00 | 220 | 00:00 | Tongi | 230 | 06:00 | 219 | 00:00
Faridpur | 232 | 16:00 | 220 | 01:00
Fenchuganj | 233 | 17:00 | 224 | 00:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 232 | 06:00 | 222 | 00:00
Gopalganj | 232 | 09:00 | 221 | 00:00
GPH | 233 | 09:00 | 227 | 23:00
Haripur | 228 | 18:00 | 219 | 00:00
Hasnabad | 228 | 08:00 | 220 | 00:00
Hathazari | 231 | 15:00 | 225 | 00:00
Ishurdi | 237 | 06:00 | 226 | 00:00
Jhenaidah | 234 | 17:00 | 219 | 00:00
Kaliakoir | 236 | 17:00 | 228 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 05:00 | 134 | 12:00 | Lalmonirhat | 132 | 05:00 | 120 | 23:00
Agargaon | 135 | 06:00 | 125 | 07:00 | Madanganj | 133 | 18:00 | 127 | 00:00
Agrabad | 132 | 07:00 | 129 | 00:00 | Madaripur | 138 | 17:00 | 130 | 00:00
AKS | 131 | 09:00 | 127 | 00:00 | Madartek | 139 | 03:00 | 123 | 12:00
Aminbazar | 135 | 07:00 | 132 | 00:00 | Madunaghat | 134 | 09:00 | 130 | 00:00
Amnura | 138 | 18:30 | 127 | 00:00 | Magura | 137 | 09:00 | 125 | 00:00
Ashuganj | 144 | 08:00 | 137 | 00:00 | Mahasthangarh | 142 | 09:00 | 127 | 00:00
Bagerhat | 139 | 17:00 | 122 | 00:00 | Maijdee | 124 | 07:00 | 116 | 00:00
Bajitpur | 132 | 04:00 | 127 | 00:00 | Manikganj | 131 | 17:00 | 124 | 00:00
Bakulia | 134 | 09:00 | 130 | 01:00 | Maniknagar | 137 | 08:00 | 131 | 00:00
Banani | 139 | 04:00 | 133 | 00:00 | Matarbari | 127 | 09:00 | 114 | 00:00
Bangabhaban | 137 | 08:00 | 131 | 00:00 | Matuail | 133 | 17:00 | 128 | 00:00
Barapukuria | 138 | 08:00 | 128 | 23:00 | Millgate | 135 | 07:00 | 129 | 00:00
Barguna | 137 | 09:00 | 131 | 00:00 | Mirpur | 134 | 08:00 | 131 | 00:00
Barishal | 137 | 17:00 | 129 | 00:00 | Mirzapur | 130 | 05:00 | 128 | 00:00
Barishal-230 | 137 | 08:00 | 128 | 00:00 | Mithapukur | 135 | 08:00 | 114 | 00:00
Baroaulia | 132 | 08:00 | 129 | 23:00 | MI_Cement | 133 | 08:00 | 128 | 00:00
Baroirhat | 126 | 06:00 | 121 | 18:30 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 141 | 04:00 | 129 | 00:00 | Mogbazar | 140 | 03:00 | 135 | 00:00
BashundharaCement | 133 | 18:00 | 127 | 00:00 | Mongla | 139 | 09:00 | 124 | 00:00
Beanibazar | 131 | 09:00 | 120 | 00:00 | Motijheel | 137 | 08:00 | 131 | 00:00
Benapole | 138 | 09:00 | 123 | 00:00 | Muktagacha | 137 | 04:00 | 126 | 18:00
Bhaluka | 133 | 06:00 | 124 | 00:00 | Munshiganj | 133 | 17:00 | 127 | 00:00
Bhandaria | 134 | 17:00 | 122 | 01:00 | Muradnagar | 128 | 08:00 | 123 | 00:00
Bhangura | 136 | 14:00 | 128 | 00:00 | Mymensingh | 139 | 06:00 | 118 | 00:00
Bheramara | 138 | 06:00 | 133 | 00:00 | Naogaon | 137 | 08:00 | 125 | 00:00
Bheramara(GK) | 138 | 09:00 | 132 | 00:00 | Narail | 138 | 09:00 | 125 | 00:00
Bhulta | 128 | 13:00 | 121 | 00:00 | Narinda | 137 | 8:00 | 131 | 0:00
Bog-Sherpur | 140 | 09:00 | 129 | 00:00 | Narshingdi | 140 | 06:00 | 122 | 00:00
Bogura | 143 | 09:00 | 131 | 00:00 | Natore | 137 | 17:00 | 128 | 00:00
Bogura-230 | 143 | 09:00 | 132 | 00:00 | Nawabganj | 138 | 17:00 | 130 | 00:00
Brahmanbaria | 138 | 07:00 | 131 | 00:00 | Netrakona | 126 | 10:00 | 117 | 00:00
Cantonment | 135 | 07:00 | 130 | 00:00 | New | 136 | 05:00 | 130 | 00:00
Chandina | 131 | 07:00 | 125 | 18:30 | Niamatpur | 139 | 09:00 | 132 | 00:00
Chandpur | 132 | 20:00 | 121 | 15:00 | Noapara | 140 | 09:00 | 127 | 00:00
Chandraghona | 134 | 08:00 | 130 | 23:00 | Pabna | 137 | 15:00 | 129 | 00:00
Chapai | 137 | 01:00 | 130 | 00:00 | Palashbari | 134 | 08:00 | 113 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 18:00 | 128 | 00:00 | Panchagarh | 139 | 09:00 | 124 | 23:00
Chauddagram | 126 | 06:00 | 121 | 19:00 | Patiya | 134 | 09:00 | 127 | 23:00
Chhatak | 130 | 08:00 | 118 | 00:00 | Patuakhali | 137 | 17:00 | 132 | 10:00
Chowmuhani | 124 | 07:00 | 115 | 20:00 | Payra | 138 | 07:00 | 135 | 00:00
Chuadanga | 136 | 09:00 | 121 | 00:00 | PHP | 126 | 08:00 | 119 | 19:00
Coxsbazar | 125 | 09:00 | 112 | 06:00 | Postogola | 136 | 18:00 | 130 | 00:00
Cumilla(N) | 131 | 05:00 | 127 | 00:00 | Purbachal | 140 | 04:00 | 128 | 00:00
Cumilla(S) | 132 | 04:00 | 125 | 00:00 | Purbasadipur | 134 | 09:00 | 122 | 23:00
Daganbhuiyan | 125 | 07:00 | 117 | 19:00 | Rahanpur | 140 | 09:00 | 133 | 00:00
Daudkandi | 127 | 08:00 | 121 | 00:00 | Rahanpur-400 | 140 | 08:00 | 133 | 00:00
Dhaka | 140 | 04:00 | 135 | 00:00 | Rahim | 132 | 08:00 | 128 | 00:00
Dhamrai | 136 | 17:00 | 128 | 00:00 | Rajbari | 137 | 17:00 | 127 | 00:00
Dhanmondi | 140 | 03:00 | 135 | 13:00 | Rajendrapur | 132 | 06:00 | 123 | 00:00
Dohazari | 131 | 09:00 | 124 | 22:00 | Rajshahi | 136 | 17:00 | 126 | 00:00
Faridpur | 138 | 16:00 | 131 | 01:00 | Rajshahi-230 | 135 | 06:00 | 126 | 00:00
Fatullah | 135 | 18:30 | 128 | 00:00 | Ramganj | 125 | 06:00 | 117 | 10:00
Fenchuganj | 138 | 07:00 | 131 | 00:00 | Rampur | 132 | 08:00 | 128 | 00:00
Feni | 125 | 06:00 | 120 | 18:30 | Rampura | 140 | 05:00 | 134 | 00:00
Ghatail | 133 | 06:00 | 124 | 18:00 | Rangamati | 133 | 09:00 | 130 | 00:00
Ghorashal | 139 | 07:00 | 131 | 00:00 | Rangpur | 133 | 07:00 | 123 | 23:00
Goalpara | 142 | 10:00 | 129 | 00:00 | Ruppur | 139 | 17:00 | 132 | 00:00
Gollamari | 142 | 09:00 | 130 | 00:00 | Saidpur | 134 | 09:00 | 120 | 23:00
Gopalganj | 139 | 09:00 | 130 | 00:00 | Satkhira | 139 | 09:00 | 125 | 00:00
Gopalganj-400 | 139 | 08:00 | 132 | 00:00 | Satmasjid | 135 | 08:00 | 129 | 00:00
Gulshan | 139 | 06:00 | 134 | 11:00 | Savar | 133 | 09:00 | 130 | 12:00
Halishahar | 134 | 09:00 | 128 | 23:00 | SevenRings | 140 | 06:00 | 132 | 00:00
Haripur | 133 | 09:00 | 128 | 00:00 | ShahCement | 134 | 18:00 | 128 | 00:00
HaripurSBU | 133 | 09:00 | 126 | 00:00 | Shahjadpur | 138 | 09:00 | 132 | 00:00
Hasnabad | 135 | 07:00 | 129 | 00:00 | Shahjibazar | 139 | 08:00 | 129 | 00:00
Hathazari | 134 | 03:00 | 130 | 00:00 | Shahmirpur | 134 | 08:00 | 129 | 23:00
Ishurdi | 139 | 06:00 | 133 | 00:00 | Shariatpur | 137 | 16:00 | 127 | 01:00
Jaldhaka | 132 | 09:00 | 117 | 23:00 | Sherpur | 137 | 06:00 | 115 | 18:00
Jamalpur | 139 | 06:00 | 118 | 18:30 | Shikalbaha | 123 | 16:00 | 119 | 00:00
Jashore | 138 | 09:00 | 123 | 00:00 | Shikalbaha-230 | 135 | 09:00 | 130 | 23:00
Jhenaidah | 139 | 08:00 | 124 | 00:00 | Shitalakhya | 133 | 08:00 | 128 | 00:00
Jhenaidah-230 | 139 | 09:00 | 127 | 00:00 | Sholosohor | 134 | 09:00 | 130 | 00:00
Joydebpur | 142 | 06:00 | 132 | 00:00 | Shyampur | 134 | 17:00 | 125 | 04:00
Joypurhat | 136 | 09:00 | 121 | 00:00 | Shyampur-230 | 134 | 08:00 | 129 | 00:00
Juldah | 134 | 09:00 | 130 | 23:00 | Siddhirganj | 134 | 17:00 | 128 | 00:00
Kabirpur | 133 | 07:00 | 124 | 00:00 | Sirajganj | 137 | 09:00 | 128 | 00:00
Kachua | 131 | 20:00 | 123 | 11:00 | Sonargaon | 132 | 18:00 | 124 | 01:00
Kaliakoir | 138 | 17:00 | 131 | 00:00 | Sreemongol | 137 | 08:00 | 128 | 00:00
Kallyanpur | 135 | 07:00 | 132 | 00:00 | Sreepur | 134 | 06:00 | 127 | 00:00
Kalurghat | 133 | 08:00 | 130 | 00:00 | Srinagar | 138 | 08:00 | 131 | 00:00
Kamrangirchar | 138 | 09:00 | 130 | 00:00 | SSM | 137 | 16:00 | 131 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 127 | 17:00 | 116 | 00:00
Kasba | 128 | 08:00 | 122 | 00:00 | Sylhet | 132 | 17:00 | 122 | 00:00
Kazla | 137 | 09:00 | 130 | 00:00 | Sylhet-132 | 131 | 08:00 | 123 | 00:00
Keranigonj | 137 | 08:00 | 131 | 00:00 | Tangail | 129 | 11:00 | 125 | 18:00
Khagrachori | 133 | 09:00 | 128 | 23:00 | Taraganj | 134 | 06:00 | 123 | 23:00
Khulna | 142 | 09:00 | 129 | 00:00 | Thakurgaon | 138 | 09:00 | 122 | 23:00
Khulna(S) | 143 | 09:00 | 130 | 00:00 | TK | 133 | 07:00 | 130 | 00:00
Khulshi | 132 | 09:00 | 129 | 00:00 | Tongi | 137 | 13:00 | 129 | 00:00
Kishoreganj | 131 | 13:00 | 125 | 00:00 | Ullahpara | 138 | 14:00 | 129 | 00:00
Kodda | 137 | 07:00 | 123 | 03:00 | Ullon | 140 | 05:00 | 134 | 00:00
KSRM | 133 | 06:00 | 130 | 01:00 | Uttara | 134 | 08:00 | 129 | 01:00
Kulaura | 136 | 08:00 | 129 | 00:00 | UttaraNew | 134 | 08:00 | 130 | 01:00
Kurigram | 132 | 06:00 | 119 | 16:00 | Zigatola | 138 | 08:00 | 131 | 00:00
Kushtia | 137 | 17:00 | 127 | 00:00
Laksam | 130 | 19:30 | 122 | 11:00
Lakshmipur | 125 | 07:00 | 118 | 00:00
Lalbag | 138 | 09:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division