## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-08-2025 | during | 11-08-2025 | during | 11-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 371 | 319 | 400.75 | 400.75 | 382 | 382 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 370 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 290 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 42 | 46 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 37 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 7 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 4.4 | 4.4 | 4.4 | 4.4 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 34 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 100 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 50 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 140 | 140 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 408 | 395 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 90 | 90 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2278 | 2571 | 5782.1 | 5794.1 | 3249.43 | 3261.43
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 28 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 73 | 218 | 225 | 225 | 153 | 153 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 27 | 105 | 105 | 105 | 105 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 34 | 70 | 70 | 70 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 20 | 100 | 100 | 25 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 22 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 70 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.59 | 0 | 3.17 | 0 | 3.17 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 5 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 35 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 550 | 540 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 14 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 780 | 770 | 780 | 780 | 780 | 780 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1719.59 | 2137 | 3829.89 | 3823.72 | 2995.89 | 3039.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 197 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 346 | 353.35 | 353.35 | 353.35 | 353.35 | machine problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 40 | 46.7 | 46.7 | 41 | 41 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 45 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 50 | 195 | 195 | 163 | 163 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 125 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 43 | 42 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 127 | 174 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 31 | 98 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 43 | 63 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 71 | 115 | 115 | 72 | 72 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1505 | 1776 | 2439.56 | 2379.56 | 2152.36 | 2092.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-08-2025 | during | 11-08-2025 | during | 11-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 97 | 93 | 157.5 | 157.5 | 156 | 156 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 185 | 200 | 200 | 196 | 196 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 84 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.92 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 36 | 36 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 311.92 | 403 | 585.2 | 549 | 536.2 | 500
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 145 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 83 | 83 | 80 | 80 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 65 | 65 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 378 | 361 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 290 | 290 | 270 | 270 | 270 | 270 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1392 | 1354 | 1447 | 1447 | 1312 | 1312
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 364 | 354 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.3 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1031 | 1232 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2405.3 | 2543 | 3643.2 | 3548.2 | 3516.2 | 3421.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 303 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 65 | 65 | 65 | 65 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1040 | 1185 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 176 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1737.61 | 1984 | 2097 | 2096 | 2047 | 2046
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 52.39 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 36 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 7 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 179 | 196 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to 4th Minor Inspection(MI) of GT.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 190 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 396 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 60 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.28 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1029 | 1320.83 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 11.24 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 57 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1881.91 | 2401.83 | 2960.47 | 2806.87 | 2875.69 | 2722.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 171 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 26 | 0 | 26 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 154 | 0 | 107.47 | 0 | 107.47 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 481.4 | 439 | 602.07 | 462 | 602.07 | 462
System Total |  |  |  |  | 28671.2 | 27843.665 | 13712.73 | 15608.83 | 23386.49 | 22906.45 | 19286.84 | 18856.8
Forecast Scenario (11-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14200 |  | 0 |  | 14200
|  |  |  | 2:00 | 13800 |  | 0 |  | 13800
|  |  |  | 3:00 | 13300 |  | 0 |  | 13300
|  |  |  | 4:00 | 12950 |  | 0 |  | 12950
|  |  |  | 5:00 | 12720 |  | 0 |  | 12720
|  |  |  | 6:00 | 12090 |  | 0 |  | 12090
|  |  |  | 7:00 | 12280 |  | 0 |  | 12280
|  |  |  | 8:00 | 12360 |  | 0 |  | 12360
|  |  |  | 9:00 | 12610 |  | 0 |  | 12610
|  |  |  | 10:00 | 12850 |  | 0 |  | 12850
|  |  |  | 11:00 | 13240 |  | 0 |  | 13240
|  |  |  | 12:00 | 13710 |  | 0 |  | 13710
|  |  |  | 13:00 | 14080 |  | 0 |  | 14080
|  |  |  | 14:00 | 14070 |  | 0 |  | 14070
|  |  |  | 15:00 | 14200 |  | 0 |  | 14200
|  |  |  | 16:00 | 14180 |  | 0 |  | 14180
|  |  |  | 17:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:00 | 13180 |  | 0 |  | 13180
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14550 |  | 0 |  | 14550
|  |  |  | 19:30 | 15670 |  | 0 |  | 15670
|  |  |  | 20:00 | 15620 |  | 0 |  | 15620
|  |  |  | 21:00 | 15410 |  | 0 |  | 15410
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13710.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 330.23 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:01 hrs on 11-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-08-2025 | [28 empty] | Date: | 10-08-2025 | [28 empty] | Date: | 10-08-2025 | [28 empty] | Date: | 10-08-2025 | [28 empty] | Date: | 10-08-2025 | [12 empty] | Date: | 10-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 19 | 0 | 70 | 15 | 0 | 0 | 17 | 16 | 0 | 380 | 292 | 395 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 16 | 0 | 25 | 24 | 0 | 221 | 0 | 37 | 780 | 0 | 0 | 19 | 8 | 0 | 151 | 0 | 0 | 0 | 520 | 0 | 51 | 0 | 71 | 0 | 354 | 330 | 47 | 193 | 38 | 103 | 50 | 159 | 63 | 19 | 61 | 44 | 16 | 0 | 30 | 315 | 260 | 386 | 0 | 30 | 156 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 17 | 77 | 120 | 133 | 0 | 0 | 6 | 7233 | 900 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 1446.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 194 | 0 | 403 | 0 | 0 | 173 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 220 | 0 | 306 | 1098 | 0 | 7060.17 | 14293.17 | 108.27
01:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 283 | 390 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 25 | 24 | 0 | 220 | 0 | 34 | 780 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 510 | 0 | 51 | 0 | 71 | 0 | 355 | 330 | 47 | 191 | 35 | 96 | 70 | 150 | 61 | 19 | 59 | 44 | 16 | 0 | 30 | 305 | 260 | 386 | 0 | 30 | 151 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 17 | 86 | 85 | 133 | 0 | 0 | 6 | 7017 | 900 | 363 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 0 | 1455.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 189 | 0 | 402 | 0 | 0 | 170 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 220 | 0 | 306 | 1000 | 0 | 6854.18 | 13871.18 | 108.26
02:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 286 | 390 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 25 | 24 | 0 | 220 | 0 | 34 | 780 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 522 | 0 | 51 | 0 | 71 | 0 | 354 | 330 | 48 | 194 | 35 | 93 | 70 | 143 | 55 | 19 | 63 | 42 | 16 | 0 | 31 | 310 | 260 | 386 | 0 | 30 | 155 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 17 | 86 | 85 | 133 | 0 | 0 | 0 | 6981 | 895 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 1303.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 193 | 0 | 409 | 0 | 0 | 170 | 48 | 110 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 220 | 0 | 305 | 990 | 0 | 6558.13 | 13539.13 | 108.25
03:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 290 | 390 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 25 | 24 | 0 | 219 | 0 | 34 | 780 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 475 | 0 | 51 | 0 | 71 | 0 | 355 | 330 | 48 | 197 | 35 | 91 | 70 | 138 | 60 | 19 | 62 | 42 | 16 | 0 | 31 | 310 | 260 | 387 | 0 | 30 | 152 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 0 | 86 | 85 | 143 | 0 | 0 | 0 | 6871 | 896 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 1318.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 190 | 0 | 410 | 0 | 0 | 170 | 48 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 220 | 0 | 305 | 900 | 0 | 6220.61 | 13091.61 | 108.24
04:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 289 | 395 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 24 | 0 | 219 | 0 | 34 | 780 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 447 | 0 | 51 | 0 | 71 | 0 | 355 | 330 | 48 | 192 | 35 | 92 | 50 | 143 | 62 | 19 | 62 | 40 | 16 | 0 | 31 | 305 | 260 | 387 | 0 | 30 | 155 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 0 | 85 | 55 | 147 | 0 | 0 | 0 | 6776 | 896 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 895 | 0 | 1202.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 193 | 0 | 406 | 0 | 0 | 173 | 47 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 220 | 0 | 304 | 890 | 0 | 6091.76 | 12867.76 | 108.23
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 288 | 390 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 219 | 0 | 36 | 780 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 71 | 0 | 355 | 330 | 48 | 189 | 35 | 73 | 50 | 137 | 63 | 19 | 61 | 40 | 0 | 0 | 31 | 310 | 260 | 387 | 0 | 30 | 151 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 0 | 65 | 45 | 148 | 0 | 0 | 0 | 6641 | 896 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 1212.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 189 | 0 | 402 | 0 | 0 | 171 | 48 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 220 | 0 | 305 | 890 | 0 | 6028.64 | 12669.64 | 108.21
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 286 | 385 | 0 | 0 | 335 | 0 | 0 | 1 | 17 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.14 | 219 | 0 | 39 | 780 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 452 | 1 | 51 | 0 | 71 | 0 | 320 | 330 | 48 | 192 | 35 | 65 | 50 | 100 | 63 | 19 | 34 | 36 | 0 | 2 | 31 | 305 | 260 | 315 | 0 | 30 | 149 | 6 | 0 | 77 | 30 | 0 | 18 | 65 | 0 | 65 | 45 | 148 | 0 | 0 | 0 | 6244.14 | 895 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.54 | 778 | 0 | 1129.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 2 | 0 | 0.27 | 185 | 0 | 0 | 0 | 186 | 0 | 402 | 0 | 0.04 | 171 | 48 | 35 | 0 | 49 | 0 | 0 | 0 | 3 | 0.02 | 0 | 169 | 0 | 220 | 0 | 304 | 880 | 0 | 5853.7 | 12097.84 | 108.19
07:00 | 0 | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 294 | 400 | 0 | 0 | 333 | 0 | 0 | 5 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.7 | 221 | 0 | 30 | 780 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 456 | 5 | 51 | 0 | 71 | 0 | 320 | 330 | 48 | 200 | 35 | 49 | 50 | 100 | 54 | 19 | 34 | 36 | 0 | 16 | 31 | 310 | 260 | 334 | 0 | 30 | 157 | 6 | 0 | 77 | 30 | 0 | 18 | 65 | 0 | 75 | 68 | 119 | 0 | 1.47 | 0 | 6388.17 | 895 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.17 | 816 | 0 | 1019.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 8 | 0 | 1.39 | 194 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 171 | 47 | 35 | 1 | 49 | 0 | 0 | 0.4 | 15 | 0.16 | 0 | 173 | 0 | 220 | 0 | 306 | 900 | 0 | 5898.03 | 12286.2 | 108.17
08:00 | 0 | 26 | 33 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 8 | 0 | 0 | 350 | 289 | 390 | 0 | 0 | 334 | 0 | 0 | 6 | 17 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 221 | 0 | 2 | 780 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 450 | 11 | 51 | 0 | 71 | 0 | 320 | 330 | 49 | 190 | 32 | 46 | 70 | 100 | 47 | 19 | 34 | 34 | 0 | 34 | 31 | 310 | 260 | 316 | 0 | 30 | 152 | 6 | 0 | 77 | 30 | 0 | 18 | 65 | 0 | 75 | 95 | 119 | 0 | 5.9 | 0 | 6394.64 | 901 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45.67 | 791 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.99 | 30 | 0 | 10.95 | 190 | 0 | 0 | 0 | 188 | 0 | 349 | 0 | 1.57 | 171 | 47 | 35 | 2 | 49 | 0 | 0 | 1.4 | 35 | 0.18 | 0 | 169 | 0 | 220 | 0 | 305 | 990 | 0 | 5969.76 | 12364.4 | 108.15
09:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 31 | 0 | 0 | 350 | 291 | 394 | 0 | 0 | 330 | 0 | 0 | 13 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3.39 | 222 | 0 | 2 | 780 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 455 | 13 | 51 | 0 | 71 | 0 | 320 | 330 | 48 | 196 | 36 | 46 | 70 | 100 | 47 | 20 | 30 | 34 | 0 | 45 | 30 | 310 | 270 | 333 | 0 | 30 | 151 | 6 | 0 | 77 | 30 | 0 | 18 | 65 | 0 | 76 | 95 | 117 | 0 | 12.53 | 4 | 6597.92 | 901 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48.71 | 793 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.69 | 40 | 0 | 18.84 | 189 | 0 | 0 | 0 | 187 | 0 | 354 | 0 | 1.85 | 159 | 47 | 35 | 5 | 48 | 0 | 0 | 2.6 | 52 | 0.3 | 0 | 172 | 0 | 220 | 0 | 304 | 988 | 0 | 6020.99 | 12618.91 | 108.13
10:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 35 | 0 | 0 | 350 | 298 | 403 | 0 | 0 | 326 | 0 | 0 | 8 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 4.03 | 221 | 0 | 5 | 784 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 455 | 17 | 51 | 0 | 71 | 0 | 320 | 330 | 46 | 206 | 37 | 48 | 52 | 99 | 53 | 20 | 33 | 34 | 0 | 41 | 30 | 315 | 285 | 340 | 0 | 30 | 141 | 6 | 0 | 76 | 30 | 0 | 18 | 65 | 0 | 75 | 95 | 101 | 1 | 6.63 | 6 | 6647.66 | 902 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 93.46 | 816 | 0 | 1040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.91 | 79 | 0 | 21.22 | 177 | 0 | 0 | 0 | 178 | 0 | 385 | 0 | 0 | 153 | 47 | 35 | 11 | 49 | 0 | 0 | 2.1 | 96 | 0.51 | 0 | 173 | 0 | 220 | 0 | 301 | 992 | 0 | 6205.2 | 12852.86 | 108.1
11:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 12 | 0 | 68 | 0 | 0 | 0 | 35 | 30 | 0 | 350 | 302 | 405 | 0 | 0 | 330 | 0 | 0 | 33 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.99 | 221 | 0 | 5 | 780 | 0 | 0 | 5 | 0 | 0 | 50 | 0 | 0 | 0 | 550 | 18 | 51 | 0 | 71 | 0 | 335 | 330 | 46 | 205 | 38 | 49 | 50 | 100 | 43 | 20 | 30 | 36 | 0 | 58 | 30 | 320 | 290 | 335 | 0 | 30 | 142 | 6 | 0 | 78 | 30 | 0 | 18 | 65 | 0 | 75 | 95 | 102 | 1 | 15.3 | 6 | 6871.29 | 901 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63.62 | 986 | 0 | 1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.04 | 98 | 0 | 31.32 | 176 | 0 | 0 | 0 | 177 | 0 | 388 | 0 | 4.59 | 150 | 47 | 35 | 7 | 49 | 0 | 0 | 5.4 | 83 | 0.69 | 0 | 172 | 0 | 220 | 0 | 301 | 994 | 0 | 6376.66 | 13247.95 | 108.07
12:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 42 | 0 | 68 | 0 | 0 | 0 | 37 | 140 | 0 | 350 | 300 | 408 | 0 | 7 | 329 | 0 | 0 | 32 | 70 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 4.59 | 221 | 0 | 7 | 780 | 0 | 0 | 28 | 0 | 0 | 73 | 0 | 0 | 0 | 550 | 19 | 51 | 3 | 26 | 0 | 339 | 330 | 44 | 197 | 38 | 49 | 50 | 127 | 43 | 20 | 31 | 40 | 0 | 74 | 43 | 320 | 290 | 378 | 0 | 30 | 145 | 6 | 0 | 75 | 30 | 0 | 18 | 100 | 0 | 75 | 96 | 97 | 1 | 36.92 | 6 | 7206.51 | 901 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71.3 | 1031 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.39 | 57 | 0 | 11.24 | 179 | 0 | 0 | 0 | 178 | 0 | 374 | 0 | 1.28 | 170 | 47 | 35 | 20 | 49 | 0 | 0 | 6.4 | 154 | 0.61 | 0 | 176 | 0 | 220 | 0 | 301 | 1040 | 0 | 6506.22 | 13712.73 | 108.05
13:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 51 | 0 | 68 | 0 | 0 | 0 | 55 | 144 | 0 | 350 | 295 | 406 | 0 | 45 | 330 | 0 | 0 | 27 | 70 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 12 | 25 | 2.39 | 220 | 0 | 7 | 770 | 0 | 0 | 40 | 0 | 0 | 85 | 0 | 0 | 0 | 550 | 18 | 51 | 46 | 26 | 0 | 341 | 330 | 42 | 191 | 33 | 49 | 50 | 143 | 52 | 14 | 29 | 40 | 0 | 36 | 43 | 315 | 300 | 365 | 0 | 30 | 156 | 6 | 0 | 75 | 30 | 0 | 18 | 100 | 0 | 84 | 120 | 91 | 1 | 19.34 | 6 | 7282.73 | 902 | 361 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27.52 | 1110 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.51 | 49 | 0 | 44.43 | 181 | 0 | 0 | 0 | 179 | 0 | 363 | 0 | 5.45 | 170 | 47 | 35 | 12 | 49 | 0 | 0 | 5.9 | 195 | 0.63 | 0 | 277 | 0 | 220 | 0 | 301 | 1105 | 0 | 6798.44 | 14081.17 | 108.02
14:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 47 | 0 | 65 | 0 | 0 | 0 | 55 | 143 | 0 | 300 | 295 | 387 | 0 | 55 | 327 | 0 | 0 | 24 | 70 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 25 | 3.31 | 219 | 0 | 2 | 766 | 0 | 0 | 50 | 0 | 0 | 213 | 0 | 0 | 0 | 555 | 13 | 51 | 24 | 26 | 0 | 341 | 330 | 42 | 192 | 37 | 48 | 50 | 167 | 44 | 6 | 30 | 44 | 0 | 63 | 42 | 305 | 300 | 346 | 0 | 30 | 137 | 6 | 0 | 74 | 30 | 0 | 18 | 100 | 0 | 92 | 120 | 91 | 1 | 20.17 | 6 | 7288.48 | 902 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92.08 | 1045 | 0 | 1169.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.43 | 54 | 0 | 50.37 | 193 | 0 | 0 | 0 | 195 | 0 | 345 | 0 | 4.04 | 166 | 47 | 35 | 11 | 34 | 0 | 0 | 2.9 | 161 | 0.22 | 0 | 246 | 0 | 220 | 0 | 301 | 1100 | 0 | 6781.34 | 14069.82 | 108
15:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 49.2 | 0 | 50 | 0 | 0 | 0 | 55 | 158 | 0 | 300 | 300 | 418 | 0 | 55 | 326 | 0 | 0 | 18 | 70 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 25 | 2.46 | 219 | 0 | 2 | 770 | 0 | 0 | 50 | 0 | 0 | 211 | 0 | 0 | 0 | 515 | 13 | 51 | 24 | 26 | 0 | 334 | 330 | 41 | 200 | 37 | 49 | 50 | 173 | 39 | 20 | 30 | 44 | 0 | 47 | 42 | 315 | 300 | 390 | 0 | 30 | 146 | 6 | 0 | 74 | 30 | 0 | 18 | 100 | 0 | 84 | 120 | 91 | 1 | 8.83 | 6 | 7347.49 | 901 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.3 | 1085 | 0 | 1183.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.68 | 73 | 0 | 39.87 | 199 | 0 | 0 | 0 | 197 | 0 | 394 | 0 | 3.42 | 168 | 47 | 35 | 7 | 34 | 0 | 0 | 4 | 103 | 0.21 | 0 | 254 | 0 | 220 | 0 | 303 | 1156 | 0 | 6858.12 | 14205.61 | 107.97
16:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 49 | 0 | 59 | 0 | 0 | 0 | 55 | 154 | 0 | 300 | 293 | 406 | 0 | 55 | 325 | 0 | 0 | 12 | 70 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 17 | 25 | 1.74 | 220 | 0 | 2 | 770 | 0 | 0 | 50 | 0 | 0 | 216 | 0 | 0 | 0 | 510 | 10 | 51 | 55 | 26 | 0 | 341 | 330 | 41 | 194 | 37 | 52 | 50 | 172 | 43 | 20 | 47 | 42 | 0 | 25 | 42 | 310 | 300 | 388 | 0 | 30 | 140 | 6 | 0 | 73 | 30 | 0 | 18 | 100 | 7 | 74 | 149 | 91 | 1 | 9.01 | 6 | 7381.75 | 901 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.94 | 1150 | 0 | 1162.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.77 | 61 | 0 | 25.14 | 195 | 0 | 0 | 0 | 190 | 0 | 348 | 0 | 2.49 | 172 | 47 | 70 | 3 | 34 | 0 | 0 | 2.9 | 53 | 0.22 | 0 | 249 | 0 | 220 | 0 | 302 | 1183 | 0 | 6801.81 | 14183.56 | 107.95
17:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 45 | 0 | 68 | 0 | 0 | 0 | 55 | 144 | 0 | 300 | 285 | 393 | 0 | 35 | 326 | 0 | 0 | 6 | 70 | 20 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 29 | 0 | 0 | 0 | 17 | 25 | 0.67 | 218 | 0 | 7 | 770 | 0 | 0 | 50 | 0 | 0 | 216 | 0 | 0 | 0 | 430 | 3 | 51 | 60 | 26 | 0 | 343 | 330 | 43 | 185 | 34 | 52 | 70 | 165 | 42 | 20 | 45 | 42 | 0 | 15 | 42 | 300 | 300 | 351 | 0 | 30 | 131 | 6 | 0 | 74 | 30 | 0 | 18 | 100 | 17 | 76 | 155 | 90 | 0 | 5.78 | 6 | 7204.45 | 902 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.68 | 1137 | 0 | 1157.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 26 | 0 | 9.9 | 187 | 0 | 0 | 0 | 182 | 0 | 332 | 0 | 0.92 | 174 | 46 | 70 | 4 | 34 | 0 | 0 | 1.9 | 14 | 0.09 | 0 | 194 | 0 | 220 | 0 | 304 | 1120 | 0 | 6528.07 | 13732.52 | 107.9
18:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 44.2 | 0 | 65 | 0 | 15 | 0 | 55 | 140 | 0 | 300 | 284 | 370 | 0 | 55 | 280 | 0 | 0 | 2 | 70 | 20 | 21 | 0 | 0 | 0 | 0 | 13 | 0 | 28 | 0 | 0 | 0 | 19 | 25 | 0.09 | 218 | 0 | 3 | 770 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 410 | 0 | 51 | 60 | 26 | 0 | 300 | 310 | 43 | 191 | 37 | 50 | 70 | 171 | 47 | 20 | 44 | 40 | 0 | 3 | 41 | 290 | 290 | 372 | 0 | 30 | 130 | 4 | 0 | 78 | 30 | 0 | 18 | 100 | 17 | 84 | 155 | 91 | 0 | 3.04 | 6 | 7033.33 | 901 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.35 | 1058 | 0 | 1058.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.43 | 7 | 0 | 4.44 | 163 | 0 | 0 | 0 | 162 | 0 | 345 | 0 | 0.37 | 176 | 47 | 70 | 2 | 34 | 0 | 0 | 0.2 | 1 | 0.01 | 0 | 199 | 0 | 220 | 0 | 305 | 1000 | 0 | 6151.91 | 13185.24 | 107.86
19:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 48 | 0 | 64 | 50 | 55 | 2 | 55 | 154 | 0 | 300 | 300 | 400 | 0 | 55 | 328 | 0 | 0 | 0 | 84 | 20 | 22 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 66 | 22 | 0 | 20 | 25 | 0 | 218 | 1 | 7 | 770 | 17 | 0 | 12 | 1 | 4 | 215 | 0 | 0 | 0 | 530 | 0 | 51 | 80 | 26 | 0 | 329 | 315 | 44 | 204 | 34 | 63 | 70 | 184 | 68 | 20 | 66 | 48 | 3 | 0 | 42 | 300 | 290 | 388 | 0 | 30 | 145 | 6 | 0 | 78 | 30 | 0 | 18 | 100 | 20 | 84 | 166 | 91 | 0 | 0 | 6 | 7750 | 902 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 17 | 1151.87 | 0 | 36 | 0 | 10 | 3 | 0 | 70 | 7 | 10 | 0 | 0 | 27 | 0 | 174 | 0 | 0 | 0 | 179 | 0 | 402 | 0 | 0 | 173 | 47 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 220 | 0 | 305 | 1030 | 0 | 6769.87 | 14519.87 | 107.83
19:30 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 46 | 0 | 100 | 80 | 160 | 15 | 55 | 140 | 0 | 370 | 290 | 395 | 0 | 55 | 331 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 15 | 70 | 0 | 14 | 66 | 34 | 0 | 20 | 25 | 0 | 218 | 5 | 22 | 770 | 35 | 0 | 50 | 8 | 27 | 218 | 0 | 0 | 0 | 540 | 0 | 51 | 125 | 50 | 0 | 346 | 330 | 45 | 189 | 40 | 71 | 70 | 174 | 63 | 20 | 98 | 46 | 16 | 0 | 42 | 285 | 290 | 361 | 0 | 30 | 156 | 6 | 0 | 78 | 30 | 0 | 18 | 100 | 35 | 84 | 185 | 93 | 0 | 0 | 6 | 8241 | 902 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 17 | 1320.83 | 0 | 36 | 0 | 60 | 50 | 0 | 94 | 7 | 25 | 0 | 0 | 27 | 0 | 196 | 0 | 0 | 0 | 190 | 0 | 396 | 0 | 0 | 171 | 47 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 220 | 0 | 303 | 1185 | 0 | 7367.83 | 15608.83 | 107.83
20:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 47 | 0 | 104 | 80 | 195 | 15 | 55 | 147 | 12 | 370 | 286 | 385 | 0 | 55 | 331 | 0 | 0 | 0 | 90 | 21 | 22 | 0 | 0 | 0 | 15 | 63 | 0 | 14 | 66 | 42 | 0 | 21 | 25 | 0 | 218 | 20 | 22 | 770 | 35 | 0 | 50 | 13 | 43 | 218 | 0 | 0 | 0 | 537 | 0 | 51 | 120 | 53 | 0 | 348 | 330 | 45 | 190 | 38 | 71 | 70 | 179 | 62 | 20 | 97 | 46 | 33 | 0 | 36 | 290 | 290 | 301 | 0 | 30 | 145 | 6 | 0 | 78 | 30 | 0 | 18 | 100 | 35 | 83 | 194 | 92 | 0 | 0 | 6 | 8287 | 903 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 19 | 1397.92 | 0 | 47 | 0 | 35 | 50 | 0 | 85 | 25 | 0 | 0 | 0 | 25 | 0 | 190 | 0 | 0 | 0 | 179 | 0 | 342 | 0 | 0 | 172 | 47 | 115 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 220 | 0 | 303 | 1200 | 0 | 7280.92 | 15567.92 | 107.8
21:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 45 | 0 | 115 | 80 | 145 | 0 | 55 | 144 | 16 | 370 | 290 | 395 | 0 | 55 | 332 | 0 | 0 | 0 | 90 | 14 | 22 | 0 | 0 | 0 | 0 | 81 | 0 | 15 | 66 | 43 | 0 | 23 | 25 | 0 | 218 | 28 | 23 | 770 | 17 | 0 | 50 | 16 | 17 | 219 | 0 | 0 | 0 | 538 | 0 | 51 | 132 | 53 | 0 | 347 | 330 | 45 | 191 | 38 | 71 | 70 | 175 | 63 | 20 | 98 | 30 | 52.2 | 0 | 36 | 280 | 280 | 358 | 0 | 30 | 137 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 35 | 83 | 196 | 92 | 0 | 0 | 6 | 8257.2 | 902 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 34 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 166 | 0 | 399 | 0 | 0 | 171 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 220 | 0 | 305 | 1230 | 0 | 7102 | 15359.2 | 107.78
22:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 48 | 0 | 90 | 80 | 15 | 0 | 35 | 108 | 16 | 370 | 299 | 405 | 0 | 17 | 330 | 0 | 0 | 0 | 90 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 66 | 43 | 0 | 24 | 25 | 0 | 218 | 0 | 30 | 770 | 0 | 0 | 50 | 8 | 16 | 219 | 0 | 0 | 0 | 550 | 0 | 51 | 135 | 76 | 0 | 344 | 330 | 45 | 201 | 41 | 71 | 70 | 180 | 63 | 17 | 106 | 30 | 52.2 | 0 | 36 | 295 | 280 | 388 | 0 | 30 | 158 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 35 | 83 | 197 | 93 | 0 | 0 | 6 | 8050.7 | 902 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 34 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 190 | 0 | 409 | 0 | 0 | 172 | 47 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 305 | 1220 | 0 | 7132 | 15182.7 | 107.76
23:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 48 | 0 | 86 | 80 | 15 | 0 | 35 | 100 | 0 | 370 | 298 | 400 | 0 | 17 | 333 | 0 | 0 | 0 | 90 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 66 | 44 | 0 | 24 | 25 | 0 | 218 | 0 | 36 | 770 | 0 | 0 | 50 | 8 | 16 | 220 | 0 | 0 | 0 | 550 | 0 | 51 | 137 | 86 | 0 | 350 | 330 | 45 | 196 | 41 | 72 | 50 | 182 | 62 | 12 | 106 | 32 | 52.2 | 0 | 43 | 295 | 270 | 385 | 0 | 30 | 158 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 35 | 84 | 195 | 97 | 0 | 0 | 0 | 8008.7 | 902 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 34 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 189 | 0 | 410 | 0 | 0 | 170 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 220 | 0 | 304 | 1230 | 0 | 7151 | 15159.7 | 107.74
Total KWH | 0 | 931200 | 750240 | 0 | 0 | 0 | 0 | 0 | 8208000 | 0 | 0 | 622440 | 0 | 1732608 | 395040 | 427800 | 31239 | 760002 | 1764000 | 38400 | 8398500 | 7025455 | 9546600 | 0 | 525754 | 7902594 | 0 | 0 | 171965 | 1503600 | 494400 | 469080 | 0 | 0 | 0 | 20073 | 227520 | 0 | 176160 | 505066 | 221239 | 0 | 344640 | 525120 | 28797 | 5277924 | 60217 | 445920 | 18603636.36 | 63564 | 0 | 580320 | 74849.4 | 144690 | 3495599 | 0 | 0 | 0 | 12109089 | 142155 | 1184858 | 1105672 | 1354909 | 0 | 8433900 | 7934000 | 1091520 | 4782000 | 885096 | 1528320 | 1421890 | 3562560 | 1310400 | 417360 | 1349760 | 918720 | 315998 | 428845 | 862640 | 7417000 | 6695100 | 9089000 | 0 | 674160 | 3552872.72 | 152520 | 0 | 1832640 | 719520 | 0 | 440000 | 1995740 | 281520 | 1892400 | 2930400 | 2538240 | 7600 | 151590 | 100320 | 174104566.48 | 21795636 | 8882784 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 481680 | 24232720 | 162720 | 28865454 | 0 | 80350 | 0 | 93888 | 124032 | 0 | 296856 | 32576 | 20635 | 297316 | 548139 | 51940 | 294000 | 4549818 | 0 | 0 | 0 | 4684527 | 0 | 9248509 | 0 | 26640 | 4143000 | 1083927 | 1592545 | 89481 | 1662441 | 0 | 0 | 36271.92 | 878400 | 4291 | 0 | 5122000 | 0 | 5431550 | 0 | 7322904 | 26090181.82 | 0 | 159139212.74 | 333243779.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13712.73 | MW | 12:00 Hr. | Energy Generated |  |  | 333.2438 |  | MKWHr.
| Day Peak Demand |  |  | 13712.73 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.206 |  | MKWHr.
| Evening Peak Generation |  |  | 15608.83 | MW | 19:30 Hr. | Energy Demand |  |  | 333.4498 |  | MKWHr.
| Evening Peak Demand |  |  | 15670.83 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 12097.84 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1016.96 |  | MMCFD
| Maximum Generation of the Day |  |  | 15608.83 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9758 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.0446 | 0 | 9.4823 | 0 | 0 | 0.17197 | 0 | 0 | 51.6989 | Gas | 141.3957 | Gas | 502872316.9352
| Chattogram Zone |  |  | 3.9415 | 30.7127 | 2.7673 | 0 | 5.2779 | 0.17095 | 0 | 0.17616 | 43.0466 | Coal | 98.7075 | Coal | 583947937.2118
| Cumilla Zone |  |  | 27.5055 | 0 | 10.0353 | 0 | 0 | 0.42884 | 0.91872 | 0 | 38.8884 | HFO | 31.6076 | HFO | 581925695.058
| Mymensingh Zone |  |  | 2.5382 | 0 | 5.2046 | 0 | 0 | 0.15919 | 0 | 0 | 7.9021 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5686 | Hydro | 5.2779 | Hydro | 527792.4
| Khulna Zone |  |  | 8.8828 | 24.2327 | 0.16272 | 0 | 0 | 0.48168 | 22.7076 | 0 | 56.4675 | Solar | 3.5872 | Solar | 52276780.4312
| Barishal Zone |  |  | 5.4315 | 38.5351 | 0 | 0 | 0 | 0.004291 | 0 | 0 | 43.9709 | Import | 52.4918 | Import | 267282890.22
| Rajshahi Zone |  |  | 18.4829 | 0 | 0.70028 | 0 | 0 | 1.1661 | 28.8655 | 0 | 49.2147 | Wind | 0.17616 | Wind | 2578982.4
| Rangpur Zone |  |  | 0 | 5.2269 | 3.255 | 0 | 0 | 1.0042 | 0 | 0 | 9.4861
| Total |  |  | 141.3957 | 98.7075 | 31.6076 | 0 | 5.2779 | 3.5872 | 52.4918 | 0.17616 | 333.2438
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 502872316.9352 |  | Hydro | 527792.4
|  |  |  | Coal | 583947937.2118 |  | Solar | 52276780.4312
|  |  |  | HFO | 581925695.058 |  | Import | 267282890.22
|  |  |  | HSD | 0 |  | Wind | 2578982.4
[5 empty] | Total: | 199,14,12,394 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7956 | Peak Hr Flow | 902.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47301163.74 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.8655 | Peak Hr Flow | 1320.83 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 676 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.91872 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1058 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.5798 | Peak Hr Flow | 2268.83 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5317
|  |  |  | Chattogram |  | 0 |  | 1458
|  |  |  | Cumilla |  | 0 |  | 1454
|  |  |  | Mymensingh |  | 10 |  | 1236
|  |  |  | Sylhet |  | 5 |  | 621
|  |  |  | Khulna |  | 0 |  | 1864
|  |  |  | Barishal |  | 0 |  | 473
|  |  |  | Rajshahi |  | 0 |  | 1599
|  |  |  | Rangpur |  | 44 |  | 1060
|  |  |  | Total |  | 59 |  | 15082
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 565
|  |  |  | Total Unavailable Capacity |  |  |  | 865
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 |  | Amtoli- Patuakhali RNPL 400 Ckt-1 Shutdown .
| 08:40 | 09:39 | Candpur- Kachua 132kV Ckt-1 Project Work S/D from Kachua 230/132/33kV end.
|  | 08:40 | Candpur- Kachua 132kV Ckt-1 is restored.
| 09:06 | 11:00 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Red Hot Maintenance at 33 kv Bus-1 | [7 empty] | 17.0MW load
|  |  | side by PBS. | [7 empty] | interrup.
|  | 09:08 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT is restored.
|  | 09:08 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT is restored.
| 09:15 |  | Bajitpur 132/33kV S/S Tr-2(414T) LT Forced S/D
| 10:35 | 11:24 | Nawabganj 132/33kV S/S TR-1 LT Forced S/D Due to Due to red hot maintenance on incomer-1
CB outgoing point.
| 10:36 | 11:22 | Nawabganj 132/33kV S/S TR-1 HT Forced S/D Due to Due to red hot maintenance on incomer-1
CB outgoing point.
| 10:50 |  | Amtoli- Patuakhali RNPL 400 Ckt-1 Shutdown Restore.
| 11:20 |  | Sikalbaha 225 MW ST was sync.
| 13:06 | 16:16 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Forced S/D Due to Oil leakage of 33kV CT.
| 13:07 | 16:15 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Forced S/D Due to Oil leakage of 33kV CT.
| 14:05 |  | Bhulta 132/33kV S/S GT2 LT Scheduled S/D Due to 33 KV Bus fault, which is connected | [7 empty] | 50.0MW load
|  |  | GT-1. Which is controlling by PBS. | [7 empty] | interrup.
| 15:05 | 16:56 | Chandpur 132/33kV S/S 402T HT Scheduled S/D Due to For set up Digital energy meter and
multifunction meter
| 15:35 | 16:30 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to T-1, 120MVA (Sec.) T-1 BUS 33 kV Side | [7 empty] | 16.0MW load
|  |  | 33/11 kV PDB Feeder 33/11 kV T-1 Transformer DS to Bus LA Loop (Y-Phase) flashing & | [7 empty] | interrup.
Cutup.
| 15:35 | 16:30 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 33/11 kV PDB Feeder 33/11 kV T-1 | [7 empty] | 16.0MW load
|  |  | Transformer DS to Bus LA Loop (Y-Phase) flashing & Cutup. | [7 empty] | interrup.
|  | 17:00 | Chandpur 132/33kV S/S 402T LT is restored.
| 17:01 |  | Chandpur 132/33kV S/S 412T LT Forced S/D Due to None
| 17:02 | 17:22 | BIPTC S/S 20DF21 Forced S/D
| 18:32 | 18:58 | Kulaura 132/33kV S/S TR-2 HT Tripped showing Transformer -2 differential protection | [7 empty] | 6.0MW load
|  |  | Relay relays Due to Oil temperature | [7 empty] | interrup.
| 18:43 |  | Raozan 25 MW PP Synchronized
| 19:30 |  | Peak generation 15608 MW
| 22:59 | 00:24 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 22:59 | 00:24 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 01:41 |  | Raozan 25 MW PP Shutdown
| 06:01 | 07:16 | Bakulia 132/33kV S/S T-3 (422T) LT Scheduled S/D Due to Emergency Hot Spot Maintenance of | [7 empty] | 6.0MW load
|  |  | T-03 Secondary Side R-Phase Bushing | [7 empty] | interrup.
| 06:02 | 07:15 | Bakulia 132/33kV S/S T-3 (422T) HT Scheduled S/D Due to Emergency Hot Spot Maintenance of | [7 empty] | 6.0MW load
|  |  | T-03 Secondary Side R-Phase Bushing. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 13033 MW.
| 07:07 |  | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Khulshi
circuit loop change
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 319 | 8208000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8398500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7025455 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 31239 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7902594 | machine problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46 | 622440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 395040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 760002 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 525754 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 494400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 469080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 750240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 427800 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 100 | 1732608 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 931200 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 38400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 1764000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171965 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 395 | 9546600 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1503600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2571 | 51698917
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 74849.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 142155 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 580320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5277924 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 3495599 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 27 | 144690 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 221239 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 505066 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 20 | 344640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 445920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 70 | 227520 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 20073 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 5 | 60217 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 525120 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 35 | 63564 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 540 | 12109089 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 176160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 770 | 18603636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2137 | 43046578.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4782000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 346 | 8433900 | machine problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7934000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 885096 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 1091520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 50 | 1354909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1184858 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1105672 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 862640 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1421890 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 174 | 3562560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 918720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 315998 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 417360 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1349760 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 1310400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 71 | 1528320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 428845 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1776 | 38888448
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 93 | 2538240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 185 | 2930400 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 1892400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 151590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 100320 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 281520 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 403 | 7902070
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 674160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3552872.72 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719520 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1832640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1995740 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 440000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 152520 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7417000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 9089000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 290 | 6695100 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2325 | 1354 | 32568552.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21795636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 354 | 8882784 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 162720 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 481680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1232 | 24232720 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2543 | 56467540
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 303 | 7322904 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1185 | 26090181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5431550 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5122000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4291 | -
Barishal Area Total |  |  |  |  | 2236 | 1984 | 43970926.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 297316 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 36 | 80350 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 7 | 32576 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4549818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Shutdown due to 4th Minor Inspection(MI) of GT.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4684527 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 396 | 9248509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 51940 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 20635 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 296856 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 124032 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 60 | 93888 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1320.83 | 28865454 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 294000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 548139 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2401.83 | 49214680
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1083927 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 171 | 4143000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1662441 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36271.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1592545 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 89481 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 878400 | -
Rangpur Area Total |  |  |  |  | 950 | 439 | 9486065.92
Eastern Grid Total |  |  |  |  | 17401.505 | 8241 | 174104566.48
Western Grid Total |  |  |  |  | 10442.16 | 7367.83 | 159139212.74
National Grid Total |  |  |  |  | 27843.665 | 15608.83 | 333243779.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10071.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4951.8 | MW
i) Dhaka area |  |  | 5317.19 |  | MW | i) Khulna area |  |  |  | 1863.6 | MW
ii) Chattogram area |  |  | 1458.5 |  | MW | ii) Barishal area |  |  |  | 473 | MW
iii) Cumilla area |  |  | 1453.87 |  | MW | iii) Rajshahi area |  |  |  | 1599.2 | MW
iv) Mymensingh area |  |  | 1226 |  | MW | iv) Rangpur area |  |  |  | 1016 | MW
v) Sylhet area |  |  | 616 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15023.36 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 19:30 | 133 | PHP | 9 | 12:00
2 | AKSML | 129 | 08:00 | 68 | Ishurdi | 87 | 20:00 | 134 | Pabna | 135 | 19:00
3 | Aftabnagar | 40 | 19:00 | 69 | Jaldhaka | 92 | 19:30 | 135 | Palashbari | 108 | 19:30
4 | Agargaon | 138 | 13:00 | 70 | Jamalpur | 144 | 20:00 | 136 | Panchagarh | 60 | 19:30
5 | Agrabad | 94 | 19:00 | 71 | Jashore | 148 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 35 | 00:00 | 72 | Jhenaidah | 138 | 19:30 | 138 | Patuakhali | 73 | 22:00
7 | Ashuganj | 95 | 02:00 | 73 | Joydebpur | 155 | 21:00 | 139 | Payra | 34 | 00:00
8 | BSRM | 199 | 04:00 | 74 | Joypurhat | 64 | 23:00 | 140 | Postogola | 55 | 19:00
9 | Bagerhat | 89 | 22:00 | 75 | Juldah | 16 | 23:00 | 141 | Purbachal | 21 | 19:00
10 | Bajitpur | 92 | 19:00 | 76 | KSRM | 25 | 18:30 | 142 | Purbasadipur | 135 | 00:00
11 | Bakulia | 94 | 19:00 | 77 | Kabirpur | 237 | 11:00 | 143 | Rahanpur | 42 | 00:00
12 | Banani | 53 | 13:00 | 78 | Kachua | 98 | 19:00 | 144 | Rahim | 43 | 15:00
13 | Bangabhaban | 19 | 11:00 | 79 | Kallyanpur | 105 | 19:00 | 145 | Rajbari | 85 | 20:00
14 | Barapukuria | 72 | 19:30 | 80 | Kalurghat | 38 | 12:00 | 146 | Rajendrapur | 141 | 19:30
15 | Barguna | 24 | 23:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi | 116 | 21:00
16 | Barishal | 119 | 19:30 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 92 | 21:00
17 | Barishal-230 | 94 | 00:00 | 83 | Kasba | 37 | 21:00 | 149 | Ramganj | 120 | 20:00
18 | Baroaulia | 72 | 15:00 | 84 | Kazla | 90 | 01:00 | 150 | Rampur | 38 | 19:00
19 | Baroirhat | 64 | 21:00 | 85 | Keranigonj | 97 | 19:00 | 151 | Rangamati | 19 | 19:30
20 | Bashundhara | 198 | 13:00 | 86 | Khagrachori | 34 | 19:00 | 152 | Rangpur | 144 | 19:00
21 | BashundharaCement | 6 | 04:00 | 87 | Khulna | 67 | 21:00 | 153 | Ruppur | 7.4 | 12:00
22 | Beanibazar | 76 | 21:00 | 88 | Khulshi | 174 | 13:00 | 154 | SSM | 10 | 00:00
23 | Benapole | 64 | 21:00 | 89 | Kishoreganj | 138 | 20:00 | 155 | Saidpur | 114 | 19:30
24 | Bhaluka | 142 | 15:00 | 90 | Kodda | 300 | 19:00 | 156 | Satkhira | 138 | 22:00
25 | Bhandaria | 68 | 22:00 | 91 | Kulaura | 50 | 23:00 | 157 | Satmasjid | 100 | 19:00
26 | Bhangura | 38 | 21:00 | 92 | Kurigram | 65 | 19:00 | 158 | Savar | 233 | 15:00
27 | Bheramara(GK) | 70 | 19:30 | 93 | Kushtia | 158 | 19:30 | 159 | SevenRings | 16.72 | 11:00
28 | Bhulta | 118 | 11:00 | 94 | Laksam | 22 | 00:00 | 160 | ShahCement | 25 | 13:00
29 | Bog-Sherpur | 76 | 21:00 | 95 | Lakshmipur | 21 | 21:00 | 161 | Shahjadpur | 93 | 19:00
30 | Bogura | 171 | 20:00 | 96 | Lalbag | 40 | 13:00 | 162 | Shahjibazar | 126 | 19:00
31 | Borhanuddin | 93 | 02:00 | 97 | Lalmonirhat | 67 | 19:00 | 163 | Shahmirpur | 56 | 00:00
32 | Brahmanbaria | 137 | 21:00 | 98 | MI_Cement | 15.7 | 09:00 | 164 | Shariatpur | 90 | 22:00
33 | Cantonment | 140 | 13:00 | 99 | Madanganj | 40 | 00:00 | 165 | Sherpur | 164 | 00:00
34 | Chandina | 18.47 | 07:00 | 100 | Madaripur | 116 | 23:00 | 166 | Shikalbaha | 14 | 12:00
35 | Chandpur | 83 | 23:00 | 101 | Madartek | 89 | 23:00 | 167 | Shitalakhya | 88.8 | 12:00
36 | Chandraghona | 38 | 19:30 | 102 | Madunaghat | 57 | 21:00 | 168 | Sholosohor | 45 | 15:00
37 | Chapai | 67 | 22:00 | 103 | Magura | 66 | 19:00 | 169 | Shyampur | 162 | 01:00
38 | Charsaidpur | 41 | 19:30 | 104 | Mahasthangarh | 94 | 23:00 | 170 | Siddhirganj | 122 | 13:00
39 | Chauddagram | 73 | 22:00 | 105 | Maijdee | 15 | 21:00 | 171 | Sirajganj | 114 | 19:30
40 | Chhatak | 38 | 22:00 | 106 | Manikganj | 134 | 21:00 | 172 | Sonargaon | 119 | 21:00
41 | Chowmuhani | 199 | 23:00 | 107 | Maniknagar | 86 | 13:00 | 173 | Sreemongol | 83 | 23:00
42 | Chuadanga | 118 | 19:30 | 108 | Matarbari | 116 | 21:00 | 174 | Sreepur | 107 | 16:00
43 | Coxsbazar | 135 | 21:00 | 109 | Matuail | 63 | 10:00 | 175 | Srinagar | 50.81 | 22:00
44 | Cumilla(N) | 145 | 20:00 | 110 | Millgate | 125 | 12:00 | 176 | Sunamganj | 63 | 21:00
45 | Cumilla(S) | 167 | 19:00 | 111 | Mirpur | 124 | 19:00 | 177 | Sylhet | 48 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 10:00 | 178 | Sylhet-132 | 114 | 17:00
47 | Daudkandi | 156 | 23:00 | 113 | Mirzapur | 48 | 21:00 | 179 | TK | 33 | 19:00
48 | Dhaka | 80 | 13:00 | 114 | Mithapukur | 69 | 19:00 | 180 | Tangail | 208 | 20:00
49 | Dhamrai | 120 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:30
50 | Dhanmondi | 150 | 13:00 | 116 | Mogbazar | 155.6 | 16:00 | 182 | Thakurgaon | 115 | 19:30
51 | Dohazari | 113 | 21:00 | 117 | Mongla | 44 | 17:00 | 183 | Tongi | 102 | 15:00
52 | Faridpur | 171 | 19:30 | 118 | Motijheel | 47 | 13:00 | 184 | Ullahpara | 41 | 19:30
53 | Fatullah | 97 | 12:00 | 119 | Muktagacha | 38 | 22:00 | 185 | Ullon | 40 | 19:00
54 | Fenchuganj | 47 | 20:00 | 120 | Munshiganj | 114 | 23:00 | 186 | Uttara | 93 | 13:00
55 | Feni | 119 | 21:00 | 121 | Muradnagar | 44 | 21:00 | 187 | UttaraNew | 61 | 23:00
56 | GPH | 79 | 15:00 | 122 | Mymensingh | 214 | 19:30 | 188 | Zigatola | 74 | 15:00
57 | Ghatail | 86 | 21:00 | 123 | Naogaon | 138 | 19:30
58 | Ghorashal | 14 | 12:00 | 124 | Narail | 62.5 | 19:30
59 | Ghorashal-230 | 105 | 23:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 39 | 19:30 | 126 | Narshingdi | 188 | 00:00
61 | Gollamari | 96 | 23:00 | 127 | Natore | 155 | 19:30
62 | Gopalganj | 112.8 | 20:00 | 128 | Nawabganj | 61.4 | 22:00
63 | Gulshan | 126 | 13:00 | 129 | Netrakona | 137 | 19:30
64 | Halishahar | 65 | 15:00 | 130 | New | 66 | 15:00
65 | HaripurSBU | 167 | 16:00 | 131 | Niamatpur | 81 | 22:00
66 | Hasnabad | 81 | 13:00 | 132 | Noapara | 41 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14293.17 | 0 |  | 14293.17
1:00 | 13871.18 | 0 |  | 13871.18
2:00 | 13539.13 | 0 |  | 13539.13
3:00 | 13091.61 | 0 |  | 13091.61
4:00 | 12867.76 | 0 |  | 12867.76
5:00 | 12669.64 | 0 |  | 12669.64
6:00 | 12097.84 | 0 |  | 12097.84
7:00 | 12286.2 | 0 |  | 12286.2
8:00 | 12364.4 | 0 |  | 12364.4
9:00 | 12618.91 | 0 |  | 12618.91
10:00 | 12852.86 | 0 |  | 12852.86
11:00 | 13247.95 | 0 |  | 13247.95
12:00 | 13712.73 | 0 |  | 13712.73
13:00 | 14081.17 | 0 |  | 14081.17
14:00 | 14069.82 | 0 |  | 14069.82
15:00 | 14205.61 | 0 |  | 14205.61
16:00 | 14183.56 | 0 |  | 14183.56
17:00 | 13732.52 | 0 |  | 13732.52
18:00 | 13185.24 | 0 |  | 13185.24
19:00 | 14519.87 | 30 |  | 14550.87
19:30 | 15608.83 | 59 |  | 15670.83
20:00 | 15567.92 | 51 |  | 15620.92
21:00 | 15359.2 | 49 |  | 15410.2
22:00 | 15182.7 | 46 |  | 15230.7
23:00 | 15159.7 | 30 |  | 15190.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7233 | 7060.17 | 14293.17 | DAILY GENERATION CURVE
00:30 | 7125 | 6957.175 | 14082.175
01:00 | 7017 | 6854.18 | 13871.18 | 10-08-2025
01:30 | 6999 | 6706.155 | 13705.155
02:00 | 6981 | 6558.13 | 13539.13
02:30 | 6926 | 6389.37 | 13315.37
03:00 | 6871 | 6220.61 | 13091.61
03:30 | 6823.5 | 6156.185 | 12979.685
04:00 | 6776 | 6091.76 | 12867.76
04:30 | 6708.5 | 6060.2 | 12768.7
05:00 | 6641 | 6028.64 | 12669.64
05:30 | 6442.57 | 5941.17 | 12383.74
06:00 | 6244.14 | 5853.7 | 12097.84
06:30 | 6316.155 | 5875.865 | 12192.02
07:00 | 6388.17 | 5898.03 | 12286.2
07:30 | 6391.405 | 5933.895 | 12325.3
08:00 | 6394.64 | 5969.76 | 12364.4
08:30 | 6496.28 | 5995.375 | 12491.655
09:00 | 6597.92 | 6020.99 | 12618.91
09:30 | 6622.79 | 6113.095 | 12735.885
10:00 | 6647.66 | 6205.2 | 12852.86
10:30 | 6759.475 | 6290.93 | 13050.405
11:00 | 6871.29 | 6376.66 | 13247.95
11:30 | 7038.9 | 6441.44 | 13480.34
12:00 | 7206.51 | 6506.22 | 13712.73
12:30 | 7244.62 | 6652.33 | 13896.95
13:00 | 7282.73 | 6798.44 | 14081.17
13:30 | 7285.605 | 6789.89 | 14075.495
14:00 | 7288.48 | 6781.34 | 14069.82
14:30 | 7317.985 | 6819.73 | 14137.715
15:00 | 7347.49 | 6858.12 | 14205.61
15:30 | 7364.62 | 6829.965 | 14194.585
16:00 | 7381.75 | 6801.81 | 14183.56
16:30 | 7293.1 | 6664.94 | 13958.04
17:00 | 7204.45 | 6528.07 | 13732.52
17:30 | 7118.89 | 6339.99 | 13458.88
18:00 | 7033.33 | 6151.91 | 13185.24
18:30 | 7391.665 | 6460.89 | 13852.555
19:00 | 7750 | 6769.87 | 14519.87
19:30 | 8241 | 7367.83 | 15608.83
20:00 | 8287 | 7280.92 | 15567.92
20:30 | 8272.1 | 7191.46 | 15463.56 |  | Executive Engineer
21:00 | 8257.2 | 7102 | 15359.2 |  | Network Operation Division
21:30 | 8153.95 | 7117 | 15270.95
22:00 | 8050.7 | 7132 | 15182.7
22:30 | 8029.7 | 7141.5 | 15171.2
23:00 | 8008.7 | 7151 | 15159.7

## En-Curve
QF-LDC-12
Date | 10-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3857 | 2108 | 900 | 38 | 44 | 1446.17 | 221 | 4375 | 0 | 247 | 1055 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3853.5 | 2081 | 900 | 38 | 44 | 1450.675 | 220.5 | 4269 | 0 | 231.5 | 993 | 0 | 0 | 1 | 0 | 10-08-2025
01:00 | 3850 | 2054 | 900 | 38 | 44 | 1455.18 | 220 | 4163 | 0 | 216 | 931 | 0 | 0 | 0 | 0
01:30 | 3868.5 | 2056.5 | 897.5 | 38 | 43 | 1379.155 | 220 | 4102 | 0 | 195 | 904 | 0 | 0 | 1.5 | 0 | Energy Generated | 333.2438 |  | MKWHr
02:00 | 3887 | 2059 | 895 | 38 | 42 | 1303.13 | 220 | 4041 | 0 | 174 | 877 | 0 | 0 | 3 | 0 | Energy not Served | 0.206 |  | MKWHr
02:30 | 3886 | 2059.5 | 895.5 | 38 | 42 | 1310.87 | 219.5 | 3892.5 | 0 | 149 | 819.5 | 0 | 0 | 3 | 0 | Total Energy Requirement | 333.4498 |  | MKWHr
03:00 | 3885 | 2060 | 896 | 38 | 42 | 1318.61 | 219 | 3744 | 0 | 124 | 762 | 0 | 0 | 3 | 0
03:30 | 3876.5 | 2061 | 896 | 38 | 41 | 1260.685 | 219 | 3724 | 0 | 115.5 | 744.5 | 0 | 0 | 3.5 | 0
04:00 | 3868 | 2062 | 896 | 38 | 40 | 1202.76 | 219 | 3704 | 0 | 107 | 727 | 0 | 0 | 4 | 0
04:30 | 3853.5 | 2060.5 | 896 | 38 | 40 | 1207.7 | 219 | 3678 | 0 | 94.5 | 676 | 0 | 0 | 5.5 | 0
05:00 | 3839 | 2059 | 896 | 38 | 40 | 1212.64 | 219 | 3652 | 0 | 82 | 625 | 0 | 0 | 7 | 0
05:30 | 3722.5 | 2029 | 895.5 | 38 | 38 | 1171.08 | 219 | 3617 | 6.16 | 73 | 566.5 | 0 | 0 | 8 | 0
06:00 | 3606 | 1999 | 895 | 38 | 36 | 1129.52 | 219 | 3582 | 12.32 | 64 | 508 | 0 | 0 | 9 | 0
06:30 | 3635.5 | 2036.5 | 895 | 38 | 36 | 1074.275 | 220 | 3615.5 | 45.745 | 74 | 513.5 | 0 | 0 | 8 | 0
07:00 | 3665 | 2074 | 895 | 38 | 36 | 1019.03 | 221 | 3649 | 79.17 | 84 | 519 | 0 | 0 | 7 | 0
07:30 | 3614 | 2051.5 | 898 | 38 | 35 | 1017.015 | 221 | 3676 | 137.785 | 95.5 | 538 | 0 | 0 | 3.5 | 0
08:00 | 3563 | 2029 | 901 | 38 | 34 | 1015 | 221 | 3703 | 196.4 | 107 | 557 | 0 | 0 | 0 | 0
08:30 | 3586.5 | 2031 | 901 | 38 | 34 | 1023.5 | 221.5 | 3700.5 | 232.155 | 145 | 578.5 | 0 | 0 | 0 | 0
09:00 | 3610 | 2033 | 901 | 38 | 34 | 1032 | 222 | 3698 | 267.91 | 183 | 600 | 0 | 0 | 0 | 0
09:30 | 3621.5 | 2038.5 | 901.5 | 38 | 34 | 1036 | 221.5 | 3709.5 | 335.885 | 183 | 616.5 | 0 | 0 | 0 | 0
10:00 | 3633 | 2044 | 902 | 38 | 34 | 1040 | 221 | 3721 | 403.86 | 183 | 633 | 0 | 0 | 0 | 0
10:30 | 3647 | 2051 | 901.5 | 38 | 35 | 1035.5 | 221 | 3850.5 | 436.905 | 183 | 651 | 0 | 0 | 0 | 0
11:00 | 3661 | 2058 | 901 | 38 | 36 | 1031 | 221 | 3980 | 469.95 | 183 | 669 | 0 | 0 | 0 | 0
11:30 | 3713 | 2035.5 | 901 | 38 | 38 | 1030 | 221 | 4037.5 | 505.84 | 189.5 | 771 | 0 | 0 | 0 | 0
12:00 | 3765 | 2013 | 901 | 38 | 40 | 1029 | 221 | 4095 | 541.73 | 196 | 873 | 0 | 0 | 0 | 0
12:30 | 3757.5 | 1998 | 901.5 | 38 | 40 | 1049 | 220.5 | 4212.5 | 518.45 | 196 | 963 | 0 | 0 | 2.5 | 0
13:00 | 3750 | 1983 | 902 | 38 | 40 | 1069 | 220 | 4330 | 495.17 | 196 | 1053 | 0 | 0 | 5 | 0
13:30 | 3787 | 1932 | 902 | 38 | 42 | 1119.15 | 219.5 | 4278 | 505.345 | 195.5 | 1052.5 | 0 | 0 | 4.5 | 0
14:00 | 3824 | 1881 | 902 | 38 | 44 | 1169.3 | 219 | 4226 | 515.52 | 195 | 1052 | 0 | 0 | 4 | 0
14:30 | 3884 | 1917.5 | 901.5 | 38 | 44 | 1176.47 | 219 | 4262 | 447.145 | 195 | 1051.1 | 0 | 0 | 2 | 0
15:00 | 3944 | 1954 | 901 | 38 | 44 | 1183.64 | 219 | 4298 | 378.77 | 195 | 1050.2 | 0 | 0 | 0 | 0
15:30 | 3910.5 | 1941.5 | 901 | 38 | 43 | 1172.995 | 219.5 | 4340.5 | 311.49 | 195 | 1111.6 | 0 | 0 | 9.5 | 0
16:00 | 3877 | 1929 | 901 | 38 | 42 | 1162.35 | 220 | 4383 | 244.21 | 195 | 1173 | 0 | 0 | 19 | 0
16:30 | 3838 | 1913 | 901.5 | 38 | 42 | 1160.065 | 219 | 4279 | 175.475 | 195 | 1173 | 0 | 0 | 24 | 0
17:00 | 3799 | 1897 | 902 | 38 | 42 | 1157.78 | 218 | 4175 | 106.74 | 195 | 1173 | 0 | 0 | 29 | 0
17:30 | 3740.5 | 1878.5 | 901.5 | 38 | 41 | 1107.945 | 218 | 4070 | 69.335 | 194.5 | 1171.1 | 0 | 0 | 28.5 | 0
18:00 | 3682 | 1860 | 901 | 38 | 40 | 1058.11 | 218 | 3965 | 31.93 | 194 | 1169.2 | 0 | 0 | 28 | 0
18:30 | 3805.5 | 1899.5 | 901.5 | 38 | 44 | 1104.99 | 218 | 4123 | 15.965 | 340.5 | 1337.1 | 0 | 0 | 24.5 | 15
19:00 | 3929 | 1939 | 902 | 38 | 48 | 1151.87 | 218 | 4281 | 0 | 487 | 1505 | 0 | 0 | 21 | 30
19:30 | 3901 | 2030 | 902 | 38 | 46 | 1320.83 | 218 | 4524 | 0 | 559 | 2056 | 0 | 0 | 14 | 59
20:00 | 3779 | 2014 | 903 | 38 | 46 | 1397.92 | 218 | 4463 | 0 | 579 | 2116 | 0 | 0 | 14 | 51
20:30 | 3817.5 | 2009.5 | 902.5 | 38 | 38 | 1424.96 | 218 | 4431.5 | 0 | 508.5 | 2060.6 | 0 | 0 | 14.5 | 50
21:00 | 3856 | 2005 | 902 | 38 | 30 | 1452 | 218 | 4400 | 0 | 438 | 2005.2 | 0 | 0 | 15 | 49
21:30 | 3910.5 | 2049.75 | 902 | 38 | 30 | 1444 | 218 | 4407 | 0 | 438 | 1821.7 | 0 | 0 | 12 | 47.5
22:00 | 3965 | 2094.5 | 902 | 38 | 30 | 1436 | 218 | 4414 | 0 | 438 | 1638.2 | 0 | 0 | 9 | 46
22:30 | 3952.5 | 2097 | 902 | 38 | 31 | 1440 | 218 | 4418 | 0 | 442.5 | 1624.7 | 0 | 0 | 7.5 | 38
23:00 | 3940 | 2099.5 | 902 | 38 | 32 | 1444 | 218 | 4422 | 0 | 447 | 1611.2 | 0 | 0 | 6 | 30
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 06:00 | 372 | 15:00 | Payra | 415 | 04:00 | 410 | 00:00
Ashuganj | 404 | 07:00 | 393 | 23:00 | Rahanpur | 401 | 08:00 | 385 | 00:00
Bhulta | 398 | 06:00 | 368 | 15:00 | Rampal | 405 | 06:00 | 391 | 15:00
Bibiana | 390 | 06:00 | 381 | 15:00
BIPTC | 404 | 07:00 | 393 | 23:00
Bogura | 384 | 08:00 | 364 | 22:00
Gopalganj | 400 | 06:00 | 386 | 15:00 |  |  |  |  | 77520
Kaliakoir | 377 | 06:00 | 362 | 15:00
Madunaghat | 391 | 06:00 | 383 | 15:00
Meghnaghat | 389 | 08:00 | 377 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 216 | 15:00 | Keranigonj | 225 | 06:00 | 215 | 13:00
AKSML | 231 | 07:00 | 221 | 14:00 | Khulna(S) | 230 | 08:00 | 219 | 00:00
Aminbazar | 227 | 04:00 | 217 | 15:00 | Madunaghat | 232 | 20:00 | 224 | 15:00
Ashuganj | 232 | 05:00 | 219 | 15:00 | Madunaghat-400 | 231 | 06:00 | 225 | 14:00
Ashuganj-400 | 232 | 05:00 | 219 | 15:00 | Maniknagar | 223 | 06:00 | 214 | 15:00
Baghabari | 235 | 06:00 | 225 | 00:00 | Meghnaghat | 230 | 08:00 | 219 | 21:00
Barapukuria | 225 | 06:00 | 218 | 19:00 | Meghnaghat-400 | 226 | 04:00 | 217 | 15:00
Barapukuria-230 | 225 | 06:00 | 218 | 19:00 | Mirsorai | 227 | 20:00 | 218 | 15:00
Barishal | 227 | 07:00 | 219 | 00:00 | Rajshahi | 232 | 08:00 | 219 | 00:00
Bheramara | 233 | 06:00 | 222 | 00:00 | Rampal | 230 | 08:00 | 219 | 00:00
Bhulta | 229 | 06:00 | 210 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 222 | 15:00 | Rampura | 228 | 06:00 | 206 | 15:00
BIPTC | 236 | 08:00 | 222 | 19:00 | Shikalbaha | 229 | 06:00 | 223 | 12:00
Bogura | 237 | 08:00 | 225 | 22:00 | Shyampur | 225 | 06:00 | 215 | 15:00
Bogura-400 | 238 | 08:00 | 226 | 22:00 | Siddhirganj | 224 | 07:00 | 216 | 16:00
Borhanuddin | 231 | 07:00 | 224 | 22:00 | Sirajgonj | 241 | 08:00 | 233 | 00:00
BSRM | 228 | 06:00 | 218 | 15:00 | Sreepur | 229 | 06:00 | 218 | 15:00
Cumilla(N) | 224 | 05:00 | 214 | 14:00 | Tongi | 229 | 06:00 | 212 | 15:00
Faridpur | 226 | 06:00 | 218 | 00:00
Fenchuganj | 231 | 06:00 | 224 | 15:00
Ghorashal | 225 | 00:00 | 220 | 15:00
Ghorashal-230 | 228 | 06:00 | 212 | 15:00
Gopalganj | 227 | 07:00 | 219 | 00:00
GPH | 229 | 03:00 | 220 | 15:00
Haripur | 224 | 06:00 | 216 | 15:00
Hasnabad | 224 | 04:00 | 215 | 15:00
Hathazari | 231 | 10:00 | 220 | 12:00
Ishurdi | 236 | 08:00 | 25 | 00:00
Jhenaidah | 230 | 09:00 | 216 | 00:00
Kaliakoir | 233 | 06:00 | 220 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 122 | 15:00 | Lalmonirhat | 133 | 07:00 | 121 | 18:30
Agargaon | 133 | 04:00 | 125 | 15:00 | Madanganj | 129 | 03:00 | 124 | 13:00
Agrabad | 131 | 21:00 | 124 | 15:00 | Madaripur | 134 | 07:00 | 129 | 22:00
AKS | 128 | 06:00 | 125 | 10:00 | Madartek | 136 | 06:00 | 13 | 02:00
Aminbazar | 133 | 04:00 | 126 | 14:00 | Madunaghat | 131 | 05:00 | 126 | 15:00
Amnura | 136 | 08:00 | 126 | 00:00 | Magura | 132 | 09:00 | 121 | 00:00
Ashuganj | 142 | 06:00 | 52 | 22:00 | Mahasthangarh | 136 | 09:00 | 126 | 23:00
Bagerhat | 132 | 08:00 | 119 | 00:00 | Maijdee | 121 | 18:30 | 111 | 15:00
Bajitpur | 131 | 05:00 | 123 | 23:00 | Manikganj | 128 | 03:00 | 120 | 15:00
Bakulia | 131 | 19:30 | 126 | 13:00 | Maniknagar | 135 | 04:00 | 126 | 11:00
Banani | 137 | 05:00 | 122 | 15:00 | Matarbari | 117 | 09:00 | 109 | 15:00
Bangabhaban | 135 | 06:00 | 127 | 15:00 | Matuail | 130 | 04:00 | 125 | 11:00
Barapukuria | 136 | 08:00 | 128 | 19:00 | Millgate | 134 | 05:00 | 123 | 15:00
Barguna | 134 | 07:00 | 130 | 00:00 | Mirpur | 132 | 06:00 | 125 | 11:00
Barishal | 133 | 08:00 | 125 | 19:00 | Mirzapur | 130 | 08:00 | 125 | 12:00
Barishal-230 | 133 | 07:00 | 126 | 00:00 | Mithapukur | 130 | 09:00 | 116 | 23:00
Baroaulia | 130 | 00:00 | 126 | 13:00 | MI_Cement | 130.2 | 05:00 | 125 | 11:00
Baroirhat | 123 | 06:00 | 117 | 15:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 137 | 04:00 | 122 | 15:00 | Mogbazar | 138 | 05:00 | 124 | 11:00
BashundharaCement | 129 | 03:00 | 124 | 13:00 | Mongla | 132 | 08:00 | 120 | 00:00
Beanibazar | 129 | 06:00 | 124 | 15:00 | Motijheel | 135 | 06:00 | 127 | 15:00
Benapole | 131 | 07:00 | 23 | 01:00 | Muktagacha | 135 | 18:00 | 132 | 02:00
Bhaluka | 130 | 06:00 | 122 | 15:00 | Munshiganj | 130 | 20:00 | 125 | 10:00
Bhandaria | 127 | 09:00 | 115 | 22:00 | Muradnagar | 125 | 06:00 | 119 | 15:00
Bhangura | 135 | 08:00 | 127 | 21:00 | Mymensingh | 136 | 09:00 | 116 | 19:30
Bheramara | 137 | 06:00 | 132 | 19:00 | Naogaon | 134 | 08:00 | 123 | 22:00
Bheramara(GK) | 137 | 06:00 | 132 | 00:00 | Narail | 131 | 09:00 | 119 | 19:00
Bhulta | 128 | 06:00 | 122 | 13:00 | Narinda | 135 | 04:00 | 126 | 11:00
Bog-Sherpur | 137 | 09:00 | 127 | 23:00 | Narshingdi | 135 | 05:00 | 122 | 12:00
Bogura | 139 | 08:00 | 130 | 22:00 | Natore | 135 | 08:00 | 127 | 22:00
Bogura-230 | 140 | 08:00 | 131 | 22:00 | Nawabganj | 161 | 18:30 | 127 | 12:00
Brahmanbaria | 136 | 03:00 | 128 | 14:00 | Netrakona | 125 | 05:00 | 113 | 19:30
Cantonment | 133 | 04:00 | 124 | 15:00 | New | 134 | 04:00 | 126 | 12:00
Chandina | 128 | 06:00 | 121 | 14:00 | Niamatpur | 136 | 06:00 | 130 | 00:00
Chandpur | 128 | 18:00 | 122 | 15:00 | Noapara | 134 | 06:00 | 124 | 00:00
Chandraghona | 131 | 05:00 | 120 | 15:00 | Pabna | 135 | 06:00 | 128 | 19:00
Chapai | 136 | 09:00 | 130 | 00:00 | Palashbari | 129 | 09:00 | 114 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 04:00 | 125 | 11:00 | Panchagarh | 131 | 18:30 | 121 | 13:00
Chauddagram | 123 | 05:00 | 117 | 14:00 | Patiya | 130 | 19:00 | 124 | 13:00
Chhatak | 130 | 07:00 | 120 | 19:30 | Patuakhali | 134 | 05:00 | 131 | 00:00
Chowmuhani | 120 | 18:00 | 111 | 15:00 | Payra | 136 | 03:00 | 134 | 00:00
Chuadanga | 131 | 08:00 | 119 | 19:00 | PHP | 123 | 18:30 | 115 | 15:00
Coxsbazar | 119 | 09:00 | 111 | 14:00 | Postogola | 133 | 05:00 | 127 | 15:00
Cumilla(N) | 128 | 07:00 | 121 | 15:00 | Purbachal | 137 | 05:00 | 122 | 15:00
Cumilla(S) | 132 | 04:00 | 120 | 15:00 | Purbasadipur | 130 | 02:00 | 122 | 15:00
Daganbhuiyan | 121 | 18:00 | 112 | 15:00 | Rahanpur | 137 | 07:00 | 131 | 00:00
Daudkandi | 126 | 18:00 | 117 | 15:00 | Rahanpur-400 | 138 | 07:00 | 132 | 00:00
Dhaka | 136 | 03:00 | 123 | 15:00 | Rahim | 131 | 06:00 | 124 | 13:00
Dhamrai | 133 | 05:00 | 123 | 15:00 | Rajbari | 133 | 06:00 | 126 | 00:00
Dhanmondi | 137 | 06:00 | 125 | 15:00 | Rajendrapur | 130 | 08:00 | 120 | 14:00
Dohazari | 127 | 19:00 | 119 | 15:00 | Rajshahi | 134 | 08:00 | 126 | 00:00
Faridpur | 135 | 07:00 | 129 | 00:00 | Rajshahi-230 | 134 | 08:00 | 126 | 00:00
Fatullah | 132 | 06:00 | 126 | 11:00 | Ramganj | 121 | 05:00 | 116 | 19:00
Fenchuganj | 136 | 05:00 | 132 | 01:00 | Rampur | 130 | 06:00 | 125 | 12:00
Feni | 123 | 18:00 | 116 | 15:00 | Rampura | 136 | 04:00 | 122 | 15:00
Ghatail | 131 | 20:00 | 127 | 01:00 | Rangamati | 130 | 03:00 | 127 | 12:00
Ghorashal | 137 | 07:00 | 128 | 15:00 | Rangpur | 131 | 12:00 | 125 | 15:00
Goalpara | 136 | 08:00 | 126 | 00:00 | Ruppur | 138 | 07:00 | 132 | 00:00
Gollamari | 136 | 06:00 | 127 | 19:00 | Saidpur | 131 | 02:00 | 124 | 15:00
Gopalganj | 135 | 06:00 | 127 | 00:00 | Satkhira | 133 | 08:00 | 122 | 00:00
Gopalganj-400 | 136 | 05:00 | 131 | 00:00 | Satmasjid | 133 | 07:00 | 125 | 12:00
Gulshan | 137 | 05:00 | 123 | 15:00 | Savar | 131 | 18:00 | 125 | 00:00
Halishahar | 131 | 02:00 | 126 | 10:00 | SevenRings | 136 | 06:00 | 125 | 15:00
Haripur | 130 | 05:00 | 126 | 11:00 | ShahCement | 130 | 04:00 | 125 | 11:00
HaripurSBU | 131 | 06:00 | 126 | 11:00 | Shahjadpur | 138 | 05:00 | 132 | 00:00
Hasnabad | 132 | 03:00 | 127 | 12:00 | Shahjibazar | 139 | 08:00 | 129 | 00:00
Hathazari | 133 | 05:00 | 127 | 13:00 | Shahmirpur | 133 | 02:00 | 126 | 15:00
Ishurdi | 139 | 08:00 | 132 | 00:00 | Shariatpur | 133 | 08:00 | 126 | 00:00
Jaldhaka | 128 | 07:00 | 121 | 19:30 | Sherpur | 137 | 11:00 | 130 | 05:00
Jamalpur | 139 | 18:00 | 132 | 05:00 | Shikalbaha | 121 | 09:00 | 115 | 15:00
Jashore | 130 | 08:00 | 119 | 00:00 | Shikalbaha-230 | 132 | 06:00 | 125 | 10:00
Jhenaidah | 134 | 07:00 | 122 | 19:00 | Shitalakhya | 130.2 | 04:00 | 125 | 11:00
Jhenaidah-230 | 135 | 10:00 | 125 | 00:00 | Sholosohor | 131 | 20:00 | 126 | 15:00
Joydebpur | 134 | 07:00 | 121 | 15:00 | Shyampur | 130 | 02:00 | 125 | 12:00
Joypurhat | 133 | 09:00 | 120 | 23:00 | Shyampur-230 | 131 | 05:00 | 125 | 15:00
Juldah | 132 | 21:00 | 126 | 12:00 | Siddhirganj | 131 | 04:00 | 126 | 11:00
Kabirpur | 131 | 05:00 | 121 | 15:00 | Sirajganj | 134 | 09:00 | 125 | 22:00
Kachua | 127 | 18:00 | 120 | 15:00 | Sonargaon | 129 | 03:00 | 123 | 14:00
Kaliakoir | 134 | 04:00 | 126 | 15:00 | Sreemongol | 135 | 08:00 | 128 | 00:00
Kallyanpur | 132 | 05:00 | 127 | 11:00 | Sreepur | 133 | 06:00 | 126 | 15:00
Kalurghat | 131 | 06:00 | 126 | 15:00 | Srinagar | 135 | 06:00 | 127 | 15:00
Kamrangirchar | 135 | 04:00 | 127 | 13:00 | SSM | 132 | 00:00 | 129 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 126 | 08:00 | 118 | 19:30
Kasba | 124 | 06:00 | 117 | 15:00 | Sylhet | 130 | 07:00 | 125 | 15:00
Kazla | 135 | 06:00 | 127 | 16:00 | Sylhet-132 | 130 | 05:00 | 126 | 14:00
Keranigonj | 135 | 05:00 | 127 | 15:00 | Tangail | 127 | 08:00 | 124 | 12:00
Khagrachori | 130 | 06:00 | 126 | 13:00 | Taraganj | 130 | 09:00 | 122 | 19:00
Khulna | 136 | 07:00 | 126 | 00:00 | Thakurgaon | 131 | 02:00 | 120 | 15:00
Khulna(S) | 137 | 08:00 | 128 | 00:00 | TK | 131 | 00:00 | 126 | 15:00
Khulshi | 129 | 04:00 | 124 | 13:00 | Tongi | 135 | 06:00 | 126 | 15:00
Kishoreganj | 129 | 07:00 | 121 | 23:00 | Ullahpara | 135 | 08:00 | 127 | 07:00
Kodda | 131 | 08:00 | 120 | 14:00 | Ullon | 136 | 05:00 | 123 | 15:00
KSRM | 132 | 23:00 | 126 | 14:00 | Uttara | 132 | 05:00 | 125 | 11:00
Kulaura | 135 | 07:00 | 130 | 17:00 | UttaraNew | 133 | 05:00 | 125 | 11:00
Kurigram | 131 | 04:00 | 121 | 19:00 | Zigatola | 135 | 05:00 | 127 | 15:00
Kushtia | 134 | 06:00 | 127 | 19:00
Laksam | 126 | 18:00 | 120 | 15:00
Lakshmipur | 121 | 18:00 | 112 | 15:00
Lalbag | 134 | 04:00 | 127 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division