## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-08-2025 | during | 14-08-2025 | during | 14-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 342 | 400.75 | 400.75 | 358 | 358 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 320 | 450 | 450 | 380 | 380 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 153 | 152 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15 | 36 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 31 | 110 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 22.5 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 87 | 129 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 145 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 21 | 0 | 21 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 395 | 385 | 583 | 583 | 525 | 525 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2012.5 | 2484.5 | 5540.7 | 5519.7 | 3202.36 | 3181.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 36 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 219 | 215 | 219 | 215 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 48 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 49 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 25 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 23 | 44 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.28 | 0 | 4.12 | 0 | 4.12 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 8 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 502 | 745 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 32 | 3 | 42 | 28 | 42 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 760 | 760 | 760 | 760 | 755 | 755 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1862.28 | 2240 | 3825.84 | 3832.72 | 3627.84 | 3634.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 195 | 189 | 221 | 221 | 203 | 203 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 357 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 42 | 46.7 | 46.7 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 46 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 45 | 45 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 12 | 110 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 108 | 200 | 200 | 52 | 100 | Loop Oil Shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 45 | 106 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 43 | 43 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 81 | 94 | 115 | 115 | 95 | 95 | Machine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 42 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1419 | 1565.2 | 2444.56 | 2379.56 | 1920.36 | 1903.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-08-2025 | during | 14-08-2025 | during | 14-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 65 | 68 | 157.5 | 157.5 | 108 | 108 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 80 | 140 | 200 | 200 | 190 | 190 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 94 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 10.92 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 3 | 6 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 233.92 | 343 | 586 | 549 | 464 | 427
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 149 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 83 | 83 | 79 | 79 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 15 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 360 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 245 | 260 | 300 | 300 | 280 | 280 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1351 | 1358 | 1507 | 1507 | 1386 | 1386
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 281 | 261 | 410 | 410 | 315 | 315 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 29 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 39 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1000 | 1105 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2271 | 2337 | 3607.2 | 3552.2 | 3357 | 3302
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 305 | 304 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1045 | 1070 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 248 | 272 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1933.31 | 1941 | 2162 | 2161 | 2072 | 2071
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 16.24 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 186 | 214 | 214 | 193 | 193 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 121 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 197 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 407 | 399 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 41 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.03 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1221 | 1271.48 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 10.1 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 12 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2034.37 | 2258.48 | 3170.97 | 3019.87 | 2990.71 | 2839.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 52 | 48 | 48 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 188 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 30 | 0 | 91.67 | 0 | 91.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 278.8 | 453 | 583.27 | 460 | 585.27 | 462
System Total |  |  |  |  | 28821.2 | 27843.665 | 13396.18 | 14980.18 | 23427.54 | 22981.05 | 19605.54 | 19207.05
Forecast Scenario (14-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14680 |  | 0 |  | 14680
|  |  |  | 1:00 | 14040 |  | 0 |  | 14040
|  |  |  | 2:00 | 13670 |  | 0 |  | 13670
|  |  |  | 3:00 | 13370 |  | 0 |  | 13370
|  |  |  | 4:00 | 13100 |  | 0 |  | 13100
|  |  |  | 5:00 | 12830 |  | 0 |  | 12830
|  |  |  | 6:00 | 12460 |  | 0 |  | 12460
|  |  |  | 7:00 | 12360 |  | 0 |  | 12360
|  |  |  | 8:00 | 12260 |  | 0 |  | 12260
|  |  |  | 9:00 | 12420 |  | 0 |  | 12420
|  |  |  | 10:00 | 12590 |  | 0 |  | 12590
|  |  |  | 11:00 | 12740 |  | 0 |  | 12740
|  |  |  | 12:00 | 13070 |  | 0 |  | 13070
|  |  |  | 13:00 | 13370 |  | 0 |  | 13370
|  |  |  | 14:00 | 13440 |  | 0 |  | 13440
|  |  |  | 15:00 | 13300 |  | 0 |  | 13300
|  |  |  | 16:00 | 13310 |  | 0 |  | 13310
|  |  |  | 17:00 | 12840 |  | 0 |  | 12840
|  |  |  | 18:00 | 12430 |  | 0 |  | 12430
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14250 |  | 0 |  | 14250
|  |  |  | 19:30 | 14790 |  | 0 |  | 14790
|  |  |  | 20:00 | 14800 |  | 0 |  | 14800
|  |  |  | 21:00 | 14810 |  | 0 |  | 14810
|  |  |  | 22:00 | 14670 |  | 0 |  | 14670
|  |  |  | 23:00 | 14800 |  | 0 |  | 14800
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 13070.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14810.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14810.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 321.61 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:51 hrs on 14-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-08-2025 | [28 empty] | Date: | 13-08-2025 | [28 empty] | Date: | 13-08-2025 | [28 empty] | Date: | 13-08-2025 | [28 empty] | Date: | 13-08-2025 | [13 empty] | Date: | 13-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [13 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 46.4 | 0 | 149 | 77 | 293 | 40 | 55 | 148 | 0 | 380 | 151 | 401 | 0 | 35 | 332 | 0 | 0 | 0 | 108 | 20 | 12 | 0 | 0 | 0 | 0 | 65 | 0 | 3 | 49 | 24 | 0 | 24 | 25 | 0 | 220 | 31 | 37 | 757 | 17 | 0 | 0 | 17 | 96 | 221 | 0 | 0 | 0 | 570 | 0 | 51 | 128 | 45 | 0 | 349 | 330 | 48 | 196 | 41 | 115 | 70 | 96 | 47 | 19 | 114 | 50 | 52.2 | 0 | 43 | 300 | 250 | 384 | 0 | 60 | 155 | 7 | 0 | 78 | 30 | 0 | 18 | 100 | 17 | 94 | 170 | 70 | 0 | 0 | 6 | 8381.6 | 907 | 290 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 51 | 1001 | 0 | 34 | 0 | 35 | 113 | 0 | 96 | 30 | 0 | 0 | 0 | 27 | 0 | 185 | 0 | 0 | 0 | 194 | 0 | 400 | 0 | 0 | 183 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 304 | 1160 | 0 | 7124 | 15505.6 | 107.06
01:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 46.4 | 0 | 138 | 30 | 45 | 0 | 55 | 148 | 0 | 380 | 150 | 401 | 0 | 35 | 330 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 49 | 24 | 0 | 24 | 25 | 0 | 220 | 32 | 31 | 757 | 0 | 0 | 0 | 17 | 94 | 221 | 0 | 0 | 0 | 582 | 0 | 51 | 135 | 45 | 0 | 347 | 330 | 48 | 201 | 41 | 115 | 70 | 53 | 47 | 19 | 114 | 50 | 52.2 | 0 | 43 | 290 | 250 | 387 | 0 | 60 | 154 | 7 | 0 | 78 | 30 | 0 | 18 | 100 | 17 | 94 | 170 | 75 | 0 | 0 | 6 | 7954.6 | 906 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 17 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 27 | 0 | 185 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 183 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0 | 278 | 115 | 220 | 0 | 304 | 1162 | 0 | 7338.31 | 15292.91 | 107.06
02:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 33.8 | 0 | 88 | 30 | 0 | 0 | 17 | 108 | 0 | 380 | 151 | 407 | 0 | 0 | 332 | 0 | 0 | 0 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 39 | 0 | 18 | 49 | 24 | 0 | 24 | 25 | 0 | 220 | 33 | 37 | 756 | 0 | 0 | 0 | 0 | 100 | 221 | 0 | 0 | 0 | 571 | 0 | 51 | 90 | 45 | 0 | 352 | 330 | 48 | 201 | 41 | 115 | 70 | 51 | 47 | 19 | 114 | 48 | 52.2 | 0 | 43 | 295 | 250 | 364 | 0 | 60 | 157 | 0 | 0 | 79 | 30 | 0 | 18 | 100 | 17 | 94 | 150 | 112 | 0 | 0 | 6 | 7675 | 909 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 17 | 1446 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 27 | 0 | 188 | 0 | 0 | 0 | 198 | 0 | 400 | 0 | 0 | 175 | 45 | 70 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 303 | 1164 | 0 | 7230 | 14905 | 107.06
03:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 151 | 399 | 0 | 0 | 330 | 0 | 0 | 0 | 90 | 26.5 | 22 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 49 | 24 | 0 | 24 | 25 | 0 | 220 | 31 | 38 | 756 | 0 | 0 | 0 | 0 | 94 | 222 | 0 | 0 | 0 | 585 | 0 | 51 | 15 | 23 | 0 | 349 | 330 | 49 | 191 | 41 | 115 | 70 | 51 | 47 | 19 | 114 | 46 | 52.2 | 0 | 43 | 295 | 250 | 384 | 0 | 60 | 154 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 17 | 94 | 150 | 108 | 0 | 0 | 6 | 7327.7 | 909 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 17 | 1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 194 | 0 | 403 | 0 | 0 | 180 | 45 | 50 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 303 | 1162 | 0 | 7054 | 14381.7 | 107.06
04:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 151 | 411 | 0 | 0 | 330 | 0 | 0 | 0 | 70 | 26.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 49 | 0 | 0 | 24 | 25 | 0 | 220 | 0 | 38 | 758 | 0 | 0 | 0 | 0 | 101 | 222 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 8 | 0 | 351 | 330 | 49 | 210 | 41 | 115 | 70 | 51 | 47 | 19 | 114 | 46 | 52.2 | 0 | 43 | 300 | 250 | 382 | 0 | 60 | 158 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 17 | 94 | 130 | 108 | 0 | 0 | 6 | 7224.7 | 909 | 287 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 200 | 0 | 403 | 0 | 0 | 180 | 45 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 115 | 220 | 0 | 303 | 1162 | 0 | 6723 | 13947.7 | 107.06
05:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 151 | 400 | 0 | 0 | 332 | 0 | 0 | 0 | 70 | 26.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 49 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 38 | 758 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 8 | 0 | 351 | 330 | 49 | 212 | 41 | 115 | 70 | 51 | 51 | 0 | 29 | 40 | 34 | 0 | 43 | 300 | 250 | 387 | 0 | 60 | 154 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 94 | 130 | 107 | 0 | 0 | 6 | 6939.5 | 908 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 192 | 0 | 407 | 0 | 0 | 179 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 115 | 220 | 0 | 303 | 1162 | 0 | 6674 | 13613.5 | 107.06
06:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 150 | 391 | 0 | 0 | 333 | 0 | 0 | 0 | 70 | 26.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 0 | 0 | 0 | 0 | 0.13 | 219 | 0 | 38 | 756 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 465 | 1 | 51 | 0 | 8 | 0 | 349 | 330 | 49 | 213 | 41 | 89 | 70 | 51 | 53 | 18 | 15 | 36 | 8 | 0 | 43 | 290 | 250 | 385 | 0 | 60 | 150 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 94 | 120 | 108 | 0 | 0.18 | 6 | 6692.81 | 908 | 292 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1052 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0 | 0 | 0.21 | 180 | 0 | 0 | 0 | 187 | 0 | 407 | 0 | 0.02 | 177 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 172 | 115 | 220 | 0 | 305 | 1050 | 0 | 6365.7 | 13058.51 | 107.06
07:00 | 0 | 54 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 68 | 46 | 0 | 0 | 0 | 0 | 0 | 380 | 150 | 396 | 0 | 0 | 334 | 0 | 0 | 2 | 70 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 0 | 0 | 0.77 | 219 | 0 | 34 | 756 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 445 | 2 | 51 | 0 | 8 | 0 | 355 | 330 | 50 | 216 | 41 | 66 | 70 | 51 | 53 | 19 | 13 | 34 | 8 | 6 | 43 | 295 | 250 | 356 | 0 | 60 | 153 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 94 | 110 | 70 | 0 | 1.38 | 6 | 6639.65 | 908 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 941 | 0 | 1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 5 | 0 | 1.22 | 182 | 0 | 0 | 0 | 190 | 0 | 386 | 0 | 0.16 | 179 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 2 | 0.12 | 0 | 162 | 115 | 220 | 0 | 305 | 1040 | 0 | 6231.24 | 12870.89 | 107.06
08:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 380 | 153 | 396 | 0 | 0 | 335 | 0 | 0 | 6 | 52 | 25.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 33 | 0 | 0 | 0 | 0 | 1.92 | 219 | 0 | 2 | 757 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 445 | 12 | 51 | 0 | 8 | 0 | 355 | 330 | 50 | 215 | 38 | 16 | 70 | 51 | 52 | 19 | 0 | 30 | 8 | 11 | 43 | 295 | 250 | 388 | 0 | 60 | 143 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 94 | 95 | 68 | 0 | 0.45 | 6 | 6592.57 | 909 | 293 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 786 | 0 | 1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.65 | 19 | 0 | 9.56 | 177 | 0 | 0 | 0 | 180 | 0 | 375 | 0 | 0.95 | 180 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.22 | 0 | 173 | 115 | 220 | 0 | 305 | 900 | 0 | 5908.88 | 12501.45 | 107.06
09:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 40 | 46 | 0 | 0 | 12 | 0 | 0 | 380 | 152 | 405 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 24.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 0 | 0 | 25 | 25 | 2.08 | 220 | 0 | 2 | 761 | 0 | 0 | 1 | 0 | 0 | 219 | 0 | 0 | 0 | 425 | 17 | 51 | 0 | 0 | 0 | 357 | 330 | 50 | 212 | 41 | 25 | 70 | 54 | 46 | 19 | 17 | 32 | 8 | 21 | 42 | 300 | 240 | 370 | 0 | 60 | 155 | 0 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 94 | 95 | 68 | 0 | 3.99 | 6 | 6660.57 | 908 | 294 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 848 | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.59 | 23 | 0 | 8.18 | 186 | 0 | 0 | 0 | 187 | 0 | 407 | 0 | 0.93 | 180 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 5 | 0.39 | 0 | 220 | 120 | 220 | 0 | 305 | 898 | 0 | 6032.59 | 12693.16 | 107.06
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 68 | 31 | 0 | 0 | 53 | 0 | 0 | 380 | 152 | 410 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 17 | 0 | 0 | 12 | 25 | 2.73 | 220 | 0 | 6 | 699 | 0 | 0 | 18 | 0 | 0 | 217 | 0 | 0 | 0 | 455 | 11 | 43 | 0 | 0 | 0 | 357 | 330 | 48 | 198 | 41 | 48 | 70 | 50 | 45 | 17 | 17 | 36 | 8 | 40 | 42 | 300 | 240 | 385 | 0 | 60 | 158 | 0 | 0 | 55 | 30 | 0 | 18 | 100 | 0 | 83 | 80 | 66 | 0 | 0.83 | 6 | 6616.36 | 913 | 287 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 910 | 0 | 1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.32 | 21 | 0 | 4.37 | 192 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 0.57 | 179 | 46 | 0 | 1 | 0 | 0 | 0 | 0 | 2.3 | 6 | 0.15 | 0 | 218 | 115 | 220 | 0 | 305 | 922 | 0 | 6182.71 | 12799.07 | 107.06
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 10 | 0 | 75 | 31 | 0 | 0 | 55 | 46 | 0 | 350 | 152 | 400 | 0 | 0 | 335 | 0 | 0 | 11 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 1 | 0 | 19 | 17 | 0 | 0 | 12 | 25 | 4.6 | 220 | 0 | 6 | 708 | 0 | 0 | 29 | 0 | 0 | 215 | 0 | 0 | 0 | 500 | 19 | 43 | 2 | 0 | 0 | 357 | 330 | 47 | 191 | 36 | 65 | 70 | 56 | 44 | 17 | 44 | 36 | 13 | 26 | 0 | 295 | 245 | 366 | 0 | 60 | 156 | 0 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 65 | 80 | 65 | 0 | 4.97 | 6 | 6700.57 | 913 | 286 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 984 | 0 | 1134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.22 | 12 | 0 | 9.64 | 178 | 0 | 0 | 0 | 188 | 0 | 404 | 0 | 1.01 | 169 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 1.6 | 9 | 0.15 | 0 | 248 | 115 | 220 | 0 | 305 | 1042 | 0 | 6380.62 | 13081.19 | 107.06
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 15 | 0 | 87 | 31 | 0 | 0 | 55 | 80 | 0 | 350 | 153 | 395 | 0 | 0 | 335 | 0 | 0 | 8 | 35 | 21.5 | 22 | 0 | 0 | 0 | 0 | 23 | 0 | 32 | 16 | 0 | 0 | 12 | 25 | 2.28 | 220 | 0 | 6 | 760 | 0 | 0 | 36 | 0 | 0 | 214 | 0 | 0 | 0 | 502 | 14 | 43 | 12 | 0 | 0 | 357 | 330 | 48 | 195 | 37 | 81 | 50 | 52 | 43 | 19 | 45 | 40 | 25 | 42 | 0 | 300 | 245 | 366 | 0 | 60 | 153 | 0 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 75 | 80 | 65 | 0 | 10.92 | 3 | 6878.7 | 913 | 281 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 1000 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.24 | 12 | 0 | 10.1 | 183 | 0 | 0 | 0 | 184 | 0 | 407 | 0 | 1.03 | 160 | 47 | 0 | 6 | 34 | 0 | 0 | 0 | 1.8 | 30 | 0.31 | 0 | 248 | 115 | 220 | 0 | 305 | 1045 | 0 | 6517.48 | 13396.18 | 107.06
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 15.5 | 0 | 87 | 31 | 0 | 0 | 55 | 85 | 0 | 320 | 152 | 450 | 0 | 0 | 335 | 0 | 0 | 12 | 35 | 21.5 | 22 | 0 | 0 | 0 | 0 | 43 | 0 | 62 | 16 | 0 | 0 | 12 | 25 | 0.63 | 220 | 0 | 20 | 780 | 0 | 0 | 39 | 7 | 0 | 215 | 0 | 0 | 0 | 490 | 9 | 43 | 12 | 0 | 0 | 354 | 330 | 47 | 195 | 42 | 92 | 50 | 51 | 41 | 19 | 51 | 40 | 38 | 41 | 0 | 300 | 245 | 377 | 0 | 60 | 157 | 0 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 84 | 80 | 64 | 0 | 16.8 | 6 | 7061.43 | 913 | 278 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 988 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.92 | 29 | 0 | 18.15 | 181 | 0 | 7 | 0 | 176 | 0 | 360 | 0 | 1.66 | 164 | 47 | 0 | 12 | 22 | 0 | 0 | 0 | 1.5 | 45 | 0.4 | 0 | 249 | 115 | 220 | 0 | 305 | 1053 | 0 | 6430.63 | 13492.06 | 107.06
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 15 | 0 | 87 | 15 | 0 | 0 | 55 | 79 | 0 | 320 | 151 | 440 | 0 | 0 | 334 | 0 | 0 | 6 | 35 | 21.5 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 3 | 16 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 8 | 761 | 0 | 0 | 39 | 8 | 0 | 220 | 0 | 0 | 0 | 503 | 18 | 43 | 12 | 0 | 0 | 351 | 330 | 47 | 200 | 42 | 94 | 50 | 51 | 35 | 19 | 80 | 44 | 52.2 | 68 | 0 | 295 | 245 | 386 | 0 | 60 | 145 | 0 | 0 | 22 | 30 | 0 | 18 | 100 | 0 | 86 | 80 | 63 | 1 | 13.02 | 6 | 6951.72 | 914 | 274 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 994 | 0 | 1067.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.35 | 26 | 0 | 16.03 | 169 | 0 | 9 | 0 | 165 | 0 | 362 | 0 | 0 | 169 | 47 | 0 | 11 | 34 | 0 | 0 | 0 | 1.5 | 51 | 0.38 | 0 | 249 | 115 | 220 | 0 | 305 | 1000 | 0 | 6289.82 | 13241.54 | 107.06
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 16.5 | 0 | 87 | 15 | 0 | 0 | 55 | 89 | 0 | 320 | 151 | 450 | 0 | 0 | 335 | 0 | 0 | 9 | 35 | 22.5 | 22 | 0 | 0 | 0 | 0 | 46 | 0 | 6 | 16 | 0 | 0 | 12 | 25 | 0 | 215 | 0 | 6 | 761 | 0 | 0 | 39 | 8 | 0 | 218 | 0 | 0 | 0 | 500 | 7 | 43 | 12 | 0 | 0 | 351 | 330 | 46 | 195 | 39 | 93 | 70 | 52 | 34 | 20 | 81 | 42 | 52.2 | 42 | 0 | 300 | 245 | 386 | 0 | 60 | 146 | 0 | 0 | 77 | 30 | 0 | 18 | 100 | 0 | 76 | 80 | 63 | 1 | 14.52 | 6 | 7019.72 | 913 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 1024 | 0 | 1114.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.34 | 31 | 0 | 11.77 | 173 | 0 | 3 | 0 | 175 | 0 | 352 | 0 | 1.08 | 169 | 48 | 0 | 11 | 34 | 0 | 30.1 | 0 | 1.5 | 50 | 0.37 | 0 | 248 | 115 | 220 | 0 | 305 | 1000 | 0 | 6385.62 | 13405.34 | 107.06
16:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 16.1 | 0 | 81 | 15 | 0 | 0 | 55 | 83 | 0 | 320 | 150 | 445 | 0 | 0 | 335 | 0 | 0 | 6 | 35 | 22.5 | 22 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 16 | 0 | 0 | 12 | 25 | 0 | 217 | 0 | 7 | 762 | 0 | 0 | 39 | 8 | 0 | 220 | 0 | 0 | 0 | 495 | 10 | 43 | 12 | 0 | 0 | 353 | 330 | 45 | 190 | 38 | 94 | 70 | 53 | 30 | 20 | 77 | 38 | 52.2 | 5 | 0 | 300 | 260 | 380 | 0 | 60 | 139 | 6 | 0 | 79 | 30 | 0 | 18 | 100 | 0 | 76 | 55 | 63 | 0 | 7.34 | 6 | 6923.14 | 913 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 1100 | 0 | 1092.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.48 | 22 | 0 | 14.89 | 168 | 0 | 3 | 0 | 169 | 0 | 339 | 0 | 1.39 | 185 | 51 | 0 | 12 | 34 | 0 | 75.1 | 0 | 0.5 | 64 | 0.18 | 0 | 243 | 115 | 220 | 0 | 305 | 900 | 0 | 6361.23 | 13284.37 | 107.06
17:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 15 | 0 | 69 | 15 | 0 | 0 | 55 | 82 | 0 | 320 | 150 | 440 | 0 | 0 | 335 | 0 | 0 | 5 | 35 | 22.5 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 9 | 16 | 0 | 0 | 12 | 25 | 0.11 | 218 | 0 | 18 | 761 | 0 | 0 | 39 | 8 | 0 | 219 | 0 | 0 | 0 | 490 | 4 | 43 | 12 | 0 | 0 | 352 | 330 | 45 | 191 | 42 | 93 | 70 | 55 | 36 | 20 | 77 | 40 | 52.2 | 3 | 0 | 295 | 260 | 365 | 0 | 60 | 135 | 6 | 0 | 81 | 30 | 0 | 18 | 100 | 0 | 86 | 65 | 65 | 0 | 3.75 | 6 | 6894.56 | 912 | 269 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 1057 | 0 | 1071.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.61 | 14 | 0 | 4.44 | 164 | 0 | 24 | 0 | 166 | 0 | 343 | 0 | 0.42 | 182 | 51 | 0 | 2 | 34 | 0 | 120.1 | 0 | 1.2 | 7 | 0.07 | 0 | 198 | 115 | 220 | 0 | 305 | 890 | 0 | 6208.46 | 13103.02 | 107.06
18:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 14.7 | 0 | 69 | 48 | 0 | 0 | 55 | 78 | 0 | 320 | 152 | 390 | 0 | 0 | 335 | 0 | 0 | 1 | 35 | 22.5 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 3 | 16 | 0 | 0 | 12 | 25 | 0.02 | 219 | 0 | 24 | 703 | 0 | 0 | 39 | 8 | 0 | 219 | 0 | 0 | 0 | 450 | 0 | 43 | 12 | 0 | 0 | 352 | 330 | 46 | 193 | 42 | 94 | 70 | 85 | 36 | 20 | 76 | 40 | 52.2 | 0 | 0 | 300 | 260 | 382 | 0 | 60 | 130 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 86 | 78 | 65 | 0 | 0.64 | 6 | 6802.06 | 913 | 269 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 967 | 0 | 1073.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 3 | 0 | 0.91 | 161 | 0 | 40 | 0 | 161 | 0 | 346 | 0 | 0.1 | 184 | 51 | 0 | 0 | 27 | 0 | 160 | 0 | 0.2 | 2 | 0.02 | 0 | 200 | 115 | 220 | 0 | 305 | 850 | 0 | 6090.81 | 12892.87 | 107.06
19:00 | 0 | 75 | 25 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 36 | 0 | 78 | 100 | 124 | 8 | 55 | 142 | 15 | 320 | 151 | 400 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 22.5 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 5 | 49 | 30 | 0 | 12 | 25 | 0 | 221 | 2 | 25 | 758 | 35 | 0 | 39 | 8 | 0 | 219 | 0 | 0 | 0 | 652 | 0 | 51 | 50 | 8 | 0 | 347 | 330 | 46 | 205 | 42 | 93 | 70 | 108 | 39 | 20 | 106 | 46 | 52.2 | 0 | 0 | 300 | 260 | 370 | 0 | 60 | 140 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 4 | 94 | 115 | 66 | 0 | 0 | 6 | 7821.7 | 913 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 972 | 29 | 1124.79 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 12 | 0 | 0 | 0 | 25 | 0 | 169 | 0 | 96 | 0 | 170 | 0 | 414 | 0 | 0 | 186 | 52 | 105 | 0 | 63 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 264 | 115 | 220 | 0 | 304 | 891 | 0 | 6634.79 | 14456.49 | 107.06
19:30 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 36 | 0 | 129 | 110 | 145 | 15 | 55 | 145 | 16 | 320 | 152 | 385 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 22.5 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 3 | 49 | 48 | 0 | 12 | 25 | 0 | 221 | 8 | 25 | 760 | 53 | 0 | 20 | 8 | 0 | 219 | 0 | 0 | 0 | 745 | 0 | 51 | 110 | 8 | 0 | 300 | 280 | 46 | 189 | 42 | 94 | 70 | 108 | 43 | 20 | 106 | 46 | 52.2 | 0 | 0 | 295 | 260 | 360 | 0 | 60 | 149 | 8 | 0 | 81 | 30 | 0 | 15 | 100 | 35 | 94 | 140 | 68 | 0 | 0 | 6 | 7990.7 | 904 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 29 | 1271.48 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 16 | 0 | 0 | 0 | 27 | 0 | 186 | 0 | 121 | 0 | 197 | 0 | 399 | 0 | 0 | 188 | 52 | 110 | 0 | 98 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 180 | 0 | 304 | 1070 | 0 | 6989.48 | 14980.18 | 107.06
20:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 45.3 | 0 | 131 | 82 | 15 | 0 | 40 | 106 | 0 | 320 | 153 | 375 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 22.5 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 13 | 49 | 61 | 0 | 12 | 25 | 0 | 221 | 0 | 27 | 761 | 17 | 0 | 19 | 8 | 0 | 222 | 0 | 0 | 0 | 774 | 0 | 51 | 80 | 8 | 0 | 300 | 280 | 47 | 187 | 42 | 94 | 70 | 113 | 43 | 20 | 106 | 46 | 52.2 | 0 | 0 | 295 | 260 | 357 | 0 | 60 | 149 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 30 | 94 | 140 | 69 | 0 | 0 | 6 | 7702 | 886 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 17 | 1325.61 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 160 | 0 | 198 | 0 | 396 | 0 | 0 | 189 | 52 | 110 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 180 | 0 | 304 | 1080 | 0 | 6994.61 | 14696.61 | 107.06
21:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 120 | 81 | 0 | 0 | 17 | 54 | 0 | 350 | 152 | 361 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 23.5 | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 11 | 49 | 61 | 0 | 12 | 25 | 0 | 221 | 0 | 31 | 761 | 0 | 0 | 19 | 8 | 0 | 221 | 0 | 0 | 0 | 880 | 0 | 51 | 0 | 8 | 0 | 354 | 330 | 50 | 196 | 38 | 93 | 70 | 112 | 42 | 20 | 106 | 42 | 52.2 | 0 | 0 | 295 | 260 | 381 | 0 | 60 | 155 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 94 | 120 | 72 | 0 | 0 | 5 | 7631.7 | 884 | 251 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 17 | 1322.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 180 | 0 | 198 | 0 | 414 | 0 | 0 | 185 | 54 | 70 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 220 | 0 | 305 | 1000 | 0 | 6981.82 | 14613.52 | 107.06
22:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 98 | 81 | 0 | 0 | 17 | 35 | 0 | 350 | 150 | 375 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23.5 | 22 | 0 | 0 | 0 | 0 | 13 | 0 | 8 | 49 | 61 | 0 | 12 | 25 | 0 | 219 | 0 | 34 | 760 | 0 | 0 | 19 | 8 | 0 | 222 | 0 | 0 | 0 | 870 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 50 | 192 | 42 | 94 | 70 | 98 | 43 | 20 | 106 | 46 | 52.2 | 0 | 0 | 290 | 260 | 368 | 0 | 60 | 152 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 90 | 120 | 72 | 0 | 0 | 0 | 7540.7 | 885 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1235 | 0 | 1326.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 178 | 0 | 198 | 0 | 414 | 0 | 0 | 185 | 52 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 115 | 220 | 0 | 305 | 995 | 0 | 6933.72 | 14474.42 | 107.06
23:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 92 | 81 | 0 | 0 | 17 | 34 | 0 | 350 | 153 | 385 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 14 | 49 | 61 | 0 | 12 | 25 | 0 | 219 | 0 | 36 | 763 | 0 | 0 | 19 | 8 | 0 | 221 | 0 | 0 | 0 | 880 | 0 | 51 | 0 | 8 | 0 | 354 | 330 | 50 | 202 | 42 | 93 | 70 | 100 | 45 | 20 | 106 | 48 | 52.2 | 0 | 0 | 295 | 250 | 391 | 0 | 30 | 156 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 120 | 74 | 0 | 0 | 1 | 7559.2 | 884 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 1324.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 174 | 0 | 194 | 0 | 414 | 0 | 0 | 182 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 115 | 220 | 0 | 304 | 1005 | 0 | 6877.75 | 14436.95 | 107.06
Total KWH | 0 | 1494720 | 616320 | 0 | 0 | 0 | 0 | 0 | 8373600 | 0 | 0 | 287280 | 0 | 2015712 | 935520 | 351273 | 46403 | 771073 | 1360800 | 21120 | 8606000 | 3618444 | 9760909 | 0 | 102473 | 8033276 | 0 | 0 | 69890 | 1650000 | 492600 | 479880 | 0 | 0 | 0 | 0 | 514560 | 0 | 391200 | 805176 | 351944 | 0 | 324480 | 506880 | 14738 | 5283678 | 135490 | 546720 | 18218181.82 | 65236 | 0 | 470400 | 122772.6 | 435745 | 5193378 | 0 | 0 | 0 | 13909089 | 114075 | 1135848 | 592145 | 234182 | 0 | 8757500 | 7926000 | 1152000 | 4881000 | 980064 | 2125440 | 1604430 | 1608480 | 1053360 | 446390 | 1722540 | 989760 | 959702 | 275582 | 443952 | 7201000 | 5983700 | 9427000 | 0 | 1382280 | 3618736.36 | 115248 | 0 | 1819200 | 714336 | 0 | 426000 | 2404890 | 112320 | 2084400 | 2697600 | 1735680 | 4100 | 88310 | 132960 | 173327171.78 | 21922909 | 6738048 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 340560 | 25301820 | 162240 | 29525038 | 0 | 31122 | 0 | 8160 | 51936 | 0 | 259056 | 33836 | 0 | 129433 | 248180 | 96667 | 112496 | 4309364 | 0 | 1141709 | 0 | 4696036 | 0 | 9435854 | 0 | 9300 | 4368000 | 1083927 | 800077 | 59292 | 1087008 | 0 | 0 | 0 | 13486.32 | 264940 | 2266 | 0 | 5608000 | 2760000 | 5404950 | 0 | 7309090 | 25556363.64 | 0 | 159783163.96 | 333110335.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13396.18 | MW | 12:00 Hr. | Energy Generated |  |  | 333.1103 |  | MKWHr.
| Day Peak Demand |  |  | 13396.18 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.166 |  | MKWHr.
| Evening Peak Generation |  |  | 14980.18 | MW | 19:30 Hr. | Energy Demand |  |  | 333.2763 |  | MKWHr.
| Evening Peak Demand |  |  | 14980.18 | MW | 19:30 Hr. | Maximum Temperature |  |  | 29 |  | °C
| Minimum Generation of the Day |  |  | 12501.45 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1030.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 15505.6 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.8829 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.3647 | 0 | 9.6527 | 0 | 0 | 0.06989 | 0 | 0 | 49.0873 | Gas | 141.5363 | Gas | 503076633.1476
| Chattogram Zone |  |  | 5.7401 | 32.1273 | 3.7327 | 0 | 5.2837 | 0.12881 | 0 | 0.3912 | 47.4037 | Coal | 101.3545 | Coal | 603899378.9796
| Cumilla Zone |  |  | 27.1174 | 0 | 8.5056 | 0 | 0 | 0.27558 | 0.98976 | 0 | 36.8884 | HFO | 29.4484 | HFO | 548415647.732
| Mymensingh Zone |  |  | 1.7357 | 0 | 5.0273 | 0 | 0 | 0.09241 | 0 | 0 | 6.8554 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.0924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.0924 | Hydro | 5.2837 | Hydro | 528367.8
| Khulna Zone |  |  | 6.738 | 25.3018 | 0.16224 | 0 | 0 | 0.34056 | 22.8349 | 0 | 55.3776 | Solar | 1.7466 | Solar | 25341440.3152
| Barishal Zone |  |  | 8.1649 | 38.4735 | 0 | 0 | 0 | 0.002266 | 0 | 0 | 46.6407 | Import | 53.3497 | Import | 272659224.31
| Rajshahi Zone |  |  | 19.583 | 0 | 0.48078 | 0 | 0 | 0.49941 | 29.525 | 0 | 50.0882 | Wind | 0.3912 | Wind | 5727168
| Rangpur Zone |  |  | 0 | 5.4519 | 1.8871 | 0 | 0 | 0.33772 | 0 | 0 | 7.6767
| Total |  |  | 141.5363 | 101.3545 | 29.4484 | 0 | 5.2837 | 1.7466 | 53.3497 | 0.3912 | 333.1103
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 503076633.1476 |  | Hydro | 528367.8
|  |  |  | Coal | 603899378.9796 |  | Solar | 25341440.3152
|  |  |  | HFO | 548415647.732 |  | Import | 272659224.31
|  |  |  | HSD | 0 |  | Wind | 5727168
[5 empty] | Total: | 195,96,47,860 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9229 | Peak Hr Flow | 904.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49867018.29 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.525 | Peak Hr Flow | 1271.48 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 892 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.98976 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1056 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.4377 | Peak Hr Flow | 2221.48 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5209
|  |  |  | Chattogram |  | 0 |  | 1456
|  |  |  | Cumilla |  | 0 |  | 1448
|  |  |  | Mymensingh |  | 0 |  | 1148
|  |  |  | Sylhet |  | 0 |  | 590
|  |  |  | Khulna |  | 0 |  | 1814
|  |  |  | Barishal |  | 0 |  | 470
|  |  |  | Rajshahi |  | 0 |  | 1440
|  |  |  | Rangpur |  | 0 |  | 891
|  |  |  | Total |  | 0 |  | 14466
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 565
|  |  |  | Total Unavailable Capacity |  |  |  | 865
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:11 | Ramganj 132/33kV S/S Transformer-01 HT is restored.
| 08:15 |  | Rampura 230/132kV S/S NLDC Trafo HT Project Work S/D Due to Breaker and CT change
| 08:25 |  | Rampura 230/132kV S/S NLDC Trafo LT Project Work S/D
|  | 09:02 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
| 09:16 |  | Amtoli- RNPL P/S 400 kv ckt-2 shutdown.
| 09:40 | 09:45 | Kulaura 132/33kV S/S TR-2 HT Tripped showing Transformer differential relay relays Due to | [7 empty] | 1.0MW load
|  |  | Oil temperature | [7 empty] | interrup.
| 09:46 | 12:38 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Oil temperature meter maintenance
| 09:47 | 12:37 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Oil temperature meter maintenance
| 10:15 |  | At Satkhira S/S 132/33 kv Txr. TR-3 S/D.
| 10:22 | 11:54 | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to New multifuntionong meter is being
installed.
| 10:22 | 11:54 | Chandpur 132/33kV S/S 402T HT Scheduled S/D Due to New multifuntionong meter is being
installed
| 12:00 |  | Day Peak Generation: 13393 MW.
| 12:03 |  | Raozan 25 MW PP Synchronized
| 12:04 | 13:14 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to New multifuntionong meter is being
installed.
| 12:04 | 13:14 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to New multifuntionong meter is being
installed.
| 12:06 |  | Sirajgonj 225MW CCPP Unit-2 GT Synchronized with remarks:- None
| 12:06 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 12:25 | 15:05 | Ghorashal 230kV S/S TARFO-2 LT Project Work S/D Due to To change the neutral PI of | [7 empty] | 75.0MW load
|  |  | Transformer-02 for Project-01( Energypac). | [7 empty] | interrup.
| 12:29 | 15:03 | Ghorashal 230kV S/S TARFO-2 HT Project Work S/D Due to To change the neutral PI of | [7 empty] | 75.0MW load
|  |  | Transformer-02 for Project-01( Energypac). | [7 empty] | interrup.
| 12:41 | 13:05 | Bogura 230/132kV S/S T-01 HT Tripped showing Lock out Relay relays Due to Rain
| 12:41 | 13:05 | Bogura 230/132kV S/S T-01 LT Tripped showing No Relay Operated relays Due to Rain
| 13:14 |  | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to 33 kv load side open
|  | 13:14 | Chandpur 132/33kV S/S 412T LT is restored.
| 13:22 | 14:40 | Rangpur 132/33kV S/S T-2 (404T) HT Forced S/D Due to 33kv Bus-2 S/D
| 13:22 | 14:40 | Rangpur 132/33kV S/S T-2 (404T) LT Forced S/D Due to 33KV BUS-2 S/D | [7 empty] | 60.0MW load
interrup.
| 13:37 | 13:51 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing O/C E/F Relay, Lockout 33KV & 132 KV
Side relays Due to Bisic Feder O/C,E/F Relay
| 13:37 | 13:49 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing O/C E/F Relay, Lockout 33KV & 132 KV
Side relays Due to Bisic Fedder O/C, E/F
| 14:48 |  | Saidpur 150 MW GT was synch.
| 14:50 | 18:48 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Forced S/D Due to ROW Clearing.
| 15:42 | 16:50 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to REB-1 Feeder red hot maintenance of | [7 empty] | 15.0MW load
|  |  | Y-Phase source side. | [7 empty] | interrup.
| 15:43 | 16:50 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to REB-1 Feeder red hot maintenance of | [7 empty] | 15.0MW load
|  |  | Y-Phase source side. | [7 empty] | interrup.
| 16:04 |  | Sirajgonj Unit-2 ST was sync.
| 16:30 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to energy meter replace
| 16:31 | 18:03 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D
|  | 16:38 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT is restored.
| 18:24 |  | Bashkhali SS Power unit-2 was sync.
| 18:24 |  | SS Power Synchronized with remarks:- unit-2
| 19:30 |  | Evening Peak Generation 14979 MW.
| 19:31 |  | Saidpur 150 MW was shut down at 19:31 hrs.
| 19:52 | 22:02 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to 33 kv Bus Red hot maitenance work
by PBS.
| 19:52 | 22:02 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to 33 kv Bus Red hot maitenance work
by PBS.
| 19:53 | 22:00 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to 33 kv Bus Red hot maitenance work
by PBS.
| 20:01 | 22:01 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to 33 kv Bus Red hot maitenance work
by PBS.
| 20:06 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 02:08 |  | Raozan 25 MW PP Shutdown
| 05:51 |  | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Redhot
maintenance work
| 06:54 |  | Rampura 230/132kV S/S Auto Transformer - 04 HT Scheduled S/D Due to 33kv nldc feeder ct
and cb change.
| 06:54 |  | Rampura 230/132kV S/S Auto Transformer - 04 LT Scheduled S/D Due to 33kv nldc feeder ct
and cb change.
| 06:54 | 07:47 | Ramganj 132/33kV S/S Transformer -02 HT Scheduled S/D Due to LT Bushing red hot point | [7 empty] | 20.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 06:54 | 07:12 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing DEF AIDED
relays.
| 06:58 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 342 | 8373600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8606000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3618444 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 46403 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 8033276 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 287280 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 110 | 935520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 771073 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 102473 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22.5 | 492600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 479880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 616320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 351273 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 129 | 2015712 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1494720 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 21120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 1360800 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 69890 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 385 | 9760909 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1650000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2484.5 | 49087293
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 122772.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114075 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 470400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5283678 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5193378 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 435745 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 351944 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 805176 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 324480 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 546720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 514560 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14738 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 8 | 135490 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 506880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 65236 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 745 | 13909089 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 391200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 760 | 18218181.82 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2240 | 47403743.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4881000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 8757500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 7926000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 980064 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1152000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 234182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1135848 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 110 | 592145 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 443952 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1604430 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 108 | 1608480 | Fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 46 | 989760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 959702 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 446390 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1722540 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 43 | 1053360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 2125440 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 275582 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1565.2 | 36888375
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 68 | 1735680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 140 | 2697600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 2084400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 88310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 132960 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 112320 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 343 | 6855370
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1382280 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3618736.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714336 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1819200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2404890 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 426000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 115248 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7201000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 9427000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 260 | 5983700 | -
Sylhet Area Total |  |  |  |  | 2325 | 1358 | 33092390.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21922909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 261 | 6738048 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 29 | 162240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 340560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1105 | 25301820 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2337 | 55377577
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7309090 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2760000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1070 | 25556363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5404950 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 272 | 5608000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2266 | -
Barishal Area Total |  |  |  |  | 2236 | 1941 | 46640669.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 129433 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 31122 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 33836 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4309364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 121 | 1141709 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4696036 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 399 | 9435854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 96667 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 41 | 259056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 51936 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 8160 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1271.48 | 29525038 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 112496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 248180 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2258.48 | 50088187
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 5 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1083927 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 188 | 4368000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1087008 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 13486.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 800077 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 59292 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 264940 | -
Rangpur Area Total |  |  |  |  | 950 | 453 | 7676730.32
Eastern Grid Total |  |  |  |  | 17401.505 | 7990.7 | 173327171.78
Western Grid Total |  |  |  |  | 10442.16 | 6989.48 | 159783163.96
National Grid Total |  |  |  |  | 27843.665 | 14980.18 | 333110335.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9851.11 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4615.4 | MW
i) Dhaka area |  |  | 5208.81 |  | MW | i) Khulna area |  |  |  | 1814.5 | MW
ii) Chattogram area |  |  | 1456 |  | MW | ii) Barishal area |  |  |  | 469.5 | MW
iii) Cumilla area |  |  | 1448.3 |  | MW | iii) Rajshahi area |  |  |  | 1440.4 | MW
iv) Mymensingh area |  |  | 1148 |  | MW | iv) Rangpur area |  |  |  | 891 | MW
v) Sylhet area |  |  | 590 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14466.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 90 | 13:00 | 133 | PHP | 9 | 06:00
2 | AKSML | 130 | 12:00 | 68 | Ishurdi | 79 | 19:30 | 134 | Pabna | 128 | 00:00
3 | Aftabnagar | 42 | 00:00 | 69 | Jaldhaka | 92 | 00:00 | 135 | Palashbari | 99 | 00:00
4 | Agargaon | 134 | 13:00 | 70 | Jamalpur | 134 | 00:00 | 136 | Panchagarh | 58 | 19:00
5 | Agrabad | 96 | 13:00 | 71 | Jashore | 152 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 130 | 00:00 | 138 | Patuakhali | 74.5 | 22:00
7 | Ashuganj | 99 | 19:30 | 73 | Joydebpur | 151 | 11:00 | 139 | Payra | 38 | 00:00
8 | BSRM | 202 | 20:00 | 74 | Joypurhat | 66 | 00:00 | 140 | Postogola | 60 | 00:00
9 | Bagerhat | 89 | 00:00 | 75 | Juldah | 17 | 15:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 87 | 00:00 | 76 | KSRM | 22 | 14:00 | 142 | Purbasadipur | 134 | 00:00
11 | Bakulia | 98 | 19:30 | 77 | Kabirpur | 251 | 19:00 | 143 | Rahanpur | 44 | 00:00
12 | Banani | 51.6 | 13:00 | 78 | Kachua | 90 | 00:00 | 144 | Rahim | 44 | 16:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 85 | 00:00
14 | Barapukuria | 69 | 00:00 | 80 | Kalurghat | 40 | 09:00 | 146 | Rajendrapur | 136 | 00:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 79 | 13:00 | 147 | Rajshahi | 131 | 01:00
16 | Barishal | 120 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 66 | 21:00
17 | Barishal-230 | 104 | 22:00 | 83 | Kasba | 36 | 00:00 | 149 | Ramganj | 116 | 20:00
18 | Baroaulia | 73 | 11:00 | 84 | Kazla | 99 | 00:00 | 150 | Rampur | 43 | 00:00
19 | Baroirhat | 63 | 00:00 | 85 | Keranigonj | 99 | 00:00 | 151 | Rangamati | 17 | 19:30
20 | Bashundhara | 189 | 00:00 | 86 | Khagrachori | 28 | 00:00 | 152 | Rangpur | 124 | 01:00
21 | BashundharaCement | 2 | 00:00 | 87 | Khulna | 68 | 00:00 | 153 | Ruppur | 7.4 | 10:00
22 | Beanibazar | 78 | 00:00 | 88 | Khulshi | 180 | 11:00 | 154 | SSM | 15 | 01:00
23 | Benapole | 66 | 00:00 | 89 | Kishoreganj | 134 | 00:00 | 155 | Saidpur | 107 | 00:00
24 | Bhaluka | 152 | 00:00 | 90 | Kodda | 305 | 09:00 | 156 | Satkhira | 141 | 00:00
25 | Bhandaria | 60 | 01:00 | 91 | Kulaura | 52 | 00:00 | 157 | Satmasjid | 102 | 00:00
26 | Bhangura | 38 | 00:00 | 92 | Kurigram | 62 | 00:00 | 158 | Savar | 227 | 09:00
27 | Bheramara(GK) | 64 | 19:00 | 93 | Kushtia | 153 | 00:00 | 159 | SevenRings | 14.29 | 19:30
28 | Bhulta | 122 | 10:00 | 94 | Laksam | 34 | 01:00 | 160 | ShahCement | 27 | 00:00
29 | Bog-Sherpur | 76 | 00:00 | 95 | Lakshmipur | 21 | 04:00 | 161 | Shahjadpur | 84 | 21:00
30 | Bogura | 171 | 00:00 | 96 | Lalbag | 43 | 13:00 | 162 | Shahjibazar | 135 | 00:00
31 | Borhanuddin | 93 | 01:00 | 97 | Lalmonirhat | 59 | 01:00 | 163 | Shahmirpur | 62 | 02:00
32 | Brahmanbaria | 138 | 00:00 | 98 | MI_Cement | 17.5 | 01:00 | 164 | Shariatpur | 96 | 00:00
33 | Cantonment | 143 | 13:00 | 99 | Madanganj | 38 | 00:00 | 165 | Sherpur | 152 | 00:00
34 | Chandina | 16.88 | 05:00 | 100 | Madaripur | 114 | 22:00 | 166 | Shikalbaha | 8 | 10:00
35 | Chandpur | 79 | 22:00 | 101 | Madartek | 104 | 00:00 | 167 | Shitalakhya | 87.4 | 12:00
36 | Chandraghona | 37 | 19:00 | 102 | Madunaghat | 56 | 19:00 | 168 | Sholosohor | 47 | 20:00
37 | Chapai | 69 | 00:00 | 103 | Magura | 68 | 00:00 | 169 | Shyampur | 168 | 04:00
38 | Charsaidpur | 20 | 02:00 | 104 | Mahasthangarh | 94 | 00:00 | 170 | Siddhirganj | 119 | 10:00
39 | Chauddagram | 70 | 22:00 | 105 | Maijdee | 15 | 23:00 | 171 | Sirajganj | 108 | 19:30
40 | Chhatak | 37 | 00:00 | 106 | Manikganj | 133 | 00:00 | 172 | Sonargaon | 126 | 00:00
41 | Chowmuhani | 199 | 19:30 | 107 | Maniknagar | 76 | 13:00 | 173 | Sreemongol | 85 | 00:00
42 | Chuadanga | 118 | 00:00 | 108 | Matarbari | 52 | 18:30 | 174 | Sreepur | 105 | 19:00
43 | Coxsbazar | 134 | 00:00 | 109 | Matuail | 64 | 10:00 | 175 | Srinagar | 49.81 | 00:00
44 | Cumilla(N) | 145 | 00:00 | 110 | Millgate | 130 | 10:00 | 176 | Sunamganj | 60 | 00:00
45 | Cumilla(S) | 147 | 15:00 | 111 | Mirpur | 125 | 00:00 | 177 | Sylhet | 57 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 19:00 | 178 | Sylhet-132 | 112 | 19:00
47 | Daudkandi | 155 | 00:00 | 113 | Mirzapur | 49 | 00:00 | 179 | TK | 36 | 00:00
48 | Dhaka | 80 | 13:00 | 114 | Mithapukur | 70 | 19:30 | 180 | Tangail | 190 | 00:00
49 | Dhamrai | 130 | 09:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 22 | 00:00
50 | Dhanmondi | 144 | 13:00 | 116 | Mogbazar | 130.6 | 15:00 | 182 | Thakurgaon | 115 | 00:00
51 | Dohazari | 111 | 19:00 | 117 | Mongla | 47 | 10:00 | 183 | Tongi | 109 | 09:00
52 | Faridpur | 175 | 00:00 | 118 | Motijheel | 45 | 13:00 | 184 | Ullahpara | 38 | 01:00
53 | Fatullah | 103 | 12:00 | 119 | Muktagacha | 34 | 00:00 | 185 | Ullon | 63 | 00:00
54 | Fenchuganj | 43 | 00:00 | 120 | Munshiganj | 122 | 00:00 | 186 | Uttara | 78 | 13:00
55 | Feni | 119 | 19:00 | 121 | Muradnagar | 43 | 00:00 | 187 | UttaraNew | 67 | 00:00
56 | GPH | 72 | 01:00 | 122 | Mymensingh | 207 | 00:00 | 188 | Zigatola | 74 | 00:00
57 | Ghatail | 88 | 00:00 | 123 | Naogaon | 134 | 00:00
58 | Ghorashal | 14 | 00:00 | 124 | Narail | 59 | 01:00
59 | Ghorashal-230 | 94 | 04:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 197 | 02:00
61 | Gollamari | 100 | 00:00 | 127 | Natore | 150 | 00:00
62 | Gopalganj | 113 | 19:30 | 128 | Nawabganj | 61.4 | 00:00
63 | Gulshan | 120 | 13:00 | 129 | Netrakona | 133 | 19:00
64 | Halishahar | 74 | 09:00 | 130 | New | 70 | 12:00
65 | HaripurSBU | 161 | 18:00 | 131 | Niamatpur | 78 | 00:00
66 | Hasnabad | 79 | 00:00 | 132 | Noapara | 50 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15505.6 | 62 |  | 15570.39
1:00 | 15292.91 | 38 |  | 15332.62
2:00 | 14905 | 36 |  | 14943
3:00 | 14381.7 | 30 |  | 14412.7
4:00 | 13947.7 | 0 |  | 13947.7
5:00 | 13613.5 | 0 |  | 13613.5
6:00 | 13058.51 | 0 |  | 13058.51
7:00 | 12870.89 | 0 |  | 12870.89
8:00 | 12501.45 | 0 |  | 12501.45
9:00 | 12693.16 | 0 |  | 12693.16
10:00 | 12799.07 | 0 |  | 12799.07
11:00 | 13081.19 | 0 |  | 13081.19
12:00 | 13396.18 | 0 |  | 13396.18
13:00 | 13492.06 | 0 |  | 13492.06
14:00 | 13241.54 | 0 |  | 13241.54
15:00 | 13405.34 | 0 |  | 13405.34
16:00 | 13284.37 | 0 |  | 13284.37
17:00 | 13103.02 | 0 |  | 13103.02
18:00 | 12892.87 | 0 |  | 12892.87
19:00 | 14456.49 | 0 |  | 14456.49
19:30 | 14980.18 | 0 |  | 14980.18
20:00 | 14696.61 | 0 |  | 14696.61
21:00 | 14613.52 | 0 |  | 14613.52
22:00 | 14474.42 | 0 |  | 14474.42
23:00 | 14436.95 | 0 |  | 14436.95
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8381.6 | 7124 | 15505.6 | DAILY GENERATION CURVE
00:30 | 8168.1 | 7231.155 | 15399.255
01:00 | 7954.6 | 7338.31 | 15292.91 | 13-08-2025
01:30 | 7814.8 | 7284.155 | 15098.955
02:00 | 7675 | 7230 | 14905
02:30 | 7501.35 | 7142 | 14643.35
03:00 | 7327.7 | 7054 | 14381.7
03:30 | 7276.2 | 6888.5 | 14164.7
04:00 | 7224.7 | 6723 | 13947.7
04:30 | 7082.1 | 6698.5 | 13780.6
05:00 | 6939.5 | 6674 | 13613.5
05:30 | 6816.155 | 6519.85 | 13336.005
06:00 | 6692.81 | 6365.7 | 13058.51
06:30 | 6666.23 | 6298.47 | 12964.7
07:00 | 6639.65 | 6231.24 | 12870.89
07:30 | 6616.11 | 6070.06 | 12686.17
08:00 | 6592.57 | 5908.88 | 12501.45
08:30 | 6626.57 | 5970.735 | 12597.305
09:00 | 6660.57 | 6032.59 | 12693.16
09:30 | 6638.465 | 6107.65 | 12746.115
10:00 | 6616.36 | 6182.71 | 12799.07
10:30 | 6658.465 | 6281.665 | 12940.13
11:00 | 6700.57 | 6380.62 | 13081.19
11:30 | 6789.635 | 6449.05 | 13238.685
12:00 | 6878.7 | 6517.48 | 13396.18
12:30 | 6970.065 | 6474.055 | 13444.12
13:00 | 7061.43 | 6430.63 | 13492.06
13:30 | 7006.575 | 6360.225 | 13366.8
14:00 | 6951.72 | 6289.82 | 13241.54
14:30 | 6985.72 | 6337.72 | 13323.44
15:00 | 7019.72 | 6385.62 | 13405.34
15:30 | 6971.43 | 6373.425 | 13344.855
16:00 | 6923.14 | 6361.23 | 13284.37
16:30 | 6908.85 | 6284.845 | 13193.695
17:00 | 6894.56 | 6208.46 | 13103.02
17:30 | 6848.31 | 6149.635 | 12997.945
18:00 | 6802.06 | 6090.81 | 12892.87
18:30 | 7311.88 | 6362.8 | 13674.68
19:00 | 7821.7 | 6634.79 | 14456.49
19:30 | 7990.7 | 6989.48 | 14980.18
20:00 | 7702 | 6994.61 | 14696.61
20:30 | 7666.85 | 6988.215 | 14655.065 |  | Executive Engineer
21:00 | 7631.7 | 6981.82 | 14613.52 |  | Network Operation Division
21:30 | 7586.2 | 6957.77 | 14543.97
22:00 | 7540.7 | 6933.72 | 14474.42
22:30 | 7549.95 | 6905.735 | 14455.685
23:00 | 7559.2 | 6877.75 | 14436.95

## En-Curve
QF-LDC-12
Date | 13-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3968 | 1924 | 907 | 38 | 50 | 1001 | 220 | 4487 | 0 | 600 | 2307.6 | 0 | 0 | 3 | 62 | DAILY ENERGY CURVE
00:30 | 3976.5 | 1910 | 906.5 | 38 | 50 | 1224.5 | 220 | 4495 | 0.155 | 544.5 | 2027.6 | 0 | 0 | 6.5 | 50 | 13-08-2025
01:00 | 3985 | 1896 | 906 | 38 | 50 | 1448 | 220 | 4503 | 0.31 | 489 | 1747.6 | 0 | 0 | 10 | 38
01:30 | 3994.5 | 1913.5 | 907.5 | 38 | 49 | 1447 | 220 | 4495 | 0.155 | 447 | 1573.3 | 0 | 0 | 14 | 37 | Energy Generated | 333.1103 |  | MKWHr
02:00 | 4004 | 1931 | 909 | 38 | 48 | 1446 | 220 | 4487 | 0 | 405 | 1399 | 0 | 0 | 18 | 36 | Energy not Served | 0.166 |  | MKWHr
02:30 | 4000 | 1921.75 | 909 | 38 | 47 | 1439 | 220 | 4493.5 | 0 | 335 | 1225.1 | 0 | 0 | 15 | 33 | Total Energy Requirement | 333.2763 |  | MKWHr
03:00 | 3996 | 1912.5 | 909 | 38 | 46 | 1432 | 220 | 4500 | 0 | 265 | 1051.2 | 0 | 0 | 12 | 30
03:30 | 4017.5 | 1915.5 | 909 | 38 | 46 | 1372 | 220 | 4427 | 0 | 243 | 963.2 | 0 | 0 | 13.5 | 15
04:00 | 4039 | 1918.5 | 909 | 38 | 46 | 1312 | 220 | 4354 | 0 | 221 | 875.2 | 0 | 0 | 15 | 0
04:30 | 4032 | 1901.5 | 908.5 | 38 | 43 | 1314 | 219.5 | 4351 | 0 | 221 | 738.6 | 0 | 0 | 13.5 | 0
05:00 | 4025 | 1884.5 | 908 | 38 | 40 | 1316 | 219 | 4348 | 0 | 221 | 602 | 0 | 0 | 12 | 0
05:30 | 4017 | 1881.5 | 908 | 38 | 38 | 1266 | 219 | 4185 | 1.505 | 213 | 553 | 0 | 0 | 16 | 0
06:00 | 4009 | 1878.5 | 908 | 38 | 36 | 1216 | 219 | 4022 | 3.01 | 205 | 504 | 0 | 0 | 20 | 0
06:30 | 3977 | 1872.5 | 908 | 38 | 35 | 1211 | 219 | 3947.5 | 17.2 | 238 | 486.5 | 0 | 0 | 15 | 0
07:00 | 3945 | 1866.5 | 908 | 38 | 34 | 1206 | 219 | 3873 | 31.39 | 271 | 469 | 0 | 0 | 10 | 0
07:30 | 3943 | 1857.85 | 908.5 | 38 | 32 | 1183.5 | 219 | 3732 | 57.32 | 270 | 420.5 | 0 | 0 | 24.5 | 0
08:00 | 3941 | 1849.2 | 909 | 38 | 30 | 1161 | 219 | 3591 | 83.25 | 269 | 372 | 0 | 0 | 39 | 0
08:30 | 3963 | 1854.35 | 908.5 | 38 | 31 | 1130.5 | 219.5 | 3637 | 101.455 | 268.5 | 410 | 0 | 0 | 35.5 | 0
09:00 | 3985 | 1859.5 | 908 | 38 | 32 | 1100 | 220 | 3683 | 119.66 | 268 | 448 | 0 | 0 | 32 | 0
09:30 | 3992 | 1842.15 | 910.5 | 38 | 34 | 1119.5 | 220 | 3708.5 | 132.465 | 234 | 480.5 | 0 | 0 | 34.5 | 0
10:00 | 3999 | 1824.8 | 913 | 38 | 36 | 1139 | 220 | 3734 | 145.27 | 200 | 513 | 0 | 0 | 37 | 0
10:30 | 3973 | 1817.4 | 913 | 38 | 36 | 1136.5 | 220 | 3868.5 | 160.23 | 179 | 570.5 | 0 | 0 | 28 | 0
11:00 | 3947 | 1810 | 913 | 38 | 36 | 1134 | 220 | 4003 | 175.19 | 158 | 628 | 0 | 0 | 19 | 0
11:30 | 3934.5 | 1809.75 | 913 | 38 | 38 | 1177.5 | 220 | 4035 | 184.435 | 157.5 | 705.5 | 0 | 0 | 25.5 | 0
12:00 | 3922 | 1809.5 | 913 | 38 | 40 | 1221 | 220 | 4067 | 193.68 | 157 | 783 | 0 | 0 | 32 | 0
12:30 | 3909 | 1830 | 913 | 38 | 40 | 1190 | 220 | 4071.5 | 214.37 | 157 | 814.25 | 0 | 0 | 47 | 0
13:00 | 3896 | 1850.5 | 913 | 38 | 40 | 1159 | 220 | 4076 | 235.06 | 157 | 845.5 | 0 | 0 | 62 | 0
13:30 | 3886.5 | 1802 | 913.5 | 38 | 42 | 1113.28 | 220 | 4052 | 249.67 | 149 | 868.35 | 0 | 0 | 32.5 | 0
14:00 | 3877 | 1753.5 | 914 | 38 | 44 | 1067.56 | 220 | 4028 | 264.28 | 141 | 891.2 | 0 | 0 | 3 | 0
14:30 | 3892 | 1788.5 | 913.5 | 38 | 43 | 1091.01 | 217.5 | 4041.5 | 243.43 | 141 | 894.45 | 15.05 | 0 | 4.5 | 0
15:00 | 3907 | 1823.5 | 913 | 38 | 42 | 1114.46 | 215 | 4055 | 222.58 | 141 | 897.7 | 30.1 | 0 | 6 | 0
15:30 | 3889.5 | 1821 | 913 | 38 | 40 | 1103.575 | 216 | 4048 | 195.68 | 141 | 875.5 | 52.6 | 0 | 11 | 0
16:00 | 3872 | 1818.5 | 913 | 38 | 38 | 1092.69 | 217 | 4041 | 168.78 | 141 | 853.3 | 75.1 | 0 | 16 | 0
16:30 | 3872 | 1818 | 912.5 | 38 | 39 | 1082.155 | 217.5 | 3987.5 | 116.69 | 141 | 859.25 | 97.6 | 0 | 12.5 | 0
17:00 | 3872 | 1817.5 | 912 | 38 | 40 | 1071.62 | 218 | 3934 | 64.6 | 141 | 865.2 | 120.1 | 0 | 9 | 0
17:30 | 3874.5 | 1797 | 912.5 | 38 | 40 | 1072.435 | 218.5 | 3822 | 38.41 | 157.5 | 881.05 | 140.05 | 0 | 6 | 0
18:00 | 3877 | 1776.5 | 913 | 38 | 40 | 1073.25 | 219 | 3710 | 12.22 | 174 | 896.9 | 160 | 0 | 3 | 0
18:30 | 3970.5 | 1794.5 | 913 | 38 | 43 | 1099.02 | 220 | 3894.5 | 6.11 | 340 | 1209.55 | 142.5 | 0 | 4 | 0
19:00 | 4064 | 1812.5 | 913 | 38 | 46 | 1124.79 | 221 | 4079 | 0 | 506 | 1522.2 | 125 | 0 | 5 | 0
19:30 | 3949 | 1764.5 | 904 | 38 | 46 | 1271.48 | 221 | 4496 | 0 | 511 | 1771.2 | 5 | 0 | 3 | 0
20:00 | 3957 | 1759.5 | 886 | 38 | 46 | 1325.61 | 221 | 4540 | 0 | 453 | 1457.5 | 0 | 0 | 13 | 0
20:30 | 4043.5 | 1794 | 885 | 38 | 44 | 1324.215 | 221 | 4590.5 | 0 | 432 | 1270.85 | 0 | 0 | 12 | 0
21:00 | 4130 | 1828.5 | 884 | 38 | 42 | 1322.82 | 221 | 4641 | 0 | 411 | 1084.2 | 0 | 0 | 11 | 0
21:30 | 4116.5 | 1832 | 884.5 | 38 | 44 | 1324.77 | 220 | 4635.5 | 0 | 402 | 1037.2 | 0 | 0 | 9.5 | 0
22:00 | 4103 | 1835.5 | 885 | 38 | 46 | 1326.72 | 219 | 4630 | 0 | 393 | 990.2 | 0 | 0 | 8 | 0
22:30 | 4101 | 1835.75 | 884.5 | 38 | 47 | 1325.735 | 219 | 4625 | 0 | 393 | 975.7 | 0 | 0 | 11 | 0
23:00 | 4099 | 1836 | 884 | 38 | 48 | 1324.75 | 219 | 4620 | 0 | 393 | 961.2 | 0 | 0 | 14 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 08:00 | 373 | 23:00 | Payra | 415 | 16:00 | 410 | 00:00
Ashuganj | 404 | 8:00 | 381 | 23:00 | Rahanpur | 404 | 18:30 | 387 | 01:00
Bhulta | 402 | 07:00 | 383 | 16:00 | Rampal | 405 | 09:00 | 393 | 01:00
Bibiana | 390 | 07:00 | 383 | 03:00
BIPTC | 402 | 05:00 | 391 | 00:00
Bogura | 389 | 18:30 | 367 | 01:00
Gopalganj | 399 | 08:00 | 387 | 02:00
Kaliakoir | 374 | 07:00 | 363 | 15:00
Madunaghat | 390 | 01:00 | 385 | 15:00
Meghnaghat | 386 | 07:00 | 377 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 08:00 | 216 | 12:00 | Keranigonj | 222 | 07:00 | 215 | 12:00
AKSML | 228 | 18:00 | 222 | 15:00 | Khulna(S) | 232 | 18:00 | 217 | 01:00
Aminbazar | 224 | 03:00 | 217 | 15:00 | Madunaghat | 230 | 02:00 | 226 | 15:00
Ashuganj | 232 | 07:00 | 222 | 23:00 | Madunaghat-400 | 231 | 00:00 | 227 | 12:00
Ashuganj-400 | 232 | 7:00 | 220 | 23:00 | Maniknagar | 221 | 06:00 | 213 | 15:00
Baghabari | 235 | 18:00 | 226 | 00:00 | Meghnaghat | 227 | 07:00 | 220 | 22:00
Barapukuria | 229 | 18:30 | 219 | 01:00 | Meghnaghat-400 | 223 | 07:00 | 216 | 15:00
Barapukuria-230 | 229 | 18:00 | 218 | 0:00 | Mirsorai | 226 | 08:00 | 219 | 22:00
Barishal | 227 | 07:00 | 218 | 00:00 | Rajshahi | 233 | 18:30 | 218 | 01:00
Bheramara | 234 | 08:00 | 221 | 01:00 | Rampal | 231 | 09:00 | 220 | 01:00
Bhulta | 226 | 07:00 | 214 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 223 | 22:00 | Rampura | 225 | 07:00 | 212 | 16:00
BIPTC | 237 | 09:00 | 221 | 01:00 | Shikalbaha | 229 | 00:00 | 223 | 16:00
Bogura | 241 | 18:30 | 227 | 01:00 | Shyampur | 222 | 07:00 | 215 | 11:00
Bogura-400 | 242 | 18:30 | 228 | 01:00 | Siddhirganj | 222 | 07:00 | 216 | 11:00
Borhanuddin | 232 | 09:00 | 225 | 00:00 | Sirajgonj | 240 | 18:30 | 234 | 01:00
BSRM | 226 | 07:00 | 218 | 22:00 | Sreepur | 229 | 08:00 | 221 | 23:00
Cumilla(N) | 222 | 07:00 | 215 | 23:00 | Tongi | 230 | 04:00 | 215 | 23:00
Faridpur | 225 | 08:00 | 216 | 00:00
Fenchuganj | 231 | 09:00 | 225 | 23:00
Ghorashal | 230 | 07:00 | 220 | 00:00
Ghorashal-230 | 226 | 08:00 | 215 | 16:00
Gopalganj | 227 | 08:00 | 218 | 00:00
GPH | 227 | 07:00 | 222 | 21:00
Haripur | 221 | 07:00 | 215 | 12:00
Hasnabad | 222 | 03:00 | 215 | 11:00
Hathazari | 225 | 04:00 | 220 | 12:00
Ishurdi | 236 | 08:00 | 224 | 01:00
Jhenaidah | 232 | 09:00 | 216 | 01:00
Kaliakoir | 232 | 07:00 | 223 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 07:00 | 130 | 15:00 | Lalmonirhat | 134 | 18:30 | 124 | 00:00
Agargaon | 131 | 06:00 | 125 | 12:00 | Madanganj | 128 | 07:00 | 124 | 10:00
Agrabad | 129 | 01:00 | 125 | 15:00 | Madaripur | 134 | 08:00 | 128 | 00:00
AKS | 127 | 00:00 | 125 | 10:00 | Madartek | 137 | 07:00 | 130 | 23:00
Aminbazar | 133 | 04:00 | 127 | 23:00 | Madunaghat | 130 | 03:00 | 127 | 15:00
Amnura | 137 | 17:00 | 128 | 02:00 | Magura | 136 | 09:00 | 123 | 00:00
Ashuganj | 141 | 07:00 | 135 | 23:00 | Mahasthangarh | 133 | 14:00 | 121 | 01:00
Bagerhat | 132 | 18:00 | 118 | 01:00 | Maijdee | 117 | 18:00 | 107 | 22:00
Bajitpur | 138 | 23:00 | 125 | 00:00 | Manikganj | 128 | 06:00 | 119 | 16:00
Bakulia | 130 | 00:00 | 127 | 10:00 | Maniknagar | 133 | 07:00 | 128 | 12:00
Banani | 138 | 06:00 | 131 | 16:00 | Matarbari | 127 | 09:00 | 109 | 00:00
Bangabhaban | 133 | 06:00 | 127 | 10:00 | Matuail | 129 | 07:00 | 125 | 10:00
Barapukuria | 140 | 18:30 | 130 | 00:00 | Millgate | 131 | 00:00 | 124 | 12:00
Barguna | 134 | 08:00 | 130 | 00:00 | Mirpur | 130 | 00:00 | 125 | 15:00
Barishal | 134 | 09:00 | 126 | 00:00 | Mirzapur | 132 | 08:00 | 125 | 16:00
Barishal-230 | 133 | 07:00 | 126 | 00:00 | Mithapukur | 127 | 14:00 | 107 | 01:00
Baroaulia | 131 | 19:00 | 127 | 12:00 | MI_Cement | 129 | 06:00 | 125 | 12:00
Baroirhat | 124 | 18:00 | 118 | 15:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 07:00 | 122 | 12:00 | Mogbazar | 139 | 01:00 | 131 | 13:00
BashundharaCement | 128 | 07:00 | 124 | 10:00 | Mongla | 133 | 18:30 | 120 | 01:00
Beanibazar | 129 | 09:00 | 122 | 00:00 | Motijheel | 133 | 06:00 | 127 | 12:00
Benapole | 135 | 18:00 | 121 | 00:00 | Muktagacha | 135 | 05:00 | 131 | 16:00
Bhaluka | 130 | 07:00 | 124 | 01:00 | Munshiganj | 129 | 07:00 | 124 | 04:00
Bhandaria | 128 | 18:00 | 116 | 01:00 | Muradnagar | 124 | 07:00 | 117 | 22:00
Bhangura | 133 | 14:00 | 127 | 00:00 | Mymensingh | 136 | 03:00 | 118 | 00:00
Bheramara | 138 | 09:00 | 131 | 01:00 | Naogaon | 132 | 18:30 | 119 | 01:00
Bheramara(GK) | 137 | 07:00 | 131 | 00:00 | Narail | 137 | 18:00 | 123 | 01:00
Bhulta | 124 | 02:00 | 120 | 10:00 | Narinda | 133 | 7:00 | 128 | 12:00
Bog-Sherpur | 133 | 13:00 | 124 | 01:00 | Narshingdi | 134 | 18:30 | 121 | 23:00
Bogura | 135 | 06:00 | 126 | 01:00 | Natore | 134 | 09:00 | 126 | 01:00
Bogura-230 | 136 | 18:30 | 126 | 01:00 | Nawabganj | 133 | 07:00 | 127 | 12:00
Brahmanbaria | 137 | 07:00 | 128 | 23:00 | Netrakona | 125 | 09:00 | 117 | 00:00
Cantonment | 131 | 07:00 | 125 | 12:00 | New | 132 | 02:00 | 125 | 12:00
Chandina | 127 | 18:00 | 121 | 22:00 | Niamatpur | 138 | 18:00 | 131 | 01:00
Chandpur | 125 | 18:30 | 117 | 22:00 | Noapara | 136 | 18:00 | 125 | 00:00
Chandraghona | 131 | 18:00 | 129 | 11:00 | Pabna | 134 | 07:00 | 127 | 01:00
Chapai | 137 | 17:00 | 131 | 00:00 | Palashbari | 127 | 10:00 | 107 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 07:00 | 125 | 12:00 | Panchagarh | 134 | 07:00 | 127 | 11:00
Chauddagram | 123 | 18:00 | 117 | 22:00 | Patiya | 129 | 09:00 | 104 | 19:00
Chhatak | 128 | 09:00 | 120 | 00:00 | Patuakhali | 134 | 08:00 | 131 | 00:00
Chowmuhani | 118 | 18:00 | 108 | 22:00 | Payra | 136 | 08:00 | 134 | 00:00
Chuadanga | 134 | 18:00 | 119 | 00:00 | PHP | 123 | 18:00 | 116 | 22:00
Coxsbazar | 120 | 18:00 | 110 | 00:00 | Postogola | 131 | 07:00 | 126 | 12:00
Cumilla(N) | 127 | 18:00 | 121 | 23:00 | Purbachal | 139 | 07:00 | 124 | 12:00
Cumilla(S) | 132 | 05:00 | 120 | 22:00 | Purbasadipur | 134 | 18:30 | 126 | 00:00
Daganbhuiyan | 120 | 18:00 | 111 | 22:00 | Rahanpur | 139 | 17:00 | 133 | 00:00
Daudkandi | 127 | 07:00 | 114 | 21:00 | Rahanpur-400 | 139 | 17:00 | 133 | 00:00
Dhaka | 137 | 00:00 | 131 | 16:00 | Rahim | 132 | 07:00 | 125 | 12:00
Dhamrai | 131 | 04:00 | 126 | 10:00 | Rajbari | 133 | 09:00 | 124 | 00:00
Dhanmondi | 139 | 07:00 | 130 | 16:00 | Rajendrapur | 131 | 08:00 | 123 | 14:00
Dohazari | 127 | 18:00 | 103 | 22:00 | Rajshahi | 134 | 18:00 | 124 | 01:00
Faridpur | 134 | 07:00 | 128 | 00:00 | Rajshahi-230 | 134 | 09:00 | 125 | 01:00
Fatullah | 130 | 08:00 | 125 | 12:00 | Ramganj | 118 | 18:00 | 109 | 22:00
Fenchuganj | 137 | 09:00 | 132 | 00:00 | Rampur | 129 | 04:00 | 125 | 15:00
Feni | 122 | 18:00 | 114 | 22:00 | Rampura | 138 | 00:00 | 130 | 16:00
Ghatail | 131 | 09:00 | 126 | 17:00 | Rangamati | 130 | 00:00 | 127 | 23:00
Ghorashal | 136 | 07:00 | 130 | 10:00 | Rangpur | 136 | 19:00 | 127 | 00:00
Goalpara | 138 | 18:00 | 126 | 01:00 | Ruppur | 137 | 07:00 | 132 | 01:00
Gollamari | 137 | 08:00 | 127 | 01:00 | Saidpur | 135 | 18:30 | 127 | 00:00
Gopalganj | 135 | 18:00 | 126 | 01:00 | Satkhira | 134 | 09:00 | 121 | 00:00
Gopalganj-400 | 136 | 08:00 | 130 | 01:00 | Satmasjid | 131 | 08:00 | 124 | 13:00
Gulshan | 137 | 00:00 | 131 | 15:00 | Savar | 132 | 01:00 | 125 | 22:00
Halishahar | 130 | 00:00 | 127 | 11:00 | SevenRings | 137 | 08:00 | 128 | 16:00
Haripur | 129 | 07:00 | 125 | 12:00 | ShahCement | 129 | 07:00 | 125 | 12:00
HaripurSBU | 129 | 06:00 | 125 | 13:00 | Shahjadpur | 136 | 06:00 | 132 | 21:00
Hasnabad | 131 | 19:30 | 126 | 12:00 | Shahjibazar | 137 | 07:00 | 127 | 23:00
Hathazari | 132 | 00:00 | 128 | 15:00 | Shahmirpur | 130 | 00:00 | 127 | 15:00
Ishurdi | 138 | 08:00 | 130 | 01:00 | Shariatpur | 133 | 09:00 | 125 | 00:00
Jaldhaka | 133 | 18:30 | 123 | 00:00 | Sherpur | 137 | 06:00 | 132 | 00:00
Jamalpur | 140 | 06:00 | 134 | 16:00 | Shikalbaha | 120 | 00:00 | 117 | 16:00
Jashore | 135 | 09:00 | 123 | 00:00 | Shikalbaha-230 | 132 | 00:00 | 128 | 16:00
Jhenaidah | 137 | 09:00 | 121 | 00:00 | Shitalakhya | 129 | 06:00 | 125 | 12:00
Jhenaidah-230 | 139 | 14:00 | 126 | 00:00 | Sholosohor | 130 | 04:00 | 128 | 05:00
Joydebpur | 135 | 19:00 | 127 | 09:00 | Shyampur | 130 | 08:00 | 126 | 13:00
Joypurhat | 131 | 18:30 | 118 | 00:00 | Shyampur-230 | 130 | 08:00 | 124 | 11:00
Juldah | 130 | 00:00 | 127 | 10:00 | Siddhirganj | 130 | 07:00 | 125 | 12:00
Kabirpur | 132 | 02:00 | 120 | 16:00 | Sirajganj | 133 | 05:00 | 126 | 21:00
Kachua | 124 | 18:30 | 115 | 22:00 | Sonargaon | 127 | 06:00 | 122 | 11:00
Kaliakoir | 134 | 07:00 | 128 | 12:00 | Sreemongol | 135 | 07:00 | 126 | 23:00
Kallyanpur | 131 | 00:00 | 125 | 14:00 | Sreepur | 132 | 06:00 | 127 | 12:00
Kalurghat | 130 | 00:00 | 128 | 10:00 | Srinagar | 133 | 07:00 | 127 | 12:00
Kamrangirchar | 132 | 06:00 | 127 | 12:00 | SSM | 132 | 18:30 | 130 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 127 | 09:00 | 118 | 00:00
Kasba | 123 | 07:00 | 116 | 23:00 | Sylhet | 131 | 09:00 | 124 | 00:00
Kazla | 133 | 07:00 | 126 | 13:00 | Sylhet-132 | 130 | 08:00 | 125 | 00:00
Keranigonj | 134 | 08:00 | 127 | 13:00 | Tangail | 129 | 09:00 | 124 | 15:00
Khagrachori | 130 | 18:00 | 126 | 12:00 | Taraganj | 135 | 19:00 | 127 | 00:00
Khulna | 137 | 18:00 | 126 | 01:00 | Thakurgaon | 134 | 18:30 | 125 | 04:00
Khulna(S) | 138 | 18:00 | 128 | 00:00 | TK | 130 | 07:00 | 128 | 03:00
Khulshi | 128 | 00:00 | 125 | 11:00 | Tongi | 134 | 04:00 | 127 | 15:00
Kishoreganj | 128 | 05:00 | 124 | 00:00 | Ullahpara | 134 | 14:00 | 128 | 00:00
Kodda | 134 | 07:00 | 123 | 10:00 | Ullon | 138 | 07:00 | 131 | 12:00
KSRM | 131 | 18:00 | 127 | 05:00 | Uttara | 131 | 07:00 | 125 | 12:00
Kulaura | 135 | 09:00 | 130 | 00:00 | UttaraNew | 130 | 00:00 | 125 | 10:00
Kurigram | 134 | 18:30 | 122 | 00:00 | Zigatola | 133 | 07:00 | 127 | 13:00
Kushtia | 134 | 09:00 | 126 | 00:00
Laksam | 122 | 18:00 | 114 | 23:00
Lakshmipur | 120 | 20:00 | 109 | 22:00
Lalbag | 132 | 06:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division