## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-08-2025 | during | 15-08-2025 | during | 15-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 356 | 356 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 380 | 380 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 152 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15.4 | 35.2 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 50 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 22 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 120 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 62 | 50 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 345 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2049.4 | 2197.2 | 5810.7 | 5822.7 | 3351.58 | 3379.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 14 | 0 | 14 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 221 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 76 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 49 | 50 | 50 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 22 | 35 | 35 | 35 | 35 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 60 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.74 | 0 | 3.7 | 0 | 3.7 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 875 | 1086 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 9 | 9 | 11 | 9 | 11 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 760 | 760 | 760 | 760 | 760 | 760 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2187.74 | 2627 | 3803.42 | 3803.72 | 3656.42 | 3656.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 187 | 221 | 221 | 203 | 203 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 352 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 42 | 38 | 46.7 | 46.7 | 42 | 42 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 48 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 20 | 195 | 195 | 45 | 45 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 4 | 40 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 53 | 157 | 200 | 200 | 52 | 100 | Loop Oil Shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 28 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 114 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 9 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 94 | 91 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1523 | 1639 | 2444.56 | 2379.56 | 1952.36 | 1935.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-08-2025 | during | 15-08-2025 | during | 15-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 62 | 72 | 157.5 | 157.5 | 112 | 112 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 120 | 175 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 84 | 84 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33.95 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 34 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 299.95 | 354 | 596 | 549 | 488 | 458
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 154 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 83 | 83 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 91 | 0 | 0 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 350 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 265 | 250 | 300 | 300 | 265 | 265 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1270 | 1334 | 1405 | 1405 | 1390 | 1390
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 883 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 188 | 198 | 410 | 410 | 293 | 293 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 49 | 0 | 49 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1017 | 1136 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2146 | 2272 | 3265.2 | 3216.2 | 3023.2 | 2974.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 303 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 790 | 1080 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 220 | 273 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.17 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1648.17 | 1991 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 15.86 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 135 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 389 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.52 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 824.17 | 1441.83 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.84 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 37 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1788.39 | 2295.83 | 3186.47 | 3019.87 | 3152.09 | 2985.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 45 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 181 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 195 | 0 | 105 | 0 | 105 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 537.6 | 453 | 608.6 | 472 | 608.6 | 472
System Total |  |  |  |  | 28821.2 | 27843.665 | 13450.25 | 15163.03 | 23281.95 | 22829.05 | 19769.25 | 19397.35
Forecast Scenario (15-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14290 |  | 0 |  | 14290
|  |  |  | 2:00 | 13860 |  | 0 |  | 13860
|  |  |  | 3:00 | 13520 |  | 0 |  | 13520
|  |  |  | 4:00 | 13220 |  | 0 |  | 13220
|  |  |  | 5:00 | 12860 |  | 0 |  | 12860
|  |  |  | 6:00 | 12160 |  | 0 |  | 12160
|  |  |  | 7:00 | 11830 |  | 0 |  | 11830
|  |  |  | 8:00 | 11720 |  | 0 |  | 11720
|  |  |  | 9:00 | 11490 |  | 0 |  | 11490
|  |  |  | 10:00 | 11470 |  | 0 |  | 11470
|  |  |  | 11:00 | 11580 |  | 0 |  | 11580
|  |  |  | 12:00 | 12200 |  | 0 |  | 12200
|  |  |  | 13:00 | 12820 |  | 0 |  | 12820
|  |  |  | 14:00 | 12320 |  | 0 |  | 12320
|  |  |  | 15:00 | 12000 |  | 0 |  | 12000
|  |  |  | 16:00 | 11760 |  | 0 |  | 11760
|  |  |  | 17:00 | 11370 |  | 0 |  | 11370
|  |  |  | 18:00 | 11270 |  | 0 |  | 11270
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13180 |  | 0 |  | 13180
|  |  |  | 19:30 | 13990 |  | 0 |  | 13990
|  |  |  | 20:00 | 13790 |  | 0 |  | 13790
|  |  |  | 21:00 | 13990 |  | 0 |  | 13990
|  |  |  | 22:00 | 14040 |  | 0 |  | 14040
|  |  |  | 23:00 | 14100 |  | 0 |  | 14100
Probable Maximum Temperature: |  |  | 32.30°C
Probable Maximum Demand at Day Peak: |  |  | 12200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13990.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13990.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 305.54 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:55 hrs on 15-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-08-2025 | [28 empty] | Date: | 14-08-2025 | [28 empty] | Date: | 14-08-2025 | [28 empty] | Date: | 14-08-2025 | [28 empty] | Date: | 14-08-2025 | [13 empty] | Date: | 14-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [13 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 88 | 81 | 0 | 0 | 17 | 33 | 0 | 350 | 151 | 390 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 49 | 61 | 0 | 12 | 25 | 0 | 219 | 0 | 37 | 763 | 0 | 0 | 19 | 8 | 0 | 222 | 0 | 0 | 0 | 892 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 49 | 195 | 42 | 94 | 70 | 74 | 44 | 20 | 106 | 46 | 52.2 | 0 | 0 | 295 | 250 | 381 | 0 | 30 | 159 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 120 | 73 | 0 | 0 | 6 | 7546.2 | 885 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 1325.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 189 | 0 | 191 | 0 | 414 | 0 | 0 | 181 | 51 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 304 | 1000 | 0 | 6874.34 | 14420.54 | 107.06
01:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 88 | 62 | 0 | 0 | 0 | 32 | 0 | 350 | 152 | 383 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 49 | 62 | 0 | 12 | 25 | 0 | 219 | 0 | 37 | 758 | 0 | 0 | 19 | 8 | 0 | 222 | 0 | 0 | 0 | 872 | 0 | 51 | 0 | 8 | 0 | 357 | 330 | 50 | 195 | 42 | 92 | 70 | 61 | 37 | 20 | 106 | 44 | 43 | 0 | 0 | 300 | 250 | 381 | 0 | 30 | 155 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 120 | 73 | 0 | 0 | 6 | 7455 | 884 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1074 | 0 | 1206.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 190 | 0 | 190 | 0 | 414 | 0 | 0 | 177 | 51 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 306 | 1000 | 0 | 6579.89 | 14034.89 | 107.06
02:00 | 0 | 68 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 79 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 153 | 381 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 49 | 39 | 0 | 12 | 25 | 0 | 218 | 0 | 37 | 760 | 0 | 0 | 0 | 3 | 0 | 222 | 0 | 0 | 0 | 875 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 50 | 193 | 39 | 89 | 70 | 52 | 36 | 20 | 106 | 44 | 43 | 0 | 0 | 300 | 250 | 371 | 0 | 30 | 155 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 120 | 74 | 0 | 0 | 0 | 7235.4 | 885 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 991 | 0 | 1164.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 190 | 0 | 190 | 0 | 414 | 0 | 0 | 175 | 51 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 220 | 0 | 306 | 1005 | 0 | 6377.09 | 13612.49 | 107.06
03:00 | 0 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 152 | 381 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 49 | 16 | 0 | 12 | 25 | 0 | 217 | 0 | 29 | 761 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 50 | 191 | 39 | 84 | 70 | 51 | 36 | 20 | 88 | 42 | 43 | 0 | 0 | 295 | 240 | 357 | 0 | 30 | 155 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 84 | 120 | 73 | 0 | 0 | 0 | 7094.4 | 885 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 916 | 0 | 1111.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 188 | 0 | 185 | 0 | 414 | 0 | 0 | 172 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 306 | 1005 | 0 | 6228.47 | 13322.87 | 107.06
04:00 | 0 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 153 | 380 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 25.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 33 | 0 | 0 | 12 | 25 | 0 | 216 | 0 | 29 | 763 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 866 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 50 | 195 | 39 | 74 | 70 | 51 | 36 | 20 | 88 | 42 | 43 | 0 | 0 | 295 | 240 | 382 | 0 | 30 | 154 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 90 | 92 | 0 | 0 | 0 | 7062.4 | 885 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 0 | 1011.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 187 | 0 | 184 | 0 | 353 | 0 | 0 | 171 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 306 | 906 | 0 | 5934.52 | 12996.92 | 107.06
05:00 | 0 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 150 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 33 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 30 | 765 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 873 | 0 | 51 | 0 | 8 | 0 | 352 | 330 | 50 | 206 | 39 | 75 | 70 | 51 | 29 | 20 | 95 | 42 | 43 | 0 | 0 | 300 | 240 | 390 | 0 | 30 | 158 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 90 | 89 | 0 | 0 | 0 | 7114 | 885 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 817 | 0 | 824.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 187 | 0 | 184 | 0 | 390 | 0 | 0 | 169 | 51 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 115 | 220 | 0 | 306 | 810 | 0 | 5585.17 | 12699.17 | 107.06
06:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 152 | 387 | 0 | 0 | 335 | 0 | 0 | 1 | 52 | 26 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 33 | 0 | 0 | 12 | 25 | 0.11 | 217 | 0 | 40 | 762 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 857 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 50 | 194 | 39 | 75 | 70 | 51 | 28 | 20 | 106 | 36 | 43 | 3 | 0 | 300 | 240 | 354 | 0 | 30 | 156 | 8 | 0 | 82 | 30 | 0 | 15 | 100 | 0 | 85 | 90 | 90 | 0 | 0.8 | 0 | 7057.91 | 884 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 811 | 0 | 817.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0 | 0 | 0.78 | 174 | 0 | 187 | 0 | 184 | 0 | 350 | 0 | 0.02 | 169 | 51 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 4 | 0.17 | 0 | 172 | 115 | 220 | 0 | 305 | 720 | 0 | 5438.42 | 12496.33 | 107.06
07:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 152 | 414 | 0 | 0 | 315 | 0 | 0 | 0 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 0 | 12 | 25 | 0.65 | 217 | 0 | 30 | 657 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 858 | 4 | 51 | 0 | 8 | 0 | 325 | 280 | 50 | 191 | 39 | 75 | 70 | 51 | 26 | 20 | 106 | 36 | 43 | 16 | 0 | 305 | 240 | 360 | 0 | 30 | 145 | 8 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 85 | 104 | 87 | 0 | 5.89 | 0 | 6817.54 | 885 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 815 | 0 | 821.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.51 | 12 | 0 | 6.53 | 177 | 0 | 187 | 0 | 184 | 0 | 359 | 0 | 0.57 | 171 | 50 | 0 | 3 | 34 | 0 | 0 | 0 | 0.7 | 25 | 0.27 | 0 | 168 | 115 | 220 | 0 | 305 | 698 | 0 | 5507.92 | 12325.46 | 107.06
08:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1 | 0 | 0 | 300 | 150 | 455 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 24 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 33 | 0 | 0 | 12 | 25 | 2.27 | 220 | 0 | 2 | 658 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 861 | 6 | 51 | 0 | 8 | 0 | 280 | 280 | 49 | 213 | 39 | 74 | 70 | 54 | 26 | 20 | 106 | 34 | 43 | 40 | 0 | 305 | 240 | 372 | 0 | 30 | 139 | 8 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 85 | 120 | 67 | 1 | 12.18 | 0 | 6819.45 | 885 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 803 | 0 | 820.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.75 | 6 | 0 | 16.44 | 174 | 0 | 187 | 0 | 184 | 0 | 369 | 0 | 1.5 | 168 | 50 | 0 | 5 | 34 | 0 | 0 | 0 | 3 | 50 | 0.18 | 0 | 174 | 115 | 220 | 0 | 305 | 692 | 0 | 5575.02 | 12394.47 | 107.06
09:00 | 0 | 70 | 10 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 28 | 0 | 0 | 300 | 150 | 461 | 0 | 0 | 330 | 0 | 0 | 23 | 52 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 0 | 0 | 12 | 25 | 3.11 | 221 | 0 | 2 | 656 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 861 | 9 | 43 | 0 | 8 | 0 | 335 | 280 | 50 | 213 | 39 | 75 | 50 | 54 | 26 | 8 | 106 | 36 | 43 | 40 | 0 | 300 | 240 | 381 | 0 | 30 | 143 | 0 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 84 | 120 | 66 | 2 | 45.7 | 0 | 6996.81 | 885 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 811 | 0 | 819.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.77 | 30 | 0 | 38.73 | 177 | 0 | 187 | 0 | 189 | 0 | 358 | 0 | 3.37 | 167 | 50 | 0 | 9 | 34 | 0 | 0 | 0 | 3.5 | 80 | 0.19 | 0 | 171 | 115 | 220 | 0 | 305 | 700 | 0 | 5664.45 | 12661.26 | 107.07
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 146 | 465 | 0 | 0 | 329 | 0 | 0 | 20 | 90 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 0 | 12 | 25 | 2.19 | 221 | 0 | 5 | 705 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 873 | 11 | 43 | 0 | 8 | 0 | 343 | 330 | 47 | 211 | 42 | 89 | 50 | 53 | 25 | 20 | 106 | 36 | 43 | 75 | 0 | 305 | 260 | 388 | 0 | 30 | 154 | 6 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 74 | 120 | 62 | 1 | 15.98 | 0 | 7265.17 | 884 | 193 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 831 | 0 | 825.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.77 | 83 | 0 | 34.22 | 180 | 0 | 170 | 0 | 150 | 0 | 393 | 0 | 3.19 | 168 | 48 | 0 | 10 | 34 | 0 | 0 | 0 | 4.2 | 105 | 0.75 | 0 | 175 | 115 | 220 | 0 | 302 | 676 | 0 | 5699.62 | 12964.79 | 107.07
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 12 | 0 | 70 | 0 | 0 | 0 | 35 | 31 | 0 | 300 | 151 | 460 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 0 | 0 | 12 | 25 | 2.69 | 222 | 0 | 2 | 763 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 862 | 13 | 43 | 0 | 8 | 0 | 348 | 330 | 46 | 212 | 42 | 93 | 70 | 53 | 22 | 20 | 106 | 38 | 43 | 72 | 0 | 305 | 265 | 378 | 0 | 30 | 158 | 7 | 0 | 79 | 30 | 0 | 15 | 25 | 0 | 74 | 120 | 62 | 1 | 29.14 | 0 | 7291.83 | 885 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 102 | 867 | 0 | 829.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.21 | 40 | 0 | 39.57 | 179 | 0 | 180 | 0 | 150 | 0 | 414 | 0 | 3.59 | 165 | 47 | 35 | 11 | 34 | 0 | 0 | 0 | 6.9 | 200 | 0.06 | 0 | 173 | 115 | 220 | 0 | 303 | 681 | 0 | 5981.49 | 13273.32 | 107.07
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 15.4 | 0 | 70 | 0 | 0 | 0 | 50 | 62 | 0 | 300 | 150 | 450 | 0 | 0 | 335 | 0 | 0 | 33 | 90 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 0 | 0 | 12 | 25 | 0.74 | 222 | 0 | 3 | 760 | 0 | 0 | 11 | 0 | 0 | 216 | 0 | 0 | 0 | 875 | 16 | 43 | 4 | 8 | 0 | 352 | 330 | 44 | 199 | 42 | 94 | 70 | 53 | 8 | 20 | 106 | 40 | 43 | 67 | 0 | 295 | 265 | 375 | 0 | 30 | 154 | 7 | 0 | 79 | 30 | 0 | 15 | 20 | 0 | 84 | 120 | 62 | 0 | 33.95 | 0 | 7330.09 | 883 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1017 | 0 | 824.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.86 | 37 | 0 | 41.84 | 172 | 0 | 150 | 0 | 130 | 0 | 414 | 0 | 3.52 | 167 | 47 | 35 | 9 | 34 | 0 | 45 | 0 | 5.6 | 195 | 0.17 | 0 | 220 | 115 | 220 | 0 | 303 | 790 | 0 | 6120.16 | 13450.25 | 107.07
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 15.8 | 0 | 70 | 0 | 0 | 0 | 55 | 66 | 0 | 300 | 149 | 460 | 0 | 0 | 333 | 0 | 0 | 35 | 90 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 33 | 0 | 0 | 12 | 25 | 0.5 | 222 | 0 | 3 | 762 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 914 | 17 | 43 | 30 | 8 | 0 | 350 | 330 | 43 | 197 | 42 | 93 | 70 | 52 | 7 | 20 | 106 | 42 | 43 | 74 | 21 | 300 | 265 | 386 | 0 | 50 | 156 | 7 | 0 | 78 | 30 | 0 | 15 | 20 | 0 | 84 | 120 | 62 | 1 | 4.05 | 1 | 7483.35 | 884 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 1102 | 0 | 822.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.92 | 43 | 0 | 41.57 | 171 | 0 | 130 | 0 | 130 | 0 | 399 | 0 | 3.02 | 170 | 45 | 35 | 19 | 34 | 0 | 105 | 0 | 7.5 | 157 | 0.18 | 0 | 219 | 115 | 220 | 0 | 303 | 820 | 0 | 6230.26 | 13713.61 | 107.07
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 15.1 | 0 | 70 | 0 | 0 | 0 | 55 | 65 | 0 | 300 | 148 | 400 | 0 | 0 | 334 | 0 | 0 | 21 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 33 | 0 | 0 | 12 | 25 | 0.5 | 222 | 0 | 3 | 763 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 967 | 14 | 43 | 30 | 8 | 0 | 300 | 280 | 44 | 191 | 38 | 93 | 70 | 52 | 8 | 20 | 106 | 42 | 43 | 65 | 21 | 300 | 265 | 354 | 0 | 58 | 144 | 7 | 0 | 80 | 30 | 0 | 15 | 20 | 0 | 83 | 120 | 62 | 1 | 9.02 | 6 | 7304.62 | 884 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1142 | 0 | 821.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.24 | 15 | 0 | 23.92 | 155 | 0 | 130 | 0 | 130 | 0 | 349 | 0 | 2.6 | 175 | 46 | 0 | 35 | 34 | 0 | 135 | 0 | 4.6 | 129 | 0.17 | 0 | 221 | 115 | 180 | 0 | 303 | 870 | 0 | 6169.59 | 13474.21 | 107.08
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 16.2 | 0 | 70 | 8 | 0 | 0 | 55 | 67 | 0 | 350 | 148 | 355 | 0 | 0 | 326 | 0 | 0 | 5 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 0 | 0 | 12 | 25 | 0.75 | 220 | 0 | 2 | 760 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 972 | 15 | 43 | 30 | 8 | 0 | 344 | 330 | 45 | 203 | 38 | 93 | 50 | 52 | 8 | 20 | 106 | 42 | 43 | 19 | 21 | 310 | 265 | 376 | 0 | 58 | 144 | 7 | 0 | 80 | 30 | 0 | 15 | 50 | 0 | 74 | 120 | 64 | 1 | 16.75 | 3 | 7371.7 | 908 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1037 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.07 | 26 | 0 | 6.74 | 157 | 0 | 130 | 0 | 130 | 0 | 385 | 0 | 0.67 | 174 | 45 | 0 | 19 | 34 | 0 | 160 | 0 | 0 | 146 | 0.15 | 0 | 220 | 115 | 220 | 0 | 302 | 940 | 0 | 6252.63 | 13624.33 | 107.08
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 15.4 | 0 | 75 | 30 | 0 | 0 | 55 | 95 | 0 | 350 | 148 | 345 | 0 | 0 | 326 | 0 | 0 | 6 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 12 | 25 | 1.22 | 220 | 0 | 2 | 761 | 0 | 0 | 29 | 0 | 0 | 222 | 0 | 0 | 0 | 948 | 12 | 43 | 12 | 8 | 0 | 355 | 330 | 45 | 214 | 38 | 92 | 50 | 51 | 8 | 20 | 106 | 28 | 52.2 | 35 | 21 | 295 | 265 | 366 | 0 | 59 | 135 | 7 | 0 | 80 | 30 | 0 | 15 | 52 | 0 | 65 | 135 | 65 | 0 | 15.51 | 4 | 7339.33 | 907 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1021 | 0 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12 | 20 | 0 | 3.71 | 151 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0.39 | 180 | 45 | 0 | 18 | 34 | 0 | 45 | 0 | 4 | 115 | 0.11 | 0 | 219 | 115 | 220 | 0 | 303 | 950 | 0 | 6126.33 | 13465.66 | 107.08
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15.4 | 0 | 102 | 30 | 0 | 0 | 55 | 97 | 2 | 350 | 150 | 345 | 0 | 0 | 328 | 0 | 0 | 4 | 70 | 22 | 21 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 33 | 8 | 0 | 12 | 25 | 0.41 | 220 | 0 | 12 | 760 | 0 | 0 | 33 | 0 | 0 | 222 | 0 | 0 | 0 | 889 | 2 | 51 | 12 | 8 | 0 | 320 | 330 | 46 | 214 | 38 | 92 | 50 | 91 | 9 | 20 | 99 | 26 | 43 | 15 | 26 | 300 | 255 | 346 | 0 | 60 | 137 | 6 | 0 | 81 | 30 | 0 | 15 | 54 | 12 | 84 | 125 | 65 | 0 | 3.31 | 6 | 7309.12 | 908 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 930 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 18 | 0 | 2.5 | 150 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0.22 | 180 | 45 | 35 | 9 | 45 | 0 | 0 | 0 | 1.9 | 73 | 0.21 | 0 | 188 | 115 | 220 | 0 | 303 | 930 | 0 | 6011.11 | 13320.23 | 107.08
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 14.4 | 0 | 102 | 30 | 0 | 0 | 55 | 68 | 14 | 320 | 150 | 335 | 0 | 0 | 280 | 0 | 0 | 1 | 70 | 21.5 | 22 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 21 | 8 | 0 | 12 | 25 | 0.03 | 220 | 0 | 15 | 678 | 0 | 0 | 33 | 0 | 0 | 221 | 0 | 0 | 0 | 914 | 1 | 51 | 12 | 8 | 0 | 300 | 300 | 45 | 192 | 38 | 91 | 70 | 116 | 8 | 20 | 97 | 28 | 43 | 0 | 35 | 290 | 255 | 308 | 0 | 60 | 134 | 6 | 0 | 42 | 30 | 0 | 15 | 68 | 17 | 84 | 125 | 65 | 0 | 1.77 | 6 | 7017.7 | 909 | 191 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 920 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 4 | 0 | 1.59 | 135 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 0.15 | 180 | 46 | 35 | 1 | 49 | 0 | 0 | 0 | 0.4 | 11 | 0.04 | 0 | 178 | 115 | 180 | 0 | 303 | 900 | 0 | 5830.55 | 12848.25 | 107.08
19:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 36 | 17 | 102 | 70 | 71 | 6 | 55 | 142 | 15 | 420 | 149 | 350 | 0 | 30 | 332 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 49 | 60 | 0 | 12 | 25 | 0 | 220 | 13 | 17 | 762 | 5 | 0 | 33 | 1 | 13 | 221 | 0 | 0 | 0 | 1026 | 0 | 51 | 38 | 8 | 0 | 348 | 330 | 48 | 205 | 38 | 92 | 70 | 148 | 9 | 20 | 114 | 30 | 43 | 0 | 42 | 295 | 250 | 371 | 0 | 60 | 146 | 0 | 0 | 81 | 30 | 0 | 15 | 80 | 17 | 84 | 137 | 65 | 0 | 0 | 6 | 8200 | 908 | 193 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 984 | 2 | 1284 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 177 | 45 | 105 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 115 | 220 | 0 | 303 | 911 | 0 | 6509 | 14709 | 107.08
19:30 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 43.2 | 35 | 110 | 62 | 95 | 30 | 35 | 126 | 14 | 370 | 151 | 338 | 0 | 35 | 310 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 49 | 64 | 0 | 12 | 25 | 0 | 220 | 17 | 19 | 760 | 17 | 0 | 35 | 8 | 30 | 221 | 0 | 0 | 0 | 1063 | 0 | 51 | 100 | 8 | 0 | 356 | 330 | 48 | 180 | 38 | 92 | 70 | 155 | 9 | 20 | 114 | 28 | 43 | 0 | 44 | 295 | 250 | 372 | 0 | 60 | 151 | 6 | 0 | 82 | 30 | 0 | 15 | 85 | 17 | 84 | 175 | 65 | 0 | 0 | 6 | 8347.2 | 908 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 10 | 1426 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 331 | 0 | 0 | 179 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 115 | 220 | 0 | 304 | 1050 | 0 | 6807 | 15154.2
20:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 44.9 | 17 | 128 | 62 | 15 | 0 | 44 | 62 | 0 | 370 | 151 | 334 | 0 | 0 | 290 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 15 | 77 | 0 | 2 | 49 | 64 | 0 | 12 | 25 | 0 | 222 | 25 | 20 | 760 | 17 | 0 | 35 | 8 | 31 | 221 | 0 | 0 | 0 | 1074 | 0 | 51 | 80 | 8 | 0 | 356 | 330 | 48 | 191 | 38 | 90 | 70 | 157 | 8 | 20 | 114 | 28 | 43 | 0 | 44 | 295 | 250 | 358 | 0 | 60 | 149 | 6 | 0 | 82 | 30 | 0 | 15 | 86 | 17 | 84 | 175 | 65 | 0 | 0 | 6 | 8125.9 | 899 | 195 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 14 | 1439 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 346 | 0 | 0 | 178 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 115 | 220 | 0 | 303 | 1070 | 0 | 6874 | 14999.9 | 107.08
21:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35.2 | 17 | 120 | 62 | 15 | 0 | 35 | 50 | 0 | 420 | 152 | 345 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 0 | 60 | 0 | 9 | 49 | 76 | 0 | 12 | 25 | 0 | 222 | 17 | 22 | 760 | 17 | 0 | 26 | 8 | 17 | 221 | 0 | 0 | 0 | 1086 | 0 | 51 | 40 | 20 | 0 | 356 | 330 | 48 | 187 | 38 | 91 | 70 | 157 | 9 | 20 | 114 | 28 | 43 | 0 | 37 | 295 | 250 | 350 | 0 | 60 | 154 | 6 | 0 | 82 | 30 | 0 | 16 | 91 | 17 | 84 | 175 | 72 | 0 | 0 | 6 | 8151.2 | 900 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 1441.83 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 389 | 0 | 0 | 181 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 303 | 1080 | 0 | 7011.83 | 15163.03 | 107.09
22:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 19.2 | 17 | 104 | 62 | 0 | 0 | 35 | 33 | 0 | 420 | 151 | 360 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 5 | 49 | 78 | 0 | 12 | 25 | 0 | 222 | 14 | 25 | 759 | 0 | 0 | 26 | 8 | 15 | 221 | 0 | 0 | 0 | 1086 | 0 | 51 | 40 | 35 | 0 | 357 | 330 | 50 | 181 | 38 | 90 | 70 | 157 | 9 | 20 | 114 | 28 | 52.2 | 0 | 37 | 290 | 250 | 350 | 0 | 60 | 149 | 6 | 0 | 82 | 30 | 0 | 16 | 111 | 17 | 84 | 175 | 72 | 0 | 0 | 6 | 8073.4 | 899 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1365.49 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 339 | 0 | 0 | 182 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 180 | 0 | 304 | 1080 | 0 | 6861.49 | 14934.89 | 107.09
23:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 15.8 | 17 | 102 | 62 | 0 | 0 | 35 | 32 | 0 | 350 | 150 | 400 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 0 | 0 | 0 | 37 | 0 | 7 | 49 | 78 | 0 | 12 | 25 | 0 | 221 | 14 | 30 | 575 | 0 | 0 | 26 | 8 | 16 | 221 | 0 | 0 | 0 | 1127 | 0 | 43 | 40 | 26 | 0 | 351 | 310 | 49 | 199 | 38 | 90 | 70 | 156 | 8 | 20 | 114 | 46 | 52.2 | 0 | 37 | 290 | 235 | 386 | 0 | 60 | 149 | 6 | 0 | 82 | 30 | 0 | 16 | 110 | 17 | 84 | 175 | 72 | 0 | 0 | 6 | 7921 | 889 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 1376.49 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 28 | 0 | 135 | 0 | 130 | 0 | 130 | 0 | 370 | 0 | 0 | 180 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 304 | 1102 | 0 | 6973.49 | 14894.49 | 107.09
Total KWH | 0 | 1692480 | 409440 | 0 | 0 | 0 | 0 | 0 | 8629200 | 0 | 0 | 271800 | 117360 | 2042640 | 553440 | 123447 | 21010 | 741431 | 948960 | 40320 | 8308000 | 3602385 | 9499838 | 0 | 48843 | 7811222 | 0 | 0 | 171916 | 1994400 | 511200 | 465120 | 0 | 0 | 0 | 15055 | 314880 | 0 | 435360 | 921920 | 555216 | 0 | 293760 | 584640 | 14602 | 5293942 | 114581 | 476640 | 17578181.82 | 35127 | 0 | 372960 | 55083.6 | 117090 | 5203269 | 0 | 0 | 0 | 13909089 | 109890 | 1123576 | 520218 | 267636 | 0 | 8521600 | 7728000 | 1144800 | 4886000 | 951120 | 2077440 | 1573340 | 1994400 | 444360 | 449970 | 2520540 | 876480 | 1065686 | 462091 | 359792 | 7227500 | 6016400 | 9302000 | 0 | 985680 | 3590509 | 150552 | 0 | 1885440 | 715296 | 0 | 373000 | 2604200 | 137520 | 1927200 | 3151200 | 1632960 | 8900 | 189440 | 74400 | 171344984.42 | 21266181 | 4958496 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 311040 | 23396360 | 27360 | 24785131 | 0 | 0 | 0 | 0 | 5664 | 0 | 228608 | 0 | 0 | 276480 | 383337 | 156393 | 289504 | 3920455 | 0 | 3987336 | 0 | 3988545 | 0 | 9072872 | 0 | 24060 | 4260000 | 1114036 | 981515 | 153161 | 1380710 | 0 | 0 | 0 | 45253.08 | 1249920 | 2610 | 0 | 4996000 | 2770000 | 5326860 | 0 | 7309091 | 22027636.36 | 0 | 149606614.44 | 320951598.86

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13450.25 | MW | 12:00 Hr. | Energy Generated |  |  | 320.9516 |  | MKWHr.
| Day Peak Demand |  |  | 13450.25 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.172 |  | MKWHr.
| Evening Peak Generation |  |  | 15163.03 | MW | 21:00 Hr. | Energy Demand |  |  | 321.1236 |  | MKWHr.
| Evening Peak Demand |  |  | 15163.03 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 12325.46 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1002.22 |  | MMCFD
| Maximum Generation of the Day |  |  | 15163.03 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9455 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.827 | 0 | 9.0056 | 0 | 0 | 0.17192 | 0 | 0 | 48.0045 | Gas | 139.661 | Gas | 496621157.63
| Chattogram Zone |  |  | 5.6799 | 31.4873 | 3.3803 | 0 | 5.2939 | 0.12449 | 0 | 0.43536 | 46.4013 | Coal | 94.5904 | Coal | 561328761.3688
| Cumilla Zone |  |  | 26.646 | 0 | 8.9824 | 0 | 0 | 0.46209 | 0.87648 | 0 | 36.967 | HFO | 29.4389 | HFO | 549400782.742
| Mymensingh Zone |  |  | 1.633 | 0 | 5.2903 | 0 | 0 | 0.19834 | 0 | 0 | 7.1216 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.8506 | Hydro | 5.2939 | Hydro | 529394.2
| Khulna Zone |  |  | 4.9585 | 23.3964 | 0.02736 | 0 | 0 | 0.31104 | 22.1782 | 0 | 50.8714 | Solar | 3.6922 | Solar | 55453534.0488
| Barishal Zone |  |  | 8.0969 | 34.3327 | 0 | 0 | 0 | 0.00261 | 0 | 0 | 42.4322 | Import | 47.8398 | Import | 238506202.7
| Rajshahi Zone |  |  | 20.9692 | 0 | 0.39066 | 0 | 0 | 0.97338 | 24.7851 | 0 | 47.1184 | Wind | 0.43536 | Wind | 6373670.4
| Rangpur Zone |  |  | 0 | 5.374 | 2.3622 | 0 | 0 | 1.4483 | 0 | 0 | 9.1846
| Total |  |  | 139.661 | 94.5904 | 29.4389 | 0 | 5.2939 | 3.6922 | 47.8398 | 0.43536 | 320.9516
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 496621157.63 |  | Hydro | 529394.2
|  |  |  | Coal | 561328761.3688 |  | Solar | 55453534.0488
|  |  |  | HFO | 549400782.742 |  | Import | 238506202.7
|  |  |  | HSD | 0 |  | Wind | 6373670.4
[5 empty] | Total: | 190,82,13,503 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2662 | Peak Hr Flow | 900.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42641963.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.7851 | Peak Hr Flow | 1441.83 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 744 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.87648 | Peak Hr Flow | 28.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 986 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.9278 | Peak Hr Flow | 2369.83 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5183
|  |  |  | Chattogram |  | 0 |  | 1434
|  |  |  | Cumilla |  | 0 |  | 1360
|  |  |  | Mymensingh |  | 0 |  | 1229
|  |  |  | Sylhet |  | 0 |  | 648
|  |  |  | Khulna |  | 0 |  | 1734
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1469
|  |  |  | Rangpur |  | 0 |  | 981
|  |  |  | Total |  | 0 |  | 14512
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Bhulta 132/33kV S/S GT1 HT is restored.
| 08:25 | 10:05 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to 33KV Bus-2 S/D | [7 empty] | 50.0MW load
interrup.
| 08:25 | 10:05 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to 33KV BUS-2 S/D
|  | 08:28 | Bhulta 132/33kV S/S GT1 LT is restored.
|  | 08:58 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
| 09:22 | 10:15 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to Project work of PDB | [7 empty] | 10.0MW load
interrup.
| 09:22 | 10:15 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to Project work of PDB | [7 empty] | 10.0MW load
interrup.
|  | 10:40 | Rampura 230/132kV S/S Auto Transformer - 04 LT is restored.
|  | 10:40 | Rampura 230/132kV S/S Auto Transformer - 04 HT is restored.
| 11:04 | 13:16 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Forced S/D from Purbasadipur 132/33kV end Due to
Redhot maintenance on R-ph DS connector.
|  | 11:05 | Fatullah-Shyampur(New) 132 kV Ckt-1 is restored.
| 11:12 |  | Saidpur 150 MW power plant was sync.
| 11:25 | 12:25 | Pabna 132/33kV S/S T-3 LT Forced S/D
| 11:25 | 12:25 | Pabna 132/33kV S/S T-3 LT Forced S/D
| 11:25 | 12:25 | Pabna 132/33kV S/S T-3 HT Forced S/D
| 11:26 |  | Bhola Nutan Biddut BD LTD GT-2 Synchronized with remarks:- GT-12 synchronized to the grid
at 21:22 hrs. on 07,July 2025.
| 11:50 | 17:12 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Development work
| 12:00 |  | Day peak generation: 13445 MW
|  | 12:05 | Shyampur 230/132kV S/S Auto TR-1 LT is restored.
| 14:20 |  | Sylhet 225 MW CCPP ST was sync.
| 15:26 | 16:57 | Haripur-Narsingdi 132kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to A
shutdown has been taken at 400kV Bhulta GSS for Bus DS Hotspot Maintenance of the 400kV
Bhulta -Narsingdi Line.
| 15:27 | 16:57 | Bhulta-Narsingdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to A
shutdown has been taken at 400kV Bhulta GSS for Bus DS Hotspot Maintenance of the 400kV
Bhulta -Narsingdi Line.
| 17:24 | 18:22 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Z1,B-phase
relays.
|  | 17:28 | Maniknagar 132/33kV S/S Motijheel Ckt-2 is restored.
|  | 18:25 | Shyampur 230/132kV S/S Bus-1 (132kV) is restored.
| 18:49 |  | Raozan 25 MW PP Synchronized
| 21:00 |  | Peak generation 15162 MW
| 23:26 | 00:30 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Due to red hot maintenance at 33 KV | [7 empty] | 45.0MW load
|  |  | TR-3 Bus Section. | [7 empty] | interrup.
| 23:26 | 00:30 | Kabirpur 132/33kV S/S XFR, T-3 LT Forced S/D Due to Due to red hot maintenance at 33 KV | [7 empty] | 45.0MW load
|  |  | tr-3 Bus section. | [7 empty] | interrup.
| 00:44 | 01:50 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Bandarban feeder CB | [7 empty] | 63.0MW load
|  |  | loop maintenance work | [7 empty] | interrup.
| 00:44 | 01:50 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Bandarban feeder CB | [7 empty] | 63.0MW load
|  |  | loop maintenance work. | [7 empty] | interrup.
| 01:11 |  | Raozan 25 MW PP Shutdown
| 04:47 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Forced S/D from Beanibazar 132/33kV end
Due to Maintenance work in Sylhet -02 line due to temperature rise and from Fenchuganj
230/132/33kV end Due to Red hot maintenance
| 04:47 | 06:23 | Fenchuganj -Sylhet 132kV Ckt-1 Forced S/D from Beanibazar 132/33kV end Due to | [7 empty] | 66.0MW load
|  |  | Maintenance work in Sylhet -02 line due to temperature rise | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 06:09 |  | Purbasadipur-Saidpur 132kV Ckt-1 Project Work S/D from Purbasadipur 132/33kV end Due to
Gantry erection work from EEGBPS project and from Saidpur 132/33kVend.
| 06:50 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Project Work S/D from Barguna | [7 empty] | 16.0MW load
|  |  | 132/33kV end Due to Barishal 132kv Grid Sub - Station project work and from Patuakhali | [7 empty] | interrup. Barguna
|  |  | 132/33kV end Due to Barishal-Patuakhali 132KV Line Barishal End Project Work. | [7 empty] | 132/33kV end
| 07:00 |  | Min. Gen. 12010 MW
| 07:00 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 07:01 |  | Meghnaghat Summit 335 MW CCPP GT-2 was sync.
| 07:01 |  | Baroaulia 132/33kV S/S T-1(405T) HT Scheduled S/D Due to TR-01 Redhot Maintenance. | [7 empty] | 10.0MW load
interrup.
| 07:06 |  | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Bus Maintenance.
| 07:11 |  | Shyampur 230/132kV S/S Bus-1 (132kV) Scheduled S/D Due to IR test of CB at E07-132kV
Shyampur -01
| 07:58 |  | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Pbs feeder Red hot maintenance | [7 empty] | 22.0MW load
interrup.
| 07:59 |  | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Pbs feeder Red hot maintenance | [7 empty] | 22.0MW load
interrup.
| 08:00 |  | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to PDB Division 05 feeder maintenance work. | [7 empty] | 10.0MW load
interrup.
| 08:00 |  | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to PDB Division 05 feeder maintenance work. | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 356 | 8629200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8308000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3602385 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 21010 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7811222 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.2 | 271800 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 553440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 741431 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 48843 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 511200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 465120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 409440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 123447 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 120 | 2042640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1692480 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 40320 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 50 | 948960 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171916 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 117360 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 345 | 9499838 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1994400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2197.2 | 48004452
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 55083.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109890 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 372960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5293942 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5203269 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 117090 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 76 | 555216 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 921920 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 293760 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 476640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 314880 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 15055 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 114581 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 584640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 35127 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1086 | 13909089 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 435360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 760 | 17578181.82 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2627 | 46401286.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 187 | 4886000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8521600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7728000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 951120 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1144800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 20 | 267636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1123576 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 520218 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 359792 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1573340 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 157 | 1994400 | Loop Oil Shortage
| Import (Tripura) |  | Import | 0 | 160 | 28 | 876480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 1065686 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 449970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2520540 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 444360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 2077440 | Machine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 462091 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1639 | 36967049
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 1632960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 175 | 3151200 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 1927200 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 189440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 74400 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 137520 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 354 | 7121620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 985680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3590509 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715296 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1885440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 91 | 2604200 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 373000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 150552 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7227500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 9302000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 250 | 6016400 | -
Sylhet Area Total |  |  |  |  | 2325 | 1334 | 32850577
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21266181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 198 | 4958496 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 27360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 311040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1136 | 23396360 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2272 | 50871437
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 303 | 7309091 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2770000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 22027636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5326860 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 4996000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2610 | -
Barishal Area Total |  |  |  |  | 2236 | 1991 | 42432197.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 276480 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 135 | 3920455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3987336 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3988545 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 389 | 9072872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 156393 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 228608 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 5664 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1441.83 | 24785131 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 289504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 383337 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2295.83 | 47118385
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1114036 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 181 | 4260000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1380710 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45253.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 981515 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 153161 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1249920 | -
Rangpur Area Total |  |  |  |  | 950 | 453 | 9184595.08
Eastern Grid Total |  |  |  |  | 17401.505 | 8151.2 | 171344984.42
Western Grid Total |  |  |  |  | 10442.16 | 7011.83 | 149606614.44
National Grid Total |  |  |  |  | 27843.665 | 15163.03 | 320951598.86
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-08-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9853.02 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4657.7 | MW
i) Dhaka area |  |  | 5182.88 |  | MW | i) Khulna area |  |  |  | 1734 | MW
ii) Chattogram area |  |  | 1433.5 |  | MW | ii) Barishal area |  |  |  | 473.5 | MW
iii) Cumilla area |  |  | 1359.64 |  | MW | iii) Rajshahi area |  |  |  | 1469.2 | MW
iv) Mymensingh area |  |  | 1229 |  | MW | iv) Rangpur area |  |  |  | 981 | MW
v) Sylhet area |  |  | 648 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14510.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 19:30 | 133 | PHP | 9 | 16:00
2 | AKSML | 125 | 23:00 | 68 | Ishurdi | 81 | 19:30 | 134 | Pabna | 124 | 19:30
3 | Aftabnagar | 38 | 11:00 | 69 | Jaldhaka | 88 | 19:30 | 135 | Palashbari | 96 | 19:00
4 | Agargaon | 130 | 16:00 | 70 | Jamalpur | 130 | 23:00 | 136 | Panchagarh | 62 | 19:30
5 | Agrabad | 94 | 12:00 | 71 | Jashore | 139 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 25 | 00:00 | 72 | Jhenaidah | 127 | 19:00 | 138 | Patuakhali | 71.5 | 01:00
7 | Ashuganj | 81 | 23:00 | 73 | Joydebpur | 151 | 12:00 | 139 | Payra | 36 | 00:00
8 | BSRM | 195 | 00:00 | 74 | Joypurhat | 62 | 22:00 | 140 | Postogola | 58 | 13:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 17.5 | 23:00 | 141 | Purbachal | 21 | 19:00
10 | Bajitpur | 87 | 21:00 | 76 | KSRM | 28 | 08:00 | 142 | Purbasadipur | 125 | 21:00
11 | Bakulia | 91 | 12:00 | 77 | Kabirpur | 260 | 12:00 | 143 | Rahanpur | 40 | 22:00
12 | Banani | 50 | 10:00 | 78 | Kachua | 90 | 22:00 | 144 | Rahim | 25 | 12:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajbari | 83 | 19:00
14 | Barapukuria | 70 | 19:30 | 80 | Kalurghat | 40 | 11:00 | 146 | Rajendrapur | 133 | 19:30
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 78 | 12:00 | 147 | Rajshahi | 123 | 19:30
16 | Barishal | 113 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 68 | 13:00
17 | Barishal-230 | 100 | 00:00 | 83 | Kasba | 34 | 20:00 | 149 | Ramganj | 112 | 19:00
18 | Baroaulia | 63 | 10:00 | 84 | Kazla | 112 | 17:00 | 150 | Rampur | 40 | 00:00
19 | Baroirhat | 63 | 19:00 | 85 | Keranigonj | 94 | 19:30 | 151 | Rangamati | 17 | 19:00
20 | Bashundhara | 195 | 14:00 | 86 | Khagrachori | 28 | 18:30 | 152 | Rangpur | 137 | 20:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulna | 66 | 19:00 | 153 | Ruppur | 7.4 | 09:00
22 | Beanibazar | 78 | 20:00 | 88 | Khulshi | 180 | 13:00 | 154 | SSM | 2 | 23:00
23 | Benapole | 58 | 19:30 | 89 | Kishoreganj | 134 | 19:30 | 155 | Saidpur | 108 | 19:30
24 | Bhaluka | 151 | 15:00 | 90 | Kodda | 300 | 12:00 | 156 | Satkhira | 134 | 00:00
25 | Bhandaria | 56 | 21:00 | 91 | Kulaura | 52 | 19:30 | 157 | Satmasjid | 97 | 19:00
26 | Bhangura | 40 | 23:00 | 92 | Kurigram | 72 | 19:00 | 158 | Savar | 228 | 11:00
27 | Bheramara(GK) | 65 | 19:00 | 93 | Kushtia | 156 | 20:00 | 159 | SevenRings | 15.74 | 20:00
28 | Bhulta | 205 | 19:30 | 94 | Laksam | 33 | 23:00 | 160 | ShahCement | 28 | 15:00
29 | Bog-Sherpur | 72 | 22:00 | 95 | Lakshmipur | 21 | 00:00 | 161 | Shahjadpur | 81 | 19:30
30 | Bogura | 163 | 20:00 | 96 | Lalbag | 56 | 18:30 | 162 | Shahjibazar | 130 | 22:00
31 | Borhanuddin | 93 | 05:00 | 97 | Lalmonirhat | 72 | 19:00 | 163 | Shahmirpur | 60 | 15:00
32 | Brahmanbaria | 126 | 20:00 | 98 | MI_Cement | 11.3 | 21:00 | 164 | Shariatpur | 92 | 23:00
33 | Cantonment | 138 | 13:00 | 99 | Madanganj | 37 | 23:00 | 165 | Sherpur | 158 | 21:00
34 | Chandina | 14.64 | 21:00 | 100 | Madaripur | 115 | 23:00 | 166 | Shikalbaha | 8 | 00:00
35 | Chandpur | 80 | 21:00 | 101 | Madartek | 88.67 | 00:00 | 167 | Shitalakhya | 85.8 | 13:00
36 | Chandraghona | 39 | 19:00 | 102 | Madunaghat | 53 | 19:00 | 168 | Sholosohor | 45 | 09:00
37 | Chapai | 64 | 00:00 | 103 | Magura | 67 | 19:00 | 169 | Shyampur | 164 | 01:00
38 | Charsaidpur | 33 | 21:00 | 104 | Mahasthangarh | 86 | 23:00 | 170 | Siddhirganj | 117 | 10:00
39 | Chauddagram | 71 | 23:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sirajganj | 106 | 21:00
40 | Chhatak | 46 | 21:00 | 106 | Manikganj | 129 | 20:00 | 172 | Sonargaon | 126 | 20:00
41 | Chowmuhani | 188 | 21:00 | 107 | Maniknagar | 78 | 16:00 | 173 | Sreemongol | 82 | 19:00
42 | Chuadanga | 113 | 19:00 | 108 | Matarbari | 52 | 21:00 | 174 | Sreepur | 103 | 11:00
43 | Coxsbazar | 138 | 19:00 | 109 | Matuail | 62 | 15:00 | 175 | Srinagar | 49.3 | 22:00
44 | Cumilla(N) | 140 | 12:00 | 110 | Millgate | 127 | 11:00 | 176 | Sunamganj | 64 | 22:00
45 | Cumilla(S) | 132 | 15:00 | 111 | Mirpur | 122 | 13:00 | 177 | Sylhet | 49 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 00:00 | 178 | Sylhet-132 | 122 | 15:00
47 | Daudkandi | 147 | 19:00 | 113 | Mirzapur | 46 | 20:00 | 179 | TK | 35 | 21:00
48 | Dhaka | 78 | 13:00 | 114 | Mithapukur | 70 | 19:30 | 180 | Tangail | 176 | 21:00
49 | Dhamrai | 128 | 11:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 23 | 21:00
50 | Dhanmondi | 140 | 13:00 | 116 | Mogbazar | 128 | 16:00 | 182 | Thakurgaon | 112 | 19:30
51 | Dohazari | 102 | 01:00 | 117 | Mongla | 41 | 12:00 | 183 | Tongi | 116 | 12:00
52 | Faridpur | 168 | 22:00 | 118 | Motijheel | 43 | 13:00 | 184 | Ullahpara | 38 | 19:30
53 | Fatullah | 102 | 12:00 | 119 | Muktagacha | 36 | 19:30 | 185 | Ullon | 54 | 18:30
54 | Fenchuganj | 43 | 19:00 | 120 | Munshiganj | 115 | 22:00 | 186 | Uttara | 82 | 11:00
55 | Feni | 116 | 19:30 | 121 | Muradnagar | 41 | 21:00 | 187 | UttaraNew | 59 | 23:00
56 | GPH | 31 | 16:00 | 122 | Mymensingh | 204 | 22:00 | 188 | Zigatola | 76 | 00:00
57 | Ghatail | 80 | 19:00 | 123 | Naogaon | 123 | 19:30
58 | Ghorashal | 13 | 00:00 | 124 | Narail | 58 | 00:00
59 | Ghorashal-230 | 97 | 03:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 188 | 01:00
61 | Gollamari | 88 | 00:00 | 127 | Natore | 147 | 22:00
62 | Gopalganj | 108 | 19:30 | 128 | Nawabganj | 61.6 | 22:00
63 | Gulshan | 122 | 16:00 | 129 | Netrakona | 142 | 20:00
64 | Halishahar | 70.5 | 15:00 | 130 | New | 68.4 | 12:00
65 | HaripurSBU | 164 | 23:00 | 131 | Niamatpur | 71 | 22:00
66 | Hasnabad | 72 | 21:00 | 132 | Noapara | 45 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14420.54 | 38 |  | 14460.25
1:00 | 14034.89 | 34 |  | 14070.42
2:00 | 13612.49 | 36 |  | 13650.11
3:00 | 13322.87 | 32 |  | 13356.31
4:00 | 12996.92 | 32 |  | 13030.36
5:00 | 12699.17 | 0 |  | 12699.17
6:00 | 12496.33 | 0 |  | 12496.33
7:00 | 12325.46 | 0 |  | 12325.46
8:00 | 12394.47 | 0 |  | 12394.47
9:00 | 12661.26 | 0 |  | 12661.26
10:00 | 12964.79 | 0 |  | 12964.79
11:00 | 13273.32 | 0 |  | 13273.32
12:00 | 13450.25 | 0 |  | 13450.25
13:00 | 13713.61 | 0 |  | 13713.61
14:00 | 13474.21 | 0 |  | 13474.21
15:00 | 13624.33 | 0 |  | 13624.33
16:00 | 13465.66 | 0 |  | 13465.66
17:00 | 13320.23 | 0 |  | 13320.23
18:00 | 12848.25 | 0 |  | 12848.25
19:00 | 14709 | 0 |  | 14709
19:30 | 15154.2 | 0 |  | 15154.2
20:00 | 14999.9 | 0 |  | 14999.9
21:00 | 15163.03 | 0 |  | 15163.03
22:00 | 14934.89 | 0 |  | 14934.89
23:00 | 14894.49 | 0 |  | 14894.49
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7546.2 | 6874.34 | 14420.54 | DAILY GENERATION CURVE
00:30 | 7500.6 | 6727.115 | 14227.715
01:00 | 7455 | 6579.89 | 14034.89 | 14-08-2025
01:30 | 7345.2 | 6478.49 | 13823.69
02:00 | 7235.4 | 6377.09 | 13612.49
02:30 | 7164.9 | 6302.78 | 13467.68
03:00 | 7094.4 | 6228.47 | 13322.87
03:30 | 7078.4 | 6081.495 | 13159.895
04:00 | 7062.4 | 5934.52 | 12996.92
04:30 | 7088.2 | 5759.845 | 12848.045
05:00 | 7114 | 5585.17 | 12699.17
05:30 | 7085.955 | 5511.795 | 12597.75
06:00 | 7057.91 | 5438.42 | 12496.33
06:30 | 6937.725 | 5473.17 | 12410.895
07:00 | 6817.54 | 5507.92 | 12325.46
07:30 | 6818.495 | 5541.47 | 12359.965
08:00 | 6819.45 | 5575.02 | 12394.47
08:30 | 6908.13 | 5619.735 | 12527.865
09:00 | 6996.81 | 5664.45 | 12661.26
09:30 | 7130.99 | 5682.035 | 12813.025
10:00 | 7265.17 | 5699.62 | 12964.79
10:30 | 7278.5 | 5840.555 | 13119.055
11:00 | 7291.83 | 5981.49 | 13273.32
11:30 | 7310.96 | 6050.825 | 13361.785
12:00 | 7330.09 | 6120.16 | 13450.25
12:30 | 7406.72 | 6175.21 | 13581.93
13:00 | 7483.35 | 6230.26 | 13713.61
13:30 | 7393.985 | 6199.925 | 13593.91
14:00 | 7304.62 | 6169.59 | 13474.21
14:30 | 7338.16 | 6211.11 | 13549.27
15:00 | 7371.7 | 6252.63 | 13624.33
15:30 | 7355.515 | 6189.48 | 13544.995
16:00 | 7339.33 | 6126.33 | 13465.66
16:30 | 7324.225 | 6068.72 | 13392.945
17:00 | 7309.12 | 6011.11 | 13320.23
17:30 | 7163.41 | 5920.83 | 13084.24
18:00 | 7017.7 | 5830.55 | 12848.25
18:30 | 7608.85 | 6169.775 | 13778.625
19:00 | 8200 | 6509 | 14709
19:30 | 8347.2 | 6807 | 15154.2
20:00 | 8125.9 | 6874 | 14999.9
20:30 | 8138.55 | 6942.915 | 15081.465 |  | Executive Engineer
21:00 | 8151.2 | 7011.83 | 15163.03 |  | Network Operation Division
21:30 | 8112.3 | 6936.66 | 15048.96
22:00 | 8073.4 | 6861.49 | 14934.89
22:30 | 7997.2 | 6917.49 | 14914.69
23:00 | 7921 | 6973.49 | 14894.49

## En-Curve
QF-LDC-12
Date | 14-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4095 | 1861 | 885 | 38 | 46 | 1325.34 | 219 | 4622 | 0 | 393 | 923.2 | 0 | 0 | 13 | 38 | DAILY ENERGY CURVE
00:30 | 4087 | 1859 | 884.5 | 38 | 45 | 1266.115 | 219 | 4544.5 | 0 | 384 | 881.1 | 0 | 0 | 19.5 | 36 | 14-08-2025
01:00 | 4079 | 1857 | 884 | 38 | 44 | 1206.89 | 219 | 4467 | 0 | 375 | 839 | 0 | 0 | 26 | 34
01:30 | 4070 | 1859.7 | 884.5 | 38 | 44 | 1185.49 | 218.5 | 4400 | 0 | 316 | 786.5 | 0 | 0 | 21 | 35 | Energy Generated | 320.9516 |  | MKWHr
02:00 | 4061 | 1862.4 | 885 | 38 | 44 | 1164.09 | 218 | 4333 | 0 | 257 | 734 | 0 | 0 | 16 | 36 | Energy not Served | 0.172 |  | MKWHr
02:30 | 4044 | 1855.4 | 885 | 38 | 43 | 1137.78 | 217.5 | 4282.5 | 0 | 234 | 708 | 0 | 0 | 22.5 | 34 | Total Energy Requirement | 321.1236 |  | MKWHr
03:00 | 4027 | 1848.4 | 885 | 38 | 42 | 1111.47 | 217 | 4232 | 0 | 211 | 682 | 0 | 0 | 29 | 32
03:30 | 4016.5 | 1847.9 | 885 | 38 | 42 | 1061.495 | 216.5 | 4178.5 | 0 | 186 | 662.5 | 0 | 0 | 25.5 | 32
04:00 | 4006 | 1847.4 | 885 | 38 | 42 | 1011.52 | 216 | 4125 | 0 | 161 | 643 | 0 | 0 | 22 | 32
04:30 | 4042 | 1847.7 | 885 | 38 | 42 | 917.845 | 217 | 4045 | 0 | 161 | 626 | 0 | 0 | 26.5 | 16
05:00 | 4078 | 1848 | 885 | 38 | 42 | 824.17 | 218 | 3965 | 0 | 161 | 609 | 0 | 0 | 31 | 0
05:30 | 4030 | 1853.5 | 884.5 | 38 | 39 | 820.835 | 217.5 | 3906 | 5.415 | 152 | 614 | 0 | 0 | 37 | 0
06:00 | 3982 | 1859 | 884 | 38 | 36 | 817.5 | 217 | 3847 | 10.83 | 143 | 619 | 0 | 0 | 43 | 0
06:30 | 3927 | 1843.5 | 884.5 | 38 | 36 | 819.42 | 217 | 3784.5 | 56.475 | 143 | 625 | 0 | 0 | 36.5 | 0
07:00 | 3872 | 1828 | 885 | 38 | 36 | 821.34 | 217 | 3722 | 102.12 | 143 | 631 | 0 | 0 | 30 | 0
07:30 | 3834.5 | 1830.5 | 885 | 38 | 35 | 820.745 | 218.5 | 3716.5 | 159.72 | 153 | 640.5 | 0 | 0 | 28 | 0
08:00 | 3797 | 1833 | 885 | 38 | 34 | 820.15 | 220 | 3711 | 217.32 | 163 | 650 | 0 | 0 | 26 | 0
08:30 | 3843.5 | 1821.5 | 885 | 38 | 35 | 820.02 | 220.5 | 3716 | 290.845 | 164 | 663.5 | 0 | 0 | 30 | 0
09:00 | 3890 | 1810 | 885 | 38 | 36 | 819.89 | 221 | 3721 | 364.37 | 165 | 677 | 0 | 0 | 34 | 0
09:30 | 3936 | 1827 | 884.5 | 38 | 36 | 822.69 | 221 | 3749.5 | 393.335 | 191.5 | 681.5 | 0 | 0 | 32 | 0
10:00 | 3982 | 1844 | 884 | 38 | 36 | 825.49 | 221 | 3778 | 422.3 | 218 | 686 | 0 | 0 | 30 | 0
10:30 | 3975.5 | 1844.5 | 884.5 | 38 | 37 | 827.325 | 221.5 | 3819.5 | 504.73 | 218 | 725.5 | 0 | 0 | 23 | 0
11:00 | 3969 | 1845 | 885 | 38 | 38 | 829.16 | 222 | 3861 | 587.16 | 218 | 765 | 0 | 0 | 16 | 0
11:30 | 3917.5 | 1830.5 | 884 | 38 | 39 | 826.665 | 222 | 4020 | 532.92 | 218 | 795.7 | 22.5 | 0 | 15 | 0
12:00 | 3866 | 1816 | 883 | 38 | 40 | 824.17 | 222 | 4179 | 478.68 | 218 | 826.4 | 45 | 0 | 14 | 0
12:30 | 3870.5 | 1823 | 883.5 | 38 | 41 | 823.12 | 222 | 4257 | 454.21 | 228.5 | 847.1 | 75 | 0 | 19 | 0
13:00 | 3875 | 1830 | 884 | 38 | 42 | 822.07 | 222 | 4335 | 429.74 | 239 | 867.8 | 105 | 0 | 24 | 0
13:30 | 3763 | 1775.5 | 884 | 38 | 42 | 821.565 | 222 | 4411 | 395.895 | 234.5 | 851.95 | 120 | 0 | 34.5 | 0
14:00 | 3651 | 1721 | 884 | 38 | 42 | 821.06 | 222 | 4487 | 362.05 | 230 | 836.1 | 135 | 0 | 45 | 0
14:30 | 3734.5 | 1748.5 | 896 | 38 | 42 | 822.53 | 221 | 4468.5 | 332.59 | 234 | 831.65 | 147.5 | 0 | 32.5 | 0
15:00 | 3818 | 1776 | 908 | 38 | 42 | 824 | 220 | 4450 | 303.13 | 238 | 827.2 | 160 | 0 | 20 | 0
15:30 | 3810 | 1748 | 907.5 | 38 | 35 | 867 | 220 | 4438.5 | 281.595 | 239 | 846.4 | 102.5 | 0 | 11.5 | 0
16:00 | 3802 | 1720 | 907 | 38 | 28 | 910 | 220 | 4427 | 260.06 | 240 | 865.6 | 45 | 0 | 3 | 0
16:30 | 3771 | 1744.5 | 907.5 | 38 | 27 | 965.5 | 220 | 4326 | 199.945 | 236.5 | 933 | 22.5 | 0 | 1.5 | 0
17:00 | 3740 | 1769 | 908 | 38 | 26 | 1021 | 220 | 4225 | 139.83 | 233 | 1000.4 | 0 | 0 | 0 | 0
17:30 | 3665 | 1704.25 | 908.5 | 38 | 27 | 1023 | 220 | 4172 | 82.59 | 231.5 | 1012.4 | 0 | 0 | 0 | 0
18:00 | 3590 | 1639.5 | 909 | 38 | 28 | 1025 | 220 | 4119 | 25.35 | 230 | 1024.4 | 0 | 0 | 0 | 0
18:30 | 3753 | 1744.25 | 908.5 | 38 | 29 | 1154.5 | 220 | 4290 | 12.675 | 374.5 | 1252.7 | 0 | 0 | 1.5 | 0
19:00 | 3916 | 1849 | 908 | 38 | 30 | 1284 | 220 | 4461 | 0 | 519 | 1481 | 0 | 0 | 3 | 0
19:30 | 3751 | 1803 | 908 | 38 | 28 | 1426 | 220 | 4679 | 0 | 517 | 1784.2 | 0 | 0 | 0 | 0
20:00 | 3753 | 1798 | 899 | 38 | 28 | 1439 | 222 | 4750 | 0 | 500 | 1570.9 | 0 | 0 | 2 | 0
20:30 | 3806 | 1838.5 | 899.5 | 38 | 28 | 1440.415 | 222 | 4807 | 0 | 502.5 | 1494.05 | 0 | 0 | 5.5 | 0
21:00 | 3859 | 1879 | 900 | 38 | 28 | 1441.83 | 222 | 4864 | 0 | 505 | 1417.2 | 0 | 0 | 9 | 0
21:30 | 3834 | 1871 | 899.5 | 38 | 28 | 1403.66 | 222 | 4871 | 0 | 506 | 1368.8 | 0 | 0 | 7 | 0
22:00 | 3809 | 1863 | 899 | 38 | 28 | 1365.49 | 222 | 4878 | 0 | 507 | 1320.4 | 0 | 0 | 5 | 0
22:30 | 3829.5 | 1861 | 894 | 38 | 37 | 1370.99 | 221.5 | 4826.5 | 0 | 515.5 | 1314.7 | 0 | 0 | 6 | 0
23:00 | 3850 | 1859 | 889 | 38 | 46 | 1376.49 | 221 | 4775 | 0 | 524 | 1309 | 0 | 0 | 7 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 07:00 | 373 | 15:00 | Payra | 416 | 06:00 | 409 | 23:00
Ashuganj | 405 | 6:00 | 383 | 15:00 | Rahanpur | 406 | 06:00 | 388 | 21:00
Bhulta | 402 | 06:00 | 378 | 14:00 | Rampal | 406 | 06:00 | 393 | 22:00
Bibiana | 390 | 06:00 | 378 | 18:00
BIPTC | 403 | 06:00 | 393 | 20:00
Bogura | 390 | 06:00 | 368 | 21:00
Gopalganj | 400 | 07:00 | 387 | 21:00
Kaliakoir | 375 | 06:00 | 362 | 14:00
Madunaghat | 390 | 06:00 | 380 | 23:00
Meghnaghat | 390 | 07:00 | 376 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 07:00 | 216 | 15:00 | Keranigonj | 224 | 07:00 | 214 | 15:00
AKSML | 228 | 06:00 | 222 | 16:00 | Khulna(S) | 232 | 06:00 | 221 | 00:00
Aminbazar | 225 | 06:00 | 217 | 15:00 | Madunaghat | 231 | 07:00 | 226 | 13:00
Ashuganj | 231 | 05:00 | 221 | 14:00 | Madunaghat-400 | 231 | 08:00 | 225 | 16:00
Ashuganj-400 | 231 | 05:00 | 221 | 14:00 | Maniknagar | 231 | 13:00 | 212 | 15:00
Baghabari | 235 | 05:00 | 225 | 19:00 | Meghnaghat | 228 | 08:00 | 220 | 12:00
Barapukuria | 228 | 09:00 | 220 | 19:30 | Meghnaghat-400 | 226 | 07:00 | 217 | 15:00
Barapukuria-230 | 228 | 09:00 | 220 | 19:30 | Mirsorai | 228 | 07:00 | 218 | 00:00
Barishal | 228 | 07:00 | 220 | 00:00 | Rajshahi | 232 | 06:00 | 222 | 0.5
Bheramara | 234 | 06:00 | 221 | 19:00 | Rampal | 232 | 06:00 | 220 | 22:00
Bhulta | 226 | 06:00 | 211 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 06:00 | 223 | 14:00 | Rampura | 225 | 06:00 | 209 | 15:00
BIPTC | 237 | 06:00 | 221 | 19:00 | Shikalbaha | 228 | 07:00 | 223 | 15:00
Bogura | 241 | 06:00 | 229 | 19:30 | Shyampur | 224 | 07:00 | 214 | 15:00
Bogura-400 | 241 | 06:00 | 230 | 19:30 | Siddhirganj | 222 | 07:00 | 215 | 13:00
Borhanuddin | 231 | 07:00 | 226 | 21:00 | Sirajgonj | 242 | 06:00 | 235 | 19:00
BSRM | 226 | 07:00 | 218 | 15:00 | Sreepur | 229 | 06:00 | 219 | 21:00
Cumilla(N) | 223 | 07:00 | 216 | 00:00 | Tongi | 223 | 18:00 | 211 | 15:00
Faridpur | 226 | 06:00 | 217 | 23:00
Fenchuganj | 230 | 06:00 | 224 | 22:00
Ghorashal | 230 | 01:00 | 220 | 00:00
Ghorashal-230 | 226 | 06:00 | 214 | 15:00
Gopalganj | 227 | 07:00 | 219 | 20:00
GPH | 229 | 07:00 | 221 | 15:00
Haripur | 222 | 07:00 | 214 | 15:00
Hasnabad | 221 | 03:00 | 215 | 13:00
Hathazari | 226 | 18:00 | 220 | 00:00
Ishurdi | 236 | 06:00 | 224 | 19:30
Jhenaidah | 232 | 06:00 | 218 | 19:30
Kaliakoir | 232 | 06:00 | 221 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 127 | 14:00 | Lalmonirhat | 132 | 09:00 | 124 | 19:00
Agargaon | 133 | 07:00 | 125 | 15:00 | Madanganj | 129 | 07:00 | 124 | 10:00
Agrabad | 130 | 06:00 | 125 | 13:00 | Madaripur | 134 | 06:00 | 129 | 00:00
AKS | 127 | 05:00 | 125 | 00:00 | Madartek | 138 | 05:00 | 127 | 14:00
Aminbazar | 131 | 06:00 | 127 | 14:00 | Madunaghat | 131 | 07:00 | 128 | 00:00
Amnura | 137 | 08:00 | 128 | 00:00 | Magura | 136 | 06:00 | 126 | 19:00
Ashuganj | 140 | 06:00 | 135 | 00:00 | Mahasthangarh | 133 | 06:00 | 122 | 19:30
Bagerhat | 133 | 08:00 | 121 | 00:00 | Maijdee | 117 | 07:00 | 107 | 22:00
Bajitpur | 130 | 04:00 | 122 | 19:00 | Manikganj | 127 | 04:00 | 118 | 21:00
Bakulia | 131 | 05:00 | 126 | 13:00 | Maniknagar | 134 | 07:00 | 127 | 13:00
Banani | 138 | 06:00 | 127 | 15:00 | Matarbari | 119 | 09:00 | 110 | 00:00
Bangabhaban | 133 | 05:00 | 126 | 15:00 | Matuail | 142 | 02:00 | 124 | 15:00
Barapukuria | 138 | 09:00 | 132 | 08:00 | Millgate | 132 | 04:00 | 122 | 12:00
Barguna | 134 | 07:00 | 130 | 00:00 | Mirpur | 131 | 06:00 | 125 | 10:00
Barishal | 132 | 06:00 | 127 | 23:00 | Mirzapur | 130 | 03:00 | 124 | 12:00
Barishal-230 | 133 | 06:00 | 127 | 23:00 | Mithapukur | 125 | 18:00 | 109 | 19:30
Baroaulia | 131 | 07:00 | 127 | 12:00 | MI_Cement | 130 | 07:00 | 124 | 15:00
Baroirhat | 124 | 07:00 | 118 | 15:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 06:00 | 121 | 12:00 | Mogbazar | 138 | 03:00 | 127 | 15:00
BashundharaCement | 129 | 08:00 | 124 | 16:00 | Mongla | 134 | 08:00 | 123 | 00:00
Beanibazar | 128 | 06:00 | 122 | 20:00 | Motijheel | 133 | 05:00 | 126 | 15:00
Benapole | 133 | 08:00 | 122 | 00:00 | Muktagacha | 134 | 08:00 | 130 | 19:00
Bhaluka | 130 | 06:00 | 121 | 19:00 | Munshiganj | 129 | 07:00 | 124 | 00:00
Bhandaria | 128 | 10:00 | 119 | 22:00 | Muradnagar | 124 | 07:00 | 117 | 00:00
Bhangura | 133 | 03:00 | 127 | 19:30 | Mymensingh | 150 | 01:00 | 111 | 19:00
Bheramara | 138 | 06:00 | 131 | 19:30 | Naogaon | 131 | 06:00 | 121 | 22:00
Bheramara(GK) | 137 | 07:00 | 131 | 19:00 | Narail | 136 | 06:00 | 125 | 19:30
Bhulta | 123 | 04:00 | 120 | 13:00 | Narinda | 134 | 07:00 | 127 | 13:00
Bog-Sherpur | 134 | 06:00 | 125 | 19:30 | Narshingdi | 134 | 06:00 | 121 | 00:00
Bogura | 135 | 06:00 | 127 | 21:00 | Natore | 134 | 06:00 | 125 | 19:30
Bogura-230 | 136 | 06:00 | 127 | 19:30 | Nawabganj | 134 | 07:00 | 126 | 23:00
Brahmanbaria | 134 | 05:00 | 128 | 00:00 | Netrakona | 124 | 06:00 | 109 | 19:00
Cantonment | 132 | 07:00 | 125 | 14:00 | New | 132 | 04:00 | 123 | 14:00
Chandina | 127 | 07:00 | 122 | 00:00 | Niamatpur | 138 | 05:00 | 131 | 22:00
Chandpur | 125 | 18:00 | 116 | 01:00 | Noapara | 135 | 08:00 | 124 | 12:00
Chandraghona | 131 | 07:00 | 128 | 15:00 | Pabna | 134 | 08:00 | 127 | 19:00
Chapai | 137 | 05:00 | 130 | 21:00 | Palashbari | 124 | 10:00 | 110 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 07:00 | 124 | 15:00 | Panchagarh | 132 | 13:00 | 123 | 08:00
Chauddagram | 124 | 07:00 | 117 | 22:00 | Patiya | 130 | 07:00 | 126 | 15:00
Chhatak | 126 | 06:00 | 119 | 21:00 | Patuakhali | 135 | 07:00 | 131 | 00:00
Chowmuhani | 117 | 07:00 | 108 | 22:00 | Payra | 136 | 07:00 | 134 | 00:00
Chuadanga | 134 | 08:00 | 121 | 19:00 | PHP | 123 | 08:00 | 116 | 22:00
Coxsbazar | 120 | 09:00 | 110 | 18:30 | Postogola | 132 | 07:00 | 126 | 15:00
Cumilla(N) | 128 | 07:00 | 122 | 00:00 | Purbachal | 139 | 06:00 | 121 | 16:00
Cumilla(S) | 133 | 04:00 | 120 | 00:00 | Purbasadipur | 130 | 00:00 | 122 | 07:00
Daganbhuiyan | 120 | 07:00 | 112 | 21:00 | Rahanpur | 139 | 05:00 | 132 | 19:30
Daudkandi | 123 | 10:00 | 114 | 00:00 | Rahanpur-400 | 139 | 05:00 | 133 | 19:30
Dhaka | 138 | 04:00 | 126 | 14:00 | Rahim | 130 | 07:00 | 125 | 13:00
Dhamrai | 131 | 05:00 | 124 | 15:00 | Rajbari | 133 | 07:00 | 126 | 00:00
Dhanmondi | 139 | 05:00 | 127 | 13:00 | Rajendrapur | 130 | 00:00 | 121 | 14:00
Dohazari | 126 | 08:00 | 121 | 00:00 | Rajshahi | 133 | 04:00 | 125 | 19:30
Faridpur | 135 | 07:00 | 128 | 23:00 | Rajshahi-230 | 134 | 06:00 | 126 | 19:00
Fatullah | 132 | 07:00 | 126 | 00:00 | Ramganj | 120 | 18:00 | 111 | 02:00
Fenchuganj | 135 | 06:00 | 131 | 23:00 | Rampur | 129 | 06:00 | 125 | 13:00
Feni | 122 | 18:00 | 115 | 22:00 | Rampura | 139 | 06:00 | 127 | 15:00
Ghatail | 131 | 18:00 | 125 | 19:00 | Rangamati | 130 | 07:00 | 127 | 00:00
Ghorashal | 134 | 01:00 | 128 | 14:00 | Rangpur | 133 | 09:00 | 128 | 08:00
Goalpara | 138 | 08:00 | 128 | 00:00 | Ruppur | 138 | 05:00 | 130 | 20:00
Gollamari | 137 | 06:00 | 129 | 00:00 | Saidpur | 132 | 01:00 | 125 | 08:00
Gopalganj | 135 | 06:00 | 128 | 00:00 | Satkhira | 135 | 09:00 | 122 | 00:00
Gopalganj-400 | 136 | 06:00 | 131 | 00:00 | Satmasjid | 132 | 07:00 | 125 | 13:00
Gulshan | 138 | 05:00 | 128 | 15:00 | Savar | 130 | 06:00 | 125 | 00:00
Halishahar | 131 | 07:00 | 125 | 13:00 | SevenRings | 135 | 06:00 | 127 | 15:00
Haripur | 130 | 07:00 | 125 | 15:00 | ShahCement | 131 | 07:00 | 124 | 15:00
HaripurSBU | 129 | 08:00 | 125 | 15:00 | Shahjadpur | 135 | 02:00 | 132 | 00:00
Hasnabad | 133 | 07:00 | 126 | 15:00 | Shahjibazar | 133 | 06:00 | 127 | 00:00
Hathazari | 132 | 06:00 | 127 | 16:00 | Shahmirpur | 131 | 07:00 | 127 | 00:00
Ishurdi | 138 | 05:00 | 131 | 19:30 | Shariatpur | 133 | 06:00 | 125 | 23:00
Jaldhaka | 131 | 13:00 | 123 | 19:30 | Sherpur | 137 | 09:00 | 128 | 15:00
Jamalpur | 139 | 09:00 | 132 | 19:00 | Shikalbaha | 121 | 06:00 | 116 | 13:00
Jashore | 136 | 06:00 | 125 | 00:00 | Shikalbaha-230 | 132 | 07:00 | 128 | 16:00
Jhenaidah | 137 | 05:00 | 121 | 19:30 | Shitalakhya | 130 | 07:00 | 124 | 15:00
Jhenaidah-230 | 138 | 06:00 | 128 | 19:30 | Sholosohor | 131 | 07:00 | 126 | 15:00
Joydebpur | 135 | 04:00 | 126 | 12:00 | Shyampur | 130 | 08:00 | 125 | 11:00
Joypurhat | 129 | 05:00 | 119 | 19:30 | Shyampur-230 | 132 | 07:00 | 125 | 00:00
Juldah | 130 | 03:00 | 126 | 15:00 | Siddhirganj | 130 | 07:00 | 125 | 10:00
Kabirpur | 130 | 01:00 | 119 | 16:00 | Sirajganj | 132 | 06:00 | 123 | 21:00
Kachua | 123 | 18:00 | 116 | 00:00 | Sonargaon | 127 | 08:00 | 122 | 02:00
Kaliakoir | 133 | 04:00 | 127 | 14:00 | Sreemongol | 133 | 07:00 | 126 | 21:00
Kallyanpur | 132 | 07:00 | 127 | 00:00 | Sreepur | 132 | 05:00 | 125 | 19:00
Kalurghat | 130 | 02:00 | 127 | 15:00 | Srinagar | 135 | 07:00 | 126 | 15:00
Kamrangirchar | 134 | 07:00 | 126 | 16:00 | SSM | 132 | 01:00 | 130 | 10:00
Kaptai | 131 | 0.25 | 124 | 0.54167 | Sunamganj | 124 | 07:00 | 117 | 21:00
Kasba | 123 | 07:00 | 117 | 00:00 | Sylhet | 129 | 06:00 | 124 | 00:00
Kazla | 133 | 08:00 | 126 | 16:00 | Sylhet-132 | 129 | 06:00 | 125 | 21:00
Keranigonj | 134 | 07:00 | 127 | 13:00 | Tangail | 129 | 03:00 | 122 | 12:00
Khagrachori | 130 | 07:00 | 126 | 15:00 | Taraganj | 132 | 13:00 | 125 | 07:00
Khulna | 137 | 08:00 | 128 | 00:00 | Thakurgaon | 131 | 13:00 | 120 | 08:00
Khulna(S) | 138 | 06:00 | 130 | 00:00 | TK | 130 | 04:00 | 127 | 15:00
Khulshi | 128 | 04:00 | 125 | 11:00 | Tongi | 132 | 04:00 | 124 | 15:00
Kishoreganj | 128 | 06:00 | 119 | 19:00 | Ullahpara | 134 | 05:00 | 126 | 19:30
Kodda | 130 | 07:00 | 121 | 12:00 | Ullon | 138 | 06:00 | 127 | 15:00
KSRM | 130 | 07:00 | 126 | 16:00 | Uttara | 131 | 06:00 | 125 | 15:00
Kulaura | 134 | 07:00 | 130 | 00:00 | UttaraNew | 138 | 17:00 | 125 | 10:00
Kurigram | 133 | 09:00 | 123 | 19:00 | Zigatola | 134 | 08:00 | 127 | 15:00
Kushtia | 134 | 05:00 | 126 | 19:00
Laksam | 150 | 08:00 | 114 | 03:00
Lakshmipur | 119 | 07:00 | 109 | 22:00
Lalbag | 134 | 06:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division