## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-08-2025 | [28 empty] | Date: | 16-08-2025 | [28 empty] | Date: | 16-08-2025 | [28 empty] | Date: | 16-08-2025 | [28 empty] | Date: | 16-08-2025 | [13 empty] | Date: | 16-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [13 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 87 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 16.5 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 302 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 17 | 23 | 0 | 70 | 0 | 0 | 0 | 0 | 1 | 49 | 78 | 0 | 12 | 12 | 0 | 219 | 0 | 34 | 769 | 0 | 0 | 12 | 8 | 0 | 220 | 0 | 0 | 0 | 1007 | 0 | 43 | 0 | 133 | 0 | 353 | 330 | 50 | 197 | 35 | 87 | 50 | 184 | 13 | 20 | 106 | 50 | 52.2 | 0 | 0 | 315 | 230 | 388 | 0 | 60 | 146 | 8 | 0 | 84 | 30 | 0 | 0 | 160 | 0 | 82 | 120 | 154 | 0 | 0 | 6 | 7776.7 | 898 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 196 | 0 | 193 | 0 | 414 | 0 | 0 | 167 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 220 | 0 | 304 | 1105 | 0 | 7091 | 14867.7 | 107.17
01:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 295 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 108 | 17 | 23 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 49 | 51 | 0 | 12 | 12 | 0 | 218 | 0 | 41 | 774 | 0 | 0 | 12 | 8 | 0 | 220 | 0 | 0 | 0 | 1007 | 0 | 43 | 0 | 155 | 0 | 354 | 330 | 50 | 193 | 35 | 84 | 50 | 176 | 0 | 20 | 114 | 46 | 52.2 | 0 | 0 | 310 | 230 | 363 | 0 | 60 | 136 | 8 | 0 | 84 | 30 | 0 | 0 | 160 | 0 | 83 | 120 | 155 | 0 | 0 | 6 | 7622.2 | 903 | 358 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 184 | 0 | 192 | 0 | 345 | 0 | 0 | 166 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 115 | 220 | 0 | 304 | 1100 | 0 | 6937 | 14559.2 | 107.19
02:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 294 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 108 | 17 | 23 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 49 | 2 | 0 | 12 | 12 | 0 | 218 | 0 | 42 | 770 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 915 | 0 | 43 | 0 | 132 | 0 | 353 | 330 | 50 | 193 | 35 | 90 | 50 | 200 | 0 | 20 | 114 | 44 | 52.2 | 0 | 0 | 310 | 230 | 328 | 0 | 60 | 136 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 83 | 120 | 155 | 0 | 0 | 6 | 7386.2 | 903 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 968 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 168 | 0 | 165 | 0 | 343 | 0 | 0 | 163 | 46 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 304 | 1105 | 0 | 6666 | 14052.2 | 107.21
03:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 295 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 90 | 17 | 23 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 42 | 770 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 895 | 0 | 43 | 0 | 71 | 0 | 353 | 330 | 50 | 195 | 35 | 93 | 50 | 200 | 0 | 20 | 114 | 44 | 16 | 0 | 0 | 315 | 230 | 328 | 0 | 60 | 140 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 83 | 85 | 155 | 0 | 0 | 6 | 7233 | 904 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 848 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 171 | 0 | 168 | 0 | 347 | 0 | 0 | 164 | 46 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 304 | 1105 | 0 | 6437 | 13670 | 107.23
04:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 295 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 17 | 23 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 42 | 770 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 856 | 0 | 43 | 0 | 71 | 0 | 355 | 330 | 49 | 195 | 35 | 92 | 70 | 200 | 0 | 20 | 93 | 42 | 16 | 0 | 0 | 310 | 230 | 334 | 0 | 60 | 137 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 83 | 65 | 155 | 0 | 0 | 6 | 7169 | 903 | 403 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 811 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 168 | 0 | 165 | 0 | 345 | 0 | 0 | 163 | 46 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 304 | 1020 | 0 | 6224 | 13393 | 107.25
05:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 90 | 17 | 23 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 42 | 715 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 858 | 0 | 43 | 0 | 71 | 0 | 351 | 330 | 50 | 202 | 35 | 92 | 70 | 200 | 0 | 20 | 97 | 42 | 16 | 0 | 0 | 310 | 230 | 346 | 0 | 60 | 141 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 83 | 45 | 156 | 0 | 0 | 6 | 7119 | 903 | 401 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 0 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 171 | 0 | 168 | 0 | 373 | 0 | 0 | 165 | 46 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 180 | 0 | 304 | 920 | 0 | 6012 | 13131 | 107.27
06:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 52 | 17 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 0.17 | 213 | 0 | 40 | 670 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 852 | 0 | 43 | 0 | 71 | 0 | 355 | 330 | 51 | 192 | 35 | 88 | 70 | 200 | 0 | 20 | 93 | 40 | 8 | 3 | 0 | 305 | 230 | 342 | 0 | 60 | 137 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 75 | 45 | 156 | 0 | 0 | 6 | 6966.17 | 903 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 802 | 0 | 873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 163 | 0 | 167 | 0 | 164 | 0 | 345 | 0 | 0.03 | 162 | 45 | 35 | 1 | 70 | 0 | 0 | 0 | 0.2 | 6 | 0.01 | 0 | 170 | 115 | 180 | 0 | 304 | 840 | 0 | 5749.41 | 12715.58 | 107.29
07:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 290 | 0 | 0 | 0 | 270 | 0 | 0 | 3 | 35 | 17 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0.83 | 212 | 0 | 38 | 658 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 854 | 5 | 43 | 0 | 45 | 0 | 320 | 300 | 49 | 192 | 38 | 68 | 70 | 199 | 0 | 20 | 66 | 36 | 8 | 12 | 0 | 310 | 225 | 328 | 0 | 60 | 138 | 8 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 75 | 45 | 156 | 0 | 0.22 | 6 | 6849.05 | 903 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 811 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.29 | 11 | 0 | 4.15 | 164 | 0 | 169 | 0 | 166 | 0 | 342 | 0 | 0.4 | 166 | 45 | 35 | 6 | 49 | 0 | 0 | 0 | 0.2 | 41 | 0.13 | 0 | 168 | 115 | 180 | 0 | 304 | 790 | 0 | 5720.17 | 12569.22 | 107.31
08:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 14 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 270 | 0 | 0 | 12 | 35 | 17 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.71 | 213 | 0 | 12 | 658 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 850 | 7 | 43 | 0 | 45 | 0 | 320 | 300 | 49 | 196 | 38 | 54 | 70 | 155 | 0 | 20 | 34 | 34 | 8 | 33 | 0 | 310 | 225 | 346 | 0 | 60 | 135 | 8 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 75 | 65 | 157 | 0 | 5.86 | 6 | 6768.57 | 904 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 790 | 0 | 825.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.61 | 35 | 0 | 9.43 | 165 | 0 | 168 | 0 | 165 | 0 | 350 | 0 | 0.83 | 164 | 46 | 35 | 15 | 48 | 0 | 0 | 0 | 3.4 | 99 | 0.28 | 0 | 172 | 115 | 180 | 0 | 304 | 750 | 0 | 5751.15 | 12519.72 | 107.32
09:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 53 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 270 | 0 | 0 | 21 | 35 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.6 | 214 | 0 | 3 | 656 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 853 | 14 | 43 | 0 | 45 | 0 | 320 | 300 | 49 | 195 | 38 | 62 | 50 | 145 | 0 | 12 | 33 | 34 | 8 | 59 | 0 | 315 | 225 | 351 | 0 | 60 | 138 | 8 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 75 | 80 | 155 | 1 | 33.12 | 6 | 6893.72 | 914 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81 | 800 | 0 | 824.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.88 | 61 | 0 | 17.11 | 168 | 0 | 172 | 0 | 169 | 0 | 348 | 0 | 1.35 | 167 | 46 | 35 | 24 | 34 | 0 | 0 | 0 | 5.3 | 90 | 0.53 | 0 | 170 | 115 | 180 | 0 | 304 | 745 | 0 | 5841.91 | 12735.63 | 107.35
10:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 55 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 270 | 0 | 0 | 17 | 35 | 26.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.95 | 215 | 0 | 2 | 626 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 856 | 10 | 43 | 0 | 45 | 0 | 320 | 300 | 49 | 196 | 35 | 64 | 50 | 137 | 7 | 12 | 28 | 36 | 8 | 67 | 0 | 305 | 230 | 342 | 0 | 60 | 131 | 8 | 0 | 79 | 30 | 0 | 0 | 160 | 0 | 75 | 65 | 154 | 1 | 46.17 | 6 | 6795.32 | 914 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 772 | 0 | 816.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.09 | 98 | 0 | 33.69 | 162 | 0 | 165 | 0 | 162 | 0 | 348 | 0 | 2.78 | 168 | 46 | 35 | 29 | 34 | 0 | 0 | 0 | 6.7 | 178 | 0.73 | 0 | 170 | 115 | 180 | 0 | 304 | 650 | 0 | 5777.49 | 12572.81 | 107.37
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 55 | 0 | 0 | 300 | 304 | 0 | 0 | 0 | 230 | 0 | 0 | 30 | 35 | 26.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.4 | 215 | 0 | 2 | 578 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 890 | 17 | 43 | 0 | 45 | 0 | 320 | 300 | 48 | 207 | 35 | 67 | 50 | 145 | 9 | 12 | 29 | 38 | 8 | 50 | 0 | 310 | 245 | 360 | 0 | 30 | 139 | 8 | 0 | 80 | 30 | 0 | 0 | 160 | 0 | 65 | 55 | 142 | 2 | 29.74 | 6 | 6736.34 | 914 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 822 | 0 | 820.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.21 | 87 | 0 | 44.2 | 172 | 0 | 171 | 0 | 170 | 0 | 392 | 0 | 4.94 | 168 | 46 | 35 | 28 | 34 | 0 | 0 | 0 | 7.8 | 203 | 0.83 | 0 | 177 | 115 | 180 | 0 | 304 | 648 | 0 | 5953.54 | 12689.88 | 107.38
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 3 | 0 | 95 | 0 | 0 | 0 | 55 | 30 | 0 | 300 | 299 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 50 | 26 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 4.25 | 215 | 0 | 3 | 580 | 0 | 0 | 2 | 0 | 0 | 214 | 0 | 0 | 0 | 920 | 16 | 43 | 0 | 45 | 0 | 344 | 320 | 48 | 200 | 38 | 68 | 50 | 146 | 8 | 12 | 31 | 42 | 8 | 62 | 0 | 315 | 255 | 386 | 0 | 30 | 157 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 65 | 55 | 142 | 3 | 46.84 | 6 | 6985.09 | 914 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 88 | 933 | 0 | 815.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.71 | 118 | 0 | 65.31 | 176 | 0 | 172 | 0 | 171 | 0 | 410 | 0 | 5.72 | 165 | 46 | 35 | 22 | 0 | 0 | 0 | 0 | 7.9 | 204 | 0.73 | 0 | 172 | 115 | 220 | 0 | 304 | 650 | 0 | 6254.51 | 13239.6 | 107.39
13:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 16 | 0 | 96 | 0 | 0 | 0 | 55 | 32 | 0 | 300 | 289 | 0 | 0 | 0 | 230 | 0 | 0 | 24 | 70 | 28 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 12 | 4.09 | 216 | 0 | 10 | 580 | 0 | 0 | 18 | 0 | 0 | 214 | 0 | 0 | 0 | 1035 | 19 | 43 | 0 | 45 | 0 | 341 | 330 | 46 | 203 | 38 | 69 | 70 | 150 | 8 | 15 | 31 | 44 | 8 | 74 | 0 | 315 | 255 | 383 | 0 | 30 | 155 | 8 | 0 | 82 | 30 | 0 | 0 | 159 | 0 | 80 | 70 | 131 | 2 | 54.39 | 6 | 7271.48 | 913 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 975 | 0 | 817.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1 | 115 | 0 | 27.58 | 186 | 0 | 191 | 0 | 171 | 0 | 406 | 0 | 2.18 | 165 | 46 | 70 | 36 | 0 | 0 | 0 | 0 | 7.9 | 199 | 0.67 | 0 | 172 | 115 | 220 | 0 | 304 | 735 | 0 | 6442.34 | 13713.82 | 107.4
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 15.5 | 0 | 96 | 0 | 0 | 0 | 55 | 31 | 0 | 300 | 303 | 0 | 0 | 0 | 230 | 0 | 0 | 28 | 70 | 27 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 3.24 | 216 | 0 | 8 | 518 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 1055 | 12 | 43 | 0 | 45 | 0 | 340 | 330 | 44 | 200 | 37 | 98 | 70 | 176 | 8 | 15 | 29 | 44 | 36 | 55 | 0 | 310 | 255 | 386 | 0 | 30 | 153 | 0 | 0 | 82 | 30 | 0 | 0 | 159 | 0 | 82 | 70 | 107 | 3 | 41.05 | 6 | 7243.79 | 914 | 366 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 99 | 1010 | 0 | 915.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 87 | 0 | 52.71 | 197 | 0 | 195 | 0 | 190 | 0 | 400 | 0 | 5.57 | 160 | 46 | 70 | 22 | 0 | 0 | 0 | 0 | 6.6 | 142 | 0.6 | 0 | 171 | 115 | 220 | 0 | 304 | 845 | 0 | 6587.45 | 13831.24 | 107.41
15:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 16.2 | 0 | 96 | 15 | 0 | 0 | 55 | 32 | 0 | 300 | 303 | 0 | 0 | 0 | 230 | 0 | 0 | 10 | 70 | 28 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 1.46 | 212 | 0 | 6 | 537 | 0 | 0 | 19 | 0 | 0 | 214 | 0 | 0 | 0 | 1125 | 9 | 43 | 0 | 45 | 0 | 331 | 330 | 45 | 206 | 37 | 105 | 70 | 181 | 8 | 19 | 35 | 46 | 48 | 36 | 0 | 315 | 255 | 379 | 0 | 30 | 153 | 8 | 0 | 82 | 30 | 0 | 0 | 159 | 0 | 72 | 95 | 107 | 1 | 26.18 | 6 | 7344.84 | 913 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 509 | 0 | 918.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.26 | 89 | 0 | 45.03 | 201 | 0 | 200 | 0 | 200 | 0 | 400 | 0 | 3.95 | 158 | 46 | 70 | 26 | 30 | 0 | 0 | 0 | 3.6 | 157 | 0.38 | 0 | 216 | 115 | 220 | 0 | 304 | 953 | 0 | 6282.57 | 13627.41 | 107.42
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 40 | 11 | 96 | 30 | 0 | 0 | 54 | 98 | 0 | 300 | 291 | 0 | 0 | 17 | 230 | 0 | 0 | 13 | 70 | 28 | 22 | 0 | 300 | 0 | 0 | 7 | 0 | 4 | 0 | 42 | 0 | 12 | 12 | 0.99 | 217 | 0 | 10 | 568 | 0 | 0 | 36 | 0 | 0 | 214 | 0 | 0 | 0 | 1105 | 8 | 43 | 15 | 70 | 0 | 341 | 330 | 45 | 193 | 37 | 107 | 70 | 187 | 10 | 19 | 61 | 44 | 52.2 | 36 | 0 | 320 | 255 | 376 | 0 | 30 | 153 | 13 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 90 | 95 | 121 | 1 | 15.08 | 6 | 7659.27 | 913 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 587 | 0 | 909.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.13 | 66 | 0 | 26.1 | 200 | 0 | 201 | 0 | 201 | 0 | 400 | 0 | 0.67 | 160 | 46 | 70 | 20 | 34 | 0 | 0 | 0 | 3 | 117 | 0.21 | 0 | 278 | 115 | 220 | 0 | 304 | 1110 | 0 | 6442 | 14101.27 | 107.43
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 45.2 | 17 | 96 | 30 | 0 | 0 | 53 | 99 | 0 | 300 | 288 | 0 | 0 | 17 | 230 | 0 | 0 | 5 | 70 | 28 | 22 | 0 | 300 | 0 | 0 | 30 | 0 | 2 | 0 | 77 | 0 | 12 | 12 | 0.27 | 217 | 0 | 21 | 605 | 0 | 0 | 40 | 0 | 0 | 215 | 0 | 0 | 0 | 1040 | 2 | 43 | 30 | 71 | 0 | 340 | 330 | 46 | 187 | 37 | 96 | 70 | 168 | 17 | 19 | 59 | 42 | 52.2 | 7 | 0 | 305 | 255 | 360 | 0 | 30 | 150 | 15 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 99 | 95 | 119 | 0 | 3.46 | 6 | 7583.13 | 913 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 596 | 0 | 911.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.96 | 38 | 0 | 6.02 | 188 | 0 | 188 | 0 | 188 | 0 | 390 | 0 | 0.76 | 160 | 46 | 70 | 9 | 34 | 0 | 0 | 0 | 2.92 | 62 | 0.11 | 0 | 274 | 115 | 220 | 0 | 304 | 1010 | 0 | 6161.89 | 13745.02 | 107.44
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 43.8 | 17 | 96 | 30 | 0 | 0 | 55 | 93 | 1 | 300 | 293 | 0 | 0 | 17 | 230 | 0 | 0 | 1 | 70 | 28 | 22 | 0 | 300 | 0 | 0 | 34 | 0 | 0 | 0 | 76 | 0 | 12 | 12 | 0.01 | 216 | 0 | 20 | 610 | 0 | 0 | 40 | 0 | 0 | 215 | 0 | 0 | 0 | 948 | 0 | 43 | 30 | 76 | 0 | 300 | 280 | 46 | 191 | 37 | 95 | 70 | 162 | 16 | 19 | 60 | 42 | 52.2 | 4 | 0 | 310 | 255 | 315 | 0 | 50 | 135 | 14 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 99 | 95 | 118 | 0 | 0.96 | 6 | 7352.97 | 913 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 791 | 0 | 912.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 6 | 0 | 0.64 | 172 | 0 | 173 | 0 | 175 | 0 | 350 | 0 | 0.1 | 159 | 46 | 70 | 2 | 36 | 0 | 0 | 0 | 0.3 | 12 | 0.03 | 0 | 229 | 115 | 180 | 0 | 304 | 900 | 0 | 5893.7 | 13246.67 | 107.45
19:00 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 47.8 | 26 | 99 | 93 | 180 | 4 | 55 | 140 | 15 | 300 | 298 | 0 | 0 | 55 | 230 | 0 | 0 | 0 | 125 | 28 | 22 | 0 | 300 | 0 | 0 | 34 | 0 | 0 | 49 | 77 | 0 | 12 | 12 | 0 | 218 | 1 | 24 | 730 | 17 | 0 | 40 | 3 | 3 | 217 | 0 | 0 | 0 | 1045 | 0 | 43 | 60 | 71 | 0 | 337 | 330 | 46 | 198 | 38 | 105 | 70 | 180 | 16 | 19 | 103 | 50 | 52.2 | 0 | 0 | 320 | 255 | 383 | 0 | 50 | 143 | 14 | 0 | 83 | 30 | 0 | 0 | 160 | 14 | 99 | 105 | 118 | 0 | 0 | 6 | 8436 | 913 | 346 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 968 | 10 | 1141.76 | 0 | 2 | 0 | 7 | 0 | 0 | 83 | 13 | 0 | 0 | 0 | 20 | 0 | 182 | 0 | 185 | 0 | 186 | 0 | 406 | 0 | 0 | 160 | 45 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 304 | 928 | 0 | 6770.76 | 15206.76 | 107.46
19:30 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 44 | 54 | 130 | 125 | 235 | 55 | 55 | 138 | 16 | 300 | 286 | 0 | 0 | 55 | 230 | 0 | 0 | 0 | 125 | 28 | 22 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 49 | 77 | 0 | 12 | 12 | 0 | 218 | 8 | 25 | 770 | 17 | 0 | 20 | 17 | 13 | 217 | 0 | 0 | 0 | 1075 | 0 | 43 | 115 | 71 | 0 | 339 | 320 | 46 | 178 | 37 | 115 | 70 | 200 | 16 | 19 | 114 | 46 | 52.2 | 0 | 0 | 305 | 250 | 350 | 0 | 50 | 147 | 14 | 0 | 83 | 30 | 0 | 0 | 160 | 35 | 99 | 145 | 120 | 0 | 0 | 6 | 8761.2 | 914 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1064 | 34 | 1310.96 | 0 | 38 | 0 | 35 | 35 | 0 | 86 | 23 | 0 | 0 | 0 | 20 | 0 | 178 | 0 | 189 | 0 | 189 | 0 | 338 | 0 | 0 | 161 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 115 | 180 | 0 | 303 | 1050 | 0 | 7189.96 | 15951.16
20:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 44.9 | 35 | 138 | 93 | 145 | 15 | 47 | 116 | 15 | 300 | 297 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 125 | 28.3 | 22 | 0 | 300 | 0 | 0 | 70 | 0 | 2 | 49 | 77 | 0 | 12 | 12 | 0 | 218 | 28 | 13 | 770 | 0 | 0 | 20 | 17 | 34 | 218 | 0 | 0 | 0 | 1115 | 0 | 43 | 70 | 71 | 0 | 300 | 300 | 47 | 191 | 37 | 106 | 70 | 186 | 16 | 19 | 114 | 44 | 52.2 | 0 | 0 | 290 | 255 | 316 | 0 | 50 | 138 | 14 | 0 | 83 | 30 | 0 | 0 | 160 | 35 | 99 | 130 | 120 | 0 | 0 | 6 | 8432.4 | 913 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 35 | 1405.99 | 0 | 48 | 0 | 35 | 28 | 0 | 86 | 38 | 0 | 0 | 0 | 20 | 0 | 170 | 0 | 177 | 0 | 178 | 0 | 300 | 0 | 0 | 159 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 180 | 0 | 304 | 1070 | 0 | 7257.99 | 15690.39 | 107.47
21:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 46.7 | 35 | 131 | 93 | 45 | 15 | 27 | 115 | 0 | 300 | 294 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 125 | 28.5 | 22 | 0 | 300 | 0 | 0 | 90 | 0 | 2 | 41 | 77 | 0 | 12 | 12 | 0 | 218 | 15 | 31 | 770 | 0 | 0 | 19 | 17 | 17 | 219 | 0 | 0 | 0 | 1120 | 0 | 43 | 18 | 71 | 0 | 346 | 330 | 47 | 184 | 37 | 115 | 70 | 200 | 16 | 19 | 114 | 48 | 52.2 | 0 | 0 | 310 | 250 | 350 | 0 | 50 | 145 | 14 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 99 | 140 | 120 | 0 | 0 | 1 | 8380.4 | 913 | 345 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1138 | 35 | 1454.27 | 0 | 41 | 0 | 35 | 35 | 0 | 86 | 38 | 0 | 0 | 0 | 20 | 0 | 185 | 0 | 180 | 0 | 178 | 0 | 389 | 0 | 0 | 158 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 303 | 1100 | 0 | 7551.27 | 15931.67 | 107.48
22:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 36.3 | 17 | 131 | 93 | 0 | 0 | 17 | 111 | 0 | 300 | 300 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 125 | 28.5 | 22 | 0 | 300 | 0 | 0 | 90 | 0 | 3 | 49 | 76 | 0 | 12 | 12 | 0 | 218 | 14 | 34 | 770 | 0 | 0 | 19 | 17 | 15 | 219 | 0 | 0 | 0 | 1150 | 0 | 43 | 12 | 71 | 0 | 344 | 330 | 48 | 195 | 37 | 103 | 70 | 199 | 16 | 19 | 114 | 50 | 52.2 | 0 | 0 | 310 | 250 | 385 | 0 | 50 | 151 | 14 | 0 | 84 | 30 | 0 | 0 | 161 | 0 | 99 | 149 | 114 | 0 | 0 | 0 | 8336 | 913 | 345 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 17 | 1447 | 0 | 41 | 0 | 35 | 35 | 0 | 86 | 38 | 0 | 0 | 0 | 20 | 0 | 200 | 0 | 188 | 0 | 188 | 0 | 414 | 0 | 0 | 160 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 303 | 1092 | 0 | 7502 | 15838 | 107.49
23:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 30.9 | 17 | 131 | 93 | 0 | 0 | 17 | 116 | 0 | 300 | 307 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 300 | 0 | 0 | 94 | 0 | 1 | 49 | 76 | 0 | 12 | 12 | 0 | 218 | 15 | 35 | 772 | 0 | 0 | 19 | 17 | 15 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 12 | 71 | 0 | 340 | 330 | 47 | 205 | 37 | 96 | 70 | 199 | 16 | 19 | 114 | 52 | 52.2 | 0 | 0 | 315 | 240 | 396 | 0 | 50 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 99 | 150 | 115 | 0 | 0 | 0 | 8396.6 | 914 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 17 | 1441.46 | 0 | 41 | 0 | 35 | 35 | 0 | 86 | 38 | 0 | 0 | 0 | 20 | 0 | 194 | 0 | 194 | 0 | 195 | 0 | 414 | 0 | 0 | 162 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 220 | 0 | 303 | 1110 | 0 | 7546.46 | 15943.06 | 107.5
Total KWH | 0 | 1166400 | 325920 | 0 | 0 | 0 | 0 | 0 | 8132400 | 0 | 0 | 430560 | 221040 | 2216448 | 614400 | 364320 | 67074 | 754884 | 1094400 | 32640 | 8272500 | 7068945 | 0 | 0 | 150118 | 6354903 | 0 | 0 | 162908 | 1950000 | 559200 | 522000 | 0 | 6697272.73 | 0 | 0 | 549120 | 0 | 48000 | 435598 | 699068 | 0 | 296640 | 296640 | 27598 | 5216756 | 112900 | 572160 | 16181818.18 | 13382 | 0 | 342720 | 95418 | 107891 | 5020385 | 0 | 0 | 0 | 23563634 | 112860 | 1004530 | 349600 | 1689455 | 0 | 8447900 | 7724000 | 1145760 | 4782000 | 887112 | 2140800 | 1497690 | 4319520 | 191520 | 426180 | 1813740 | 1025280 | 803232 | 524609 | 0 | 7602500 | 5741900 | 8898000 | 0 | 1162080 | 3466309 | 226200 | 0 | 1980480 | 715488 | 0 | 0 | 3396850 | 99000 | 2013600 | 2265600 | 3159360 | 13200 | 292160 | 125040 | 180781615.91 | 21669090 | 8615808 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 776880 | 21345455 | 123360 | 24321091 | 0 | 207255 | 0 | 183552 | 178464 | 0 | 456720 | 171693 | 0 | 294463 | 847600 | 113789 | 341248 | 4374182 | 0 | 4553136 | 0 | 4524273 | 0 | 8989236 | 0 | 29400 | 4017000 | 1053818 | 1771496 | 233476 | 1659062 | 0 | 0 | 0 | 50245.44 | 1474560 | 5026 | 0 | 5127000 | 2762000 | 5177410 | 0 | 7301818 | 23112727 | 0 | 156774333.44 | 337555949.35

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-08-2025 | during | 17-08-2025 | during | 17-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 342 | 305 | 400.75 | 400.75 | 370.8 | 370.8 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 286 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 230 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 102 | 7 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 3 | 44 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 235 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 130 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 30 | 138 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 35 | 35 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 50 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 1802 | 2606 | 5807.7 | 5874.7 | 3888.83 | 3955.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 215 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 215 | 219 | 215 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 13 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 77 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 50 | 50 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 25 | 2 | 24 | 2 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.25 | 0 | 1.64 | 0 | 1.64 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 8 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 920 | 1075 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 10 | 28 | 10 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 580 | 770 | 770 | 770 | 760 | 760 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1978.25 | 2580 | 3773.36 | 3825.72 | 3616.36 | 3668.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 178 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 339 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 320 | 320 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 37 | 46.7 | 46.7 | 42 | 42 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 46 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 71 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 115 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 146 | 200 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 31 | 114 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 16 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 68 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1465 | 1781.2 | 2444.56 | 2379.56 | 2233.36 | 2168.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-08-2025 | during | 17-08-2025 | during | 17-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 142 | 120 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 145 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 99 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.84 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 34 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 317.84 | 405 | 592 | 549 | 529.5 | 503.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 50 | 60 | 60 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 83 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 14 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 350 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 255 | 250 | 260 | 260 | 260 | 260 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1422 | 1389 | 1527 | 1527 | 1414 | 1414
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 914 | 914 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 362 | 350 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 933 | 1064 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2335 | 2400 | 3647.2 | 3552.2 | 3522 | 3427
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 304 | 303 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 1050 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 266 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1461.73 | 1914 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 44.71 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 42 | 42 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 178 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 189 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 189 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 338 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.72 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 815.14 | 1310.96 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.31 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 118 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1977.88 | 2441.96 | 2485.69 | 2333.99 | 2383.31 | 2231.61
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 45 | 48 | 48 | 45 | 45 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 161 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 171.96 | 0 | 171.96 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 479.9 | 434 | 668.56 | 460 | 675.56 | 467
System Total |  |  |  |  | 28671.2 | 27843.665 | 13239.6 | 15951.16 | 23108.07 | 22663.17 | 20409.92 | 19982.02
Forecast Scenario (17-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15880 |  | 0 |  | 15880
|  |  |  | 1:00 | 15240 |  | 0 |  | 15240
|  |  |  | 2:00 | 14870 |  | 0 |  | 14870
|  |  |  | 3:00 | 14570 |  | 0 |  | 14570
|  |  |  | 4:00 | 14300 |  | 0 |  | 14300
|  |  |  | 5:00 | 14030 |  | 0 |  | 14030
|  |  |  | 6:00 | 13660 |  | 0 |  | 13660
|  |  |  | 7:00 | 13560 |  | 0 |  | 13560
|  |  |  | 8:00 | 13460 |  | 0 |  | 13460
|  |  |  | 9:00 | 13620 |  | 0 |  | 13620
|  |  |  | 10:00 | 13790 |  | 0 |  | 13790
|  |  |  | 11:00 | 13940 |  | 0 |  | 13940
|  |  |  | 12:00 | 14270 |  | 0 |  | 14270
|  |  |  | 13:00 | 14570 |  | 0 |  | 14570
|  |  |  | 14:00 | 14640 |  | 0 |  | 14640
|  |  |  | 15:00 | 14500 |  | 0 |  | 14500
|  |  |  | 16:00 | 14510 |  | 0 |  | 14510
|  |  |  | 17:00 | 14040 |  | 0 |  | 14040
|  |  |  | 18:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15550 |  | 0 |  | 15550
|  |  |  | 19:30 | 16050 |  | 0 |  | 16050
|  |  |  | 20:00 | 16200 |  | 0 |  | 16200
|  |  |  | 21:00 | 16010 |  | 0 |  | 16010
|  |  |  | 22:00 | 15970 |  | 0 |  | 15970
|  |  |  | 23:00 | 16100 |  | 0 |  | 16100
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 14270.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 351.01 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:29 hrs on 17-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13239.6 | MW | 12:00 Hr. | Energy Generated |  |  | 337.5559 |  | MKWHr.
| Day Peak Demand |  |  | 13239.6 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.406 |  | MKWHr.
| Evening Peak Generation |  |  | 15951.16 | MW | 19:30 Hr. | Energy Demand |  |  | 337.9619 |  | MKWHr.
| Evening Peak Demand |  |  | 16046.16 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 12519.72 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1060.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 15951.16 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0066 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.6072 | 0 | 9.3882 | 0 | 0 | 0.16291 | 0 | 0 | 47.1583 | Gas | 146.1496 | Gas | 521589224.1741
| Chattogram Zone |  |  | 5.5925 | 39.7455 | 2.9494 | 0 | 5.2168 | 0.14046 | 0 | 0.048 | 53.6926 | Coal | 101.7033 | Coal | 608532242.6608
| Cumilla Zone |  |  | 27.6046 | 0 | 9.6184 | 0 | 0 | 0.52461 | 1.0253 | 0 | 38.7729 | HFO | 31.3246 | HFO | 578636674.85
| Mymensingh Zone |  |  | 3.1594 | 0 | 4.5032 | 0 | 0 | 0.30536 | 0 | 0 | 7.968 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1898 | Hydro | 5.2168 | Hydro | 521675.6
| Khulna Zone |  |  | 8.6158 | 21.3455 | 0.12336 | 0 | 0 | 0.77688 | 22.5811 | 0 | 53.4426 | Solar | 5.1862 | Solar | 79582171.9784
| Barishal Zone |  |  | 7.9394 | 35.5415 | 0 | 0 | 0 | 0.005026 | 0 | 0 | 43.486 | Import | 47.9275 | Import | 237988001.39
| Rajshahi Zone |  |  | 22.4408 | 0 | 1.3115 | 0 | 0 | 1.5127 | 24.3211 | 0 | 49.5861 | Wind | 0.048 | Wind | 702720
| Rangpur Zone |  |  | 0 | 5.0708 | 3.4306 | 0 | 0 | 1.7583 | 0 | 0 | 10.2597
| Total |  |  | 146.1496 | 101.7033 | 31.3246 | 0 | 5.2168 | 5.1862 | 47.9275 | 0.048 | 337.5559
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 521589224.1741 |  | Hydro | 521675.6
|  |  |  | Coal | 608532242.6608 |  | Solar | 79582171.9784
|  |  |  | HFO | 578636674.85 |  | Import | 237988001.39
|  |  |  | HSD | 0 |  | Wind | 702720
[5 empty] | Total: | 202,75,52,710 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6691 | Peak Hr Flow | 914.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35413836.46 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.3211 | Peak Hr Flow | 1310.96 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 748 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0253 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 984 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.0155 | Peak Hr Flow | 2270.96 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5445
|  |  |  | Chattogram |  | 0 |  | 1542
|  |  |  | Cumilla |  | 10 |  | 1395
|  |  |  | Mymensingh |  | 21 |  | 1313
|  |  |  | Sylhet |  | 0 |  | 698
|  |  |  | Khulna |  | 0 |  | 1927
|  |  |  | Barishal |  | 0 |  | 484
|  |  |  | Rajshahi |  | 0 |  | 1644
|  |  |  | Rangpur |  | 60 |  | 1040
|  |  |  | Total |  | 91 |  | 15488
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 |  | Md. Mizanur Rahman, Supervisor, G4S Md. Shopon Ali, S. Guard, PGCB Bulbul Ahmmed,
OA, PGCB
| 08:16 | 16:34 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Shutdown taken by Khulna PBS due to
replace bus raiser and loop conductor.
| 08:17 | 16:33 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Shutdown taken by Khulna PBS due to
replace bus raiser and loop conductor.
| 08:41 | 10:53 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to 33 kv bus section-4 DS
redhot problem.
| 08:41 | 10:53 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to 33 kv bus section-4 DS
redhot problem.
| 08:46 | 14:20 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to loop change of T-1 and T-2
Transformer.
| 08:52 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO turned off at 07:14
| 09:01 | 12:10 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to loop change of T-2 Transformer.
| 09:01 | 11:58 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to loop change of T-2 Transformer.
|  | 10:15 | Fenchuganj 230/132/33kV S/S TR-01 HT is restored.
|  | 10:31 | Fenchuganj 230/132/33kV S/S AT-02 LT is restored.
|  | 10:54 | BIPTC S/S Baharampur-4 is restored.
| 11:11 | 14:50 | Ghorashal 230kV S/S TARFO-2 LT Scheduled S/D Due to 33kv CT, PT junction point | [7 empty] | 55.0MW load
|  |  | tightening. | [7 empty] | interrup.
| 11:12 | 14:48 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to 33 kv CT, PT junction point | [7 empty] | 55.0MW load
|  |  | tightening. | [7 empty] | interrup.
| 11:24 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:-
| 11:49 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:-
| 12:15 | 14:10 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Loop change
| 12:18 | 14:09 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Loop change
| 14:41 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U2
| 14:42 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U-1 Runnings
| 14:42 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U-1 Running
| 17:14 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
|  | 17:44 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT is restored.
|  | 17:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
| 18:29 |  | Raozan 25 MW PP Synchronized
| 19:30 |  | Evening peak Generation is 15950 MW
| 01:14 |  | Raozan 25 MW PP Shutdown
| 03:59 |  | Adani U-1 FSD Due to PA fan probleblem
| 07:00 |  | minimum generation 13615 MW
| 07:26 | 07:50 | Keranigonj 230/132/33kV S/S TR-2 LT Tripped showing 86.1 Trip Relay Operated relays Due | [7 empty] | 36.0MW load
|  |  | to Due to PBS 33kV feeder fault. | [7 empty] | interrup.
| 07:26 | 07:50 | Keranigonj 230/132/33kV S/S TR-2 LT Tripped showing 86.1 Trip Relay Operated relays Due | [7 empty] | 36.0MW load
|  |  | to Due to PBS 33kV feeder fault. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 305 | 8132400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8272500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 7068945 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 67074 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 230 | 6354903 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 430560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 614400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 754884 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 150118 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 28 | 559200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 325920 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 235 | 364320 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 130 | 2216448 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1166400 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 32640 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 138 | 1094400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 162908 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 221040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 6697272.73 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1950000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2606 | 47158332.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 95418 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112860 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 342720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5216756 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5020385 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 13 | 107891 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 77 | 699068 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 435598 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 296640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 572160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 549120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27598 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 8 | 112900 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 296640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 13382 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1075 | 23563634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 48000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 770 | 16181818.18 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2580 | 53692588.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 178 | 4782000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 339 | 8447900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 320 | 7724000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 887112 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1145760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 71 | 1689455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1004530 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 349600 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1497690 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4319520 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1025280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 803232 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 426180 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1813740 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 16 | 191520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2140800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 524609 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1781.2 | 38772928
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 120 | 3159360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 145 | 2265600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 2013600 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 292160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 125040 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 99000 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 405 | 7967960
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 1162080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3466309 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715488 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1980480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3396850 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 14 | 226200 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7602500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8898000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 250 | 5741900 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2325 | 1389 | 33189807
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 914 | 21669090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 350 | 8615808 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 123360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 776880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1064 | 21345455 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2400 | 53442593
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 303 | 7301818 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2762000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 23112727 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5177410 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 266 | 5127000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5026 | -
Barishal Area Total |  |  |  |  | 2236 | 1914 | 43485981
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 294463 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 207255 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 171693 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 4374182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4553136 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 189 | 4524273 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 338 | 8989236 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 113789 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 456720 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 178464 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 183552 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1310.96 | 24321091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 341248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 847600 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2441.96 | 49586102
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1053818 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 4017000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1659062 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50245.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1771496 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 233476 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1474560 | -
Rangpur Area Total |  |  |  |  | 950 | 434 | 10259657.44
Eastern Grid Total |  |  |  |  | 17401.505 | 8761.2 | 180781615.91
Western Grid Total |  |  |  |  | 10442.16 | 7189.96 | 156774333.44
National Grid Total |  |  |  |  | 27843.665 | 15951.16 | 337555949.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10362.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5035.3 | MW
i) Dhaka area |  |  | 5445.4 |  | MW | i) Khulna area |  |  |  | 1927 | MW
ii) Chattogram area |  |  | 1542.5 |  | MW | ii) Barishal area |  |  |  | 484.5 | MW
iii) Cumilla area |  |  | 1384.52 |  | MW | iii) Rajshahi area |  |  |  | 1643.8 | MW
iv) Mymensingh area |  |  | 1292 |  | MW | iv) Rangpur area |  |  |  | 980 | MW
v) Sylhet area |  |  | 698 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15397.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 86 | 20:00 | 133 | PHP | 9 | 10:00
2 | AKSML | 123 | 05:00 | 68 | Ishurdi | 89 | 19:30 | 134 | Pabna | 138 | 19:30
3 | Aftabnagar | 40 | 22:00 | 69 | Jaldhaka | 94 | 19:00 | 135 | Palashbari | 112 | 19:30
4 | Agargaon | 129 | 23:00 | 70 | Jamalpur | 139 | 21:00 | 136 | Panchagarh | 68 | 20:00
5 | Agrabad | 92 | 19:00 | 71 | Jashore | 146 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 28 | 00:00 | 72 | Jhenaidah | 136 | 19:30 | 138 | Patuakhali | 74 | 23:00
7 | Ashuganj | 83 | 00:00 | 73 | Joydebpur | 161 | 19:00 | 139 | Payra | 36 | 00:00
8 | BSRM | 198 | 07:00 | 74 | Joypurhat | 67 | 23:00 | 140 | Postogola | 59 | 23:00
9 | Bagerhat | 86 | 20:00 | 75 | Juldah | 17 | 13:00 | 141 | Purbachal | 24 | 23:00
10 | Bajitpur | 95 | 19:30 | 76 | KSRM | 26 | 15:00 | 142 | Purbasadipur | 132 | 00:00
11 | Bakulia | 90 | 14:00 | 77 | Kabirpur | 249 | 12:00 | 143 | Rahanpur | 45 | 22:00
12 | Banani | 37.6 | 13:00 | 78 | Kachua | 96 | 22:00 | 144 | Rahim | 25 | 07:00
13 | Bangabhaban | 6 | 11:00 | 79 | Kallyanpur | 111 | 22:00 | 145 | Rajbari | 88 | 19:00
14 | Barapukuria | 82 | 21:00 | 80 | Kalurghat | 36 | 10:00 | 146 | Rajendrapur | 145 | 21:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 80 | 13:00 | 147 | Rajshahi | 144 | 22:00
16 | Barishal | 117 | 23:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 83 | 21:00
17 | Barishal-230 | 106 | 21:00 | 83 | Kasba | 39 | 22:00 | 149 | Ramganj | 120 | 21:00
18 | Baroaulia | 68 | 14:00 | 84 | Kazla | 116 | 13:00 | 150 | Rampur | 41 | 23:00
19 | Baroirhat | 65 | 19:30 | 85 | Keranigonj | 98 | 19:00 | 151 | Rangamati | 17 | 18:30
20 | Bashundhara | 197 | 19:00 | 86 | Khagrachori | 30 | 18:00 | 152 | Rangpur | 145 | 14:00
21 | BashundharaCement | 9 | 17:00 | 87 | Khulna | 71 | 19:30 | 153 | Ruppur | 5.6 | 11:00
22 | Beanibazar | 88 | 19:00 | 88 | Khulshi | 180 | 17:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 68 | 19:30 | 89 | Kishoreganj | 146 | 21:00 | 155 | Saidpur | 108 | 14:00
24 | Bhaluka | 161 | 19:00 | 90 | Kodda | 296 | 19:00 | 156 | Satkhira | 136 | 19:30
25 | Bhandaria | 59 | 22:00 | 91 | Kulaura | 57 | 20:00 | 157 | Satmasjid | 101 | 20:00
26 | Bhangura | 41 | 19:00 | 92 | Kurigram | 74 | 19:00 | 158 | Savar | 215 | 15:00
27 | Bheramara(GK) | 73 | 19:00 | 93 | Kushtia | 165 | 19:00 | 159 | SevenRings | 15.74 | 01:00
28 | Bhulta | 199 | 22:00 | 94 | Laksam | 40 | 06:00 | 160 | ShahCement | 25 | 08:00
29 | Bog-Sherpur | 80 | 23:00 | 95 | Lakshmipur | 25 | 11:00 | 161 | Shahjadpur | 92 | 20:00
30 | Bogura | 179 | 19:30 | 96 | Lalbag | 54 | 18:00 | 162 | Shahjibazar | 135 | 21:00
31 | Borhanuddin | 93 | 19:00 | 97 | Lalmonirhat | 73 | 19:00 | 163 | Shahmirpur | 60 | 16:00
32 | Brahmanbaria | 141 | 22:00 | 98 | MI_Cement | 15.4 | 15:00 | 164 | Shariatpur | 97 | 22:00
33 | Cantonment | 140 | 19:00 | 99 | Madanganj | 36 | 23:00 | 165 | Sherpur | 174 | 22:00
34 | Chandina | 18.15 | 22:00 | 100 | Madaripur | 126 | 23:00 | 166 | Shikalbaha | 14 | 15:00
35 | Chandpur | 83 | 19:30 | 101 | Madartek | 80.37 | 00:00 | 167 | Shitalakhya | 85.1 | 16:00
36 | Chandraghona | 36 | 20:00 | 102 | Madunaghat | 58 | 19:00 | 168 | Sholosohor | 46 | 16:00
37 | Chapai | 75 | 23:00 | 103 | Magura | 70 | 19:30 | 169 | Shyampur | 150 | 23:00
38 | Charsaidpur | 32 | 11:00 | 104 | Mahasthangarh | 98 | 23:00 | 170 | Siddhirganj | 113 | 16:00
39 | Chauddagram | 75 | 19:00 | 105 | Maijdee | 14 | 04:00 | 171 | Sirajganj | 120 | 19:30
40 | Chhatak | 44 | 00:00 | 106 | Manikganj | 130 | 19:30 | 172 | Sonargaon | 136 | 20:00
41 | Chowmuhani | 181 | 23:00 | 107 | Maniknagar | 68 | 23:00 | 173 | Sreemongol | 92 | 19:30
42 | Chuadanga | 134 | 19:00 | 108 | Matarbari | 53 | 19:30 | 174 | Sreepur | 102 | 19:00
43 | Coxsbazar | 136 | 00:00 | 109 | Matuail | 62 | 23:00 | 175 | Srinagar | 50.26 | 21:00
44 | Cumilla(N) | 147 | 00:00 | 110 | Millgate | 126 | 12:00 | 176 | Sunamganj | 66 | 21:00
45 | Cumilla(S) | 155 | 15:00 | 111 | Mirpur | 128 | 19:00 | 177 | Sylhet | 52 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 09:00 | 178 | Sylhet-132 | 150 | 20:00
47 | Daudkandi | 144 | 20:00 | 113 | Mirzapur | 55 | 21:00 | 179 | TK | 36 | 18:30
48 | Dhaka | 58 | 13:00 | 114 | Mithapukur | 72 | 19:00 | 180 | Tangail | 190 | 19:00
49 | Dhamrai | 132 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:00
50 | Dhanmondi | 130 | 13:00 | 116 | Mogbazar | 113.6 | 15:00 | 182 | Thakurgaon | 122 | 22:00
51 | Dohazari | 111 | 19:30 | 117 | Mongla | 37 | 13:00 | 183 | Tongi | 106 | 15:00
52 | Faridpur | 173 | 21:00 | 118 | Motijheel | 41 | 13:00 | 184 | Ullahpara | 41 | 19:30
53 | Fatullah | 104 | 15:00 | 119 | Muktagacha | 41 | 19:30 | 185 | Ullon | 60 | 23:00
54 | Fenchuganj | 47 | 20:00 | 120 | Munshiganj | 120 | 00:00 | 186 | Uttara | 81 | 19:00
55 | Feni | 128 | 21:00 | 121 | Muradnagar | 44 | 22:00 | 187 | UttaraNew | 67 | 22:00
56 | GPH | 90 | 22:00 | 122 | Mymensingh | 220 | 20:00 | 188 | Zigatola | 76 | 20:00
57 | Ghatail | 88 | 22:00 | 123 | Naogaon | 143 | 22:00
58 | Ghorashal | 16 | 10:00 | 124 | Narail | 64.5 | 20:00
59 | Ghorashal-230 | 86 | 21:00 | 125 | Narinda | 68 | 13:00
60 | Goalpara | 42 | 23:00 | 126 | Narshingdi | 195 | 23:00
61 | Gollamari | 98 | 19:00 | 127 | Natore | 159 | 23:00
62 | Gopalganj | 114 | 21:00 | 128 | Nawabganj | 90.8 | 21:00
63 | Gulshan | 98 | 15:00 | 129 | Netrakona | 140 | 00:00
64 | Halishahar | 64 | 14:00 | 130 | New | 63.6 | 19:00
65 | HaripurSBU | 140 | 00:00 | 131 | Niamatpur | 80 | 22:00
66 | Hasnabad | 77 | 22:00 | 132 | Noapara | 50 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14867.7 | 39 |  | 14908.46
1:00 | 14559.2 | 0 |  | 14559.2
2:00 | 14052.2 | 0 |  | 14052.2
3:00 | 13670 | 0 |  | 13670
4:00 | 13393 | 0 |  | 13393
5:00 | 13131 | 0 |  | 13131
6:00 | 12715.58 | 0 |  | 12715.58
7:00 | 12569.22 | 0 |  | 12569.22
8:00 | 12519.72 | 0 |  | 12519.72
9:00 | 12735.63 | 0 |  | 12735.63
10:00 | 12572.81 | 0 |  | 12572.81
11:00 | 12689.88 | 0 |  | 12689.88
12:00 | 13239.6 | 0 |  | 13239.6
13:00 | 13713.82 | 0 |  | 13713.82
14:00 | 13831.24 | 0 |  | 13831.24
15:00 | 13627.41 | 0 |  | 13627.41
16:00 | 14101.27 | 0 |  | 14101.27
17:00 | 13745.02 | 0 |  | 13745.02
18:00 | 13246.67 | 0 |  | 13246.67
19:00 | 15206.76 | 0 |  | 15206.76
19:30 | 15951.16 | 91 |  | 16046.16
20:00 | 15690.39 | 88 |  | 15782.39
21:00 | 15931.67 | 86 |  | 16021.67
22:00 | 15838 | 98 |  | 15940.41
23:00 | 15943.06 | 95 |  | 16042.34
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7776.7 | 7091 | 14867.7 | DAILY GENERATION CURVE
00:30 | 7699.45 | 7014 | 14713.45
01:00 | 7622.2 | 6937 | 14559.2 | 16-08-2025
01:30 | 7504.2 | 6801.5 | 14305.7
02:00 | 7386.2 | 6666 | 14052.2
02:30 | 7309.6 | 6551.5 | 13861.1
03:00 | 7233 | 6437 | 13670
03:30 | 7201 | 6330.5 | 13531.5
04:00 | 7169 | 6224 | 13393
04:30 | 7144 | 6118 | 13262
05:00 | 7119 | 6012 | 13131
05:30 | 7042.585 | 5880.705 | 12923.29
06:00 | 6966.17 | 5749.41 | 12715.58
06:30 | 6907.61 | 5734.79 | 12642.4
07:00 | 6849.05 | 5720.17 | 12569.22
07:30 | 6808.81 | 5735.66 | 12544.47
08:00 | 6768.57 | 5751.15 | 12519.72
08:30 | 6831.145 | 5796.53 | 12627.675
09:00 | 6893.72 | 5841.91 | 12735.63
09:30 | 6844.52 | 5809.7 | 12654.22
10:00 | 6795.32 | 5777.49 | 12572.81
10:30 | 6765.83 | 5865.515 | 12631.345
11:00 | 6736.34 | 5953.54 | 12689.88
11:30 | 6860.715 | 6104.025 | 12964.74
12:00 | 6985.09 | 6254.51 | 13239.6
12:30 | 7128.285 | 6348.425 | 13476.71
13:00 | 7271.48 | 6442.34 | 13713.82
13:30 | 7257.635 | 6514.895 | 13772.53
14:00 | 7243.79 | 6587.45 | 13831.24
14:30 | 7294.315 | 6435.01 | 13729.325
15:00 | 7344.84 | 6282.57 | 13627.41
15:30 | 7502.055 | 6362.285 | 13864.34
16:00 | 7659.27 | 6442 | 14101.27
16:30 | 7621.2 | 6301.945 | 13923.145
17:00 | 7583.13 | 6161.89 | 13745.02
17:30 | 7468.05 | 6027.795 | 13495.845
18:00 | 7352.97 | 5893.7 | 13246.67
18:30 | 7894.485 | 6332.23 | 14226.715
19:00 | 8436 | 6770.76 | 15206.76
19:30 | 8761.2 | 7189.96 | 15951.16
20:00 | 8432.4 | 7257.99 | 15690.39
20:30 | 8406.4 | 7404.63 | 15811.03 |  | Executive Engineer
21:00 | 8380.4 | 7551.27 | 15931.67 |  | Network Operation Division
21:30 | 8358.2 | 7526.635 | 15884.835
22:00 | 8336 | 7502 | 15838
22:30 | 8366.3 | 7524.23 | 15890.53
23:00 | 8396.6 | 7546.46 | 15943.06

## En-Curve
QF-LDC-12
Date | 16-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4380 | 1915 | 898 | 38 | 50 | 1223 | 219 | 4788 | 0 | 347 | 1008.7 | 0 | 0 | 1 | 39 | DAILY ENERGY CURVE
00:30 | 4309.5 | 1918.5 | 900.5 | 38 | 48 | 1219.5 | 218.5 | 4761 | 0 | 306.5 | 992.95 | 0 | 0 | 0.5 | 19.5 | 16-08-2025
01:00 | 4239 | 1922 | 903 | 38 | 46 | 1216 | 218 | 4734 | 0 | 266 | 977.2 | 0 | 0 | 0 | 0
01:30 | 4187.5 | 1917 | 903 | 38 | 45 | 1215 | 218 | 4588 | 0 | 224.5 | 969.7 | 0 | 0 | 0 | 0 | Energy Generated | 337.5559 |  | MKWHr
02:00 | 4136 | 1912 | 903 | 38 | 44 | 1214 | 218 | 4442 | 0 | 183 | 962.2 | 0 | 0 | 0 | 0 | Energy not Served | 0.406 |  | MKWHr
02:30 | 4153.5 | 1885.5 | 903.5 | 38 | 44 | 1165 | 218 | 4372.5 | 0 | 173 | 908.1 | 0 | 0 | 0 | 0 | Total Energy Requirement | 337.9619 |  | MKWHr
03:00 | 4171 | 1859 | 904 | 38 | 44 | 1116 | 218 | 4303 | 0 | 163 | 854 | 0 | 0 | 0 | 0
03:30 | 4185.5 | 1877 | 903.5 | 38 | 43 | 1070 | 218 | 4222 | 0 | 141.5 | 833 | 0 | 0 | 0 | 0
04:00 | 4200 | 1895 | 903 | 38 | 42 | 1024 | 218 | 4141 | 0 | 120 | 812 | 0 | 0 | 0 | 0
04:30 | 4224.5 | 1880 | 903 | 38 | 42 | 976 | 218 | 4067 | 0 | 117 | 796.5 | 0 | 0 | 0 | 0
05:00 | 4249 | 1865 | 903 | 38 | 42 | 928 | 218 | 3993 | 0 | 114 | 781 | 0 | 0 | 0 | 0
05:30 | 4180 | 1877.5 | 903 | 38 | 41 | 900.5 | 215.5 | 3919 | 7.29 | 95 | 745 | 0 | 0 | 1.5 | 0
06:00 | 4111 | 1890 | 903 | 38 | 40 | 873 | 213 | 3845 | 14.58 | 76 | 709 | 0 | 0 | 3 | 0
06:30 | 4061.5 | 1917.5 | 903 | 38 | 38 | 848.5 | 212.5 | 3820.5 | 65.4 | 67.5 | 667.5 | 0 | 0 | 2.5 | 0
07:00 | 4012 | 1945 | 903 | 38 | 36 | 824 | 212 | 3796 | 116.22 | 59 | 626 | 0 | 0 | 2 | 0
07:30 | 3998 | 1906 | 903.5 | 38 | 35 | 824.8 | 212.5 | 3765 | 203.67 | 59 | 598 | 0 | 0 | 1 | 0
08:00 | 3984 | 1867 | 904 | 38 | 34 | 825.6 | 213 | 3734 | 291.12 | 59 | 570 | 0 | 0 | 0 | 0
08:30 | 3967 | 1864 | 909 | 38 | 34 | 825.17 | 213.5 | 3737.5 | 367.005 | 80 | 592.5 | 0 | 0 | 0 | 0
09:00 | 3950 | 1861 | 914 | 38 | 34 | 824.74 | 214 | 3741 | 442.89 | 101 | 615 | 0 | 0 | 0 | 0
09:30 | 3899.5 | 1827.6 | 914 | 38 | 35 | 820.62 | 214.5 | 3666.5 | 518 | 101 | 619.5 | 0 | 0 | 0 | 0
10:00 | 3849 | 1794.2 | 914 | 38 | 36 | 816.5 | 215 | 3592 | 593.11 | 101 | 624 | 0 | 0 | 0 | 0
10:30 | 3864.5 | 1806.7 | 914 | 38 | 37 | 818.53 | 215 | 3612.5 | 611.115 | 93 | 621 | 0 | 0 | 0 | 0
11:00 | 3880 | 1819.2 | 914 | 38 | 38 | 820.56 | 215 | 3633 | 629.12 | 85 | 618 | 0 | 0 | 0 | 0
11:30 | 4013.5 | 1849.1 | 914 | 38 | 40 | 817.85 | 215 | 3701.5 | 658.79 | 92.5 | 624.5 | 0 | 0 | 0 | 0
12:00 | 4147 | 1879 | 914 | 38 | 42 | 815.14 | 215 | 3770 | 688.46 | 100 | 631 | 0 | 0 | 0 | 0
12:30 | 4168 | 1878.5 | 913.5 | 38 | 43 | 816.525 | 215.5 | 3891 | 709.185 | 118 | 682 | 0 | 0 | 3.5 | 0
13:00 | 4189 | 1878 | 913 | 38 | 44 | 817.91 | 216 | 4012 | 729.91 | 136 | 733 | 0 | 0 | 7 | 0
13:30 | 4189 | 1875 | 913.5 | 38 | 44 | 866.64 | 216 | 4060.5 | 651.64 | 136 | 774.25 | 0 | 0 | 8 | 0
14:00 | 4189 | 1872 | 914 | 38 | 44 | 915.37 | 216 | 4109 | 573.37 | 136 | 815.5 | 0 | 0 | 9 | 0
14:30 | 4198 | 1880.5 | 913.5 | 38 | 45 | 916.86 | 214 | 3978.5 | 541.615 | 139.5 | 853.85 | 0 | 0 | 10 | 0
15:00 | 4207 | 1889 | 913 | 38 | 46 | 918.35 | 212 | 3848 | 509.86 | 143 | 892.2 | 0 | 0 | 11 | 0
15:30 | 4213 | 1902.5 | 913 | 38 | 45 | 914.12 | 214.5 | 4003 | 437.02 | 175.5 | 1001.2 | 0 | 0 | 7.5 | 0
16:00 | 4219 | 1916 | 913 | 38 | 44 | 909.89 | 217 | 4158 | 364.18 | 208 | 1110.2 | 0 | 0 | 4 | 0
16:30 | 4168 | 1913 | 913 | 38 | 43 | 910.505 | 217 | 4096.5 | 266.84 | 225.5 | 1128.8 | 0 | 0 | 3 | 0
17:00 | 4117 | 1910 | 913 | 38 | 42 | 911.12 | 217 | 4035 | 169.5 | 243 | 1147.4 | 0 | 0 | 2 | 0
17:30 | 3983.5 | 1889 | 913 | 38 | 42 | 911.825 | 216.5 | 4011 | 102.82 | 242.5 | 1144.7 | 0 | 0 | 1 | 0
18:00 | 3850 | 1868 | 913 | 38 | 42 | 912.53 | 216 | 3987 | 36.14 | 242 | 1142 | 0 | 0 | 0 | 0
18:30 | 4016.5 | 1899.5 | 913 | 38 | 46 | 1027.145 | 217 | 4222.5 | 18.07 | 397.5 | 1431.5 | 0 | 0 | 0 | 0
19:00 | 4183 | 1931 | 913 | 38 | 50 | 1141.76 | 218 | 4458 | 0 | 553 | 1721 | 0 | 0 | 0 | 0
19:30 | 4015 | 1869 | 914 | 38 | 46 | 1310.96 | 218 | 4734 | 0 | 646 | 2160.2 | 0 | 0 | 0 | 91
20:00 | 3831 | 1845.3 | 913 | 38 | 44 | 1405.99 | 218 | 4848 | 0 | 639 | 1906.1 | 0 | 0 | 2 | 88
20:30 | 3965 | 1886.4 | 913 | 38 | 46 | 1430.13 | 218 | 4877 | 0 | 631.5 | 1804 | 0 | 0 | 2 | 87
21:00 | 4099 | 1927.5 | 913 | 38 | 48 | 1454.27 | 218 | 4906 | 0 | 624 | 1701.9 | 0 | 0 | 2 | 86
21:30 | 4144 | 1936 | 913 | 38 | 49 | 1450.635 | 218 | 4880 | 0 | 627.5 | 1626.2 | 0 | 0 | 2.5 | 92
22:00 | 4189 | 1944.5 | 913 | 38 | 50 | 1447 | 218 | 4854 | 0 | 631 | 1550.5 | 0 | 0 | 3 | 98
22:30 | 4212 | 1951 | 913.5 | 38 | 51 | 1444.23 | 218 | 4871.5 | 0 | 631 | 1558.3 | 0 | 0 | 2 | 96.5
23:00 | 4235 | 1957.5 | 914 | 38 | 52 | 1441.46 | 218 | 4889 | 0 | 631 | 1566.1 | 0 | 0 | 1 | 95
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 06:00 | 333 | 15:00 | Payra | 416 | 06:00 | 410 | 15:00
Ashuganj | 410 | 6:00 | 385 | 23:00 | Rahanpur | 399 | 10:00 | 378 | 22:00
Bhulta | 408 | 06:00 | 382 | 23:00 | Rampal | 406 | 06:00 | 390 | 14:00
Bibiana | 391 | 06:00 | 382 | 14:00
BIPTC | 399 | 18:00 | 388 | 00:00
Bogura | 385 | 10:00 | 362 | 22:00
Gopalganj | 400 | 06:00 | 385 | 22:00
Kaliakoir | 376 | 05:00 | 361 | 23:00
Madunaghat | 393 | 06:00 | 387 | 13:00
Meghnaghat | 387 | 06:00 | 375 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 216 | 15:00 | Keranigonj | 224 | 06:00 | 213 | 23:00
AKSML | 230 | 08:00 | 222 | 23:00 | Khulna(S) | 232 | 09:00 | 218 | 19:00
Aminbazar | 227 | 06:00 | 217 | 15:00 | Madunaghat | 230 | 05:00 | 226 | 14:00
Ashuganj | 234 | 05:00 | 221 | 21:00 | Madunaghat-400 | 231 | 06:00 | 227 | 00:00
Ashuganj-400 | 234 | 05:00 | 221 | 21:00 | Maniknagar | 221 | 06:00 | 213 | 22:00
Baghabari | 235 | 06:00 | 225 | 20:00 | Meghnaghat | 229 | 08:00 | 222 | 00:00
Barapukuria | 225 | 10:00 | 218 | 21:00 | Meghnaghat-400 | 225 | 06:00 | 217 | 23:00
Barapukuria-230 | 225 | 10:00 | 218 | 21:00 | Mirsorai | 226 | 06:00 | 217 | 22:00
Barishal | 229 | 07:00 | 218 | 23:00 | Rajshahi | 233 | 07:00 | 219 | 19:00
Bheramara | 233 | 06:00 | 222 | 19:30 | Rampal | 233 | 09:00 | 219 | 00:00
Bhulta | 230 | 06:00 | 214 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 05:00 | 222 | 23:00 | Rampura | 229 | 06:00 | 213 | 22:00
BIPTC | 237 | 06:00 | 222 | 19:30 | Shikalbaha | 228 | 07:00 | 223 | 15:00
Bogura | 239 | 10:00 | 225 | 22:00 | Shyampur | 224 | 06:00 | 214 | 23:00
Bogura-400 | 239 | 10:00 | 226 | 22:00 | Siddhirganj | 223 | 05:00 | 215 | 19:30
Borhanuddin | 233 | 07:00 | 227 | 00:00 | Sirajgonj | 241 | 06:00 | 233 | 22:00
BSRM | 225 | 06:00 | 217 | 23:00 | Sreepur | 230 | 06:00 | 218 | 22:00
Cumilla(N) | 223 | 05:00 | 214 | 23:00 | Tongi | 226 | 08:00 | 215 | 15:00
Faridpur | 227 | 07:00 | 215 | 21:00
Fenchuganj | 231 | 08:00 | 224 | 00:00
Ghorashal | 230 | 01:00 | 220 | 17:00
Ghorashal-230 | 228 | 06:00 | 214 | 15:00
Gopalganj | 228 | 07:00 | 217 | 23:00
GPH | 228 | 06:00 | 221 | 23:00
Haripur | 222 | 05:00 | 214 | 23:00
Hasnabad | 224 | 06:00 | 214 | 15:00
Hathazari | 227 | 09:00 | 220 | 15:00
Ishurdi | 236 | 06:00 | 224 | 22:00
Jhenaidah | 230 | 06:00 | 213 | 19:30
Kaliakoir | 233 | 05:00 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 126 | 14:00 | Lalmonirhat | 130 | 18:30 | 121 | 21:00
Agargaon | 133 | 06:00 | 125 | 15:00 | Madanganj | 129 | 07:00 | 124 | 15:00
Agrabad | 130 | 07:00 | 126 | 12:00 | Madaripur | 135 | 10:00 | 127 | 23:00
AKS | 126 | 05:00 | 124 | 14:00 | Madartek | 137 | 06:00 | 125 | 15:00
Aminbazar | 133 | 06:00 | 127 | 00:00 | Madunaghat | 130 | 04:00 | 127 | 14:00
Amnura | 135 | 10:00 | 126 | 00:00 | Magura | 132 | 09:00 | 119 | 19:00
Ashuganj | 141 | 07:00 | 134 | 21:00 | Mahasthangarh | 131 | 10:00 | 120 | 22:00
Bagerhat | 136 | 09:00 | 119 | 19:00 | Maijdee | 118 | 10:00 | 106 | 23:00
Bajitpur | 130 | 06:00 | 122 | 21:00 | Manikganj | 128 | 06:00 | 118 | 21:00
Bakulia | 132 | 02:00 | 126 | 13:00 | Maniknagar | 134 | 06:00 | 128 | 13:00
Banani | 138 | 06:00 | 127 | 14:00 | Matarbari | 117 | 09:00 | 108 | 00:00
Bangabhaban | 134 | 06:00 | 128 | 13:00 | Matuail | 130 | 06:00 | 124 | 23:00
Barapukuria | 136 | 10:00 | 129 | 12:00 | Millgate | 134 | 05:00 | 123 | 15:00
Barguna | 135 | 09:00 | 130 | 00:00 | Mirpur | 131 | 04:00 | 123 | 15:00
Barishal | 135 | 07:00 | 125 | 23:00 | Mirzapur | 129 | 05:00 | 123 | 23:00
Barishal-230 | 134 | 07:00 | 126 | 22:00 | Mithapukur | 123 | 10:00 | 107 | 22:00
Baroaulia | 129 | 07:00 | 126 | 14:00 | MI_Cement | 130.5 | 06:00 | 125 | 15:00
Baroirhat | 123 | 05:00 | 117 | 23:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 03:00 | 122 | 15:00 | Mogbazar | 140 | 06:00 | 127 | 15:00
BashundharaCement | 129 | 07:00 | 124 | 15:00 | Mongla | 135 | 09:00 | 120 | 19:00
Beanibazar | 125 | 03:00 | 122 | 00:00 | Motijheel | 134 | 06:00 | 128 | 13:00
Benapole | 134 | 09:00 | 119 | 22:00 | Muktagacha | 136 | 18:00 | 125 | 19:00
Bhaluka | 130 | 06:00 | 121 | 22:00 | Munshiganj | 129 | 04:00 | 124 | 15:00
Bhandaria | 130 | 09:00 | 117 | 22:00 | Muradnagar | 124 | 10:00 | 116 | 22:00
Bhangura | 132 | 01:00 | 126 | 19:30 | Mymensingh | 137 | 09:00 | 111 | 23:00
Bheramara | 137 | 09:00 | 132 | 00:00 | Naogaon | 129 | 10:00 | 117 | 22:00
Bheramara(GK) | 137 | 09:00 | 131 | 19:00 | Narail | 131 | 09:00 | 115 | 19:00
Bhulta | 125 | 01:00 | 120 | 16:00 | Narinda | 134 | 06:00 | 128 | 13:00
Bog-Sherpur | 133 | 10:00 | 123 | 22:00 | Narshingdi | 136 | 05:00 | 120 | 21:00
Bogura | 134 | 11:00 | 125 | 00:00 | Natore | 133 | 08:00 | 125 | 00:00
Bogura-230 | 134 | 10:00 | 125 | 22:00 | Nawabganj | 134 | 05:00 | 125 | 23:00
Brahmanbaria | 136 | 06:00 | 127 | 21:00 | Netrakona | 124 | 09:00 | 109 | 23:00
Cantonment | 170 | 19:30 | 125 | 15:00 | New | 134 | 04:00 | 123 | 15:00
Chandina | 127 | 06:00 | 120 | 23:00 | Niamatpur | 136 | 06:00 | 127 | 19:30
Chandpur | 126 | 15:00 | 118 | 23:00 | Noapara | 137 | 09:00 | 123 | 19:00
Chandraghona | 131 | 06:00 | 128 | 15:00 | Pabna | 134 | 10:00 | 126 | 19:30
Chapai | 135 | 06:00 | 125 | 21:00 | Palashbari | 121 | 10:00 | 105 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 05:00 | 125 | 15:00 | Panchagarh | 135 | 18:30 | 123 | 12:00
Chauddagram | 122 | 07:00 | 115 | 23:00 | Patiya | 129 | 19:00 | 125 | 13:00
Chhatak | 125 | 04:00 | 118 | 21:00 | Patuakhali | 134 | 06:00 | 131 | 21:00
Chowmuhani | 119 | 10:00 | 107 | 23:00 | Payra | 137 | 09:00 | 133 | 22:00
Chuadanga | 131 | 06:00 | 116 | 19:00 | PHP | 122 | 10:00 | 115 | 22:00
Coxsbazar | 117 | 09:00 | 107 | 22:00 | Postogola | 132 | 07:00 | 126 | 23:00
Cumilla(N) | 127 | 06:00 | 121 | 22:00 | Purbachal | 138 | 06:00 | 122 | 15:00
Cumilla(S) | 132 | 02:00 | 119 | 23:00 | Purbasadipur | 129 | 18:00 | 122 | 12:00
Daganbhuiyan | 119 | 10:00 | 110 | 22:00 | Rahanpur | 136 | 06:00 | 128 | 22:00
Daudkandi | 128 | 05:00 | 114 | 22:00 | Rahanpur-400 | 137 | 07:00 | 130 | 20:00
Dhaka | 138 | 06:00 | 127 | 15:00 | Rahim | 130 | 06:00 | 126 | 00:00
Dhamrai | 133 | 06:00 | 124 | 15:00 | Rajbari | 133 | 06:00 | 125 | 22:00
Dhanmondi | 138 | 06:00 | 127 | 15:00 | Rajendrapur | 130 | 06:00 | 120 | 12:00
Dohazari | 126 | 19:00 | 121 | 00:00 | Rajshahi | 133 | 06:00 | 125 | 00:00
Faridpur | 135 | 10:00 | 127 | 22:00 | Rajshahi-230 | 133 | 06:00 | 126 | 21:00
Fatullah | 132 | 05:00 | 126 | 15:00 | Ramganj | 120 | 09:00 | 110 | 22:00
Fenchuganj | 134 | 04:00 | 131 | 00:00 | Rampur | 130 | 00:00 | 124 | 14:00
Feni | 121 | 06:00 | 115 | 15:00 | Rampura | 137 | 06:00 | 126 | 15:00
Ghatail | 131 | 09:00 | 121 | 19:00 | Rangamati | 131 | 06:00 | 127 | 14:00
Ghorashal | 137 | 06:00 | 129 | 15:00 | Rangpur | 132 | 03:00 | 125 | 00:00
Goalpara | 138 | 07:00 | 126 | 19:00 | Ruppur | 137 | 06:00 | 130 | 00:00
Gollamari | 139 | 09:00 | 127 | 19:00 | Saidpur | 130 | 05:00 | 123 | 23:00
Gopalganj | 135 | 06:00 | 126 | 22:00 | Satkhira | 135 | 09:00 | 120 | 19:30
Gopalganj-400 | 136 | 06:00 | 130 | 21:00 | Satmasjid | 133 | 08:00 | 125 | 21:00
Gulshan | 137 | 05:00 | 126 | 15:00 | Savar | 131 | 05:00 | 123 | 15:00
Halishahar | 130 | 06:00 | 126 | 12:00 | SevenRings | 137 | 06:00 | 129 | 15:00
Haripur | 130 | 07:00 | 125 | 23:00 | ShahCement | 130 | 05:00 | 125 | 15:00
HaripurSBU | 130 | 05:00 | 125 | 23:00 | Shahjadpur | 136 | 02:00 | 130 | 21:00
Hasnabad | 132 | 04:00 | 126 | 15:00 | Shahjibazar | 135 | 07:00 | 127 | 21:00
Hathazari | 132 | 18:00 | 128 | 16:00 | Shahmirpur | 131 | 19:00 | 127 | 14:00
Ishurdi | 138 | 08:00 | 131 | 19:30 | Shariatpur | 134 | 09:00 | 124 | 22:00
Jaldhaka | 129 | 18:30 | 120 | 21:00 | Sherpur | 136 | 09:00 | 120 | 19:00
Jamalpur | 138 | 09:00 | 125 | 19:00 | Shikalbaha | 120 | 05:00 | 116 | 14:00
Jashore | 130 | 06:00 | 115 | 19:30 | Shikalbaha-230 | 132 | 19:00 | 128 | 00:00
Jhenaidah | 134 | 05:00 | 120 | 19:30 | Shitalakhya | 130.5 | 06:00 | 125 | 15:00
Jhenaidah-230 | 135 | 06:00 | 122 | 19:30 | Sholosohor | 130 | 07:00 | 127 | 14:00
Joydebpur | 136 | 05:00 | 124 | 15:00 | Shyampur | 131 | 00:00 | 127 | 13:00
Joypurhat | 127 | 10:00 | 114 | 22:00 | Shyampur-230 | 132 | 06:00 | 125 | 23:00
Juldah | 130 | 06:00 | 126 | 14:00 | Siddhirganj | 130 | 04:00 | 126 | 15:00
Kabirpur | 132 | 07:00 | 119 | 22:00 | Sirajganj | 131 | 10:00 | 122 | 22:00
Kachua | 124 | 09:00 | 115 | 23:00 | Sonargaon | 128 | 06:00 | 123 | 15:00
Kaliakoir | 135 | 04:00 | 127 | 14:00 | Sreemongol | 132 | 06:00 | 126 | 21:00
Kallyanpur | 137 | 02:00 | 125 | 15:00 | Sreepur | 133 | 06:00 | 124 | 23:00
Kalurghat | 130 | 06:00 | 128 | 00:00 | Srinagar | 134 | 06:00 | 126 | 16:00
Kamrangirchar | 134 | 07:00 | 126 | 15:00 | SSM | 134 | 07:00 | 130 | 10:00
Kaptai | 132 | 1:00 | 132 | 12:00 | Sunamganj | 123 | 06:00 | 116 | 21:00
Kasba | 123 | 10:00 | 115 | 22:00 | Sylhet | 127 | 07:00 | 121 | 21:00
Kazla | 134 | 06:00 | 128 | 16:00 | Sylhet-132 | 127 | 06:00 | 125 | 00:00
Keranigonj | 135 | 06:00 | 126 | 23:00 | Tangail | 129 | 07:00 | 120 | 22:00
Khagrachori | 130 | 06:00 | 126 | 14:00 | Taraganj | 131 | 16:00 | 123 | 12:00
Khulna | 138 | 09:00 | 124 | 19:00 | Thakurgaon | 134 | 18:30 | 121 | 12:00
Khulna(S) | 139 | 09:00 | 127 | 19:00 | TK | 131 | 05:00 | 128 | 00:00
Khulshi | 128 | 06:00 | 125 | 13:00 | Tongi | 133 | 07:00 | 124 | 16:00
Kishoreganj | 129 | 10:00 | 117 | 21:00 | Ullahpara | 134 | 04:00 | 127 | 01:00
Kodda | 131 | 10:00 | 120 | 12:00 | Ullon | 137 | 06:00 | 126 | 15:00
KSRM | 130 | 10:00 | 125 | 13:00 | Uttara | 132 | 05:00 | 124 | 21:00
Kulaura | 133 | 15:00 | 129 | 20:00 | UttaraNew | 132 | 06:00 | 123 | 15:00
Kurigram | 130 | 10:00 | 122 | 12:00 | Zigatola | 146 | 11:00 | 126 | 23:00
Kushtia | 134 | 10:00 | 125 | 19:30
Laksam | 124 | 10:00 | 114 | 23:00
Lakshmipur | 119 | 10:00 | 108 | 23:00
Lalbag | 134 | 06:00 | 126 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division