## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-08-2025 | during | 19-08-2025 | during | 19-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 371 | 321 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 298 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 270 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 32 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 44.1 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 122 | 133 | 133 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 25.5 | 33 | 33 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 47 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 55 | 86 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 133 | 144 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 54 | 55 | 55 | 35 | 35 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2105 | 2765.6 | 5811.54 | 5778.54 | 3791.83 | 3758.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 221 | 215 | 219 | 215 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 64 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 50 | 50 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 37 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 15 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 77 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 4.13 | 0 | 4.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 46 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 47 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1147 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 40 | 41 | 55 | 48 | 55 | 48 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 724 | 770 | 770 | 760 | 760 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2373 | 2853 | 3830.85 | 3846.72 | 3643.85 | 3659.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 197 | 194 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 41 | 46.7 | 46.7 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 48 | 55 | 55 | 49 | 49 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 88 | 195 | 195 | 123 | 123 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 128 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 184 | 173 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 17.75 | 17.75 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 33 | 114 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 58 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 85 | 92 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1520 | 1755.2 | 2427.81 | 2372.81 | 2162.36 | 2107.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-08-2025 | during | 19-08-2025 | during | 19-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 71 | 83 | 157.5 | 157.5 | 134 | 134 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 103 | 55 | 75 | 200 | 200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 73 | 71 | 95 | 103 | 100 | 100 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 17 | 34 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 294 | 269 | 430.2 | 412 | 509.2 | 480
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 59 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 137 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 161 | 162 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 12 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 390 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 250 | 250 | 250 | 250 | 250 | 250 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1430 | 1424 | 1491 | 1491 | 1395 | 1395
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 275 | 236 | 410 | 410 | 376 | 376 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 17 | 0 | 71 | 0 | 71 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 821 | 1106 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2049 | 2337 | 3619.2 | 3548.2 | 3428 | 3357
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 304 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 975 | 1086 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 221 | 278 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1835 | 1963 | 2162 | 2161 | 2117 | 2116
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 153 | 186 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 192 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 192 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 364 | 348 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 748 | 755.99 | 748 | 748 | 748 | 748 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 55 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1812 | 2149.19 | 2454.59 | 2304.99 | 2380.8 | 2231.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 45 | 50 | 50 | 45 | 45 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 155 | 157 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 210 | 0 | 188.07 | 0 | 188.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 593 | 430 | 686.67 | 462 | 691.67 | 467
System Total |  |  |  |  | 28821.2 | 27843.665 | 14011 | 15945.99 | 22913.86 | 22377.26 | 20119.71 | 19572.11
Forecast Scenario (19-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15980 |  | 0 |  | 15980
|  |  |  | 1:00 | 15340 |  | 0 |  | 15340
|  |  |  | 2:00 | 14970 |  | 0 |  | 14970
|  |  |  | 3:00 | 14670 |  | 0 |  | 14670
|  |  |  | 4:00 | 14400 |  | 0 |  | 14400
|  |  |  | 5:00 | 14130 |  | 0 |  | 14130
|  |  |  | 6:00 | 13760 |  | 0 |  | 13760
|  |  |  | 7:00 | 13660 |  | 0 |  | 13660
|  |  |  | 8:00 | 13560 |  | 0 |  | 13560
|  |  |  | 9:00 | 13720 |  | 0 |  | 13720
|  |  |  | 10:00 | 13890 |  | 0 |  | 13890
|  |  |  | 11:00 | 14040 |  | 0 |  | 14040
|  |  |  | 12:00 | 14370 |  | 0 |  | 14370
|  |  |  | 13:00 | 14670 |  | 0 |  | 14670
|  |  |  | 14:00 | 14740 |  | 0 |  | 14740
|  |  |  | 15:00 | 14600 |  | 0 |  | 14600
|  |  |  | 16:00 | 14610 |  | 0 |  | 14610
|  |  |  | 17:00 | 14140 |  | 0 |  | 14140
|  |  |  | 18:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15550 |  | 0 |  | 15550
|  |  |  | 19:30 | 16090 |  | 0 |  | 16090
|  |  |  | 20:00 | 16100 |  | 0 |  | 16100
|  |  |  | 21:00 | 16110 |  | 0 |  | 16110
|  |  |  | 22:00 | 15970 |  | 0 |  | 15970
|  |  |  | 23:00 | 16100 |  | 0 |  | 16100
Probable Maximum Temperature: |  |  | 32.50°C
Probable Maximum Demand at Day Peak: |  |  | 14370.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16110.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16110.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 352.81 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:10 hrs on 19-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-08-2025 | [28 empty] | Date: | 18-08-2025 | [28 empty] | Date: | 18-08-2025 | [28 empty] | Date: | 18-08-2025 | [28 empty] | Date: | 18-08-2025 | [13 empty] | Date: | 18-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [13 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 46 | 40 | 132 | 124 | 160 | 0 | 55 | 140 | 0 | 300 | 291 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 125 | 28 | 23 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 49 | 74 | 0 | 12 | 12 | 0 | 220 | 0 | 32 | 767 | 17 | 0 | 19 | 17 | 0 | 221 | 0 | 0 | 0 | 1180 | 0 | 51 | 115 | 51 | 0 | 349 | 330 | 47 | 203 | 35 | 109 | 70 | 200 | 8 | 20 | 114 | 50 | 53 | 0 | 0 | 300 | 230 | 360 | 0 | 60 | 142 | 8 | 0 | 83 | 30 | 0 | 0 | 161 | 17 | 102 | 75 | 96 | 0 | 0 | 0 | 8731 | 868 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 54 | 765 | 0 | 49 | 0 | 113 | 113 | 0 | 95 | 37 | 16 | 0 | 0 | 28 | 0 | 188 | 0 | 179 | 0 | 179 | 0 | 390 | 0 | 0 | 150 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 304 | 1125 | 0 | 6968 | 15699 | 107.75
01:00 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 44 | 54 | 106 | 124 | 45 | 0 | 17 | 138 | 0 | 300 | 288 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 90 | 28 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 49 | 74 | 0 | 12 | 12 | 0 | 218 | 0 | 32 | 765 | 0 | 0 | 18 | 0 | 0 | 221 | 0 | 0 | 0 | 1147 | 0 | 51 | 100 | 8 | 0 | 352 | 330 | 48 | 187 | 35 | 114 | 70 | 197 | 8 | 20 | 114 | 46 | 53 | 0 | 0 | 300 | 220 | 360 | 0 | 60 | 149 | 12 | 0 | 83 | 30 | 0 | 0 | 161 | 17 | 92 | 57 | 99 | 0 | 0 | 0 | 8297 | 867 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 17 | 772 | 0 | 49 | 0 | 70 | 113 | 0 | 95 | 0 | 16 | 0 | 0 | 28 | 0 | 182 | 0 | 183 | 0 | 183 | 0 | 344 | 0 | 0 | 151 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 180 | 0 | 304 | 1160 | 0 | 6739 | 15036 | 107.76
02:00 | 0 | 86 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 44 | 0 | 87 | 124 | 0 | 0 | 0 | 88 | 0 | 300 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1130 | 0 | 51 | 30 | 8 | 0 | 337 | 330 | 47 | 206 | 32 | 114 | 70 | 200 | 8 | 20 | 105 | 44 | 53 | 0 | 0 | 305 | 220 | 387 | 0 | 60 | 150 | 12 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 93 | 57 | 104 | 0 | 0 | 3 | 7852 | 868 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 17 | 764 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 185 | 0 | 185 | 0 | 391 | 0 | 0 | 148 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 115 | 180 | 0 | 304 | 1120 | 0 | 6630 | 14482 | 107.77
03:00 | 0 | 86 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 45 | 0 | 68 | 80 | 0 | 0 | 0 | 81 | 0 | 300 | 292 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 16 | 0 | 0 | 12 | 12 | 0 | 214 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1130 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 47 | 180 | 32 | 114 | 70 | 199 | 9 | 20 | 105 | 44 | 53 | 0 | 0 | 295 | 220 | 324 | 0 | 60 | 145 | 12 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 92 | 57 | 105 | 0 | 0 | 6 | 7636 | 869 | 281 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 974 | 17 | 774 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 182 | 0 | 182 | 0 | 334 | 0 | 0 | 151 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 304 | 1106 | 0 | 6419 | 14055 | 107.78
04:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 44 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 295 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 23 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 12 | 12 | 0 | 214 | 0 | 36 | 770 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 48 | 192 | 32 | 114 | 50 | 199 | 8 | 20 | 105 | 42 | 25 | 0 | 0 | 300 | 220 | 341 | 0 | 60 | 129 | 12 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 35 | 35 | 106 | 0 | 0 | 6 | 7224 | 869 | 283 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 164 | 0 | 164 | 0 | 348 | 0 | 0 | 150 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 304 | 1000 | 0 | 6251 | 13475 | 107.79
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 45 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 23 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 35 | 6 | 0 | 0 | 12 | 12 | 0 | 214 | 0 | 37 | 713 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 48 | 194 | 32 | 114 | 50 | 199 | 15 | 20 | 105 | 42 | 25 | 0 | 0 | 305 | 220 | 358 | 0 | 60 | 136 | 0 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 45 | 47 | 106 | 0 | 0 | 6 | 7151 | 887 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 0 | 678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 171 | 0 | 171 | 0 | 355 | 0 | 0 | 151 | 46 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 115 | 220 | 0 | 304 | 990 | 0 | 6155 | 13306 | 107.8
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 19 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 23 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 12 | 1 | 214 | 0 | 38 | 705 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 995 | 1 | 51 | 0 | 8 | 0 | 355 | 330 | 48 | 189 | 29 | 112 | 70 | 199 | 25 | 20 | 60 | 40 | 25 | 2 | 0 | 310 | 220 | 340 | 0 | 60 | 140 | 0 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 70 | 55 | 106 | 0 | 1 | 6 | 7060 | 886 | 287 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1052 | 0 | 678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 167 | 0 | 170 | 0 | 170 | 0 | 347 | 0 | 1 | 150 | 48 | 50 | 1 | 70 | 0 | 0 | 0 | 1 | 8 | 1 | 0 | 219 | 115 | 220 | 0 | 304 | 950 | 0 | 5937 | 12997 | 107.81
07:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 8 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 22 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 1 | 207 | 0 | 39 | 705 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1003 | 3 | 51 | 0 | 8 | 0 | 352 | 330 | 48 | 195 | 29 | 88 | 70 | 170 | 26 | 20 | 60 | 38 | 25 | 10 | 0 | 315 | 220 | 346 | 0 | 60 | 144 | 0 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 94 | 56 | 106 | 0 | 6 | 6 | 7105 | 887 | 287 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 956 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 15 | 0 | 11 | 171 | 0 | 174 | 0 | 174 | 0 | 354 | 0 | 1 | 151 | 48 | 50 | 5 | 49 | 0 | 0 | 0 | 2 | 26 | 1 | 0 | 221 | 115 | 220 | 0 | 303 | 950 | 0 | 5856 | 12961 | 107.82
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 17 | 0 | 0 | 300 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 20 | 17 | 29 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 12 | 12 | 2 | 207 | 0 | 13 | 706 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 990 | 8 | 43 | 0 | 8 | 0 | 350 | 330 | 48 | 188 | 29 | 79 | 70 | 162 | 26 | 20 | 54 | 36 | 25 | 25 | 0 | 305 | 250 | 336 | 0 | 60 | 141 | 0 | 0 | 82 | 30 | 0 | 0 | 160 | 17 | 88 | 66 | 101 | 1 | 13 | 6 | 7076 | 898 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 943 | 0 | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 27 | 0 | 22 | 168 | 0 | 171 | 0 | 171 | 0 | 343 | 0 | 3 | 153 | 48 | 50 | 16 | 49 | 0 | 0 | 0 | 4 | 88 | 1 | 0 | 215 | 115 | 220 | 0 | 304 | 940 | 0 | 5936 | 13012 | 107.83
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 28 | 0 | 0 | 300 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 25 | 52 | 28 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 12 | 4 | 207 | 0 | 5 | 675 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 990 | 15 | 43 | 0 | 8 | 0 | 320 | 280 | 47 | 186 | 35 | 86 | 70 | 160 | 26 | 20 | 33 | 36 | 8 | 56 | 0 | 300 | 250 | 322 | 0 | 60 | 139 | 0 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 83 | 67 | 101 | 1 | 41 | 6 | 6938 | 898 | 286 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 934 | 0 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 71 | 0 | 39 | 166 | 0 | 169 | 0 | 168 | 0 | 342 | 0 | 3 | 164 | 48 | 35 | 25 | 34 | 0 | 0 | 0 | 6 | 63 | 1 | 0 | 214 | 115 | 220 | 0 | 305 | 940 | 0 | 6029 | 12967 | 107.84
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 55 | 25 | 0 | 300 | 304 | 0 | 0 | 0 | 280 | 0 | 0 | 31 | 52 | 26 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 12 | 12 | 4 | 207 | 0 | 10 | 728 | 0 | 0 | 2 | 0 | 0 | 215 | 0 | 0 | 0 | 1005 | 13 | 43 | 0 | 8 | 0 | 320 | 280 | 46 | 200 | 37 | 86 | 50 | 163 | 18 | 20 | 31 | 38 | 8 | 68 | 0 | 310 | 250 | 350 | 0 | 60 | 147 | 8 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 74 | 76 | 70 | 2 | 48 | 6 | 7134 | 898 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 826 | 0 | 674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 44 | 0 | 53 | 173 | 0 | 172 | 0 | 167 | 0 | 388 | 0 | 4 | 165 | 48 | 35 | 30 | 34 | 0 | 0 | 0 | 3 | 115 | 1 | 0 | 223 | 115 | 220 | 0 | 304 | 945 | 0 | 6093 | 13227 | 107.85
11:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 34 | 30 | 0 | 0 | 55 | 99 | 0 | 300 | 303 | 0 | 0 | 0 | 280 | 0 | 0 | 35 | 52 | 24 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 12 | 12 | 5 | 207 | 0 | 5 | 734 | 0 | 0 | 30 | 0 | 0 | 214 | 0 | 0 | 0 | 1005 | 17 | 43 | 0 | 8 | 0 | 335 | 290 | 44 | 201 | 37 | 92 | 50 | 177 | 12 | 20 | 29 | 54 | 8 | 57 | 0 | 305 | 250 | 350 | 0 | 60 | 148 | 8 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 73 | 75 | 72 | 2 | 41 | 6 | 7371 | 898 | 278 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 812 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 63 | 0 | 53 | 174 | 0 | 176 | 0 | 177 | 0 | 380 | 0 | 6 | 165 | 47 | 0 | 20 | 30 | 0 | 80 | 0 | 8 | 200 | 1 | 0 | 221 | 115 | 220 | 0 | 304 | 950 | 0 | 6197 | 13568 | 107.86
12:00 | 0 | 55 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 47 | 30 | 0 | 0 | 55 | 133 | 0 | 300 | 294 | 0 | 0 | 0 | 328 | 0 | 0 | 35 | 70 | 23 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 12 | 2 | 218 | 0 | 8 | 720 | 0 | 0 | 39 | 0 | 0 | 214 | 0 | 0 | 0 | 1100 | 8 | 43 | 0 | 8 | 0 | 339 | 330 | 44 | 197 | 34 | 85 | 70 | 184 | 28 | 20 | 33 | 58 | 8 | 39 | 0 | 305 | 250 | 386 | 0 | 60 | 150 | 8 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 73 | 75 | 71 | 1 | 51 | 6 | 7722 | 898 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 821 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 63 | 153 | 0 | 179 | 0 | 190 | 0 | 364 | 0 | 6 | 155 | 47 | 0 | 12 | 0 | 0 | 165 | 0 | 4 | 210 | 1 | 0 | 221 | 115 | 220 | 0 | 303 | 975 | 0 | 6289 | 14011 | 107.87
13:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 68 | 30 | 0 | 0 | 55 | 147 | 0 | 300 | 288 | 0 | 0 | 0 | 327 | 0 | 0 | 35 | 70 | 6 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 12 | 2 | 218 | 0 | 13 | 724 | 0 | 0 | 39 | 0 | 0 | 215 | 0 | 0 | 0 | 1120 | 18 | 43 | 0 | 12 | 0 | 340 | 330 | 44 | 186 | 40 | 85 | 70 | 180 | 33 | 20 | 33 | 62 | 8 | 71 | 0 | 300 | 250 | 373 | 0 | 58 | 147 | 8 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 73 | 75 | 71 | 2 | 43 | 6 | 7819 | 898 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 808 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 102 | 0 | 46 | 173 | 0 | 196 | 0 | 185 | 0 | 390 | 0 | 6 | 167 | 47 | 0 | 30 | 0 | 0 | 167 | 0 | 2 | 209 | 1 | 0 | 219 | 115 | 220 | 0 | 303 | 1000 | 0 | 6450 | 14269 | 107.88
14:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 28 | 17 | 68 | 30 | 0 | 0 | 55 | 144 | 0 | 300 | 303 | 0 | 0 | 0 | 325 | 0 | 0 | 31 | 70 | 25 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 12 | 12 | 1 | 218 | 0 | 14 | 765 | 0 | 0 | 39 | 0 | 0 | 215 | 0 | 0 | 0 | 1145 | 19 | 43 | 0 | 26 | 0 | 340 | 330 | 43 | 194 | 39 | 88 | 70 | 175 | 38 | 20 | 27 | 58 | 8 | 66 | 0 | 300 | 250 | 378 | 0 | 58 | 152 | 8 | 0 | 79 | 30 | 0 | 0 | 159 | 17 | 71 | 75 | 71 | 1 | 47 | 6 | 7938 | 897 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 797 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 91 | 0 | 47 | 204 | 0 | 203 | 0 | 205 | 0 | 397 | 0 | 5 | 160 | 45 | 0 | 36 | 0 | 0 | 167 | 0 | 1 | 141 | 1 | 0 | 220 | 115 | 180 | 0 | 303 | 1040 | 0 | 6384 | 14322 | 107.89
15:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 42 | 17 | 68 | 30 | 30 | 0 | 55 | 144 | 0 | 300 | 301 | 0 | 0 | 30 | 323 | 0 | 0 | 25 | 90 | 25 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 4 | 770 | 0 | 0 | 39 | 0 | 0 | 212 | 0 | 0 | 0 | 1165 | 8 | 43 | 1 | 41 | 0 | 333 | 330 | 43 | 206 | 37 | 108 | 70 | 175 | 18 | 20 | 56 | 60 | 25 | 43 | 0 | 310 | 260 | 377 | 0 | 57 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 159 | 17 | 71 | 74 | 70 | 1 | 31 | 6 | 8063 | 897 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 890 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 95 | 0 | 44 | 200 | 0 | 199 | 0 | 200 | 0 | 397 | 0 | 4 | 150 | 45 | 50 | 11 | 32 | 0 | 171 | 0 | 4 | 41 | 1 | 0 | 227 | 115 | 220 | 0 | 303 | 1050 | 0 | 6467 | 14530 | 107.9
16:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 48 | 34 | 96 | 30 | 195 | 13 | 55 | 144 | 0 | 300 | 288 | 0 | 0 | 55 | 324 | 0 | 0 | 18 | 90 | 25 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 15 | 12 | 2 | 220 | 0 | 8 | 770 | 0 | 0 | 39 | 0 | 0 | 218 | 0 | 0 | 0 | 1145 | 11 | 43 | 46 | 45 | 0 | 300 | 330 | 40 | 192 | 40 | 96 | 70 | 179 | 20 | 20 | 96 | 54 | 34 | 12 | 0 | 310 | 260 | 302 | 0 | 57 | 147 | 8 | 0 | 82 | 30 | 0 | 0 | 161 | 0 | 71 | 65 | 70 | 1 | 21 | 6 | 8181 | 904 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 972 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 23 | 0 | 21 | 200 | 0 | 160 | 0 | 179 | 0 | 346 | 0 | 4 | 149 | 45 | 70 | 17 | 70 | 0 | 16 | 0 | 4 | 62 | 1 | 0 | 219 | 115 | 180 | 0 | 304 | 1051 | 0 | 6254 | 14435 | 107.91
17:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 44 | 54 | 149 | 60 | 195 | 30 | 55 | 144 | 0 | 300 | 289 | 0 | 0 | 55 | 323 | 0 | 0 | 10 | 90 | 24 | 14 | 0 | 300 | 0 | 0 | 19 | 0 | 53 | 0 | 0 | 0 | 37 | 25 | 1 | 220 | 0 | 10 | 770 | 0 | 0 | 31 | 0 | 0 | 218 | 0 | 0 | 0 | 1060 | 4 | 43 | 110 | 71 | 0 | 300 | 280 | 40 | 199 | 37 | 92 | 50 | 171 | 23 | 20 | 114 | 46 | 53 | 19 | 0 | 295 | 260 | 298 | 0 | 58 | 140 | 8 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 71 | 75 | 70 | 0 | 8 | 6 | 8273 | 903 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 935 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 8 | 200 | 0 | 160 | 0 | 160 | 0 | 355 | 0 | 1 | 165 | 44 | 70 | 3 | 70 | 0 | 0 | 0 | 2 | 34 | 1 | 0 | 221 | 115 | 180 | 0 | 304 | 910 | 0 | 5942 | 14215 | 107.92
18:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 45 | 54 | 149 | 60 | 195 | 25 | 55 | 144 | 0 | 300 | 293 | 0 | 0 | 55 | 270 | 0 | 0 | 1 | 90 | 17 | 14 | 0 | 300 | 0 | 0 | 40 | 0 | 43 | 40 | 0 | 0 | 37 | 25 | 1 | 221 | 0 | 5 | 770 | 0 | 0 | 34 | 0 | 0 | 219 | 0 | 0 | 0 | 970 | 1 | 51 | 123 | 71 | 0 | 280 | 280 | 43 | 158 | 37 | 91 | 50 | 170 | 27 | 20 | 114 | 42 | 53 | 1 | 0 | 295 | 260 | 297 | 0 | 59 | 138 | 8 | 0 | 82 | 30 | 0 | 0 | 162 | 0 | 71 | 103 | 71 | 0 | 2 | 7 | 8102 | 904 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 878 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 191 | 0 | 140 | 0 | 140 | 0 | 336 | 0 | 1 | 162 | 45 | 70 | 1 | 72 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 215 | 100 | 180 | 0 | 304 | 850 | 0 | 5641 | 13743 | 107.93
19:00 | 5 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 48 | 54 | 149 | 106 | 255 | 35 | 55 | 144 | 0 | 300 | 294 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 108 | 25.5 | 22 | 0 | 350 | 2 | 10 | 51 | 0 | 31 | 49 | 32 | 0 | 37 | 25 | 0 | 221 | 4 | 7 | 690 | 60 | 0 | 39 | 3 | 13 | 219 | 0 | 0 | 0 | 1105 | 0 | 51 | 130 | 71 | 0 | 355 | 330 | 45 | 187 | 42 | 91 | 70 | 178 | 47 | 20 | 114 | 46 | 53 | 0 | 0 | 300 | 260 | 362 | 0 | 59 | 147 | 10 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 71 | 103 | 83 | 0 | 0 | 12 | 8876.5 | 903 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 20 | 765 | 0 | 48 | 0 | 100 | 30 | 0 | 93 | 14 | 52.2 | 0 | 0 | 28 | 0 | 160 | 0 | 190 | 0 | 191 | 0 | 400 | 0 | 0 | 164 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 304 | 920 | 0 | 6591.2 | 15467.7 | 107.95
19:30 | 24 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 46 | 54 | 149 | 116 | 295 | 55 | 55 | 144 | 0 | 300 | 292 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 25.5 | 22 | 0 | 300 | 17 | 16 | 78 | 0 | 48 | 49 | 41 | 0 | 37 | 25 | 0 | 221 | 22 | 9 | 694 | 46 | 0 | 39 | 17 | 48 | 220 | 0 | 0 | 0 | 1135 | 0 | 51 | 124 | 80 | 0 | 300 | 320 | 45 | 188 | 42 | 92 | 70 | 171 | 55 | 20 | 114 | 48 | 52.2 | 0 | 0 | 305 | 250 | 382 | 0 | 59 | 145 | 12 | 0 | 83 | 30 | 0 | 0 | 162 | 0 | 71 | 103 | 83 | 0 | 0 | 12 | 8968.7 | 904 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 52 | 758.79 | 0 | 48 | 0 | 108 | 100 | 0 | 93 | 24 | 52.2 | 0 | 0 | 28 | 0 | 174 | 0 | 192 | 0 | 192 | 0 | 343 | 0 | 0 | 163 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 180 | 0 | 304 | 1080 | 0 | 6921.99 | 15890.69
20:00 | 32 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 44.1 | 54 | 149 | 122 | 300 | 55 | 55 | 144 | 0 | 300 | 298 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 25.5 | 22 | 0 | 300 | 17 | 15 | 77 | 0 | 41 | 49 | 51 | 0 | 37 | 25 | 0 | 221 | 46 | 15 | 724 | 47 | 0 | 39 | 17 | 64 | 221 | 0 | 0 | 0 | 1147 | 0 | 51 | 128 | 88 | 0 | 300 | 280 | 48 | 194 | 41 | 92 | 70 | 173 | 58 | 20 | 114 | 46 | 52.2 | 0 | 0 | 300 | 250 | 390 | 0 | 59 | 137 | 12 | 0 | 84 | 30 | 0 | 0 | 162 | 0 | 71 | 103 | 83 | 0 | 0 | 12 | 9066.8 | 904 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 53 | 755.99 | 0 | 48 | 0 | 108 | 108 | 0 | 93 | 38 | 52.2 | 0 | 0 | 28 | 0 | 186 | 0 | 192 | 0 | 192 | 0 | 348 | 0 | 0 | 157 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 180 | 0 | 304 | 1086 | 0 | 6879.19 | 15945.99 | 107.97
21:00 | 8 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 46 | 54 | 149 | 120 | 180 | 30 | 55 | 144 | 0 | 300 | 288 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 108 | 26.5 | 22 | 0 | 300 | 17 | 15 | 83 | 0 | 30 | 49 | 59 | 0 | 37 | 25 | 0 | 222 | 47 | 19 | 706 | 15 | 0 | 26 | 17 | 65 | 221 | 0 | 0 | 0 | 1130 | 0 | 51 | 118 | 127 | 0 | 353 | 330 | 48 | 186 | 41 | 93 | 70 | 179 | 60 | 20 | 114 | 48 | 52.2 | 0 | 0 | 295 | 225 | 358 | 0 | 60 | 149 | 6 | 0 | 84 | 30 | 0 | 0 | 162 | 0 | 82 | 95 | 84 | 0 | 0 | 12 | 8973.7 | 904 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 54 | 757 | 0 | 48 | 0 | 70 | 70 | 0 | 93 | 38 | 24 | 0 | 0 | 28 | 0 | 208 | 0 | 192 | 0 | 192 | 0 | 390 | 0 | 0 | 156 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 304 | 1108 | 0 | 6782 | 15755.7 | 107.99
22:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 45.6 | 54 | 149 | 108 | 95 | 15 | 37 | 114 | 0 | 300 | 296 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 108 | 25.8 | 22 | 0 | 300 | 17 | 15 | 35 | 0 | 38 | 33 | 59 | 0 | 37 | 25 | 0 | 222 | 46 | 26 | 700 | 0 | 0 | 19 | 17 | 64 | 221 | 0 | 0 | 0 | 1140 | 0 | 51 | 70 | 127 | 0 | 352 | 330 | 48 | 192 | 41 | 111 | 70 | 175 | 60 | 20 | 114 | 50 | 52.2 | 0 | 0 | 295 | 225 | 370 | 0 | 60 | 153 | 6 | 0 | 84 | 30 | 0 | 0 | 163 | 0 | 100 | 76 | 82 | 0 | 0 | 12 | 8710.6 | 904 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 54 | 749 | 0 | 48 | 0 | 35 | 70 | 0 | 93 | 38 | 8 | 0 | 0 | 28 | 0 | 208 | 0 | 192 | 0 | 192 | 0 | 404 | 0 | 0 | 153 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 304 | 1107 | 0 | 6852 | 15562.6 | 108.01
23:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 45.6 | 54 | 149 | 108 | 95 | 15 | 35 | 110 | 0 | 300 | 296 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 26.2 | 22 | 0 | 300 | 0 | 0 | 31 | 0 | 14 | 33 | 59 | 0 | 37 | 25 | 0 | 220 | 51 | 28 | 757 | 0 | 0 | 19 | 17 | 64 | 221 | 0 | 0 | 0 | 1145 | 0 | 51 | 70 | 47 | 0 | 353 | 330 | 47 | 170 | 41 | 115 | 50 | 175 | 60 | 20 | 114 | 50 | 52.2 | 0 | 0 | 295 | 225 | 373 | 0 | 60 | 152 | 6 | 0 | 84 | 30 | 0 | 0 | 163 | 0 | 100 | 76 | 81 | 0 | 0 | 12 | 8592 | 904 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1236 | 54 | 756 | 0 | 48 | 0 | 35 | 70 | 0 | 93 | 38 | 8 | 0 | 0 | 28 | 0 | 205 | 0 | 192 | 0 | 191 | 0 | 405 | 0 | 0 | 157 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 304 | 1095 | 0 | 6971 | 15563 | 108.04
Total KWH | 54432 | 1638720 | 447840 | 0 | 0 | 0 | 0 | 0 | 8211600 | 0 | 0 | 730800 | 623520 | 2205936 | 1320000 | 1728262 | 256425 | 895861 | 2280960 | 0 | 7573500 | 7076975 | 0 | 0 | 508640 | 7493612 | 0 | 0 | 262186 | 1662000 | 579600 | 491760 | 0 | 7668636.36 | 71509 | 65236 | 383040 | 0 | 720480 | 392630 | 411392 | 0 | 490560 | 389760 | 20883 | 5217140 | 296100 | 478560 | 17701818.18 | 90327 | 0 | 500160 | 106983 | 342909 | 5246011 | 0 | 0 | 0 | 26039998 | 128115 | 1131830 | 1104000 | 903272 | 0 | 8411600 | 7744000 | 1096320 | 4660000 | 884016 | 2382720 | 1512130 | 4348800 | 717360 | 466110 | 2009820 | 1135680 | 819331 | 498055 | 0 | 7323500 | 5703900 | 8841000 | 0 | 1392000 | 3502064 | 175392 | 0 | 1976640 | 714144 | 0 | 0 | 3748930 | 270720 | 1862400 | 1723200 | 2000640 | 13850 | 347720 | 177360 | 192403380.54 | 21626909 | 6425856 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 573120 | 23454540 | 381120 | 17541818 | 0 | 312264 | 0 | 635040 | 936864 | 0 | 655056 | 195088 | 148219 | 398630 | 666770 | 190870 | 424504 | 4503818 | 0 | 4537245 | 0 | 4539127 | 0 | 8830327 | 0 | 36960 | 3846000 | 1073890 | 1775041 | 198779 | 17337984 | 0 | 766000 | 0 | 34505.16 | 1283760 | 4693 | 0 | 5826000 | 2724000 | 5249230 | 0 | 7293816 | 25284363.64 | 0 | 170624206.8 | 363027587.34

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14011 | MW | 12:00 Hr. | Energy Generated |  |  | 363.0276 |  | MKWHr.
| Day Peak Demand |  |  | 14011 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.056 |  | MKWHr.
| Evening Peak Generation |  |  | 15945.99 | MW | 20:00 Hr. | Energy Demand |  |  | 364.0836 |  | MKWHr.
| Evening Peak Demand |  |  | 16151.86 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.1 |  | °C
| Minimum Generation of the Day |  |  | 12961 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1048.32 |  | MMCFD
| Maximum Generation of the Day |  |  | 15945.99 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.9382 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.0957 | 0 | 14.3534 | 0 | 0 | 0.26219 | 0 | 0 | 53.7113 | Gas | 143.8173 | Gas | 512386585.4012
| Chattogram Zone |  |  | 5.7246 | 43.7418 | 3.5406 | 0 | 5.2171 | 0.149 | 0 | 0.72048 | 59.0936 | Coal | 110.5204 | Coal | 654515378.7484
| Cumilla Zone |  |  | 26.8093 | 0 | 11.382 | 0 | 0 | 0.49806 | 1.1357 | 0 | 39.825 | HFO | 55.8773 | HFO | 1033208706.41
| Mymensingh Zone |  |  | 2.0006 | 0 | 4.0337 | 0 | 0 | 0.36157 | 0 | 0 | 6.3959 | HSD | 0.766 | HSD | 0
| Sylhet Zone |  |  | 33.3776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.3776 | Hydro | 5.2171 | Hydro | 521714
| Khulna Zone |  |  | 6.4259 | 23.4545 | 0.38112 | 0 | 0 | 0.57312 | 22.5389 | 0 | 53.3735 | Solar | 4.8925 | Solar | 73448187.7236
| Barishal Zone |  |  | 7.9732 | 38.4042 | 0 | 0 | 0 | 0.004693 | 0 | 0 | 46.3821 | Import | 41.2164 | Import | 234072816.13
| Rajshahi Zone |  |  | 22.4105 | 0 | 3.0734 | 0 | 0 | 1.5269 | 17.5418 | 0 | 44.5526 | Wind | 0.72048 | Wind | 10619875.2
| Rangpur Zone |  |  | 0 | 4.9199 | 19.113 | 0.766 | 0 | 1.517 | 0 | 0 | 26.316
| Total |  |  | 143.8173 | 110.5204 | 55.8773 | 0.766 | 5.2171 | 4.8925 | 41.2164 | 0.72048 | 363.0276
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 512386585.4012 |  | Hydro | 521714
|  |  |  | Coal | 654515378.7484 |  | Solar | 73448187.7236
|  |  |  | HFO | 1033208706.41 |  | Import | 234072816.13
|  |  |  | HSD | 0 |  | Wind | 10619875.2
[5 empty] | Total: | 251,87,73,263 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6269 | Peak Hr Flow | 904.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41192909.15 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.5418 | Peak Hr Flow | 755.99 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 520 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1357 | Peak Hr Flow | 46.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 942 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.3044 | Peak Hr Flow | 1705.99 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5511
|  |  |  | Chattogram |  | 0 |  | 1555
|  |  |  | Cumilla |  | 0 |  | 1456
|  |  |  | Mymensingh |  | 107 |  | 1300
|  |  |  | Sylhet |  | 0 |  | 661
|  |  |  | Khulna |  | 0 |  | 1799
|  |  |  | Barishal |  | 0 |  | 442
|  |  |  | Rajshahi |  | 0 |  | 1611
|  |  |  | Rangpur |  | 90 |  | 1112
|  |  |  | Total |  | 197 |  | 15447
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Teesta Solar Limited |  |  | 200
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 600
|  |  |  | Total Unavailable Capacity |  |  |  | 900
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:23 | 08:36 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to For Detect Gas
Leakage of Circuit Breaker and Load Shift to transfer bus.
| 08:23 | 08:36 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to S/D taken for
GCB Gas leakage finding; Load Share by Bus-Coupler
| 08:30 | 12:51 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to 33KV BUS Section 3 shutdown for | [7 empty] | 130.0MW load
|  |  | PBS. | [7 empty] | interrup.
| 08:30 | 12:51 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to 33 KV BUS section 3 shutdown
| 08:38 | 10:23 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D
| 08:40 | 10:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D
| 08:40 | 10:21 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end.
|  | 08:54 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT is restored.
|  | 08:54 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT is restored.
| 08:59 | 10:13 | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end Due to Red
hot maintenance at Ashugonj end
| 09:10 | 09:20 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing D/R Overcurrent Relay & E/F Relay relays | [7 empty] | 53.0MW load
|  |  | Due to Due to PBS Langolbandh Feeder Trip | [7 empty] | interrup.
|  | 09:53 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT is restored.
|  | 09:54 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT is restored.
| 12:00 |  | Day Peak Generation: 14004 MW.
| 12:08 | 12:40 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Mymensingh 132/33kV end showing Distance
Z-1, C-phase, 41.0km at Mymen end. Distance Z-1, (B & C) phase, 1.323 km at Kish end.
relays.
| 12:37 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Low gas pressure
| 13:08 |  | Kachua–Gazaria 230 kV circuits 1, 2, 3, and 4 were charged from the Kachua end at 13:08,
13:08, 13:09, and 13:09 hrs. respectively, for the first time.
| 18:35 |  | Raozan 25 MW PP Synchronized
| 20:00 |  | Evening Peak Generation 15944 MW.
| 01:23 |  | Raozan 25 MW PP Shutdown
| 05:38 | 07:49 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT Scheduled S/D Due to Maintenance
Work
| 05:39 | 07:49 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Scheduled S/D Due to Maintenance
Work
| 06:51 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red-hot maintenance | [7 empty] | 25.0MW load
interrup.
| 06:51 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red-hot maintenance | [7 empty] | 25.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 321 | 8211600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7573500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 7076975 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 256425 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 7493612 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 54432 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.1 | 730800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 1320000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 895861 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 508640 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25.5 | 579600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 491760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 447840 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 1728262 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2205936 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 86 | 1638720 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2280960 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 262186 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 623520 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7668636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1662000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2765.6 | 53711265.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 106983 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128115 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 500160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5217140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5246011 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 342909 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 411392 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 392630 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 490560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 478560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 77 | 383040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20883 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 65236 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 46 | 296100 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 389760 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 71509 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 47 | 90327 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1147 | 26039998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 41 | 720480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 724 | 17701818.18 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2853 | 59093611.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 194 | 4660000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 8411600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 7744000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 41 | 884016 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1096320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 88 | 903272 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1131830 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 128 | 1104000 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1512130 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 173 | 4348800 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1135680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 819331 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 466110 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2009820 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 717360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 2382720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 498055 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1755.2 | 39825044
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 83 | 2000640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 103 | 1723200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 71 | 1862400 | BPDB delayed to fuel purchase payment.
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 347720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 177360 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 270720 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 269 | 6395890
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 59 | 1392000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 137 | 3502064 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714144 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1976640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 3748930 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 12 | 175392 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7323500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 8841000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 250 | 5703900 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2325 | 1424 | 33377570
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21626909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 236 | 6425856 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 381120 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 573120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1106 | 23454540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2337 | 53373545
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7293816 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2724000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1086 | 25284363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5249230 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5826000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4693 | -
Barishal Area Total |  |  |  |  | 2236 | 1963 | 46382102.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 398630 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 312264 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 195088 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4503818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4537245 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 192 | 4539127 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 348 | 8830327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 190870 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 148219 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 655056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 936864 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 108 | 635040 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 755.99 | 17541818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 424504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 666770 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2149.19 | 44552600
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 766000 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1073890 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3846000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 17337984 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34505.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1775041 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 198779 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1283760 | -
Rangpur Area Total |  |  |  |  | 950 | 430 | 26315959.16
Eastern Grid Total |  |  |  |  | 17401.505 | 9066.8 | 192403380.54
Western Grid Total |  |  |  |  | 10442.16 | 6879.19 | 170624206.8
National Grid Total |  |  |  |  | 27843.665 | 15945.99 | 363027587.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-08-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10375.82 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4873.9 | MW
i) Dhaka area |  |  | 5510.94 |  | MW | i) Khulna area |  |  |  | 1799 | MW
ii) Chattogram area |  |  | 1555 |  | MW | ii) Barishal area |  |  |  | 441.5 | MW
iii) Cumilla area |  |  | 1455.88 |  | MW | iii) Rajshahi area |  |  |  | 1611.4 | MW
iv) Mymensingh area |  |  | 1193 |  | MW | iv) Rangpur area |  |  |  | 1022 | MW
v) Sylhet area |  |  | 661 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15249.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 86 | 18:30 | 133 | PHP | 8 | 22:00
2 | AKSML | 20.8 | 00:00 | 68 | Ishurdi | 91 | 19:30 | 134 | Pabna | 132 | 19:30
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 96 | 22:00 | 135 | Palashbari | 106 | 20:00
4 | Agargaon | 143 | 13:00 | 70 | Jamalpur | 137 | 02:00 | 136 | Panchagarh | 67 | 00:00
5 | Agrabad | 98 | 15:00 | 71 | Jashore | 138 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 130 | 19:00 | 138 | Patuakhali | 71 | 22:00
7 | Ashuganj | 98 | 00:00 | 73 | Joydebpur | 167 | 19:00 | 139 | Payra | 34 | 00:00
8 | BSRM | 196 | 19:00 | 74 | Joypurhat | 69 | 00:00 | 140 | Postogola | 58 | 18:30
9 | Bagerhat | 86 | 19:00 | 75 | Juldah | 17 | 14:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 88 | 19:30 | 76 | KSRM | 23 | 06:00 | 142 | Purbasadipur | 131 | 00:00
11 | Bakulia | 95 | 19:00 | 77 | Kabirpur | 244 | 16:00 | 143 | Rahanpur | 45 | 22:00
12 | Banani | 56.8 | 13:00 | 78 | Kachua | 100 | 21:00 | 144 | Rahim | 23 | 17:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 108 | 00:00 | 145 | Rajbari | 85 | 21:00
14 | Barapukuria | 70 | 19:30 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajendrapur | 141 | 21:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 81 | 16:00 | 147 | Rajshahi | 138 | 19:30
16 | Barishal | 113 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 76 | 00:00
17 | Barishal-230 | 110 | 22:00 | 83 | Kasba | 37 | 00:00 | 149 | Ramganj | 118 | 22:00
18 | Baroaulia | 68 | 11:00 | 84 | Kazla | 111 | 13:00 | 150 | Rampur | 41 | 00:00
19 | Baroirhat | 63 | 18:30 | 85 | Keranigonj | 82 | 19:30 | 151 | Rangamati | 18 | 19:00
20 | Bashundhara | 219 | 16:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rangpur | 152 | 19:30
21 | BashundharaCement | 3 | 00:00 | 87 | Khulna | 67 | 19:00 | 153 | Ruppur | 7.4 | 10:00
22 | Beanibazar | 88 | 20:00 | 88 | Khulshi | 172 | 14:00 | 154 | SSM | 12 | 02:00
23 | Benapole | 64 | 00:00 | 89 | Kishoreganj | 146 | 20:00 | 155 | Saidpur | 104 | 15:00
24 | Bhaluka | 156 | 00:00 | 90 | Kodda | 289 | 19:30 | 156 | Satkhira | 132 | 00:00
25 | Bhandaria | 59 | 00:00 | 91 | Kulaura | 61 | 19:00 | 157 | Satmasjid | 104 | 16:00
26 | Bhangura | 40 | 00:00 | 92 | Kurigram | 74 | 21:00 | 158 | Savar | 243 | 15:00
27 | Bheramara(GK) | 70 | 19:00 | 93 | Kushtia | 155 | 00:00 | 159 | SevenRings | 5.59 | 19:30
28 | Bhulta | 206 | 19:30 | 94 | Laksam | 36 | 00:00 | 160 | ShahCement | 11 | 00:00
29 | Bog-Sherpur | 80 | 21:00 | 95 | Lakshmipur | 22 | 22:00 | 161 | Shahjadpur | 90 | 20:00
30 | Bogura | 177 | 23:00 | 96 | Lalbag | 62 | 17:00 | 162 | Shahjibazar | 142 | 22:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 70 | 01:00 | 163 | Shahmirpur | 61 | 00:00
32 | Brahmanbaria | 140 | 00:00 | 98 | MI_Cement | 11.6 | 16:00 | 164 | Shariatpur | 92 | 00:00
33 | Cantonment | 152 | 13:00 | 99 | Madanganj | 41 | 22:00 | 165 | Sherpur | 150 | 00:00
34 | Chandina | 17.14 | 22:00 | 100 | Madaripur | 124 | 00:00 | 166 | Shikalbaha | 14 | 16:00
35 | Chandpur | 84 | 23:00 | 101 | Madartek | 86 | 23:00 | 167 | Shitalakhya | 75.9 | 13:00
36 | Chandraghona | 37 | 18:30 | 102 | Madunaghat | 56 | 19:00 | 168 | Sholosohor | 42 | 16:00
37 | Chapai | 78 | 23:00 | 103 | Magura | 67 | 19:00 | 169 | Shyampur | 156 | 00:00
38 | Charsaidpur | 33 | 00:00 | 104 | Mahasthangarh | 102 | 00:00 | 170 | Siddhirganj | 123 | 12:00
39 | Chauddagram | 76 | 00:00 | 105 | Maijdee | 15 | 21:00 | 171 | Sirajganj | 124 | 20:00
40 | Chhatak | 41 | 00:00 | 106 | Manikganj | 134 | 21:00 | 172 | Sonargaon | 134 | 06:00
41 | Chowmuhani | 202 | 21:00 | 107 | Maniknagar | 88 | 13:00 | 173 | Sreemongol | 86 | 23:00
42 | Chuadanga | 119 | 00:00 | 108 | Matarbari | 54 | 19:00 | 174 | Sreepur | 102 | 19:00
43 | Coxsbazar | 134 | 00:00 | 109 | Matuail | 74 | 15:00 | 175 | Srinagar | 50.68 | 22:00
44 | Cumilla(N) | 151 | 10:00 | 110 | Millgate | 133 | 12:00 | 176 | Sunamganj | 67 | 21:00
45 | Cumilla(S) | 151 | 23:00 | 111 | Mirpur | 131 | 16:00 | 177 | Sylhet | 59 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 15:00 | 178 | Sylhet-132 | 148 | 18:30
47 | Daudkandi | 154 | 19:30 | 113 | Mirzapur | 46 | 00:00 | 179 | TK | 33 | 23:00
48 | Dhaka | 92 | 13:00 | 114 | Mithapukur | 77 | 19:00 | 180 | Tangail | 194 | 19:00
49 | Dhamrai | 122 | 15:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:30
50 | Dhanmondi | 153.4 | 13:00 | 116 | Mogbazar | 150.5 | 16:00 | 182 | Thakurgaon | 121 | 20:00
51 | Dohazari | 116 | 19:30 | 117 | Mongla | 39 | 15:00 | 183 | Tongi | 124 | 11:00
52 | Faridpur | 177 | 23:00 | 118 | Motijheel | 49 | 13:00 | 184 | Ullahpara | 41 | 19:00
53 | Fatullah | 110 | 15:00 | 119 | Muktagacha | 41 | 02:00 | 185 | Ullon | 44 | 00:00
54 | Fenchuganj | 50 | 19:00 | 120 | Munshiganj | 117 | 00:00 | 186 | Uttara | 92 | 13:00
55 | Feni | 122 | 19:00 | 121 | Muradnagar | 46 | 21:00 | 187 | UttaraNew | 65 | 00:00
56 | GPH | 89 | 02:00 | 122 | Mymensingh | 220 | 19:00 | 188 | Zigatola | 76 | 13:00
57 | Ghatail | 84 | 02:00 | 123 | Naogaon | 146 | 00:00
58 | Ghorashal | 15 | 21:00 | 124 | Narail | 61 | 19:00
59 | Ghorashal-230 | 88 | 21:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 191 | 22:00
61 | Gollamari | 94 | 00:00 | 127 | Natore | 157 | 19:30
62 | Gopalganj | 109 | 19:30 | 128 | Nawabganj | 57.2 | 00:00
63 | Gulshan | 140 | 13:00 | 129 | Netrakona | 151 | 19:00
64 | Halishahar | 69 | 10:00 | 130 | New | 71.6 | 12:00
65 | HaripurSBU | 170 | 17:00 | 131 | Niamatpur | 82 | 00:00
66 | Hasnabad | 98 | 16:00 | 132 | Noapara | 48 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15699 | 144 |  | 15849.48
1:00 | 15036 | 135 |  | 15177.08
2:00 | 14482 | 48 |  | 14532.16
3:00 | 14055 | 41 |  | 14097.85
4:00 | 13475 | 0 |  | 13475
5:00 | 13306 | 0 |  | 13306
6:00 | 12997 | 0 |  | 12997
7:00 | 12961 | 0 |  | 12961
8:00 | 13012 | 0 |  | 13012
9:00 | 12967 | 0 |  | 12967
10:00 | 13227 | 0 |  | 13227
11:00 | 13568 | 0 |  | 13568
12:00 | 14011 | 0 |  | 14011
13:00 | 14269 | 0 |  | 14269
14:00 | 14322 | 0 |  | 14322
15:00 | 14530 | 0 |  | 14530
16:00 | 14435 | 0 |  | 14435
17:00 | 14215 | 0 |  | 14215
18:00 | 13743 | 0 |  | 13743
19:00 | 15467.7 | 79 |  | 15550.26
19:30 | 15890.69 | 154 |  | 16051.62
20:00 | 15945.99 | 197 |  | 16151.86
21:00 | 15755.7 | 186 |  | 15950.07
22:00 | 15562.6 | 104 |  | 15671.6
23:00 | 15563 | 122 |  | 15690
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8731 | 6968 | 15699 | DAILY GENERATION CURVE
00:30 | 8514 | 6853.5 | 15367.5
01:00 | 8297 | 6739 | 15036 | 18-08-2025
01:30 | 8074.5 | 6684.5 | 14759
02:00 | 7852 | 6630 | 14482
02:30 | 7744 | 6524.5 | 14268.5
03:00 | 7636 | 6419 | 14055
03:30 | 7430 | 6335 | 13765
04:00 | 7224 | 6251 | 13475
04:30 | 7187.5 | 6203 | 13390.5
05:00 | 7151 | 6155 | 13306
05:30 | 7105.5 | 6046 | 13151.5
06:00 | 7060 | 5937 | 12997
06:30 | 7082.5 | 5896.5 | 12979
07:00 | 7105 | 5856 | 12961
07:30 | 7090.5 | 5896 | 12986.5
08:00 | 7076 | 5936 | 13012
08:30 | 7007 | 5982.5 | 12989.5
09:00 | 6938 | 6029 | 12967
09:30 | 7036 | 6061 | 13097
10:00 | 7134 | 6093 | 13227
10:30 | 7252.5 | 6145 | 13397.5
11:00 | 7371 | 6197 | 13568
11:30 | 7546.5 | 6243 | 13789.5
12:00 | 7722 | 6289 | 14011
12:30 | 7770.5 | 6369.5 | 14140
13:00 | 7819 | 6450 | 14269
13:30 | 7878.5 | 6417 | 14295.5
14:00 | 7938 | 6384 | 14322
14:30 | 8000.5 | 6425.5 | 14426
15:00 | 8063 | 6467 | 14530
15:30 | 8122 | 6360.5 | 14482.5
16:00 | 8181 | 6254 | 14435
16:30 | 8227 | 6098 | 14325
17:00 | 8273 | 5942 | 14215
17:30 | 8187.5 | 5791.5 | 13979
18:00 | 8102 | 5641 | 13743
18:30 | 8489.25 | 6116.1 | 14605.35
19:00 | 8876.5 | 6591.2 | 15467.7
19:30 | 8968.7 | 6921.99 | 15890.69
20:00 | 9066.8 | 6879.19 | 15945.99
20:30 | 9020.25 | 6830.595 | 15850.845 |  | Executive Engineer
21:00 | 8973.7 | 6782 | 15755.7 |  | Network Operation Division
21:30 | 8842.15 | 6817 | 15659.15
22:00 | 8710.6 | 6852 | 15562.6
22:30 | 8651.3 | 6911.5 | 15562.8
23:00 | 8592 | 6971 | 15563

## En-Curve
QF-LDC-12
Date | 18-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4143 | 1946 | 868 | 38 | 50 | 765 | 220 | 4952 | 0 | 683 | 2022 | 0 | 0 | 12 | 144 | DAILY ENERGY CURVE
00:30 | 4102.5 | 1884 | 867.5 | 38 | 48 | 768.5 | 219 | 4919.5 | 0 | 647 | 1859.5 | 0 | 0 | 14 | 139.5 | 18-08-2025
01:00 | 4062 | 1822 | 867 | 38 | 46 | 772 | 218 | 4887 | 0 | 611 | 1697 | 0 | 0 | 16 | 135
01:30 | 4108.5 | 1831.5 | 867.5 | 38 | 45 | 768 | 218 | 4914.5 | 0 | 443 | 1506.5 | 0 | 0 | 18.5 | 91.5 | Energy Generated | 363.0276 |  | MKWHr
02:00 | 4155 | 1841 | 868 | 38 | 44 | 764 | 218 | 4942 | 0 | 275 | 1316 | 0 | 0 | 21 | 48 | Energy not Served | 1.056 |  | MKWHr
02:30 | 4085 | 1846.5 | 868.5 | 38 | 44 | 769 | 216 | 4846.5 | 0 | 250 | 1289.5 | 0 | 0 | 15.5 | 44.5 | Total Energy Requirement | 364.0836 |  | MKWHr
03:00 | 4015 | 1852 | 869 | 38 | 44 | 774 | 214 | 4751 | 0 | 225 | 1263 | 0 | 0 | 10 | 41
03:30 | 3996.5 | 1850.5 | 869 | 38 | 43 | 769 | 214 | 4734 | 0 | 158 | 1076.5 | 0 | 0 | 16.5 | 20.5
04:00 | 3978 | 1849 | 869 | 38 | 42 | 764 | 214 | 4717 | 0 | 91 | 890 | 0 | 0 | 23 | 0
04:30 | 4007.5 | 1851.5 | 878 | 38 | 42 | 721 | 214 | 4659 | 0 | 69.5 | 881 | 0 | 0 | 29 | 0
05:00 | 4037 | 1854 | 887 | 38 | 42 | 678 | 214 | 4601 | 0 | 48 | 872 | 0 | 0 | 35 | 0
05:30 | 4002.5 | 1858.5 | 886.5 | 38 | 41 | 678 | 214 | 4512 | 10.5 | 53.5 | 827 | 0 | 0 | 30 | 0
06:00 | 3968 | 1863 | 886 | 38 | 40 | 678 | 214 | 4423 | 21 | 59 | 782 | 0 | 0 | 25 | 0
06:30 | 3987.5 | 1868 | 886.5 | 38 | 39 | 651.5 | 210.5 | 4380 | 64.5 | 83 | 752.5 | 0 | 0 | 18 | 0
07:00 | 4007 | 1873 | 887 | 38 | 38 | 625 | 207 | 4337 | 108 | 107 | 723 | 0 | 0 | 11 | 0
07:30 | 3995.5 | 1849.5 | 892.5 | 38 | 37 | 621 | 207 | 4318 | 191 | 107 | 718 | 0 | 0 | 12 | 0
08:00 | 3984 | 1826 | 898 | 38 | 36 | 617 | 207 | 4299 | 274 | 107 | 713 | 0 | 0 | 13 | 0
08:30 | 3931 | 1812.5 | 898 | 38 | 36 | 617.5 | 207 | 4284.5 | 375.5 | 92 | 682.5 | 0 | 0 | 15 | 0
09:00 | 3878 | 1799 | 898 | 38 | 36 | 618 | 207 | 4270 | 477 | 77 | 652 | 0 | 0 | 17 | 0
09:30 | 3908.5 | 1822 | 898 | 38 | 37 | 646 | 207 | 4257 | 513.5 | 77 | 670 | 0 | 0 | 23 | 0
10:00 | 3939 | 1845 | 898 | 38 | 38 | 674 | 207 | 4244 | 550 | 77 | 688 | 0 | 0 | 29 | 0
10:30 | 3967.5 | 1837.5 | 898 | 38 | 46 | 667.5 | 207 | 4241 | 589 | 100.5 | 733 | 40 | 0 | 32.5 | 0
11:00 | 3996 | 1830 | 898 | 38 | 54 | 661 | 207 | 4238 | 628 | 124 | 778 | 80 | 0 | 36 | 0
11:30 | 4056.5 | 1827.5 | 898 | 38 | 56 | 704.5 | 212.5 | 4290 | 593 | 152 | 801 | 122.5 | 0 | 38 | 0
12:00 | 4117 | 1825 | 898 | 38 | 58 | 748 | 218 | 4342 | 558 | 180 | 824 | 165 | 0 | 40 | 0
12:30 | 4130 | 1814 | 898 | 38 | 60 | 757.5 | 218 | 4365 | 608 | 196 | 842 | 166 | 0 | 47.5 | 0
13:00 | 4143 | 1803 | 898 | 38 | 62 | 767 | 218 | 4388 | 658 | 212 | 860 | 167 | 0 | 55 | 0
13:30 | 4169.5 | 1805 | 897.5 | 38 | 60 | 764 | 218 | 4431.5 | 606.5 | 211.5 | 870 | 167 | 0 | 57 | 0
14:00 | 4196 | 1807 | 897 | 38 | 58 | 761 | 218 | 4475 | 555 | 211 | 880 | 167 | 0 | 59 | 0
14:30 | 4199.5 | 1834.5 | 897 | 38 | 59 | 762 | 218.5 | 4537.5 | 466.5 | 221 | 981 | 169 | 0 | 42.5 | 0
15:00 | 4203 | 1862 | 897 | 38 | 60 | 763 | 219 | 4600 | 378 | 231 | 1082 | 171 | 0 | 26 | 0
15:30 | 4080 | 1836 | 900.5 | 38 | 57 | 759.5 | 219.5 | 4627.5 | 339 | 231 | 1270.5 | 93.5 | 0 | 30.5 | 0
16:00 | 3957 | 1810 | 904 | 38 | 54 | 756 | 220 | 4655 | 300 | 231 | 1459 | 16 | 0 | 35 | 0
16:30 | 3909 | 1813.5 | 903.5 | 38 | 50 | 758.5 | 220 | 4532 | 226.5 | 246 | 1576 | 8 | 0 | 44 | 0
17:00 | 3861 | 1817 | 903 | 38 | 46 | 761 | 220 | 4409 | 153 | 261 | 1693 | 0 | 0 | 53 | 0
17:30 | 3747 | 1817 | 903.5 | 38 | 44 | 764 | 220.5 | 4301.5 | 88.5 | 281 | 1726 | 0 | 0 | 48 | 0
18:00 | 3633 | 1817 | 904 | 38 | 42 | 767 | 221 | 4194 | 24 | 301 | 1759 | 0 | 0 | 43 | 0
18:30 | 3867 | 1881.25 | 903.5 | 38 | 44 | 766 | 221 | 4374.5 | 12 | 445 | 2016.1 | 0 | 0 | 37 | 39.5
19:00 | 4101 | 1945.5 | 903 | 38 | 46 | 765 | 221 | 4555 | 0 | 589 | 2273.2 | 0 | 0 | 31 | 79
19:30 | 3944 | 1869.5 | 904 | 38 | 48 | 758.79 | 221 | 4885 | 0 | 618 | 2556.4 | 0 | 0 | 48 | 154
20:00 | 3940 | 1880.5 | 904 | 38 | 46 | 755.99 | 221 | 4847 | 0 | 648 | 2624.5 | 0 | 0 | 41 | 197
20:30 | 4024 | 1918 | 904 | 38 | 47 | 756.495 | 221.5 | 4783.5 | 0 | 651 | 2471.85 | 0 | 0 | 35.5 | 191.5
21:00 | 4108 | 1955.5 | 904 | 38 | 48 | 757 | 222 | 4720 | 0 | 654 | 2319.2 | 0 | 0 | 30 | 186
21:30 | 4121.5 | 1964.65 | 904 | 38 | 49 | 753 | 222 | 4781 | 0 | 640 | 2152 | 0 | 0 | 34 | 145
22:00 | 4135 | 1973.8 | 904 | 38 | 50 | 749 | 222 | 4842 | 0 | 626 | 1984.8 | 0 | 0 | 38 | 104
22:30 | 4112.5 | 1934 | 904 | 38 | 50 | 752.5 | 221 | 4930.5 | 0 | 626 | 1968.3 | 0 | 0 | 26 | 113
23:00 | 4090 | 1894.2 | 904 | 38 | 50 | 756 | 220 | 5019 | 0 | 626 | 1951.8 | 0 | 0 | 14 | 122
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 18:00 | 368 | 15:00 | Payra | 413 | 18:00 | 408 | 00:00
Ashuganj | 403 | 6:00 | 368 | 15:00 | Rahanpur | 400 | 18:30 | 391 | 22:00
Bhulta | 402 | 06:00 | 366 | 15:00 | Rampal | 406 | 18:00 | 391 | 22:00
Bibiana | 389 | 18:00 | 381 | 15:00
BIPTC | 402 | 06:00 | 389 | 22:00
Bogura | 386 | 18:30 | 375 | 22:00
Gopalganj | 397 | 18:00 | 386 | 22:00
Kaliakoir | 374 | 18:00 | 358 | 15:00
Madunaghat | 391 | 18:00 | 384 | 15:00
Meghnaghat | 384 | 08:00 | 372 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 213 | 15:00 | Keranigonj | 221 | 06:00 | 210 | 15:00
AKSML | 231 | 19:30 | 221 | 15:00 | Khulna(S) | 229 | 18:00 | 218 | 22:00
Aminbazar | 224 | 04:00 | 214 | 14:00 | Madunaghat | 232 | 18:00 | 224 | 14:00
Ashuganj | 230 | 06:00 | 216 | 15:00 | Madunaghat-400 | 231 | 19:00 | 225 | 15:00
Ashuganj-400 | 230 | 06:00 | 216 | 15:00 | Maniknagar | 218 | 05:00 | 210 | 15:00
Baghabari | 234 | 18:00 | 226 | 22:00 | Meghnaghat | 225 | 07:00 | 219 | 11:00
Barapukuria | 227 | 18:30 | 220 | 22:00 | Meghnaghat-400 | 222 | 03:00 | 215 | 15:00
Barapukuria-230 | 227 | 18:30 | 220 | 22:00 | Mirsorai | 226 | 20:00 | 218 | 15:00
Barishal | 228 | 18:00 | 219 | 23:00 | Rajshahi | 230 | 18:30 | 220 | 22:00
Bheramara | 231 | 18:00 | 221 | 22:00 | Rampal | 231 | 18:00 | 219 | 22:00
Bhulta | 226 | 06:00 | 203 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 03:00 | 221 | 15:00 | Rampura | 225 | 06:00 | 199 | 15:00
BIPTC | 234 | 09:00 | 222 | 22:00 | Shikalbaha | 229 | 19:30 | 222 | 15:00
Bogura | 239 | 18:00 | 232 | 22:00 | Shyampur | 220 | 07:00 | 211 | 15:00
Bogura-400 | 239 | 18:00 | 232 | 22:00 | Siddhirganj | 218 | 01:00 | 213 | 12:00
Borhanuddin | 232 | 07:00 | 226 | 00:00 | Sirajgonj | 241 | 18:00 | 234 | 12:00
BSRM | 225 | 19:30 | 219 | 13:00 | Sreepur | 230 | 18:00 | 218 | 13:00
Cumilla(N) | 224 | 18:00 | 213 | 15:00 | Tongi | 226 | 04:00 | 213 | 11:00
Faridpur | 226 | 18:00 | 215 | 23:00
Fenchuganj | 229 | 05:00 | 223 | 15:00
Ghorashal | 230 | 00:00 | 220 | 13:00
Ghorashal-230 | 225 | 03:00 | 207 | 15:00
Gopalganj | 226 | 18:00 | 218 | 22:00
GPH | 227 | 19:30 | 220 | 15:00
Haripur | 219 | 03:00 | 212 | 15:00
Hasnabad | 221 | 04:00 | 211 | 14:00
Hathazari | 228 | 07:00 | 218 | 15:00
Ishurdi | 234 | 18:30 | 224 | 22:00
Jhenaidah | 229 | 09:00 | 216 | 22:00
Kaliakoir | 232 | 18:00 | 219 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 18:00 | 120 | 14:00 | Lalmonirhat | 130 | 16:00 | 122 | 11:00
Agargaon | 131 | 06:00 | 122 | 15:00 | Madanganj | 128 | 18:30 | 123 | 10:00
Agrabad | 129 | 06:00 | 124 | 14:00 | Madaripur | 134 | 09:00 | 128 | 00:00
AKS | 129 | 18:00 | 123 | 15:00 | Madartek | 136 | 21:00 | 120 | 15:00
Aminbazar | 132 | 00:00 | 125 | 14:00 | Madunaghat | 131 | 18:00 | 126 | 15:00
Amnura | 136 | 08:00 | 127 | 13:00 | Magura | 133 | 09:00 | 121 | 00:00
Ashuganj | 142 | 18:00 | 132 | 15:00 | Mahasthangarh | 131 | 18:00 | 125 | 22:00
Bagerhat | 131 | 08:00 | 121 | 00:00 | Maijdee | 124 | 18:30 | 111 | 00:00
Bajitpur | 129 | 04:00 | 123 | 14:00 | Manikganj | 126 | 06:00 | 116 | 15:00
Bakulia | 131 | 07:00 | 125 | 15:00 | Maniknagar | 132 | 06:00 | 124 | 13:00
Banani | 140 | 15:00 | 122 | 11:00 | Matarbari | 118 | 07:00 | 111 | 23:00
Bangabhaban | 132 | 06:00 | 124 | 13:00 | Matuail | 128 | 03:00 | 122.6 | 15:00
Barapukuria | 138 | 18:30 | 130 | 19:30 | Millgate | 132 | 06:00 | 119 | 15:00
Barguna | 134 | 09:00 | 129 | 00:00 | Mirpur | 130 | 00:00 | 123 | 15:00
Barishal | 135 | 18:00 | 126 | 22:00 | Mirzapur | 129 | 03:00 | 122 | 15:00
Barishal-230 | 134 | 18:00 | 127 | 22:00 | Mithapukur | 123 | 04:00 | 112 | 22:00
Baroaulia | 130 | 18:00 | 127 | 12:00 | MI_Cement | 128 | 04:00 | 123 | 12:00
Baroirhat | 128 | 18:00 | 117 | 15:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 05:00 | 120 | 15:00 | Mogbazar | 136 | 05:00 | 121 | 15:00
BashundharaCement | 128 | 18:30 | 123 | 10:00 | Mongla | 132 | 18:00 | 122 | 00:00
Beanibazar | 131 | 07:00 | 122 | 15:00 | Motijheel | 132 | 06:00 | 124 | 13:00
Benapole | 131 | 18:00 | 120 | 00:00 | Muktagacha | 134 | 09:00 | 123 | 23:00
Bhaluka | 129 | 18:00 | 120 | 15:00 | Munshiganj | 128 | 20:00 | 122 | 15:00
Bhandaria | 130 | 17:00 | 118 | 00:00 | Muradnagar | 124 | 18:00 | 116 | 15:00
Bhangura | 132 | 18:00 | 128 | 13:00 | Mymensingh | 137 | 03:00 | 112 | 19:00
Bheramara | 137 | 18:00 | 131 | 21:00 | Naogaon | 130 | 18:30 | 123 | 22:00
Bheramara(GK) | 137 | 18:30 | 131 | 22:00 | Narail | 134 | 09:00 | 118 | 00:00
Bhulta | 124 | 18:00 | 120 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 133 | 11:00 | 127 | 22:00 | Narshingdi | 134 | 00:00 | 119 | 11:00
Bogura | 133 | 18:00 | 128 | 22:00 | Natore | 133 | 18:30 | 127 | 21:00
Bogura-230 | 134 | 18:00 | 129 | 22:00 | Nawabganj | 132 | 05:00 | 124 | 15:00
Brahmanbaria | 137 | 18:00 | 126 | 15:00 | Netrakona | 125 | 02:00 | 108 | 18:30
Cantonment | 130 | 05:00 | 122 | 15:00 | New | 132 | 18:00 | 119 | 15:00
Chandina | 129 | 18:00 | 121 | 15:00 | Niamatpur | 136 | 06:00 | 132 | 23:00
Chandpur | 133 | 18:00 | 125 | 00:00 | Noapara | 134 | 18:00 | 124 | 00:00
Chandraghona | 132 | 18:00 | 128 | 12:00 | Pabna | 133 | 09:00 | 127 | 23:00
Chapai | 136 | 18:00 | 131 | 22:00 | Palashbari | 123 | 03:00 | 110 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 20:00 | 123 | 12:00 | Panchagarh | 139 | 18:30 | 124 | 07:00
Chauddagram | 124 | 17:00 | 118 | 15:00 | Patiya | 130 | 18:30 | 125 | 13:00
Chhatak | 127 | 06:00 | 119 | 20:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chowmuhani | 124 | 18:00 | 112 | 00:00 | Payra | 136 | 18:00 | 132 | 00:00
Chuadanga | 132 | 09:00 | 119 | 00:00 | PHP | 125 | 18:00 | 116 | 15:00
Coxsbazar | 120 | 18:00 | 111 | 00:00 | Postogola | 130 | 05:00 | 124 | 15:00
Cumilla(N) | 130 | 18:00 | 122 | 14:00 | Purbachal | 136 | 21:00 | 120 | 15:00
Cumilla(S) | 132 | 03:00 | 120 | 15:00 | Purbasadipur | 134 | 18:30 | 121 | 00:00
Daganbhuiyan | 125 | 18:00 | 113 | 15:00 | Rahanpur | 139 | 16:00 | 133 | 22:00
Daudkandi | 121 | 18:00 | 113 | 15:00 | Rahanpur-400 | 138 | 18:30 | 134 | 22:00
Dhaka | 136 | 21:00 | 122 | 15:00 | Rahim | 128 | 05:00 | 123 | 12:00
Dhamrai | 135 | 08:00 | 123 | 15:00 | Rajbari | 133 | 18:00 | 125 | 22:00
Dhanmondi | 136 | 21:00 | 119 | 15:00 | Rajendrapur | 132 | 03:00 | 120 | 10:00
Dohazari | 127 | 17:00 | 121 | 15:00 | Rajshahi | 134 | 04:00 | 127 | 15:00
Faridpur | 134 | 18:00 | 128 | 00:00 | Rajshahi-230 | 133 | 18:30 | 127 | 13:00
Fatullah | 129 | 03:00 | 124 | 12:00 | Ramganj | 127 | 18:00 | 115 | 15:00
Fenchuganj | 136 | 06:00 | 131 | 15:00 | Rampur | 130 | 19:30 | 124 | 14:00
Feni | 126 | 18:00 | 115 | 15:00 | Rampura | 135 | 06:00 | 120 | 15:00
Ghatail | 129 | 06:00 | 119 | 23:00 | Rangamati | 131 | 18:00 | 126 | 15:00
Ghorashal | 137 | 18:00 | 126 | 11:00 | Rangpur | 134 | 16:00 | 128 | 08:00
Goalpara | 136 | 18:00 | 127 | 00:00 | Ruppur | 137 | 18:00 | 131 | 22:00
Gollamari | 136 | 18:00 | 127 | 01:00 | Saidpur | 133 | 16:00 | 122 | 00:00
Gopalganj | 134 | 18:00 | 127 | 00:00 | Satkhira | 133 | 18:00 | 121 | 00:00
Gopalganj-400 | 136 | 18:00 | 130 | 22:00 | Satmasjid | 131 | 07:00 | 121 | 15:00
Gulshan | 136 | 21:00 | 120 | 15:00 | Savar | 131 | 00:00 | 124 | 10:00
Halishahar | 132 | 21:00 | 125 | 15:00 | SevenRings | 136 | 18:00 | 123 | 15:00
Haripur | 128 | 03:00 | 123 | 15:00 | ShahCement | 129 | 05:00 | 123 | 12:00
HaripurSBU | 128 | 02:00 | 123 | 17:00 | Shahjadpur | 135 | 02:00 | 134 | 00:00
Hasnabad | 130 | 01:00 | 125 | 12:00 | Shahjibazar | 135 | 18:00 | 126 | 15:00
Hathazari | 132 | 05:00 | 127 | 13:00 | Shahmirpur | 132 | 18:00 | 126 | 14:00
Ishurdi | 137 | 09:00 | 131 | 22:00 | Shariatpur | 133 | 18:00 | 124 | 23:00
Jaldhaka | 132 | 16:00 | 119 | 00:00 | Sherpur | 133 | 09:00 | 120 | 23:00
Jamalpur | 136 | 03:00 | 124 | 19:00 | Shikalbaha | 120 | 06:00 | 113 | 15:00
Jashore | 130 | 09:00 | 119 | 00:00 | Shikalbaha-230 | 132 | 17:00 | 127 | 15:00
Jhenaidah | 135 | 18:00 | 121 | 22:00 | Shitalakhya | 128 | 04:00 | 123 | 12:00
Jhenaidah-230 | 135 | 09:00 | 125 | 00:00 | Sholosohor | 130 | 06:00 | 126 | 15:00
Joydebpur | 135 | 18:00 | 118 | 15:00 | Shyampur | 130 | 18:00 | 124 | 12:00
Joypurhat | 128 | 18:00 | 120 | 22:00 | Shyampur-230 | 129 | 03:00 | 123 | 15:00
Juldah | 132 | 18:00 | 125 | 15:00 | Siddhirganj | 128 | 01:00 | 124 | 12:00
Kabirpur | 133 | 19:30 | 120 | 10:00 | Sirajganj | 130 | 08:00 | 124 | 22:00
Kachua | 129 | 18:00 | 122 | 00:00 | Sonargaon | 126 | 06:00 | 121 | 11:00
Kaliakoir | 133 | 01:00 | 126 | 15:00 | Sreemongol | 133 | 07:00 | 126 | 15:00
Kallyanpur | 131 | 00:00 | 125 | 13:00 | Sreepur | 132 | 18:00 | 125 | 13:00
Kalurghat | 130 | 06:00 | 127 | 12:00 | Srinagar | 132 | 06:00 | 125 | 15:00
Kamrangirchar | 133 | 07:00 | 125 | 15:00 | SSM | 132 | 05:00 | 129 | 15:00
Kaptai | 133 | 8:00 | 130 | 15:00 | Sunamganj | 123 | 07:00 | 117 | 01:00
Kasba | 125 | 18:00 | 117 | 14:00 | Sylhet | 130 | 08:00 | 124 | 15:00
Kazla | 131 | 02:00 | 124 | 13:00 | Sylhet-132 | 129 | 06:00 | 124 | 15:00
Keranigonj | 133 | 06:00 | 125 | 15:00 | Tangail | 127 | 08:00 | 119 | 22:00
Khagrachori | 130 | 07:00 | 125 | 15:00 | Taraganj | 133 | 16:00 | 124 | 00:00
Khulna | 135 | 18:00 | 127 | 00:00 | Thakurgaon | 138 | 18:30 | 121 | 07:00
Khulna(S) | 136 | 18:00 | 128 | 00:00 | TK | 131 | 18:00 | 126 | 15:00
Khulshi | 129 | 18:00 | 124 | 14:00 | Tongi | 133 | 00:00 | 126 | 11:00
Kishoreganj | 128 | 18:00 | 119 | 15:00 | Ullahpara | 132 | 09:00 | 127 | 22:00
Kodda | 133 | 18:00 | 117 | 15:00 | Ullon | 135 | 06:00 | 120 | 15:00
KSRM | 132 | 23:00 | 127 | 00:00 | Uttara | 130 | 01:00 | 122 | 15:00
Kulaura | 134 | 06:00 | 129 | 15:00 | UttaraNew | 130 | 06:00 | 124 | 14:00
Kurigram | 130 | 16:00 | 123 | 21:00 | Zigatola | 133 | 07:00 | 125 | 13:00
Kushtia | 133 | 18:00 | 125 | 22:00
Laksam | 130 | 18:30 | 121 | 00:00
Lakshmipur | 124 | 18:00 | 112 | 15:00
Lalbag | 132 | 06:00 | 124 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division