## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-08-2025 | during | 21-08-2025 | during | 21-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 395 | 322 | 400.75 | 400.75 | 368 | 368 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 300.01 | 300.01 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 295 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 45 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 111 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 37 | 54 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 22 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 20 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 69 | 68 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 137 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 350 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2020.5 | 2501 | 5797.34 | 5806.34 | 3851.48 | 3876.48
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 219 | 214 | 214 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 58 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 66 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 30 | 49 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 17 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 85 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.69 | 0 | 4.1 | 0 | 4.1 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 40 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1094 | 1150 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 22 | 44 | 48 | 19 | 48 | 19 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 740 | 702 | 720 | 720 | 760 | 760 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2395.69 | 2784 | 3801.82 | 3780.72 | 3648.82 | 3640.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 330 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 40 | 46.7 | 46.7 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 45 | 55 | 55 | 47 | 47 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 60 | 8 | 195 | 195 | 71 | 71 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 120 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 172 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 20 | 20 | Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 96 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 61 | 61 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 100 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 78 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1457 | 1724.2 | 2427.81 | 2372.81 | 2115.36 | 2060.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-08-2025 | during | 21-08-2025 | during | 21-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 71 | 157.5 | 157.5 | 105 | 105 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 76 | 96 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 73 | 82 | 95 | 103 | 95 | 103 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9.27 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | Liquid fuel Shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 34 | Liquid fuel Shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 248.27 | 278 | 427 | 412 | 327 | 329
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 59 | 60 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 156 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 161 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 15 | 25 | 25 | 11 | 11 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 393 | 367 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1210 | 1182 | 1206 | 1206 | 1112 | 1112
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 172 | 153 | 410 | 410 | 223 | 223 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 12 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 19.7 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 927 | 1175 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2032.7 | 2255 | 3256.2 | 3216.2 | 2897 | 2857
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 296 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 835 | 1190 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 248 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1653.51 | 2104 | 2162 | 2161 | 2117 | 2116
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 14.63 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 8 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 150 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 140 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 144 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 395 | 345 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.91 | 0 | 5.4 | 0 | 5.4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 762 | 755.47 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.23 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 46 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1808.77 | 1855.47 | 2469.39 | 2307.99 | 2428.01 | 2266.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 46 | 0 | 0 | 45 | 45 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 154 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 102 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 70 | 0 | 111.96 | 0 | 111.96 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 391.5 | 417 | 546.56 | 398 | 601.56 | 453
System Total |  |  |  |  | 28821.2 | 27843.665 | 13217.94 | 15100.67 | 22094.12 | 21661.06 | 19098.23 | 18711.17
Forecast Scenario (21-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14750 |  | 0 |  | 14750
|  |  |  | 1:00 | 14500 |  | 0 |  | 14500
|  |  |  | 2:00 | 14100 |  | 0 |  | 14100
|  |  |  | 3:00 | 13760 |  | 0 |  | 13760
|  |  |  | 4:00 | 13490 |  | 0 |  | 13490
|  |  |  | 5:00 | 13200 |  | 0 |  | 13200
|  |  |  | 6:00 | 12600 |  | 0 |  | 12600
|  |  |  | 7:00 | 12450 |  | 0 |  | 12450
|  |  |  | 8:00 | 12280 |  | 0 |  | 12280
|  |  |  | 9:00 | 12450 |  | 0 |  | 12450
|  |  |  | 10:00 | 12790 |  | 0 |  | 12790
|  |  |  | 11:00 | 12970 |  | 0 |  | 12970
|  |  |  | 12:00 | 13210 |  | 0 |  | 13210
|  |  |  | 13:00 | 13660 |  | 0 |  | 13660
|  |  |  | 14:00 | 13560 |  | 0 |  | 13560
|  |  |  | 15:00 | 13680 |  | 0 |  | 13680
|  |  |  | 16:00 | 13540 |  | 0 |  | 13540
|  |  |  | 17:00 | 13240 |  | 0 |  | 13240
|  |  |  | 18:00 | 12620 |  | 0 |  | 12620
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14190 |  | 0 |  | 14190
|  |  |  | 19:30 | 15100 |  | 0 |  | 15100
|  |  |  | 20:00 | 15010 |  | 0 |  | 15010
|  |  |  | 21:00 | 14930 |  | 0 |  | 14930
|  |  |  | 22:00 | 14820 |  | 0 |  | 14820
|  |  |  | 23:00 | 14800 |  | 0 |  | 14800
Probable Maximum Temperature: |  |  | 31.30°C
Probable Maximum Demand at Day Peak: |  |  | 13210.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 326.60 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:35 hrs on 21-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-08-2025 | [28 empty] | Date: | 20-08-2025 | [28 empty] | Date: | 20-08-2025 | [28 empty] | Date: | 20-08-2025 | [28 empty] | Date: | 20-08-2025 | [13 empty] | Date: | 20-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [13 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 46 | 54 | 0 | 110 | 75 | 15 | 55 | 145 | 0 | 300 | 290 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 21.5 | 22 | 0 | 350 | 0 | 0 | 75 | 0 | 24 | 49 | 74 | 0 | 12 | 12 | 0 | 221 | 32 | 27 | 752 | 0 | 0 | 33 | 0 | 49 | 223 | 0 | 0 | 0 | 1135 | 0 | 51 | 50 | 8 | 0 | 354 | 330 | 46 | 193 | 38 | 109 | 50 | 173 | 57 | 14 | 88 | 50 | 52.2 | 0 | 0 | 300 | 30 | 314 | 0 | 60 | 154 | 11 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 101 | 76 | 72 | 0 | 0 | 10 | 8214.7 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 17 | 763.76 | 0 | 40 | 0 | 0 | 50 | 0 | 87 | 37 | 0 | 0 | 0 | 27 | 0 | 191 | 0 | 180 | 0 | 180 | 0 | 344 | 0 | 0 | 155 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 303 | 1220 | 0 | 6831.76 | 15046.46 | 108.25
01:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 44 | 54 | 71 | 78 | 0 | 0 | 55 | 143 | 0 | 300 | 294 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 108 | 20.5 | 15 | 0 | 350 | 0 | 0 | 70 | 0 | 17 | 49 | 36 | 0 | 12 | 12 | 0 | 220 | 31 | 30 | 752 | 0 | 0 | 33 | 0 | 46 | 223 | 0 | 0 | 0 | 1150 | 0 | 51 | 12 | 8 | 0 | 355 | 330 | 47 | 198 | 38 | 115 | 50 | 173 | 57 | 14 | 88 | 48 | 52.2 | 0 | 0 | 300 | 0 | 332 | 0 | 60 | 151 | 11 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 93 | 57 | 72 | 0 | 0 | 0 | 8009.7 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 14 | 768 | 0 | 0 | 0 | 0 | 50 | 0 | 87 | 0 | 0 | 0 | 0 | 27 | 0 | 180 | 0 | 172 | 0 | 172 | 0 | 354 | 0 | 0 | 158 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 303 | 1150 | 0 | 6662 | 14671.7 | 108.26
02:00 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35.2 | 35 | 133 | 78 | 0 | 0 | 51 | 90 | 0 | 300 | 295 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 108 | 20.5 | 22 | 0 | 350 | 0 | 0 | 32 | 0 | 20 | 49 | 0 | 0 | 12 | 12 | 0 | 221 | 33 | 32 | 753 | 0 | 0 | 12 | 0 | 48 | 223 | 0 | 0 | 0 | 1147 | 0 | 51 | 12 | 8 | 0 | 354 | 330 | 47 | 207 | 38 | 101 | 50 | 176 | 55 | 14 | 88 | 46 | 52.2 | 0 | 0 | 310 | 0 | 334 | 0 | 60 | 156 | 11 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 91 | 57 | 73 | 0 | 0 | 0 | 7891.9 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 172 | 0 | 171 | 0 | 359 | 0 | 0 | 151 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 303 | 1110 | 0 | 6373 | 14264.9 | 108.26
03:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 27.6 | 17 | 105 | 78 | 0 | 0 | 32 | 35 | 0 | 300 | 290 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 49 | 0 | 0 | 12 | 12 | 0 | 221 | 30 | 32 | 755 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 48 | 215 | 35 | 93 | 51 | 173 | 62 | 14 | 88 | 44 | 52.2 | 0 | 0 | 305 | 0 | 313 | 0 | 60 | 152 | 11 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 91 | 57 | 87 | 0 | 0 | 0 | 7577.3 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 172 | 0 | 171 | 0 | 344 | 0 | 0 | 152 | 45 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 304 | 1102 | 0 | 6267 | 13844.3 | 108.27
04:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 60 | 62 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 21 | 49 | 0 | 0 | 12 | 12 | 0 | 221 | 0 | 32 | 753 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 47 | 215 | 35 | 93 | 51 | 173 | 61 | 14 | 88 | 42 | 52.2 | 0 | 0 | 310 | 0 | 316 | 0 | 60 | 153 | 11 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 92 | 56 | 87 | 0 | 0 | 3 | 7385.7 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 172 | 0 | 171 | 0 | 350 | 0 | 0 | 152 | 45 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 115 | 220 | 0 | 305 | 1100 | 0 | 6157 | 13542.7 | 108.27
05:00 | 0 | 70 | 12 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 300 | 290 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 20.5 | 16 | 0 | 350 | 0 | 0 | 0 | 0 | 32 | 49 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 37 | 753 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 48 | 216 | 35 | 68 | 51 | 179 | 63 | 14 | 70 | 44 | 25 | 0 | 0 | 310 | 0 | 316 | 0 | 60 | 153 | 11 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 92 | 57 | 87 | 0 | 0 | 6 | 7284.5 | 876 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 927 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 172 | 0 | 171 | 0 | 344 | 0 | 0 | 152 | 45 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 115 | 220 | 0 | 303 | 1108 | 0 | 5968 | 13252.5 | 108.28
06:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 21.5 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 12 | 12 | 0.05 | 222 | 0 | 33 | 753 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 900 | 1 | 43 | 0 | 8 | 0 | 356 | 330 | 47 | 215 | 35 | 50 | 50 | 155 | 64 | 14 | 34 | 40 | 0 | 4 | 0 | 305 | 0 | 313 | 0 | 60 | 152 | 8 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 90 | 57 | 86 | 0 | 0.94 | 6 | 6882.49 | 876 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 987 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 2 | 0 | 1.15 | 175 | 0 | 172 | 0 | 171 | 0 | 345 | 0 | 0.11 | 153 | 45 | 35 | 1 | 70 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 168 | 115 | 220 | 0 | 304 | 900 | 0 | 5757.24 | 12639.73 | 108.29
07:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 21.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 0.64 | 222 | 0 | 35 | 753 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 905 | 4 | 43 | 0 | 8 | 0 | 300 | 330 | 48 | 214 | 35 | 50 | 70 | 113 | 63 | 14 | 34 | 36 | 0 | 16 | 0 | 310 | 0 | 335 | 0 | 60 | 154 | 8 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 92 | 57 | 86 | 0 | 11.76 | 6 | 6824.9 | 876 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.87 | 958 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.71 | 13 | 0 | 7.83 | 175 | 0 | 172 | 0 | 171 | 0 | 357 | 0 | 0.7 | 155 | 44 | 35 | 6 | 49 | 0 | 0 | 0 | 1.2 | 45 | 0.01 | 0 | 172 | 115 | 180 | 0 | 303 | 800 | 0 | 5664.32 | 12489.22 | 108.3
08:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 52 | 93 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 280 | 0 | 0 | 7 | 17 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 12 | 12 | 1.56 | 220 | 0 | 10 | 753 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 902 | 9 | 43 | 0 | 8 | 0 | 300 | 280 | 47 | 190 | 35 | 50 | 70 | 108 | 64 | 14 | 17 | 32 | 0 | 10 | 0 | 310 | 0 | 315 | 0 | 60 | 146 | 8 | 0 | 82 | 30 | 0 | 0 | 162 | 0 | 92 | 57 | 70 | 1 | 7.78 | 6 | 6692.34 | 877 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.95 | 907 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.82 | 38 | 0 | 5.63 | 175 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 0.55 | 153 | 44 | 35 | 14 | 49 | 0 | 0 | 0 | 2.3 | 86 | 0.01 | 0 | 170 | 100 | 180 | 0 | 304 | 790 | 0 | 5593.26 | 12285.6 | 108.31
09:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 90 | 93 | 0 | 0 | 3 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 19 | 17 | 22.5 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 12 | 2.15 | 220 | 0 | 5 | 744 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 905 | 6 | 43 | 0 | 8 | 0 | 300 | 280 | 47 | 200 | 35 | 50 | 70 | 112 | 63 | 14 | 14 | 34 | 0 | 22 | 0 | 305 | 0 | 335 | 0 | 60 | 143 | 8 | 0 | 82 | 30 | 0 | 0 | 162 | 9 | 83 | 66 | 70 | 0 | 14.61 | 6 | 6776.26 | 877 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.23 | 908 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.29 | 32 | 0 | 23.94 | 175 | 0 | 140 | 0 | 140 | 0 | 370 | 0 | 2.32 | 157 | 46 | 35 | 7 | 49 | 0 | 0 | 0 | 1.6 | 129 | 0.03 | 0 | 170 | 100 | 180 | 0 | 304 | 800 | 0 | 5682.41 | 12458.67 | 108.32
10:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 70 | 60 | 0 | 0 | 35 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 52 | 21 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 12 | 12 | 2 | 220 | 0 | 4 | 743 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 905 | 7 | 43 | 0 | 8 | 0 | 351 | 330 | 47 | 203 | 35 | 54 | 50 | 100 | 64 | 14 | 0 | 34 | 0 | 42 | 0 | 320 | 0 | 387 | 0 | 60 | 145 | 8 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 74 | 76 | 66 | 2 | 4.37 | 6 | 6927.37 | 876 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8.12 | 912 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.28 | 19 | 0 | 21.12 | 175 | 0 | 177 | 0 | 170 | 0 | 410 | 0 | 5.22 | 157 | 46 | 35 | 33 | 0 | 0 | 0 | 0 | 3.6 | 173 | 0.1 | 0 | 171 | 115 | 220 | 0 | 304 | 800 | 0 | 5865.44 | 12792.81 | 108.32
11:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 17 | 70 | 45 | 0 | 0 | 35 | 25 | 0 | 300 | 304 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 52 | 20.5 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 12 | 12 | 2.52 | 220 | 0 | 3 | 743 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 904 | 8 | 43 | 0 | 8 | 0 | 345 | 330 | 46 | 199 | 35 | 50 | 50 | 96 | 63 | 14 | 0 | 32 | 0 | 47 | 0 | 310 | 0 | 390 | 0 | 59 | 142 | 8 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 73 | 75 | 66 | 0 | 29.11 | 6 | 6986.13 | 876 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.54 | 912 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.38 | 43 | 0 | 61.29 | 175 | 0 | 185 | 0 | 185 | 0 | 411 | 0 | 5.27 | 159 | 46 | 35 | 14 | 0 | 0 | 43 | 0 | 7.8 | 186 | 0.24 | 0 | 174 | 115 | 220 | 0 | 304 | 800 | 0 | 5990.52 | 12976.65 | 108.33
12:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 17 | 70 | 30 | 0 | 0 | 37 | 54 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 52 | 20.5 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 22 | 30 | 0 | 0 | 12 | 12 | 3.69 | 220 | 0 | 8 | 740 | 0 | 0 | 21 | 0 | 0 | 216 | 0 | 0 | 0 | 1094 | 17 | 43 | 0 | 60 | 0 | 340 | 330 | 46 | 208 | 35 | 54 | 50 | 100 | 61 | 14 | 0 | 38 | 0 | 78 | 0 | 320 | 0 | 393 | 0 | 59 | 155 | 8 | 0 | 83 | 30 | 0 | 0 | 162 | 17 | 73 | 76 | 66 | 1 | 9.27 | 6 | 7331.46 | 876 | 172 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.7 | 927 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.63 | 46 | 0 | 54.23 | 175 | 0 | 178 | 0 | 179 | 0 | 395 | 0 | 4.91 | 157 | 46 | 35 | 36 | 0 | 0 | 43 | 0 | 4.5 | 70 | 0.51 | 0 | 180 | 115 | 220 | 0 | 303 | 835 | 0 | 5886.48 | 13217.94 | 108.33
13:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 12 | 17 | 70 | 60 | 0 | 0 | 55 | 118 | 0 | 300 | 290 | 0 | 0 | 0 | 280 | 0 | 0 | 17 | 52 | 20.5 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 26 | 35 | 0 | 0 | 12 | 12 | 4.36 | 220 | 0 | 11 | 725 | 0 | 0 | 25 | 0 | 0 | 217 | 0 | 0 | 0 | 1130 | 16 | 43 | 0 | 63 | 0 | 342 | 330 | 46 | 187 | 35 | 72 | 50 | 130 | 61 | 14 | 0 | 40 | 0 | 55 | 0 | 310 | 0 | 362 | 0 | 59 | 155 | 8 | 0 | 83 | 30 | 0 | 0 | 161 | 11 | 73 | 76 | 66 | 0 | 15.71 | 6 | 7438.57 | 876 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36.15 | 1000 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.46 | 90 | 0 | 62.27 | 183 | 0 | 175 | 0 | 178 | 0 | 337 | 0 | 5.75 | 159 | 46 | 70 | 33 | 34 | 0 | 43 | 0 | 4.5 | 104 | 0.22 | 0 | 168 | 115 | 220 | 0 | 302 | 1000 | 0 | 6226.35 | 13664.92 | 108.34
14:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 14.3 | 17 | 70 | 60 | 0 | 0 | 55 | 140 | 0 | 300 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 24 | 52 | 21.5 | 15 | 0 | 350 | 0 | 0 | 1 | 0 | 25 | 63 | 0 | 0 | 12 | 12 | 2.77 | 220 | 0 | 6 | 720 | 0 | 0 | 25 | 0 | 0 | 217 | 0 | 0 | 0 | 1138 | 12 | 43 | 0 | 63 | 0 | 332 | 325 | 45 | 183 | 37 | 67 | 50 | 163 | 66 | 14 | 0 | 42 | 0 | 71 | 0 | 300 | 0 | 330 | 0 | 59 | 137 | 8 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 73 | 76 | 63 | 1 | 23.66 | 6 | 7405.23 | 876 | 153 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63.15 | 1035 | 0 | 757.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.49 | 33 | 0 | 61.31 | 173 | 0 | 174 | 0 | 181 | 0 | 327 | 0 | 5.66 | 160 | 45 | 74 | 11 | 34 | 0 | 43 | 0 | 2.3 | 81 | 0.52 | 0 | 159 | 115 | 180 | 0 | 303 | 1050 | 0 | 6162.8 | 13568.03 | 108.34
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 16 | 17 | 65 | 46 | 0 | 0 | 55 | 142 | 0 | 300 | 306 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 52 | 21.2 | 15 | 0 | 350 | 0 | 0 | 30 | 0 | 29 | 66 | 0 | 0 | 12 | 12 | 1 | 220 | 0 | 3 | 718 | 0 | 0 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 1162 | 12 | 43 | 0 | 63 | 0 | 320 | 280 | 44 | 204 | 36 | 67 | 50 | 173 | 64 | 14 | 0 | 42 | 0 | 61 | 0 | 315 | 0 | 337 | 0 | 60 | 152 | 10 | 0 | 83 | 30 | 0 | 0 | 160 | 12 | 73 | 76 | 66 | 0 | 15.91 | 6 | 7440.11 | 876 | 112 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74.14 | 1074 | 0 | 753.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.65 | 11 | 0 | 46.93 | 175 | 0 | 173 | 0 | 178 | 0 | 384 | 0 | 4.96 | 161 | 46 | 70 | 27 | 34 | 0 | 43 | 0 | 3.8 | 144 | 0.1 | 0 | 173 | 100 | 180 | 0 | 297 | 1050 | 0 | 6240.16 | 13680.27 | 108.34
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 16.5 | 17 | 40 | 30 | 0 | 0 | 55 | 144 | 0 | 300 | 296 | 0 | 0 | 0 | 280 | 0 | 0 | 21 | 52 | 21 | 15 | 0 | 350 | 0 | 15 | 32 | 0 | 44 | 52 | 0 | 0 | 12 | 12 | 2.24 | 220 | 0 | 6 | 720 | 0 | 0 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 1092 | 8 | 43 | 0 | 61 | 0 | 348 | 325 | 42 | 194 | 37 | 77 | 70 | 169 | 63 | 14 | 0 | 40 | 0 | 22 | 0 | 320 | 0 | 361 | 0 | 60 | 151 | 11 | 0 | 83 | 30 | 0 | 0 | 162 | 17 | 73 | 76 | 70 | 1 | 7.92 | 6 | 7432.66 | 877 | 145 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.48 | 1075 | 0 | 751.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.91 | 20 | 0 | 32.22 | 176 | 0 | 171 | 0 | 176 | 0 | 350 | 0 | 1.57 | 163 | 46 | 50 | 6 | 34 | 0 | 43 | 0 | 5.2 | 56 | 0.92 | 0 | 172 | 115 | 220 | 0 | 295 | 1051 | 0 | 6109.03 | 13541.69 | 108.34
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 15.4 | 17 | 0 | 30 | 0 | 0 | 55 | 126 | 0 | 300 | 291 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 52 | 20.5 | 22 | 0 | 350 | 0 | 15 | 37 | 0 | 55 | 40 | 0 | 0 | 25 | 12 | 0.44 | 220 | 0 | 16 | 713 | 0 | 0 | 45 | 0 | 0 | 217 | 0 | 0 | 0 | 1042 | 3 | 43 | 0 | 63 | 0 | 347 | 315 | 43 | 190 | 37 | 77 | 70 | 144 | 63 | 14 | 0 | 38 | 0 | 11 | 0 | 315 | 0 | 364 | 0 | 60 | 141 | 11 | 0 | 83 | 30 | 0 | 0 | 162 | 17 | 72 | 76 | 70 | 1 | 5.17 | 7 | 7261.51 | 876 | 143 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.3 | 1049 | 0 | 755.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.91 | 18 | 0 | 15.16 | 176 | 0 | 171 | 0 | 175 | 0 | 340 | 0 | 1.03 | 160 | 46 | 50 | 4 | 34 | 0 | 43 | 0 | 1.7 | 16 | 0.1 | 0 | 168 | 115 | 220 | 0 | 295 | 1050 | 0 | 5978.98 | 13240.49 | 108.34
18:00 | 0 | 33 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 14 | 17 | 0 | 30 | 15 | 4 | 55 | 102 | 0 | 300 | 290 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 52 | 20.5 | 22 | 0 | 300 | 2 | 15 | 33 | 0 | 55 | 49 | 0 | 0 | 25 | 12 | 0 | 220 | 6 | 17 | 712 | 0 | 0 | 50 | 0 | 10 | 217 | 0 | 0 | 0 | 1009 | 0 | 51 | 15 | 63 | 0 | 300 | 305 | 45 | 190 | 37 | 100 | 70 | 134 | 61 | 14 | 17 | 38 | 3 | 2 | 0 | 305 | 0 | 341 | 0 | 60 | 137 | 11 | 0 | 42 | 20 | 0 | 0 | 161 | 17 | 81 | 87 | 70 | 0 | 0 | 12 | 7087.5 | 877 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.3 | 961 | 0 | 754.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.09 | 5 | 0 | 2.29 | 150 | 0 | 130 | 0 | 130 | 0 | 343 | 0 | 0.21 | 160 | 46 | 50 | 2 | 34 | 0 | 43 | 0 | 0.5 | 13 | 0.01 | 0 | 169 | 100 | 180 | 0 | 296 | 900 | 0 | 5534.3 | 12621.8 | 108.34
19:00 | 0 | 48 | 25 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 22 | 17 | 0 | 93 | 132 | 20 | 49 | 144 | 0 | 300 | 286 | 0 | 0 | 50 | 300 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 16 | 15 | 60 | 0 | 26 | 49 | 40 | 0 | 25 | 12 | 0 | 220 | 28 | 22 | 713 | 17 | 0 | 33 | 1 | 35 | 219 | 0 | 0 | 0 | 1153 | 0 | 51 | 66 | 8 | 0 | 330 | 330 | 45 | 190 | 40 | 113 | 70 | 150 | 61 | 14 | 94 | 44 | 32 | 0 | 0 | 315 | 0 | 386 | 0 | 60 | 151 | 15 | 0 | 83 | 30 | 0 | 0 | 162 | 17 | 81 | 95 | 71 | 0 | 0 | 12 | 8110 | 877 | 143 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 10 | 753.68 | 0 | 0 | 0 | 70 | 20 | 0 | 86 | 24 | 0 | 0 | 0 | 28 | 0 | 150 | 0 | 140 | 0 | 140 | 0 | 349 | 0 | 0 | 156 | 46 | 90 | 0 | 56 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 238 | 115 | 220 | 0 | 297 | 975 | 0 | 6084.68 | 14194.68 | 108.35
19:30 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 45 | 17 | 20 | 111 | 195 | 55 | 54 | 137 | 0 | 300 | 295 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 15 | 15 | 85 | 0 | 44 | 49 | 66 | 0 | 25 | 12 | 0 | 220 | 40 | 17 | 702 | 17 | 0 | 33 | 17 | 58 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 120 | 8 | 0 | 330 | 330 | 45 | 189 | 40 | 100 | 70 | 172 | 61 | 14 | 96 | 46 | 52.2 | 0 | 0 | 310 | 0 | 367 | 0 | 60 | 156 | 15 | 0 | 83 | 30 | 0 | 0 | 161 | 17 | 82 | 96 | 71 | 0 | 0 | 12 | 8469.2 | 877 | 153 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 12 | 755.47 | 0 | 8 | 0 | 70 | 100 | 0 | 86 | 30 | 0 | 0 | 0 | 27 | 0 | 150 | 0 | 140 | 0 | 144 | 0 | 345 | 0 | 0 | 154 | 46 | 115 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 115 | 220 | 0 | 296 | 1190 | 35 | 6631.47 | 15100.67
20:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 46.4 | 17 | 52 | 111 | 195 | 55 | 35 | 141 | 0 | 300 | 296 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 22 | 18 | 0 | 350 | 0 | 0 | 85 | 0 | 55 | 49 | 66 | 0 | 25 | 12 | 0 | 220 | 48 | 20 | 700 | 17 | 0 | 33 | 17 | 65 | 218 | 0 | 0 | 0 | 1148 | 0 | 51 | 108 | 8 | 0 | 330 | 330 | 46 | 183 | 37 | 102 | 70 | 168 | 63 | 14 | 96 | 44 | 52.2 | 0 | 0 | 305 | 0 | 361 | 0 | 60 | 152 | 15 | 0 | 84 | 30 | 0 | 0 | 162 | 17 | 91 | 86 | 71 | 0 | 0 | 12 | 8445.6 | 875 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1189 | 12 | 756.8 | 0 | 44 | 0 | 0 | 50 | 0 | 86 | 39 | 0 | 0 | 0 | 26 | 0 | 150 | 0 | 140 | 0 | 140 | 0 | 335 | 0 | 0 | 153 | 46 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 115 | 220 | 0 | 296 | 1208 | 35 | 6573.8 | 15019.4 | 108.35
21:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 45.2 | 17 | 146 | 111 | 95 | 0 | 17 | 136 | 0 | 300 | 300 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 22 | 15 | 0 | 350 | 0 | 0 | 75 | 0 | 35 | 49 | 66 | 0 | 25 | 12 | 0 | 222 | 47 | 31 | 706 | 17 | 0 | 33 | 17 | 66 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 100 | 8 | 0 | 330 | 330 | 46 | 191 | 41 | 101 | 70 | 171 | 69 | 10 | 59 | 42 | 52.2 | 0 | 0 | 305 | 0 | 382 | 0 | 60 | 153 | 15 | 0 | 84 | 30 | 0 | 0 | 161 | 0 | 91 | 86 | 72 | 0 | 0 | 12 | 8338.4 | 876 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 12 | 752.89 | 0 | 48 | 0 | 0 | 0 | 0 | 86 | 37 | 0 | 0 | 0 | 26 | 0 | 150 | 0 | 140 | 0 | 140 | 0 | 346 | 0 | 0 | 154 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 115 | 220 | 0 | 297 | 1220 | 35 | 6592.89 | 14931.29 | 108.35
22:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 45.4 | 17 | 149 | 111 | 95 | 0 | 17 | 139 | 0 | 300 | 300 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 0 | 0 | 89 | 0 | 15 | 49 | 66 | 0 | 25 | 12 | 0 | 222 | 48 | 32 | 701 | 0 | 0 | 33 | 17 | 63 | 221 | 0 | 0 | 0 | 1135 | 0 | 51 | 100 | 8 | 0 | 350 | 330 | 46 | 192 | 41 | 101 | 70 | 173 | 72 | 14 | 59 | 46 | 52.2 | 0 | 0 | 310 | 0 | 368 | 0 | 60 | 153 | 15 | 0 | 84 | 30 | 0 | 0 | 161 | 0 | 91 | 86 | 72 | 0 | 0 | 12 | 8330.6 | 877 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1231 | 21 | 754.58 | 0 | 48 | 0 | 0 | 0 | 0 | 86 | 37 | 0 | 0 | 0 | 26 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 344 | 0 | 0 | 155 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 115 | 220 | 0 | 297 | 1220 | 35 | 6630.58 | 14961.18 | 108.35
23:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 45 | 17 | 149 | 111 | 95 | 0 | 17 | 142 | 0 | 300 | 305 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 0 | 0 | 88 | 0 | 27 | 49 | 59 | 0 | 25 | 12 | 0 | 221 | 48 | 35 | 703 | 0 | 0 | 19 | 0 | 62 | 222 | 0 | 0 | 0 | 1158 | 0 | 51 | 100 | 8 | 0 | 351 | 330 | 46 | 195 | 41 | 100 | 50 | 171 | 71 | 14 | 62 | 46 | 52.2 | 0 | 0 | 315 | 0 | 386 | 0 | 60 | 152 | 15 | 0 | 84 | 30 | 0 | 0 | 161 | 0 | 91 | 86 | 72 | 0 | 0 | 12 | 8338.2 | 876 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 17 | 753.56 | 0 | 48 | 0 | 0 | 0 | 0 | 86 | 37 | 0 | 0 | 0 | 26 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 360 | 0 | 0 | 157 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 115 | 220 | 0 | 296 | 1220 | 35 | 6612.56 | 14950.76 | 108.35
Total KWH | 0 | 1674240 | 541440 | 0 | 0 | 0 | 0 | 0 | 8470800 | 0 | 0 | 459360 | 511920 | 1662768 | 1737120 | 678960 | 105644 | 761730 | 1972800 | 0 | 7577000 | 7145222 | 0 | 0 | 381414 | 6985521 | 0 | 0 | 135929 | 1706400 | 507600 | 426240 | 0 | 8335454.55 | 32618 | 75273 | 701760 | 0 | 708960 | 891379 | 401280 | 0 | 379200 | 288960 | 24480 | 5345995 | 379709 | 523200 | 17687272.73 | 53527 | 0 | 469920 | 74878.2 | 511854 | 5201708 | 0 | 0 | 0 | 25707270 | 101385 | 1138356 | 677454 | 602181.81 | 0 | 8466100 | 7772000 | 1103520 | 4873000 | 880776 | 1966080 | 1411420 | 3603840 | 1531320 | 322480 | 978120 | 976320 | 559104 | 390164 | 0 | 7536000 | 40200 | 8803000 | 0 | 1405800 | 3607445 | 267984 | 0 | 1944960 | 702812 | 0 | 0 | 3766570 | 311040 | 2008800 | 1732800 | 1693440 | 9250 | 201970 | 171120 | 182793618.29 | 21194909 | 4389405 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 169200 | 25265450 | 106560 | 18357384 | 0 | 247911 | 0 | 75264 | 234720 | 0 | 593172 | 190600 | 0 | 242060 | 505680 | 186800 | 354000 | 4114909 | 0 | 4110736 | 0 | 4151409 | 0 | 8676436 | 0 | 30600 | 3829000 | 1073890 | 1761464 | 199858 | 1576694 | 0 | 360360 | 0 | 46044.12 | 1230480 | 2227.5 | 0 | 4970000 | 2692000 | 5301060 | 0 | 7235640 | 25309090.91 | 180000 | 149877013.53 | 332670631.82

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13217.94 | MW | 12:00 Hr. | Energy Generated |  |  | 332.6706 |  | MKWHr.
| Day Peak Demand |  |  | 13217.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.145 |  | MKWHr.
| Evening Peak Generation |  |  | 15100.67 | MW | 19:30 Hr. | Energy Demand |  |  | 332.8156 |  | MKWHr.
| Evening Peak Demand |  |  | 15100.67 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 12285.6 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 975.42 |  | MMCFD
| Maximum Generation of the Day |  |  | 15100.67 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.2801 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.4478 | 0 | 12.1938 | 0 | 0 | 0.13593 | 0 | 0 | 51.7776 | Gas | 134.9467 | Gas | 483110878.6912
| Chattogram Zone |  |  | 5.7249 | 43.3945 | 4.2604 | 0 | 5.346 | 0.12587 | 0 | 0.70896 | 59.5606 | Coal | 111.0776 | Coal | 658498648.4383
| Cumilla Zone |  |  | 26.5698 | 0 | 9.3159 | 0 | 0 | 0.39016 | 0.97632 | 0 | 37.2522 | HFO | 35.147 | HFO | 645122795.226
| Mymensingh Zone |  |  | 1.6934 | 0 | 4.2238 | 0 | 0 | 0.21122 | 0 | 0 | 6.1284 | HSD | 0.36036 | HSD | 0
| Sylhet Zone |  |  | 28.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.0748 | Hydro | 5.346 | Hydro | 534599.5
| Khulna Zone |  |  | 4.3894 | 25.2655 | 0.10656 | 0 | 0 | 0.1692 | 22.1069 | 0 | 52.0375 | Solar | 3.6433 | Solar | 55596983.6502
| Barishal Zone |  |  | 7.9931 | 37.5147 | 0.18 | 0 | 0 | 0.0022275 | 0 | 0 | 45.69 | Import | 41.4406 | Import | 235891255.71
| Rajshahi Zone |  |  | 21.0535 | 0 | 1.5285 | 0 | 0 | 1.1323 | 18.3574 | 0 | 42.0717 | Wind | 0.70896 | Wind | 10450070.4
| Rangpur Zone |  |  | 0 | 4.9029 | 3.3382 | 0.36036 | 0 | 1.4764 | 0 | 0 | 10.0778
| Total |  |  | 134.9467 | 111.0776 | 35.147 | 0.36036 | 5.346 | 3.6433 | 41.4406 | 0.70896 | 332.6706
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 483110878.6912 |  | Hydro | 534599.5
|  |  |  | Coal | 658498648.4383 |  | Solar | 55596983.6502
|  |  |  | HFO | 645122795.226 |  | Import | 235891255.71
|  |  |  | HSD | 0 |  | Wind | 10450070.4
[5 empty] | Total: | 208,92,05,231 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1949 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43661254.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.3574 | Peak Hr Flow | 755.47 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 478 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.97632 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 948 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.5286 | Peak Hr Flow | 1678.47 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5185
|  |  |  | Chattogram |  | 0 |  | 1500
|  |  |  | Cumilla |  | 0 |  | 1399
|  |  |  | Mymensingh |  | 0 |  | 1213
|  |  |  | Sylhet |  | 0 |  | 648
|  |  |  | Khulna |  | 0 |  | 1712
|  |  |  | Barishal |  | 0 |  | 413
|  |  |  | Rajshahi |  | 0 |  | 1505
|  |  |  | Rangpur |  | 0 |  | 1009
|  |  |  | Total |  | 0 |  | 14584
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 12:05 | Baroirhat 132/33kV S/S TR-2, 416T HT Scheduled S/D Due to PBS maintenance work | [7 empty] | 20.0MW load
interrup.
|  | 08:47 | Jamalpur 132/33kV S/S T-2 HT is restored.
|  | 08:47 | Jamalpur 132/33kV S/S T-2 LT is restored.
|  | 09:06 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
|  | 09:06 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
| 09:17 | 13:05 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Maintenance Work by PBS | [7 empty] | 27.0MW load
interrup.
| 09:18 | 13:03 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Maintenance Work by PBS | [7 empty] | 27.0MW load
interrup.
|  | 09:28 | Kushtia 132/33kV S/S T-1 HT is restored.
|  | 09:29 | Kushtia 132/33kV S/S T-1 LT is restored.
| 10:05 | 12:44 | BIPTC S/S Block-01, Trafo-02 HT Forced S/D
| 12:00 |  | Day peak Generation is 13212 MW
| 17:10 | 17:30 | Gollamari 132/33kV S/S Tr-2 LT Tripped showing 50/51 OC/EF relays Due to Pbs sadar feeder | [7 empty] | 68.0MW load
interrup.
| 17:10 | 17:29 | Gollamari 132/33kV S/S Tr-1 LT Tripped showing 50/51 OC/EF relays Due to Pbs sadar feeder | [7 empty] | 68.0MW load
interrup.
| 19:01 | 20:38 | Narshingdi 132/33kV S/S T-1 LT Forced S/D Due to নরসিংদী ১৩২ কেভি গ্রিড উপকেন্দ্রের T-1 | [7 empty] | 55.0MW load
|  |  | ট্রান্সফরমারের ৩৩ কেভি বাস এর Y-Phase T - Clamp Maintenance Work by PBS. | [7 empty] | interrup.
| 19:02 | 20:37 | Narshingdi 132/33kV S/S T-1 HT Forced S/D Due to নরসিংদী ১৩২ কেভি গ্রিড উপকেন্দ্রের T-1 | [7 empty] | 55.0MW load
|  |  | ট্রান্সফরমারের ৩৩ কেভি বাস এর Y-Phase T - Clamp Maintenance Work by PBS. | [7 empty] | interrup.
| 19:30 |  | Evening Peak Generation: 15100 MW
| 21:27 | 01:08 | Narshingdi 132/33kV S/S T-1 LT Tripped showing Inter trip relays Due to 33 kV DS fault | [7 empty] | 37.0MW load
interrup.
| 21:28 | 01:02 | Narshingdi 132/33kV S/S T-1 HT Tripped showing 86T relays Due to 33 kV DS fault | [7 empty] | 37.0MW load
interrup.
| 22:30 | 01:02 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to Maintenance work | [7 empty] | 40.0MW load
interrup.
| 22:30 | 01:08 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to Maintenance work | [7 empty] | 40.0MW load
interrup.
| 03:37 | 03:47 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Ins O/c,deff O/c relays Due to 33 kv | [7 empty] | 38.0MW load
|  |  | wzpdco T4 feeder faulty trip | [7 empty] | interrup.
| 05:55 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to sylhet -
chattak ckt-02 tower loop maintenance.
| 06:23 | 06:49 | Ashuganj-Kishoreganj 132kV Ckt-2 Forced S/D from Bajitpur 132/33kV end Due to Ashuganj
end busbar tree trimming.
| 07:00 |  | Minimum Generation: 12524 MW.
| 07:30 |  | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to Maintenance work of string cutting
of t1 LT Bushing y phase.
| 07:30 |  | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to Maintenance work of string cutting
of t1 LT Bushing y phase.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 322 | 8470800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7577000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 7145222 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 105644 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6985521 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 459360 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 111 | 1737120 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 54 | 761730 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 381414 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 507600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 426240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 541440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 678960 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 20 | 1662768 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 68 | 1674240 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 137 | 1972800 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 135929 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 511920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8335454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1706400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2501 | 51777562.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 74878.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 101385 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 469920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5345995 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5201708 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 58 | 511854 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 401280 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 891379 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 379200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 523200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 701760 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 75273 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 40 | 379709 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 288960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 32618 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 53527 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 25707270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 44 | 708960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 702 | 17687272.73 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2784 | 59560628.93
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4873000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 330 | 8466100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7772000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 880776 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 1103520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 602181.81 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1138356 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 677454 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1411420 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3603840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 976320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 559104 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 322480 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 978120 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 61 | 1531320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 1966080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 390164 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1724.2 | 37252235.81
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1693440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 96 | 1732800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 82 | 2008800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 201970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 171120 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 311040 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 278 | 6128420
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1405800 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3607445 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 702812 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1944960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 161 | 3766570 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 15 | 267984 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7536000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8803000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 40200 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2325 | 1182 | 28074771
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 21194909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 153 | 4389405 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 12 | 106560 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 169200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1175 | 25265450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2255 | 52037524
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 296 | 7235640 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2692000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 25309090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5301060 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 180000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 248 | 4970000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2227.5 | -
Barishal Area Total |  |  |  |  | 2236 | 2104 | 45690018.41
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 242060 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 8 | 247911 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 190600 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 4114909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4110736 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 144 | 4151409 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8676436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 186800 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 593172 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 234720 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 75264 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 755.47 | 18357384 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 354000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 505680 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 1855.47 | 42071681
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 360360 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1073890 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3829000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 1576694 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46044.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1761464 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199858 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1230480 | -
Rangpur Area Total |  |  |  |  | 950 | 417 | 10077790.12
Eastern Grid Total |  |  |  |  | 17401.505 | 8469.2 | 182793618.29
Western Grid Total |  |  |  |  | 10442.16 | 6631.47 | 149877013.53
National Grid Total |  |  |  |  | 27843.665 | 15100.67 | 332670631.82
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9945.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4639.3 | MW
i) Dhaka area |  |  | 5184.88 |  | MW | i) Khulna area |  |  |  | 1712.5 | MW
ii) Chattogram area |  |  | 1500.5 |  | MW | ii) Barishal area |  |  |  | 413 | MW
iii) Cumilla area |  |  | 1399.37 |  | MW | iii) Rajshahi area |  |  |  | 1504.8 | MW
iv) Mymensingh area |  |  | 1213 |  | MW | iv) Rangpur area |  |  |  | 1009 | MW
v) Sylhet area |  |  | 648 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14585.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 19:30 | 133 | PHP | 9 | 01:00
2 | AKSML | 83 | 10:00 | 68 | Ishurdi | 82 | 19:30 | 134 | Pabna | 129 | 19:30
3 | Aftabnagar | 40 | 13:00 | 69 | Jaldhaka | 90 | 19:00 | 135 | Palashbari | 102 | 01:00
4 | Agargaon | 133 | 13:00 | 70 | Jamalpur | 128 | 07:00 | 136 | Panchagarh | 62 | 19:00
5 | Agrabad | 98 | 16:00 | 71 | Jashore | 136 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 28 | 22:00 | 72 | Jhenaidah | 128 | 19:30 | 138 | Patuakhali | 69 | 22:00
7 | Ashuganj | 93 | 20:00 | 73 | Joydebpur | 141 | 08:00 | 139 | Payra | 32 | 00:00
8 | BSRM | 196 | 18:30 | 74 | Joypurhat | 64 | 00:00 | 140 | Postogola | 58 | 13:00
9 | Bagerhat | 80 | 00:00 | 75 | Juldah | 18.5 | 00:00 | 141 | Purbachal | 21 | 00:00
10 | Bajitpur | 92 | 20:00 | 76 | KSRM | 21 | 09:00 | 142 | Purbasadipur | 130 | 21:00
11 | Bakulia | 103 | 18:30 | 77 | Kabirpur | 238 | 08:00 | 143 | Rahanpur | 40 | 00:00
12 | Banani | 47.8 | 13:00 | 78 | Kachua | 94 | 21:00 | 144 | Rahim | 26 | 08:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajbari | 80 | 19:00
14 | Barapukuria | 68 | 19:30 | 80 | Kalurghat | 40 | 16:00 | 146 | Rajendrapur | 138 | 18:30
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 75 | 12:00 | 147 | Rajshahi | 134 | 21:00
16 | Barishal | 114 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 70 | 13:00
17 | Barishal-230 | 90 | 00:00 | 83 | Kasba | 37 | 21:00 | 149 | Ramganj | 114 | 00:00
18 | Baroaulia | 71 | 15:00 | 84 | Kazla | 96 | 18:30 | 150 | Rampur | 41 | 00:00
19 | Baroirhat | 64 | 19:00 | 85 | Keranigonj | 89 | 17:00 | 151 | Rangamati | 18 | 19:00
20 | Bashundhara | 188 | 12:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rangpur | 154 | 12:00
21 | BashundharaCement | 10 | 14:00 | 87 | Khulna | 74 | 20:00 | 153 | Ruppur | 7 | 11:00
22 | Beanibazar | 80 | 00:00 | 88 | Khulshi | 170 | 16:00 | 154 | SSM | 13 | 00:00
23 | Benapole | 60 | 00:00 | 89 | Kishoreganj | 140 | 19:30 | 155 | Saidpur | 109 | 19:00
24 | Bhaluka | 152 | 19:00 | 90 | Kodda | 301 | 15:00 | 156 | Satkhira | 120 | 00:00
25 | Bhandaria | 53 | 00:00 | 91 | Kulaura | 54 | 21:00 | 157 | Satmasjid | 101 | 13:00
26 | Bhangura | 38 | 19:30 | 92 | Kurigram | 64 | 18:30 | 158 | Savar | 227 | 16:00
27 | Bheramara(GK) | 66 | 19:00 | 93 | Kushtia | 154 | 19:00 | 159 | SevenRings | 15.34 | 23:00
28 | Bhulta | 212 | 19:30 | 94 | Laksam | 44 | 10:00 | 160 | ShahCement | 11 | 18:00
29 | Bog-Sherpur | 76 | 01:00 | 95 | Lakshmipur | 19 | 01:00 | 161 | Shahjadpur | 86 | 20:00
30 | Bogura | 166 | 00:00 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 136 | 22:00
31 | Borhanuddin | 92 | 21:00 | 97 | Lalmonirhat | 68 | 22:00 | 163 | Shahmirpur | 69 | 18:30
32 | Brahmanbaria | 134 | 21:00 | 98 | MI_Cement | 15 | 16:00 | 164 | Shariatpur | 85 | 00:00
33 | Cantonment | 138 | 13:00 | 99 | Madanganj | 41 | 00:00 | 165 | Sherpur | 146 | 22:00
34 | Chandina | 20.21 | 19:00 | 100 | Madaripur | 109 | 00:00 | 166 | Shikalbaha | 8 | 00:00
35 | Chandpur | 78 | 00:00 | 101 | Madartek | 91.83 | 00:00 | 167 | Shitalakhya | 74.9 | 15:00
36 | Chandraghona | 39 | 19:00 | 102 | Madunaghat | 57 | 19:00 | 168 | Sholosohor | 46 | 15:00
37 | Chapai | 71 | 21:00 | 103 | Magura | 65 | 19:00 | 169 | Shyampur | 164 | 12:00
38 | Charsaidpur | 32 | 03:00 | 104 | Mahasthangarh | 84 | 22:00 | 170 | Siddhirganj | 115 | 13:00
39 | Chauddagram | 73 | 00:00 | 105 | Maijdee | 14 | 00:00 | 171 | Sirajganj | 116 | 19:30
40 | Chhatak | 39 | 00:00 | 106 | Manikganj | 126 | 20:00 | 172 | Sonargaon | 125 | 18:30
41 | Chowmuhani | 193 | 00:00 | 107 | Maniknagar | 86 | 14:00 | 173 | Sreemongol | 89 | 22:00
42 | Chuadanga | 114 | 19:00 | 108 | Matarbari | 51 | 19:00 | 174 | Sreepur | 107 | 19:00
43 | Coxsbazar | 130 | 19:30 | 109 | Matuail | 70 | 12:00 | 175 | Srinagar | 45.77 | 00:00
44 | Cumilla(N) | 140 | 00:00 | 110 | Millgate | 134 | 12:00 | 176 | Sunamganj | 61 | 00:00
45 | Cumilla(S) | 151 | 00:00 | 111 | Mirpur | 122 | 12:00 | 177 | Sylhet | 53 | 01:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 132 | 19:30
47 | Daudkandi | 152 | 19:00 | 113 | Mirzapur | 48 | 22:00 | 179 | TK | 36 | 19:00
48 | Dhaka | 82 | 13:00 | 114 | Mithapukur | 72 | 19:00 | 180 | Tangail | 178 | 23:00
49 | Dhamrai | 128 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:00
50 | Dhanmondi | 145 | 13:00 | 116 | Mogbazar | 131.4 | 13:00 | 182 | Thakurgaon | 110 | 19:30
51 | Dohazari | 113 | 20:00 | 117 | Mongla | 36 | 19:00 | 183 | Tongi | 108 | 11:00
52 | Faridpur | 166 | 00:00 | 118 | Motijheel | 44 | 13:00 | 184 | Ullahpara | 38 | 19:30
53 | Fatullah | 104 | 12:00 | 119 | Muktagacha | 36 | 21:00 | 185 | Ullon | 40 | 00:00
54 | Fenchuganj | 51 | 00:00 | 120 | Munshiganj | 111 | 00:00 | 186 | Uttara | 79 | 13:00
55 | Feni | 120 | 19:00 | 121 | Muradnagar | 42 | 20:00 | 187 | UttaraNew | 60 | 00:00
56 | GPH | 87 | 05:00 | 122 | Mymensingh | 208 | 20:00 | 188 | Zigatola | 72 | 14:00
57 | Ghatail | 80 | 19:00 | 123 | Naogaon | 132 | 00:00
58 | Ghorashal | 15 | 09:00 | 124 | Narail | 56 | 00:00
59 | Ghorashal-230 | 92 | 21:00 | 125 | Narinda | 76 | 13:00
60 | Goalpara | 33 | 00:00 | 126 | Narshingdi | 182 | 01:00
61 | Gollamari | 98 | 00:00 | 127 | Natore | 147 | 22:00
62 | Gopalganj | 101 | 20:00 | 128 | Nawabganj | 57.2 | 22:00
63 | Gulshan | 124 | 14:00 | 129 | Netrakona | 142 | 22:00
64 | Halishahar | 69 | 15:00 | 130 | New | 74.6 | 19:30
65 | HaripurSBU | 162 | 09:00 | 131 | Niamatpur | 74 | 22:00
66 | Hasnabad | 87 | 00:00 | 132 | Noapara | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15046.46 | 62 |  | 15111.25
1:00 | 14671.7 | 28 |  | 14700.96
2:00 | 14264.9 | 34 |  | 14300.43
3:00 | 13844.3 | 21 |  | 13866.25
4:00 | 13542.7 | 0 |  | 13542.7
5:00 | 13252.5 | 0 |  | 13252.5
6:00 | 12639.73 | 0 |  | 12639.73
7:00 | 12489.22 | 0 |  | 12489.22
8:00 | 12285.6 | 0 |  | 12285.6
9:00 | 12458.67 | 0 |  | 12458.67
10:00 | 12792.81 | 0 |  | 12792.81
11:00 | 12976.65 | 0 |  | 12976.65
12:00 | 13217.94 | 0 |  | 13217.94
13:00 | 13664.92 | 0 |  | 13664.92
14:00 | 13568.03 | 0 |  | 13568.03
15:00 | 13680.27 | 0 |  | 13680.27
16:00 | 13541.69 | 0 |  | 13541.69
17:00 | 13240.49 | 0 |  | 13240.49
18:00 | 12621.8 | 0 |  | 12621.8
19:00 | 14194.68 | 0 |  | 14194.68
19:30 | 15100.67 | 0 |  | 15100.67
20:00 | 15019.4 | 0 |  | 15019.4
21:00 | 14931.29 | 0 |  | 14931.29
22:00 | 14961.18 | 0 |  | 14961.18
23:00 | 14950.76 | 0 |  | 14950.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8214.7 | 6831.76 | 15046.46 | DAILY GENERATION CURVE
00:30 | 8112.2 | 6746.88 | 14859.08
01:00 | 8009.7 | 6662 | 14671.7 | 20-08-2025
01:30 | 7950.8 | 6517.5 | 14468.3
02:00 | 7891.9 | 6373 | 14264.9
02:30 | 7734.6 | 6320 | 14054.6
03:00 | 7577.3 | 6267 | 13844.3
03:30 | 7481.5 | 6212 | 13693.5
04:00 | 7385.7 | 6157 | 13542.7
04:30 | 7335.1 | 6062.5 | 13397.6
05:00 | 7284.5 | 5968 | 13252.5
05:30 | 7083.495 | 5862.62 | 12946.115
06:00 | 6882.49 | 5757.24 | 12639.73
06:30 | 6853.695 | 5710.78 | 12564.475
07:00 | 6824.9 | 5664.32 | 12489.22
07:30 | 6758.62 | 5628.79 | 12387.41
08:00 | 6692.34 | 5593.26 | 12285.6
08:30 | 6734.3 | 5637.835 | 12372.135
09:00 | 6776.26 | 5682.41 | 12458.67
09:30 | 6851.815 | 5773.925 | 12625.74
10:00 | 6927.37 | 5865.44 | 12792.81
10:30 | 6956.75 | 5927.98 | 12884.73
11:00 | 6986.13 | 5990.52 | 12976.65
11:30 | 7158.795 | 5938.5 | 13097.295
12:00 | 7331.46 | 5886.48 | 13217.94
12:30 | 7385.015 | 6056.415 | 13441.43
13:00 | 7438.57 | 6226.35 | 13664.92
13:30 | 7421.9 | 6194.575 | 13616.475
14:00 | 7405.23 | 6162.8 | 13568.03
14:30 | 7422.67 | 6201.48 | 13624.15
15:00 | 7440.11 | 6240.16 | 13680.27
15:30 | 7436.385 | 6174.595 | 13610.98
16:00 | 7432.66 | 6109.03 | 13541.69
16:30 | 7347.085 | 6044.005 | 13391.09
17:00 | 7261.51 | 5978.98 | 13240.49
17:30 | 7174.505 | 5756.64 | 12931.145
18:00 | 7087.5 | 5534.3 | 12621.8
18:30 | 7598.75 | 5809.49 | 13408.24
19:00 | 8110 | 6084.68 | 14194.68
19:30 | 8469.2 | 6631.47 | 15100.67
20:00 | 8445.6 | 6573.8 | 15019.4
20:30 | 8392 | 6583.345 | 14975.345 |  | Executive Engineer
21:00 | 8338.4 | 6592.89 | 14931.29 |  | Network Operation Division
21:30 | 8334.5 | 6611.735 | 14946.235
22:00 | 8330.6 | 6630.58 | 14961.18
22:30 | 8334.4 | 6621.57 | 14955.97
23:00 | 8338.2 | 6612.56 | 14950.76

## En-Curve
QF-LDC-12
Date | 20-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3722 | 1898.5 | 876 | 38 | 50 | 763.76 | 221 | 5124 | 0 | 643 | 1686.2 | 0 | 0 | 24 | 62 | DAILY ENERGY CURVE
00:30 | 3705.5 | 1897 | 876 | 38 | 49 | 765.88 | 220.5 | 5093 | 0 | 569.5 | 1624.2 | 0 | 0 | 20.5 | 45 | 20-08-2025
01:00 | 3689 | 1895.5 | 876 | 38 | 48 | 768 | 220 | 5062 | 0 | 496 | 1562.2 | 0 | 0 | 17 | 28
01:30 | 3704 | 1908 | 876 | 38 | 47 | 768.5 | 220.5 | 5004.5 | 0 | 408.5 | 1474.8 | 0 | 0 | 18.5 | 31 | Energy Generated | 332.6706 |  | MKWHr
02:00 | 3719 | 1920.5 | 876 | 38 | 46 | 769 | 221 | 4947 | 0 | 321 | 1387.4 | 0 | 0 | 20 | 34 | Energy not Served | 0.145 |  | MKWHr
02:30 | 3706.5 | 1914 | 876 | 38 | 45 | 768.5 | 221 | 4936 | 0 | 294 | 1234.1 | 0 | 0 | 21.5 | 27.5 | Total Energy Requirement | 332.8156 |  | MKWHr
03:00 | 3694 | 1907.5 | 876 | 38 | 44 | 768 | 221 | 4925 | 0 | 267 | 1080.8 | 0 | 0 | 23 | 21
03:30 | 3697.5 | 1911.5 | 876 | 38 | 43 | 766.5 | 221 | 4870.5 | 0 | 259 | 988.5 | 0 | 0 | 22 | 10.5
04:00 | 3701 | 1915.5 | 876 | 38 | 42 | 765 | 221 | 4816 | 0 | 251 | 896.2 | 0 | 0 | 21 | 0
04:30 | 3699.5 | 1914 | 876 | 38 | 43 | 763 | 221.5 | 4742 | 0 | 257 | 817.1 | 0 | 0 | 26.5 | 0
05:00 | 3698 | 1912.5 | 876 | 38 | 44 | 761 | 222 | 4668 | 0 | 263 | 738 | 0 | 0 | 32 | 0
05:30 | 3694.5 | 1902 | 876 | 38 | 42 | 765.5 | 222 | 4439 | 6.615 | 245 | 678.5 | 0 | 0 | 37 | 0
06:00 | 3691 | 1891.5 | 876 | 38 | 40 | 770 | 222 | 4210 | 13.23 | 227 | 619 | 0 | 0 | 42 | 0
06:30 | 3685 | 1881.5 | 876 | 38 | 38 | 768.5 | 222 | 4150 | 67.975 | 219.5 | 588 | 0 | 0 | 30 | 0
07:00 | 3679 | 1871.5 | 876 | 38 | 36 | 767 | 222 | 4090 | 122.72 | 212 | 557 | 0 | 0 | 18 | 0
07:30 | 3576 | 1852.25 | 876.5 | 38 | 34 | 764.5 | 221 | 4056.5 | 165.66 | 216.5 | 564 | 0 | 0 | 22.5 | 0
08:00 | 3473 | 1833 | 877 | 38 | 32 | 762 | 220 | 4023 | 208.6 | 221 | 571 | 0 | 0 | 27 | 0
08:30 | 3503.5 | 1826.75 | 877 | 38 | 33 | 762.5 | 220 | 4028.5 | 247.385 | 221 | 596 | 0 | 0 | 18.5 | 0
09:00 | 3534 | 1820.5 | 877 | 38 | 34 | 763 | 220 | 4034 | 286.17 | 221 | 621 | 0 | 0 | 10 | 0
09:30 | 3663 | 1837.25 | 876.5 | 38 | 34 | 765 | 220 | 4036 | 321.49 | 222.5 | 596.5 | 0 | 0 | 15.5 | 0
10:00 | 3792 | 1854 | 876 | 38 | 34 | 767 | 220 | 4038 | 356.81 | 224 | 572 | 0 | 0 | 21 | 0
10:30 | 3809 | 1856.75 | 876 | 38 | 33 | 764 | 220 | 4040 | 402.98 | 224 | 579 | 21.5 | 0 | 20.5 | 0
11:00 | 3826 | 1859.5 | 876 | 38 | 32 | 761 | 220 | 4042 | 449.15 | 224 | 586 | 43 | 0 | 20 | 0
11:30 | 3802 | 1900 | 876 | 38 | 35 | 761.5 | 220 | 4162 | 408.295 | 215 | 615.5 | 43 | 0 | 21 | 0
12:00 | 3778 | 1940.5 | 876 | 38 | 38 | 762 | 220 | 4282 | 367.44 | 206 | 645 | 43 | 0 | 22 | 0
12:30 | 3703 | 1934.5 | 876 | 38 | 39 | 764.5 | 220 | 4406 | 420.43 | 223.5 | 749.5 | 43 | 0 | 24 | 0
13:00 | 3628 | 1928.5 | 876 | 38 | 40 | 767 | 220 | 4530 | 473.42 | 241 | 854 | 43 | 0 | 26 | 0
13:30 | 3568 | 1891.5 | 876 | 38 | 41 | 762.185 | 220 | 4570 | 446.64 | 255 | 879.65 | 43 | 0 | 25.5 | 0
14:00 | 3508 | 1854.5 | 876 | 38 | 42 | 757.37 | 220 | 4610 | 419.86 | 269 | 905.3 | 43 | 0 | 25 | 0
14:30 | 3507 | 1876.85 | 876 | 38 | 42 | 755.475 | 220 | 4645.5 | 420.175 | 246 | 927.15 | 43 | 0 | 27 | 0
15:00 | 3506 | 1899.2 | 876 | 38 | 42 | 753.58 | 220 | 4681 | 420.49 | 223 | 949 | 43 | 0 | 29 | 0
15:30 | 3569 | 1916.1 | 876.5 | 38 | 41 | 752.655 | 220 | 4647.5 | 321.475 | 208 | 941.25 | 43 | 0 | 36.5 | 0
16:00 | 3632 | 1933 | 877 | 38 | 40 | 751.73 | 220 | 4614 | 222.46 | 193 | 933.5 | 43 | 0 | 44 | 0
16:30 | 3611.5 | 1932.75 | 876.5 | 38 | 39 | 753.755 | 220 | 4568.5 | 161.135 | 187 | 910.45 | 43 | 0 | 49.5 | 0
17:00 | 3591 | 1932.5 | 876 | 38 | 38 | 755.78 | 220 | 4523 | 99.81 | 181 | 887.4 | 43 | 0 | 55 | 0
17:30 | 3464.5 | 1865 | 876.5 | 38 | 38 | 755.34 | 220 | 4388 | 63.605 | 186.5 | 937.7 | 43 | 0 | 55 | 0
18:00 | 3338 | 1797.5 | 877 | 38 | 38 | 754.9 | 220 | 4253 | 27.4 | 192 | 988 | 43 | 0 | 55 | 0
18:30 | 3442.5 | 1850.75 | 877 | 38 | 41 | 754.29 | 220 | 4425.5 | 13.7 | 346.5 | 1315.5 | 43 | 0 | 40.5 | 0
19:00 | 3547 | 1904 | 877 | 38 | 44 | 753.68 | 220 | 4598 | 0 | 501 | 1643 | 43 | 0 | 26 | 0
19:30 | 3536 | 1908 | 877 | 38 | 46 | 755.47 | 220 | 4961 | 0 | 578 | 2137.2 | 0 | 0 | 44 | 0
20:00 | 3511 | 1901 | 875 | 38 | 44 | 756.8 | 220 | 4983 | 0 | 622 | 2013.6 | 0 | 0 | 55 | 0
20:30 | 3534 | 1905.5 | 875.5 | 38 | 43 | 754.845 | 221 | 5019 | 0 | 623 | 1916.5 | 0 | 0 | 45 | 0
21:00 | 3557 | 1910 | 876 | 38 | 42 | 752.89 | 222 | 5055 | 0 | 624 | 1819.4 | 0 | 0 | 35 | 0
21:30 | 3573.5 | 1918.5 | 876.5 | 38 | 44 | 753.735 | 222 | 5044 | 0 | 624 | 1827 | 0 | 0 | 25 | 0
22:00 | 3590 | 1927 | 877 | 38 | 46 | 754.58 | 222 | 5033 | 0 | 624 | 1834.6 | 0 | 0 | 15 | 0
22:30 | 3582.5 | 1933 | 876.5 | 38 | 46 | 754.07 | 221.5 | 5046 | 0 | 620.5 | 1816.9 | 0 | 0 | 21 | 0
23:00 | 3575 | 1939 | 876 | 38 | 46 | 753.56 | 221 | 5059 | 0 | 617 | 1799.2 | 0 | 0 | 27 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 06:00 | 371 | 15:00 | Payra | 413 | 06:00 | 406 | 17:00
Ashuganj | 408 | 6:00 | 381 | 15:00 | Rahanpur | 400 | 09:00 | 388 | 21:00
Bhulta | 404 | 05:00 | 379 | 15:00 | Rampal | 406 | 07:00 | 392 | 00:00
Bibiana | 390 | 07:00 | 380 | 15:00
BIPTC | 403 | 06:00 | 392 | 21:00
Bogura | 385 | 08:00 | 372 | 21:00
Gopalganj | 398 | 07:00 | 385 | 23:00
Kaliakoir | 373 | 06:00 | 361 | 16:00
Madunaghat | 391 | 07:00 | 385 | 16:00
Meghnaghat | 384 | 06:00 | 372 | 19:30
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 07:00 | 215 | 15:00 | Keranigonj | 221 | 06:00 | 213 | 15:00
AKSML | 229 | 18:00 | 222 | 15:00 | Khulna(S) | 233 | 08:00 | 218 | 00:00
Aminbazar | 225 | 7:00 | 217 | 16:00 | Madunaghat | 232 | 19:30 | 226 | 13:00
Ashuganj | 231 | 06:00 | 221 | 15:00 | Madunaghat-400 | 231 | 08:00 | 226 | 15:00
Ashuganj-400 | 231 | 06:00 | 221 | 15:00 | Maniknagar | 219 | 05:00 | 211 | 15:00
Baghabari | 235 | 05:00 | 226 | 21:00 | Meghnaghat | 226 | 07:00 | 220 | 15:00
Barapukuria | 227 | 19:00 | 220 | 21:00 | Meghnaghat-400 | 223 | 06:00 | 216 | 15:00
Barapukuria-230 | 227 | 19:00 | 220 | 21:00 | Mirsorai | 226 | 06:00 | 220 | 13:00
Barishal | 229 | 08:00 | 220 | 00:00 | Rajshahi | 231 | 06:00 | 219 | 21:00
Bheramara | 233 | 06:00 | 221 | 19:30 | Rampal | 232 | 08:00 | 220 | 00:00
Bhulta | 228 | 03:00 | 212 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 222 | 15:00 | Rampura | 229 | 06:00 | 209 | 15:00
BIPTC | 237 | 06:00 | 222 | 19:30 | Shikalbaha | 230 | 19:30 | 224 | 12:00
Bogura | 240 | 18:30 | 230 | 21:00 | Shyampur | 221 | 06:00 | 213 | 15:00
Bogura-400 | 239 | 08:00 | 230 | 21:00 | Siddhirganj | 220 | 06:00 | 214 | 15:00
Borhanuddin | 234 | 08:00 | 227 | 00:00 | Sirajgonj | 241 | 06:00 | 236 | 21:00
BSRM | 226 | 06:00 | 219 | 15:00 | Sreepur | 230 | 06:00 | 222 | 00:00
Cumilla(N) | 223 | 08:00 | 215 | 15:00 | Tongi | 225 | 07:00 | 215 | 15:00
Faridpur | 227 | 07:00 | 217 | 00:00
Fenchuganj | 229 | 07:00 | 224 | 01:00
Ghorashal | 230 | 00:00 | 220 | 13:00
Ghorashal-230 | 227 | 06:00 | 212 | 15:00
Gopalganj | 228 | 08:00 | 219 | 00:00
GPH | 228 | 06:00 | 222 | 15:00
Haripur | 220 | 06:00 | 213 | 15:00
Hasnabad | 222 | 04:00 | 214 | 14:00
Hathazari | 228 | 18:00 | 220 | 13:00
Ishurdi | 236 | 06:00 | 224 | 19:00
Jhenaidah | 233 | 06:00 | 217 | 19:30
Kaliakoir | 231 | 06:00 | 222 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 124 | 15:00 | Lalmonirhat | 131 | 14:00 | 124 | 12:00
Agargaon | 131 | 05:00 | 124 | 15:00 | Madanganj | 128 | 20:00 | 123 | 12:00
Agrabad | 131 | 19:30 | 125 | 13:00 | Madaripur | 134 | 09:00 | 129 | 00:00
AKS | 128 | 18:00 | 125 | 12:00 | Madartek | 138 | 06:00 | 124 | 15:00
Aminbazar | 133 | 04:00 | 127 | 11:00 | Madunaghat | 131 | 18:00 | 128 | 13:00
Amnura | 136 | 18:00 | 128 | 15:00 | Magura | 138 | 09:00 | 125 | 19:30
Ashuganj | 140 | 06:00 | 135 | 15:00 | Mahasthangarh | 132 | 18:30 | 122 | 23:00
Bagerhat | 135 | 07:00 | 122 | 00:00 | Maijdee | 124 | 08:00 | 114 | 00:00
Bajitpur | 130 | 06:00 | 123 | 19:30 | Manikganj | 126 | 06:00 | 118 | 14:00
Bakulia | 133 | 21:00 | 127 | 10:00 | Maniknagar | 133 | 08:00 | 126 | 12:00
Banani | 138 | 06:00 | 125 | 15:00 | Matarbari | 120 | 18:00 | 112 | 00:00
Bangabhaban | 132 | 03:00 | 126 | 12:00 | Matuail | 128 | 06:00 | 124 | 12:00
Barapukuria | 137 | 13:00 | 131 | 12:00 | Millgate | 132 | 03:00 | 122 | 15:00
Barguna | 134 | 05:00 | 129 | 00:00 | Mirpur | 130 | 01:00 | 125 | 10:00
Barishal | 136 | 08:00 | 126 | 00:00 | Mirzapur | 129 | 01:00 | 124 | 16:00
Barishal-230 | 135 | 08:00 | 128 | 00:00 | Mithapukur | 124 | 17:00 | 110 | 22:00
Baroaulia | 132 | 18:30 | 127 | 02:00 | MI_Cement | 129 | 06:00 | 123 | 12:00
Baroirhat | 126 | 09:00 | 119 | 15:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 03:00 | 123 | 15:00 | Mogbazar | 139 | 04:00 | 125 | 15:00
BashundharaCement | 128 | 20:00 | 123 | 15:00 | Mongla | 135 | 10:00 | 122 | 00:00
Beanibazar | 127 | 08:00 | 122 | 00:00 | Motijheel | 132 | 04:00 | 126 | 12:00
Benapole | 135 | 09:00 | 122 | 00:00 | Muktagacha | 133 | 11:00 | 126 | 00:00
Bhaluka | 130 | 06:00 | 122 | 15:00 | Munshiganj | 128 | 06:00 | 123 | 11:00
Bhandaria | 134 | 08:00 | 119 | 00:00 | Muradnagar | 124 | 06:00 | 118 | 15:00
Bhangura | 133 | 18:00 | 127 | 21:00 | Mymensingh | 135 | 11:00 | 115 | 00:00
Bheramara | 137 | 09:00 | 130 | 21:00 | Naogaon | 131 | 18:30 | 121 | 21:00
Bheramara(GK) | 137 | 08:00 | 131 | 19:00 | Narail | 138 | 08:00 | 125 | 19:30
Bhulta | 122 | 22:00 | 118 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 133 | 18:30 | 125 | 22:00 | Narshingdi | 138 | 23:00 | 119 | 19:30
Bogura | 134 | 08:00 | 126 | 21:00 | Natore | 134 | 08:00 | 126 | 21:00
Bogura-230 | 135 | 18:30 | 127 | 21:00 | Nawabganj | 133 | 03:00 | 126 | 15:00
Brahmanbaria | 135 | 09:00 | 129 | 00:00 | Netrakona | 125 | 07:00 | 112 | 19:00
Cantonment | 131 | 06:00 | 124 | 15:00 | New | 132 | 03:00 | 123 | 15:00
Chandina | 129 | 08:00 | 122 | 15:00 | Niamatpur | 136 | 08:00 | 131 | 22:00
Chandpur | 131 | 18:00 | 125 | 12:00 | Noapara | 136 | 07:00 | 126 | 00:00
Chandraghona | 132 | 21:00 | 129 | 03:00 | Pabna | 134 | 06:00 | 127 | 19:30
Chapai | 136 | 18:00 | 131 | 21:00 | Palashbari | 123 | 17:00 | 109 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 06:00 | 124 | 11:00 | Panchagarh | 135 | 19:00 | 123 | 19:30
Chauddagram | 126 | 07:00 | 117 | 15:00 | Patiya | 131 | 18:00 | 126 | 10:00
Chhatak | 126 | 06:00 | 119 | 00:00 | Patuakhali | 134 | 09:00 | 130 | 01:00
Chowmuhani | 123 | 08:00 | 114 | 00:00 | Payra | 136 | 06:00 | 133 | 00:00
Chuadanga | 135 | 18:00 | 122 | 00:00 | PHP | 124 | 08:00 | 117 | 15:00
Coxsbazar | 120 | 17:00 | 112 | 00:00 | Postogola | 131 | 06:00 | 126 | 12:00
Cumilla(N) | 127 | 06:00 | 122 | 15:00 | Purbachal | 137 | 02:00 | 122 | 15:00
Cumilla(S) | 132 | 01:00 | 121 | 15:00 | Purbasadipur | 132 | 17:00 | 122 | 19:30
Daganbhuiyan | 124 | 08:00 | 116 | 00:00 | Rahanpur | 137 | 06:00 | 133 | 21:00
Daudkandi | 125 | 18:00 | 117 | 00:00 | Rahanpur-400 | 138 | 18:00 | 133 | 21:00
Dhaka | 138 | 03:00 | 125 | 15:00 | Rahim | 128 | 06:00 | 124 | 13:00
Dhamrai | 131 | 03:00 | 123 | 15:00 | Rajbari | 133 | 08:00 | 125 | 00:00
Dhanmondi | 138 | 04:00 | 125 | 15:00 | Rajendrapur | 132 | 07:00 | 121 | 19:30
Dohazari | 130 | 18:00 | 123 | 02:00 | Rajshahi | 133 | 06:00 | 127 | 19:00
Faridpur | 134 | 06:00 | 128 | 00:00 | Rajshahi-230 | 133 | 06:00 | 126 | 21:00
Fatullah | 129 | 06:00 | 124 | 15:00 | Ramganj | 126 | 08:00 | 117 | 00:00
Fenchuganj | 135 | 06:00 | 131 | 00:00 | Rampur | 131 | 18:00 | 126 | 12:00
Feni | 124 | 08:00 | 116 | 12:00 | Rampura | 139 | 06:00 | 125 | 15:00
Ghatail | 129 | 08:00 | 122 | 01:00 | Rangamati | 131 | 18:00 | 128 | 12:00
Ghorashal | 136 | 23:00 | 128 | 15:00 | Rangpur | 134 | 13:00 | 128 | 11:00
Goalpara | 139 | 08:00 | 129 | 00:00 | Ruppur | 137 | 07:00 | 131 | 19:30
Gollamari | 139 | 07:00 | 130 | 00:00 | Saidpur | 133 | 18:00 | 124 | 19:30
Gopalganj | 136 | 08:00 | 128 | 00:00 | Satkhira | 136 | 09:00 | 123 | 00:00
Gopalganj-400 | 137 | 08:00 | 131 | 00:00 | Satmasjid | 131 | 06:00 | 125 | 12:00
Gulshan | 139 | 06:00 | 125 | 15:00 | Savar | 131 | 18:00 | 124 | 10:00
Halishahar | 132 | 18:00 | 126 | 10:00 | SevenRings | 138 | 08:00 | 127 | 16:00
Haripur | 129 | 06:00 | 124 | 15:00 | ShahCement | 129 | 06:00 | 124 | 11:00
HaripurSBU | 129 | 06:00 | 125 | 13:00 | Shahjadpur | 136 | 15:00 | 133 | 19:30
Hasnabad | 130 | 05:00 | 125 | 11:00 | Shahjibazar | 134 | 08:00 | 128 | 00:00
Hathazari | 132 | 02:00 | 127 | 15:00 | Shahmirpur | 133 | 21:00 | 127 | 13:00
Ishurdi | 138 | 06:00 | 131 | 19:30 | Shariatpur | 134 | 06:00 | 126 | 00:00
Jaldhaka | 131 | 18:00 | 122 | 19:30 | Sherpur | 134 | 08:00 | 121 | 01:00
Jamalpur | 136 | 08:00 | 124 | 01:00 | Shikalbaha | 122 | 18:00 | 117 | 12:00
Jashore | 137 | 07:00 | 124 | 23:00 | Shikalbaha-230 | 134 | 19:30 | 129 | 13:00
Jhenaidah | 138 | 07:00 | 121 | 19:30 | Shitalakhya | 129 | 06:00 | 123 | 12:00
Jhenaidah-230 | 139 | 08:00 | 128 | 19:30 | Sholosohor | 131 | 18:00 | 127 | 15:00
Joydebpur | 140 | 22:00 | 126 | 12:00 | Shyampur | 129 | 07:00 | 125 | 10:00
Joypurhat | 130 | 18:30 | 118 | 22:00 | Shyampur-230 | 131 | 06:00 | 124 | 12:00
Juldah | 132 | 20:00 | 127 | 13:00 | Siddhirganj | 129 | 08:00 | 124 | 12:00
Kabirpur | 132 | 04:00 | 118 | 15:00 | Sirajganj | 131 | 09:00 | 123 | 21:00
Kachua | 129 | 07:00 | 124 | 15:00 | Sonargaon | 127 | 05:00 | 122 | 11:00
Kaliakoir | 133 | 03:00 | 126 | 16:00 | Sreemongol | 132 | 06:00 | 127 | 00:00
Kallyanpur | 131 | 01:00 | 126 | 10:00 | Sreepur | 133 | 06:00 | 128 | 00:00
Kalurghat | 131 | 07:00 | 128 | 12:00 | Srinagar | 133 | 05:00 | 126 | 15:00
Kamrangirchar | 133 | 06:00 | 126 | 12:00 | SSM | 135 | 19:30 | 131 | 14:00
Kaptai | 134 | 8:00 | 132 | 1:00 | Sunamganj | 123 | 06:00 | 118 | 21:00
Kasba | 123 | 06:00 | 117 | 15:00 | Sylhet | 128 | 07:00 | 124 | 00:00
Kazla | 132 | 06:00 | 126 | 13:00 | Sylhet-132 | 127 | 04:00 | 125 | 00:00
Keranigonj | 133 | 06:00 | 126 | 15:00 | Tangail | 128 | 05:00 | 122 | 00:00
Khagrachori | 131 | 07:00 | 126 | 13:00 | Taraganj | 133 | 14:00 | 124 | 09:00
Khulna | 138 | 08:00 | 128 | 00:00 | Thakurgaon | 134 | 19:00 | 122 | 19:30
Khulna(S) | 140 | 08:00 | 129 | 00:00 | TK | 131 | 03:00 | 127 | 15:00
Khulshi | 130 | 18:00 | 125 | 12:00 | Tongi | 133 | 07:00 | 126 | 15:00
Kishoreganj | 128 | 05:00 | 121 | 14:00 | Ullahpara | 133 | 06:00 | 127 | 21:00
Kodda | 137 | 22:00 | 121 | 16:00 | Ullon | 138 | 06:00 | 124 | 15:00
KSRM | 132 | 04:00 | 127 | 15:00 | Uttara | 131 | 02:00 | 124 | 10:00
Kulaura | 133 | 07:00 | 130 | 00:00 | UttaraNew | 130 | 01:00 | 124 | 10:00
Kurigram | 131 | 13:00 | 125 | 00:00 | Zigatola | 133 | 06:00 | 126 | 16:00
Kushtia | 135 | 09:00 | 125 | 21:00
Laksam | 128 | 08:00 | 123 | 00:00
Lakshmipur | 125 | 08:00 | 116 | 00:00
Lalbag | 131 | 04:00 | 126 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division