## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-08-2025 | during | 24-08-2025 | during | 24-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 331 | 310 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 282 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 20 | 43.5 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 126 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 29 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.8 | 28 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 95 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 33 | 50 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 3 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 350 | 584 | 584 | 526 | 526
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 1739.8 | 2218.5 | 5363.54 | 5371.54 | 5037.6 | 5045.6
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 222 | 214 | 214 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 14 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 16 | 0 | 0 | 56 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 100 | 100 | 13 | 13 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 25 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.3 | 0 | 4.11 | 0 | 4.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 10 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 13 | 13 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 847 | 900 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 55 | 8 | 8 | 4 | 8 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 626 | 626 | 690 | 690 | 660 | 660 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1975.3 | 2218 | 3647.83 | 3636.72 | 3469.83 | 3474.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 39 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 23 | 44 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 32 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 18 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 35 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 15 | 117 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 16 | 17.75 | 17.75 | 17.75 | 17.75 | Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 99 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 54 | 113 | 113 | 55 | 55 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 97 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 26 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1173 | 1610 | 2417.81 | 2372.81 | 2333.81 | 2288.81
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-08-2025 | during | 24-08-2025 | during | 24-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 104 | 103 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 0 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 50 | 100 | 95 | 103 | 95 | 103 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.12 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 6 | 12 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 34 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 191.12 | 232 | 425 | 412 | 371.5 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 164 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 356 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1194 | 1171 | 1133 | 1133 | 1083 | 1083
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 872 | 866 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 350 | 373 | 410 | 410 | 410 | 410
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 28 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 449 | 986 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | Partial Shutdown due to maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1737 | 2280 | 3490.2 | 3405.2 | 3461.2 | 3376.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 299 | 300 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 1020 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 270 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.21 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1416.21 | 1925 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 18.14 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 183 | 214 | 214 | 192 | 192 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 185 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 183 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 361 | 387 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.17 | 0 | 5.4 | 0 | 5.4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 822.65 | 1120.67 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 22.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 90 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1778.16 | 2109.67 | 3158.27 | 2991.87 | 3050.48 | 2884.08
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 165 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 0 | 50 | 50 | 45 | 45 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 152 | 150 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 111 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 154 | 0 | 142.58 | 0 | 142.58 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 536.8 | 516 | 641.18 | 462 | 636.18 | 457
System Total |  |  |  |  | 28821.2 | 27843.665 | 11741.39 | 14280.17 | 22438.83 | 21946.14 | 21525.6 | 21071.91
Forecast Scenario (24-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14110 |  | 0 |  | 14110
|  |  |  | 1:00 | 13800 |  | 0 |  | 13800
|  |  |  | 2:00 | 13500 |  | 0 |  | 13500
|  |  |  | 3:00 | 13160 |  | 0 |  | 13160
|  |  |  | 4:00 | 12940 |  | 0 |  | 12940
|  |  |  | 5:00 | 12750 |  | 0 |  | 12750
|  |  |  | 6:00 | 12240 |  | 0 |  | 12240
|  |  |  | 7:00 | 12180 |  | 0 |  | 12180
|  |  |  | 8:00 | 12080 |  | 0 |  | 12080
|  |  |  | 9:00 | 12350 |  | 0 |  | 12350
|  |  |  | 10:00 | 12740 |  | 0 |  | 12740
|  |  |  | 11:00 | 12920 |  | 0 |  | 12920
|  |  |  | 12:00 | 13160 |  | 0 |  | 13160
|  |  |  | 13:00 | 13610 |  | 0 |  | 13610
|  |  |  | 14:00 | 13560 |  | 0 |  | 13560
|  |  |  | 15:00 | 13680 |  | 0 |  | 13680
|  |  |  | 16:00 | 13540 |  | 0 |  | 13540
|  |  |  | 17:00 | 13240 |  | 0 |  | 13240
|  |  |  | 18:00 | 12620 |  | 0 |  | 12620
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 14190 |  | 0 |  | 14190
|  |  |  | 19:30 | 15100 |  | 0 |  | 15100
|  |  |  | 20:00 | 15010 |  | 0 |  | 15010
|  |  |  | 21:00 | 14930 |  | 0 |  | 14930
|  |  |  | 22:00 | 14960 |  | 0 |  | 14960
|  |  |  | 23:00 | 14950 |  | 0 |  | 14950
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 13160.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 322.22 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:03 hrs on 24-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-08-2025 | [28 empty] | Date: | 23-08-2025 | [28 empty] | Date: | 23-08-2025 | [28 empty] | Date: | 23-08-2025 | [28 empty] | Date: | 23-08-2025 | [13 empty] | Date: | 23-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [13 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 17 | 62 | 0 | 0 | 0 | 0 | 0 | 320 | 289 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 36 | 626 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 945 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 47 | 196 | 40 | 102 | 70 | 111 | 44 | 14 | 30 | 44 | 0 | 0 | 0 | 310 | 0 | 376 | 0 | 60 | 141 | 8 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 100 | 0 | 132 | 0 | 0 | 12 | 6845 | 838 | 329 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1042 | 0 | 1210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 169 | 0 | 168 | 0 | 344 | 0 | 0 | 152 | 46 | 114 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 298 | 1050 | 0 | 6640 | 13485 | 108.23
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 320 | 285 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 40 | 625 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 945 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 47 | 194 | 40 | 100 | 70 | 108 | 44 | 11 | 29 | 42 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 60 | 137 | 8 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 91 | 0 | 136 | 0 | 0 | 1 | 6721 | 838 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 163 | 0 | 163 | 0 | 342 | 0 | 0 | 153 | 46 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 300 | 1000 | 0 | 6418 | 13139 | 108.22
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 320 | 285 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 40 | 626 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 940 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 48 | 194 | 40 | 101 | 70 | 108 | 49 | 11 | 30 | 40 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 60 | 138 | 8 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 91 | 0 | 136 | 0 | 0 | 0 | 6708 | 838 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 929 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 165 | 0 | 164 | 0 | 343 | 0 | 0 | 152 | 46 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 300 | 900 | 0 | 6001 | 12709 | 108.22
03:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 38 | 626 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 8 | 0 | 357 | 330 | 48 | 195 | 40 | 101 | 70 | 108 | 48 | 11 | 0 | 40 | 0 | 0 | 0 | 310 | 0 | 387 | 0 | 60 | 137 | 6 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 91 | 0 | 136 | 0 | 0 | 0 | 6575 | 852 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 818 | 0 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 165 | 0 | 164 | 0 | 346 | 0 | 0 | 151 | 46 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 300 | 870 | 0 | 5716 | 12291 | 108.22
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 21 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 38 | 629 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 48 | 196 | 40 | 101 | 70 | 85 | 49 | 11 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 381 | 0 | 60 | 141 | 6 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 90 | 0 | 138 | 0 | 0 | 3 | 6512 | 858 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 169 | 0 | 168 | 0 | 347 | 0 | 0 | 150 | 47 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 300 | 700 | 0 | 5493 | 12005 | 108.22
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 21 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 39 | 627 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 851 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 48 | 196 | 40 | 100 | 70 | 68 | 49 | 11 | 0 | 38 | 0 | 0 | 0 | 305 | 0 | 362 | 0 | 60 | 138 | 6 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 90 | 0 | 138 | 0 | 0 | 6 | 6455 | 858 | 381 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 166 | 0 | 165 | 0 | 345 | 0 | 0 | 150 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 299 | 600 | 0 | 5353 | 11808 | 108.21
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | 17 | 21 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.11 | 220 | 0 | 39 | 625 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 846 | 0 | 51 | 0 | 8 | 0 | 300 | 280 | 48 | 193 | 37 | 68 | 70 | 34 | 48 | 13 | 0 | 36 | 0 | 1 | 0 | 300 | 0 | 320 | 0 | 60 | 134 | 6 | 0 | 84 | 30 | 0 | 16 | 161 | 0 | 90 | 0 | 138 | 0 | 1.23 | 5 | 6046.34 | 858 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.8 | 778 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 0 | 1.56 | 163 | 0 | 160 | 0 | 159 | 0 | 341 | 0 | 0.13 | 150 | 47 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 170 | 100 | 180 | 0 | 299 | 600 | 0 | 5232.34 | 11278.68 | 108.21
07:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 320 | 287 | 0 | 0 | 0 | 250 | 0 | 0 | 8 | 17 | 21 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.61 | 220 | 0 | 35 | 626 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 854 | 6 | 51 | 0 | 8 | 0 | 280 | 280 | 47 | 194 | 40 | 34 | 70 | 30 | 44 | 13 | 0 | 32 | 0 | 3 | 0 | 305 | 0 | 321 | 0 | 60 | 136 | 0 | 0 | 43 | 20 | 0 | 16 | 161 | 0 | 90 | 0 | 138 | 0 | 3.24 | 4 | 5976.85 | 858 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 796 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.58 | 13 | 0 | 2.94 | 166 | 0 | 163 | 0 | 162 | 0 | 342 | 0 | 0.28 | 150 | 47 | 0 | 9 | 49 | 0 | 0 | 0 | 1.2 | 37 | 0.19 | 0 | 171 | 100 | 180 | 0 | 300 | 601 | 0 | 5336.19 | 11313.04 | 108.21
08:00 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 6 | 0 | 21 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 2.82 | 221 | 0 | 12 | 629 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 870 | 9 | 10 | 0 | 8 | 0 | 280 | 280 | 46 | 160 | 40 | 22 | 70 | 17 | 45 | 13 | 0 | 30 | 0 | 2 | 0 | 300 | 0 | 360 | 0 | 60 | 135 | 0 | 0 | 13 | 20 | 0 | 16 | 161 | 0 | 90 | 0 | 138 | 0 | 16.63 | 6 | 5817.45 | 867 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 785 | 0 | 827.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 49 | 0 | 5.98 | 140 | 0 | 152 | 0 | 150 | 0 | 357 | 0 | 0.74 | 144 | 47 | 70 | 10 | 49 | 0 | 0 | 0 | 0.6 | 105 | 0.18 | 0 | 156 | 100 | 180 | 0 | 301 | 580 | 0 | 5364.65 | 11182.1 | 108.21
09:00 | 0 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 0 | 5 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 300 | 0 | 0 | 11 | 0 | 21.8 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 1.73 | 221 | 0 | 8 | 628 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 827 | 6 | 10 | 0 | 8 | 0 | 320 | 280 | 12 | 190 | 40 | 16 | 70 | 16 | 42 | 13 | 0 | 30 | 0 | 10 | 0 | 310 | 0 | 316 | 0 | 60 | 144 | 0 | 0 | 13 | 20 | 0 | 16 | 163 | 0 | 91 | 0 | 137 | 1 | 12.39 | 6 | 5941.92 | 866 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 805 | 0 | 821.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.44 | 27 | 0 | 6.61 | 140 | 0 | 130 | 0 | 152 | 0 | 340 | 0 | 0.4 | 146 | 47 | 90 | 28 | 49 | 0 | 0 | 0 | 3 | 154 | 0.67 | 0 | 144 | 100 | 180 | 0 | 301 | 560 | 0 | 5400.68 | 11342.6 | 108.2
10:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 16.1 | 0 | 51 | 0 | 0 | 0 | 30 | 0 | 0 | 300 | 244 | 0 | 0 | 0 | 250 | 0 | 0 | 9 | 0 | 21.8 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 3.38 | 221 | 0 | 5 | 628 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 808 | 15 | 10 | 0 | 8 | 0 | 280 | 280 | 20 | 145 | 31 | 14 | 50 | 14 | 25 | 13 | 0 | 32 | 0 | 15 | 0 | 295 | 0 | 347 | 0 | 60 | 134 | 0 | 0 | 32 | 20 | 0 | 16 | 162 | 0 | 50 | 0 | 129 | 2 | 13.09 | 6 | 5722.37 | 872 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 761 | 0 | 820.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.27 | 86 | 0 | 21.64 | 140 | 0 | 130 | 0 | 148 | 0 | 280 | 0 | 2.63 | 146 | 47 | 35 | 17 | 38 | 0 | 20 | 0 | 2.7 | 159 | 0.01 | 0 | 143 | 100 | 180 | 0 | 301 | 545 | 0 | 5340.2 | 11062.57 | 108.2
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 14.7 | 0 | 51 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 12 | 0 | 21.8 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 4.05 | 222 | 0 | 4 | 630 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 846 | 10 | 10 | 0 | 8 | 0 | 347 | 330 | 20 | 200 | 35 | 15 | 70 | 15 | 25 | 13 | 0 | 34 | 0 | 58 | 0 | 305 | 0 | 325 | 0 | 60 | 138 | 0 | 0 | 32 | 20 | 0 | 16 | 163 | 0 | 50 | 0 | 115 | 1 | 38.28 | 6 | 6117.83 | 872 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 466 | 0 | 822.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.22 | 14 | 0 | 17.87 | 160 | 0 | 160 | 0 | 130 | 0 | 347 | 0 | 2.27 | 150 | 47 | 0 | 11 | 0 | 0 | 165 | 0 | 6.1 | 140 | 0.04 | 0 | 172 | 100 | 220 | 0 | 299 | 590 | 0 | 5347.21 | 11465.04 | 108.19
12:00 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 20 | 0 | 51 | 15 | 0 | 0 | 29 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 0 | 21.8 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 1.3 | 221 | 0 | 6 | 626 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 847 | 1 | 18 | 0 | 8 | 0 | 344 | 330 | 23 | 203 | 37 | 15 | 70 | 15 | 37 | 13 | 0 | 34 | 0 | 26 | 0 | 310 | 0 | 386 | 0 | 60 | 140 | 6 | 0 | 82 | 30 | 0 | 16 | 164 | 0 | 50 | 0 | 104 | 1 | 30.12 | 6 | 6273.22 | 872 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 449 | 0 | 822.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.14 | 90 | 0 | 22.2 | 165 | 0 | 167 | 0 | 130 | 0 | 361 | 0 | 2.17 | 152 | 47 | 0 | 15 | 0 | 0 | 165 | 0 | 3.8 | 154 | 0.21 | 0 | 172 | 115 | 220 | 0 | 299 | 610 | 0 | 5468.17 | 11741.39 | 108.19
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 32.7 | 0 | 67 | 15 | 0 | 0 | 35 | 8 | 0 | 300 | 283 | 0 | 0 | 0 | 280 | 0 | 0 | 7 | 0 | 21.8 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 2.36 | 219 | 0 | 15 | 625 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 861 | 1 | 51 | 0 | 8 | 0 | 349 | 330 | 30 | 194 | 37 | 24 | 70 | 21 | 42 | 13 | 14 | 32 | 0 | 78 | 0 | 310 | 0 | 380 | 0 | 60 | 157 | 6 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 0 | 98 | 1 | 29.95 | 6 | 6526.81 | 872 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 485 | 0 | 822.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 59 | 0 | 13.21 | 177 | 0 | 178 | 0 | 138 | 0 | 399 | 0 | 0.75 | 151 | 47 | 0 | 9 | 0 | 0 | 165 | 0 | 3.8 | 165 | 0.19 | 0 | 196 | 115 | 220 | 0 | 299 | 780 | 0 | 5718.52 | 12245.33 | 108.18
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 30.8 | 0 | 69 | 15 | 0 | 0 | 35 | 14 | 0 | 300 | 288 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 28 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 3.52 | 217 | 0 | 8 | 626 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 895 | 1 | 51 | 0 | 8 | 0 | 347 | 330 | 30 | 196 | 37 | 32 | 50 | 33 | 37 | 14 | 31 | 40 | 0 | 8 | 0 | 310 | 0 | 376 | 0 | 60 | 152 | 6 | 0 | 82 | 30 | 0 | 16 | 164 | 0 | 90 | 0 | 101 | 0 | 23.73 | 6 | 6505.05 | 872 | 307 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 495 | 0 | 862.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.16 | 4 | 0 | 3.46 | 165 | 0 | 187 | 0 | 166 | 0 | 343 | 0 | 0.37 | 152 | 47 | 0 | 19 | 0 | 0 | 165 | 0 | 8 | 197 | 0.16 | 0 | 198 | 115 | 180 | 0 | 299 | 800 | 0 | 5668.76 | 12173.81 | 108.17
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 30 | 0 | 69 | 0 | 0 | 0 | 35 | 14 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 12 | 17 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 2.57 | 217 | 0 | 2 | 626 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 898 | 5 | 51 | 0 | 8 | 0 | 348 | 330 | 30 | 202 | 38 | 47 | 70 | 61 | 45 | 14 | 30 | 38 | 0 | 5 | 0 | 305 | 0 | 382 | 0 | 60 | 153 | 6 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 90 | 0 | 102 | 1 | 10.89 | 6 | 6559.46 | 872 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 497 | 0 | 864.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.46 | 8 | 0 | 3.13 | 170 | 0 | 167 | 0 | 166 | 0 | 393 | 0 | 0.35 | 153 | 47 | 0 | 26 | 0 | 0 | 114 | 0 | 6.4 | 143 | 0.05 | 0 | 202 | 115 | 220 | 0 | 299 | 790 | 0 | 5671.28 | 12230.74 | 108.16
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 30 | 0 | 69 | 0 | 0 | 0 | 35 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 1.28 | 217 | 0 | 9 | 626 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 873 | 1 | 51 | 0 | 8 | 0 | 355 | 330 | 33 | 191 | 37 | 48 | 70 | 62 | 36 | 14 | 29 | 34 | 0 | 11 | 0 | 305 | 0 | 384 | 0 | 60 | 151 | 6 | 0 | 84 | 30 | 0 | 16 | 164 | 13 | 91 | 0 | 102 | 0 | 9.34 | 6 | 6531.62 | 872 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 501 | 0 | 860.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.37 | 5 | 0 | 0.54 | 177 | 0 | 164 | 0 | 164 | 0 | 340 | 0 | 0.11 | 155 | 47 | 0 | 20 | 0 | 0 | 164 | 0 | 5 | 116 | 0.1 | 0 | 194 | 115 | 220 | 0 | 299 | 780 | 0 | 5597.58 | 12129.2 | 108.15
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 29.4 | 0 | 69 | 0 | 0 | 0 | 35 | 14 | 0 | 300 | 283 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 17 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.22 | 218 | 0 | 9 | 625 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 778 | 2 | 51 | 0 | 8 | 0 | 300 | 280 | 43 | 196 | 32 | 46 | 70 | 60 | 42 | 14 | 29 | 32 | 0 | 6 | 0 | 300 | 0 | 316 | 0 | 60 | 141 | 6 | 0 | 84 | 30 | 0 | 16 | 164 | 17 | 90 | 0 | 102 | 0 | 1.35 | 7 | 6206.97 | 873 | 335 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 753 | 0 | 821.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 25 | 0 | 7.14 | 140 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 158 | 47 | 0 | 9 | 0 | 0 | 164 | 0 | 2.5 | 13 | 0.14 | 0 | 199 | 115 | 180 | 0 | 299 | 700 | 0 | 5519.42 | 11726.39 | 108.14
18:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 29.8 | 0 | 69 | 0 | 0 | 0 | 35 | 14 | 0 | 300 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | 17 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 0 | 0.03 | 219 | 0 | 13 | 628 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 790 | 0 | 51 | 0 | 8 | 0 | 300 | 280 | 44 | 206 | 39 | 48 | 70 | 61 | 42 | 14 | 30 | 34 | 0 | 1 | 0 | 305 | 0 | 346 | 0 | 60 | 139 | 7 | 0 | 84 | 30 | 0 | 16 | 164 | 17 | 99 | 0 | 102 | 0 | 0.24 | 12 | 6395.07 | 872 | 366 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 812 | 0 | 827.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 0 | 0.66 | 140 | 0 | 140 | 0 | 140 | 0 | 387 | 0 | 0 | 159 | 9 | 0 | 3 | 0 | 0 | 167 | 0 | 0.5 | 2 | 0.01 | 0 | 204 | 115 | 180 | 0 | 299 | 690 | 0 | 5553.87 | 11948.94 | 108.13
19:00 | 7 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 39.5 | 8 | 78 | 120 | 30 | 10 | 40 | 82 | 0 | 300 | 291 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 90 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 39 | 66 | 16 | 0 | 40 | 20 | 0 | 220 | 1 | 8 | 626 | 17 | 0 | 5 | 0 | 4 | 221 | 0 | 0 | 0 | 887 | 0 | 51 | 12 | 32 | 0 | 351 | 330 | 44 | 195 | 39 | 62 | 70 | 88 | 50 | 16 | 98 | 42 | 16 | 0 | 0 | 320 | 0 | 360 | 0 | 60 | 154 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 17 | 99 | 0 | 103 | 0 | 0 | 12 | 7257.5 | 870 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 7 | 953.8 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 153 | 0 | 175 | 0 | 408 | 0 | 0 | 154 | 0 | 105 | 0 | 42 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 220 | 0 | 300 | 814 | 0 | 6290.8 | 13548.3 | 108.12
19:30 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 43.5 | 35 | 95 | 126 | 30 | 30 | 55 | 54 | 0 | 300 | 282 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 125 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 66 | 16 | 0 | 50 | 25 | 0 | 220 | 10 | 25 | 626 | 17 | 0 | 19 | 0 | 14 | 222 | 0 | 0 | 0 | 900 | 0 | 51 | 35 | 32 | 0 | 355 | 330 | 44 | 186 | 39 | 97 | 70 | 117 | 54 | 16 | 99 | 42 | 43 | 0 | 0 | 305 | 0 | 356 | 0 | 60 | 148 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 17 | 100 | 0 | 103 | 0 | 0 | 12 | 7449.5 | 866 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 986 | 17 | 1120.67 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 185 | 0 | 183 | 0 | 387 | 0 | 0 | 150 | 0 | 111 | 0 | 90 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 300 | 1020 | 0 | 6830.67 | 14280.17
20:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 44.1 | 35 | 86 | 110 | 30 | 15 | 55 | 54 | 0 | 300 | 282 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 125 | 28 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 1 | 66 | 16 | 0 | 50 | 25 | 0 | 221 | 17 | 20 | 626 | 15 | 0 | 19 | 0 | 14 | 224 | 0 | 0 | 0 | 950 | 0 | 51 | 12 | 35 | 0 | 356 | 330 | 45 | 183 | 39 | 96 | 70 | 120 | 52 | 16 | 98 | 42 | 43 | 0 | 0 | 300 | 0 | 364 | 0 | 60 | 149 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 99 | 0 | 103 | 0 | 0 | 12 | 7423.1 | 865 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 17 | 1172.13 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 186 | 0 | 184 | 0 | 384 | 0 | 0 | 150 | 0 | 114 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 300 | 1058 | 0 | 6778.13 | 14201.23 | 108.11
21:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 44.5 | 17 | 68 | 110 | 0 | 0 | 24 | 17 | 0 | 300 | 288 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 29 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 32 | 626 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 962 | 0 | 51 | 0 | 60 | 0 | 356 | 330 | 46 | 190 | 39 | 98 | 70 | 124 | 49 | 16 | 98 | 42 | 16 | 0 | 0 | 310 | 0 | 363 | 0 | 60 | 148 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 100 | 0 | 103 | 0 | 0 | 12 | 7203.5 | 865 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 1218.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 190 | 0 | 189 | 0 | 401 | 0 | 0 | 151 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 300 | 1110 | 0 | 6909.48 | 14112.98 | 108.1
22:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 45 | 17 | 68 | 109 | 0 | 0 | 17 | 0 | 0 | 300 | 286 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 29 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 12 | 25 | 0 | 222 | 0 | 23 | 626 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 989 | 0 | 51 | 0 | 63 | 0 | 356 | 330 | 46 | 190 | 39 | 71 | 70 | 121 | 54 | 16 | 97 | 44 | 16 | 0 | 0 | 305 | 0 | 360 | 0 | 60 | 151 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 100 | 0 | 103 | 0 | 0 | 12 | 7155 | 865 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 1214.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 189 | 0 | 188 | 0 | 397 | 0 | 0 | 152 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 115 | 220 | 0 | 300 | 1110 | 0 | 6817.28 | 13972.28 | 108.09
23:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 33 | 17 | 68 | 124 | 0 | 0 | 17 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 29 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 12 | 25 | 0 | 222 | 0 | 27 | 626 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 63 | 0 | 355 | 330 | 46 | 196 | 40 | 61 | 70 | 120 | 63 | 16 | 98 | 44 | 16 | 0 | 0 | 305 | 0 | 368 | 0 | 60 | 151 | 8 | 0 | 84 | 30 | 0 | 16 | 163 | 0 | 100 | 0 | 103 | 0 | 0 | 9 | 7203 | 866 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 0 | 1229.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 190 | 0 | 189 | 0 | 407 | 0 | 0 | 152 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 298 | 1110 | 0 | 6792.19 | 13995.19 | 108.08
Total KWH | 6192 | 834240 | 273600 | 0 | 0 | 0 | 0 | 0 | 7952400 | 0 | 0 | 459720 | 127440 | 1178208 | 796800 | 47673 | 44176 | 477599 | 246240 | 0 | 7579500 | 6780567 | 0 | 0 | 32460 | 6998276 | 0 | 0 | 118210 | 1070400 | 592800 | 479160 | 0 | 8125000 | 0 | 0 | 0 | 0 | 805920 | 254593 | 23046 | 0 | 125760 | 118080 | 22199 | 5289713 | 54364 | 534240 | 12116363.64 | 25091 | 0 | 28800 | 0 | 34291 | 4979069 | 0 | 0 | 0 | 21299998 | 49140 | 1084400 | 51854 | 434909 | 0 | 8451600 | 7674000 | 936960 | 4735000 | 919008 | 1447680 | 1579670 | 1683840 | 1106280 | 323150 | 780900 | 893760 | 135158 | 184836 | 0 | 7447000 | 0 | 8985000 | 0 | 1410720 | 3466309 | 138960 | 0 | 1716480 | 668352 | 0 | 390000 | 4405680 | 77040 | 2100000 | 0 | 2747520 | 9100 | 210190 | 155040 | 156331724.64 | 20909090 | 8183232 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 228960 | 18814545 | 30240 | 22640909 | 0 | 0 | 0 | 0 | 0 | 0 | 95536 | 0 | 0 | 214897 | 388272 | 0 | 159000 | 4108636 | 0 | 4199818 | 0 | 4146464 | 0 | 8714909 | 0 | 13840 | 3714000 | 812945 | 1016583 | 192377 | 1010726 | 0 | 1574016 | 0 | 39504.84 | 1290960 | 1891 | 0 | 4756000 | 2661000 | 5259190 | 0 | 7200000 | 19588363.64 | 0 | 142877904.48 | 299209629.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11741.39 | MW | 12:00 Hr. | Energy Generated |  |  | 299.2096 |  | MKWHr.
| Day Peak Demand |  |  | 11741.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14280.17 | MW | 19:30 Hr. | Energy Demand |  |  | 299.2096 |  | MKWHr.
| Evening Peak Demand |  |  | 14280.17 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 11062.57 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1013.75 |  | MMCFD
| Maximum Generation of the Day |  |  | 14280.17 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.4381 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.5077 | 0 | 5.5947 | 0 | 0 | 0.11821 | 0 | 0 | 44.2207 | Gas | 138.809 | Gas | 496631649.33
| Chattogram Zone |  |  | 5.5133 | 33.4164 | 0.66402 | 0 | 5.2897 | 0.071339 | 0 | 0.80592 | 45.7607 | Coal | 88.3022 | Coal | 516397080.4876
| Cumilla Zone |  |  | 26.1387 | 0 | 5.2057 | 0 | 0 | 0.18484 | 0.89376 | 0 | 32.423 | HFO | 15.9497 | HFO | 290157357.8
| Mymensingh Zone |  |  | 2.7475 | 0 | 2.3321 | 0 | 0 | 0.21929 | 0 | 0 | 5.2989 | HSD | 1.574 | HSD | 0
| Sylhet Zone |  |  | 28.6285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6285 | Hydro | 5.2897 | Hydro | 528971.3
| Khulna Zone |  |  | 8.1832 | 18.8145 | 0.03024 | 0 | 0 | 0.22896 | 21.8211 | 0 | 49.0781 | Solar | 3.1234 | Solar | 49787225.5964
| Barishal Zone |  |  | 7.9202 | 31.5444 | 0 | 0 | 0 | 0.001891 | 0 | 0 | 39.4664 | Import | 45.3558 | Import | 261753612.07
| Rajshahi Zone |  |  | 21.1698 | 0 | 0.095536 | 0 | 0 | 0.77601 | 22.6409 | 0 | 44.6823 | Wind | 0.80592 | Wind | 11879260.8
| Rangpur Zone |  |  | 0 | 4.5269 | 2.0273 | 1.574 | 0 | 1.5228 | 0 | 0 | 9.6511
| Total |  |  | 138.809 | 88.3022 | 15.9497 | 1.574 | 5.2897 | 3.1234 | 45.3558 | 0.80592 | 299.2096
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 496631649.33 |  | Hydro | 528971.3
|  |  |  | Coal | 516397080.4876 |  | Solar | 49787225.5964
|  |  |  | HFO | 290157357.8 |  | Import | 261753612.07
|  |  |  | HSD | 0 |  | Wind | 11879260.8
[5 empty] | Total: | 162,71,35,157 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9091 | Peak Hr Flow | 866.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43769745.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.6409 | Peak Hr Flow | 1120.67 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 854 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.89376 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1092 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.4438 | Peak Hr Flow | 2028.67 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5017
|  |  |  | Chattogram |  | 0 |  | 1299
|  |  |  | Cumilla |  | 0 |  | 1304
|  |  |  | Mymensingh |  | 0 |  | 1127
|  |  |  | Sylhet |  | 0 |  | 616
|  |  |  | Khulna |  | 0 |  | 1689
|  |  |  | Barishal |  | 0 |  | 407
|  |  |  | Rajshahi |  | 0 |  | 1328
|  |  |  | Rangpur |  | 0 |  | 958
|  |  |  | Total |  | 0 |  | 13745
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:35 | 10:48 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to redhot maintenance from pbs | [7 empty] | 34.0MW load interrup.
| 08:35 | 10:45 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Redhot maintenance from pbs | [7 empty] | 34.0MW load interrup.
| 08:44 | 11:45 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to 33 KV Incomer | [7 empty] | 20.0MW load
|  |  | -01 Red hot Extinguish | [7 empty] | interrup.
| 08:45 | 11:44 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to 33 KV Incomer | [7 empty] | 20.0MW load
|  |  | -01 Red hot Extinguish | [7 empty] | interrup.
|  | 09:18 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT is restored.
|  | 09:20 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT is restored.
|  | 09:38 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
| 09:40 | 13:50 | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to Section DS and Faulty insulator Repair | [7 empty] | 20.0MW load interrup.
| 09:40 | 13:51 | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to Section DS and Faulty insulator Repair | [7 empty] | 20.0MW load interrup.
| 09:40 |  | Madaripur 132/33kV S/S T3-426T HT Scheduled S/D Due to Section DS and Faulty insulator Repair | [7 empty] | 20.0MW load interrup.
| 09:40 |  | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D Due to Section DS and Faulty insulator Repair | [7 empty] | 20.0MW load interrup.
|  | 09:42 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 09:44 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 09:44 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
|  | 09:54 | Mirpur-Uttara 132kV Ckt-1 is restored.
| 10:34 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 10:35 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-2 ( False )
| 11:07 |  | BIPTC S/S 20DF24 Forced S/D Due to Shutdown is taken for emergency maintenance work
| 11:07 | 14:10 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 50.0MW load interrup.
| 11:07 | 14:11 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 6.0MW load interrup.
| 11:08 | 15:55 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 kv bus section maintenance | [7 empty] | 50.0MW load interrup.
| 11:08 | 15:56 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33 Bus section maintenance | [7 empty] | 50.0MW load interrup.
| 11:17 | 21:22 | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing ditance
relay operated,18.7km,Zone-03,RYB Phase. relays Due to Heavy Rainfals,Bad Weather.
| 12:00 |  | Day Peak Generation: 11738 MW.
| 14:25 | 15:36 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Red hot remove of 33kv Vabki feeder incooming D.S. | [7 empty] | 12.0MW load interrup.
interrup.
| 14:25 | 15:36 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to red hot remove of 33kv Vabki feeder incooming D.S. | [7 empty] | 12.0MW load interrup.
| 14:26 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
| 14:48 |  | Rejection test of Saidpur 150MW occurred at 14:48 hrs.
| 15:08 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- at 14:52
| 15:58 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 15:59 |  | Rampal 1320 MW (BIFPCL) Unit-1 was syn. at 1559 hrs.
| 16:43 | 17:39 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Red hot at 33KV Bus DS of 33KV Betka feeder. | [7 empty] | 40.0MW load interrup.
| 16:44 | 17:38 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Red hot at 33KV Bus DS of 33KV Betka feeder. | [7 empty] | 40.0MW load interrup.
| 17:08 | 17:41 | Bogura 132/33kV S/S Transformer-1 LT Tripped showing SIPROTEC 7SJ81 relays Due to | [7 empty] | 37.0MW load
|  |  | Shajahanpur PBS-1 feeder fault. | [7 empty] | interrup.
| 18:00 |  | Barapukuria PS Unit-1 was shut down at 18:00 hrs due to UPS system not working.
| 18:24 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:-
| 19:30 |  | Evening Peak Generation 14279 MW.
| 19:48 | 22:25 | Pabna 132/33kV S/S T-3 LT Forced S/D Due to 33 kv CT R Phase hethot and flashing | [7 empty] | 10.0MW load interrup.
| 19:48 | 22:23 | Pabna 132/33kV S/S T-3 HT Forced S/D Due to 33 kv CT R Phase hethot and flashing | [7 empty] | 10.0MW load interrup.
| 20:17 |  | Saidpur 150 MW Power Plant Syn. Time: 14.55 and S/D time:19:45 (23/08/2025)
|  | 20:20 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) is restored.
|  | 20:51 | Fatullah 132/33kV S/S 132 kV Hasnabad is restored.
|  | 20:57 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 310 | 7952400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7579500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 282 | 6780567 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 44176 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6998276 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 6192 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 43.5 | 459720 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 796800 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 477599 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 32460 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 28 | 592800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 479160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 273600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 47673 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 1178208 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 834240 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 246240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 118210 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 127440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8125000 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1070400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2218.5 | 44220661
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 49140 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 28800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5289713 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 4979069 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 14 | 34291 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 23046 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 254593 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 125760 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 534240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 10 | 54364 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 118080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 25091 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 900 | 21299998 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 805920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 626 | 12116363.64 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2218 | 45760667.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 186 | 4735000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8451600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7674000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 919008 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 936960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 32 | 434909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1084400 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 35 | 51854 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1579670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 117 | 1683840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 42 | 893760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 135158 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 323150 | Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 780900 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 54 | 1106280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 1447680 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 184836 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1610 | 32423005
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 103 | 2747520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 0 | PSD taken from PDB, ref UMPL/BPDB/Vol-III/25/0583
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 100 | 2100000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 210190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 155040 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 77040 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 232 | 5298890
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1410720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3466309 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 668352 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1716480 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 4405680 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 390000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 138960 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7447000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 8985000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1171 | 28628501
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 866 | 20909090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 373 | 8183232 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 30240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 228960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 986 | 18814545 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2280 | 49078067
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 300 | 7200000 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2661000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 19588363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5259190 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 270 | 4756000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1891 | -
Barishal Area Total |  |  |  |  | 2236 | 1925 | 39466444.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 214897 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 183 | 4108636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4199818 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 183 | 4146464 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 387 | 8714909 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 95536 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1120.67 | 22640909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 159000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 388272 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2109.67 | 44682281
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 165 | 1574016 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 812945 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3714000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 1010726 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39504.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 111 | 1016583 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 192377 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1290960 | -
Rangpur Area Total |  |  |  |  | 950 | 516 | 9651111.84
Eastern Grid Total |  |  |  |  | 17401.505 | 7449.5 | 156331724.64
Western Grid Total |  |  |  |  | 10442.16 | 6830.67 | 142877904.48
National Grid Total |  |  |  |  | 27843.665 | 14280.17 | 299209629.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9362.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4381.8 | MW
i) Dhaka area |  |  | 5017.04 |  | MW | i) Khulna area |  |  |  | 1689 | MW
ii) Chattogram area |  |  | 1299 |  | MW | ii) Barishal area |  |  |  | 407 | MW
iii) Cumilla area |  |  | 1303.64 |  | MW | iii) Rajshahi area |  |  |  | 1327.8 | MW
iv) Mymensingh area |  |  | 1127 |  | MW | iv) Rangpur area |  |  |  | 958 | MW
v) Sylhet area |  |  | 616 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13744.48 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 72 | 19:30 | 133 | PHP | 8 | 08:00
2 | AKSML | 89 | 15:00 | 68 | Ishurdi | 76 | 21:00 | 134 | Pabna | 113 | 23:00
3 | Aftabnagar | 36 | 18:00 | 69 | Jaldhaka | 82 | 00:00 | 135 | Palashbari | 112 | 19:30
4 | Agargaon | 119 | 13:00 | 70 | Jamalpur | 122 | 22:00 | 136 | Panchagarh | 60 | 19:30
5 | Agrabad | 72 | 19:00 | 71 | Jashore | 125 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 27 | 22:00 | 72 | Jhenaidah | 121 | 19:00 | 138 | Patuakhali | 59.1 | 23:00
7 | Ashuganj | 82 | 00:00 | 73 | Joydebpur | 146 | 16:00 | 139 | Payra | 48 | 17:00
8 | BSRM | 175 | 03:00 | 74 | Joypurhat | 56 | 00:00 | 140 | Postogola | 56 | 13:00
9 | Bagerhat | 74 | 19:00 | 75 | Juldah | 18 | 10:00 | 141 | Purbachal | 19 | 19:00
10 | Bajitpur | 86 | 19:00 | 76 | KSRM | 13 | 21:00 | 142 | Purbasadipur | 124 | 19:30
11 | Bakulia | 82 | 12:00 | 77 | Kabirpur | 234 | 12:00 | 143 | Rahanpur | 35 | 23:00
12 | Banani | 38.4 | 13:00 | 78 | Kachua | 80 | 21:00 | 144 | Rahim | 21 | 11:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kallyanpur | 96 | 15:00 | 145 | Rajbari | 80 | 19:00
14 | Barapukuria | 63 | 21:00 | 80 | Kalurghat | 36 | 10:00 | 146 | Rajendrapur | 127 | 20:00
15 | Barguna | 20 | 22:00 | 81 | Kamrangirchar | 73 | 13:00 | 147 | Rajshahi | 104 | 21:00
16 | Barishal | 106 | 14:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 88 | 13:00
17 | Barishal-230 | 82 | 22:00 | 83 | Kasba | 35 | 13:00 | 149 | Ramganj | 108 | 00:00
18 | Baroaulia | 61 | 10:00 | 84 | Kazla | 93 | 11:00 | 150 | Rampur | 35 | 18:00
19 | Baroirhat | 53 | 20:00 | 85 | Keranigonj | 75 | 19:00 | 151 | Rangamati | 14 | 19:30
20 | Bashundhara | 175 | 19:00 | 86 | Khagrachori | 30 | 18:30 | 152 | Rangpur | 148 | 19:00
21 | BashundharaCement | 8 | 15:00 | 87 | Khulna | 65 | 12:00 | 153 | Ruppur | 5 | 11:00
22 | Beanibazar | 76 | 18:30 | 88 | Khulshi | 175 | 13:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 54 | 21:00 | 89 | Kishoreganj | 123 | 21:00 | 155 | Saidpur | 106 | 19:30
24 | Bhaluka | 144 | 19:00 | 90 | Kodda | 291 | 18:30 | 156 | Satkhira | 110 | 19:30
25 | Bhandaria | 50 | 22:00 | 91 | Kulaura | 59 | 22:00 | 157 | Satmasjid | 94 | 13:00
26 | Bhangura | 35 | 19:30 | 92 | Kurigram | 62 | 22:00 | 158 | Savar | 220 | 12:00
27 | Bheramara(GK) | 65 | 19:00 | 93 | Kushtia | 150 | 19:00 | 159 | SevenRings | 19.82 | 08:00
28 | Bhulta | 210 | 16:00 | 94 | Laksam | 36 | 19:00 | 160 | ShahCement | 12 | 20:00
29 | Bog-Sherpur | 70 | 00:00 | 95 | Lakshmipur | 18 | 00:00 | 161 | Shahjadpur | 78 | 19:00
30 | Bogura | 153 | 21:00 | 96 | Lalbag | 57 | 13:00 | 162 | Shahjibazar | 125 | 22:00
31 | Borhanuddin | 89 | 01:00 | 97 | Lalmonirhat | 65 | 19:00 | 163 | Shahmirpur | 60 | 14:00
32 | Brahmanbaria | 126 | 19:30 | 98 | MI_Cement | 11.8 | 10:00 | 164 | Shariatpur | 82 | 23:00
33 | Cantonment | 127 | 14:00 | 99 | Madanganj | 41 | 20:00 | 165 | Sherpur | 132 | 20:00
34 | Chandina | 17.05 | 00:00 | 100 | Madaripur | 112 | 19:30 | 166 | Shikalbaha | 14 | 11:00
35 | Chandpur | 75 | 21:00 | 101 | Madartek | 82 | 00:00 | 167 | Shitalakhya | 69.5 | 12:00
36 | Chandraghona | 32 | 23:00 | 102 | Madunaghat | 50 | 21:00 | 168 | Sholosohor | 44 | 16:00
37 | Chapai | 64 | 23:00 | 103 | Magura | 62 | 19:00 | 169 | Shyampur | 160 | 11:00
38 | Charsaidpur | 36 | 18:30 | 104 | Mahasthangarh | 76 | 22:00 | 170 | Siddhirganj | 110 | 15:00
39 | Chauddagram | 65 | 22:00 | 105 | Maijdee | 13 | 01:00 | 171 | Sirajganj | 98 | 19:30
40 | Chhatak | 40 | 20:00 | 106 | Manikganj | 116 | 21:00 | 172 | Sonargaon | 109 | 10:00
41 | Chowmuhani | 177 | 19:30 | 107 | Maniknagar | 58 | 13:00 | 173 | Sreemongol | 79 | 20:00
42 | Chuadanga | 108 | 19:00 | 108 | Matarbari | 43 | 18:30 | 174 | Sreepur | 95 | 19:00
43 | Coxsbazar | 131 | 19:00 | 109 | Matuail | 64 | 09:00 | 175 | Srinagar | 43.82 | 00:00
44 | Cumilla(N) | 121 | 00:00 | 110 | Millgate | 117 | 12:00 | 176 | Sunamganj | 62 | 21:00
45 | Cumilla(S) | 134 | 15:00 | 111 | Mirpur | 114 | 19:00 | 177 | Sylhet | 55 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 9 | 09:00 | 178 | Sylhet-132 | 134 | 18:30
47 | Daudkandi | 140 | 22:00 | 113 | Mirzapur | 43 | 19:00 | 179 | TK | 31 | 23:00
48 | Dhaka | 66 | 12:00 | 114 | Mithapukur | 70 | 19:00 | 180 | Tangail | 168 | 19:30
49 | Dhamrai | 112 | 19:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 20 | 00:00
50 | Dhanmondi | 122 | 13:00 | 116 | Mogbazar | 96.4 | 14:00 | 182 | Thakurgaon | 102 | 00:00
51 | Dohazari | 102 | 18:30 | 117 | Mongla | 34 | 12:00 | 183 | Tongi | 89 | 18:30
52 | Faridpur | 169 | 19:00 | 118 | Motijheel | 41 | 13:00 | 184 | Ullahpara | 33 | 00:00
53 | Fatullah | 101 | 12:00 | 119 | Muktagacha | 32 | 00:00 | 185 | Ullon | 51 | 19:00
54 | Fenchuganj | 48 | 22:00 | 120 | Munshiganj | 106 | 00:00 | 186 | Uttara | 72 | 19:00
55 | Feni | 102 | 21:00 | 121 | Muradnagar | 40 | 21:00 | 187 | UttaraNew | 55 | 13:00
56 | GPH | 83 | 04:00 | 122 | Mymensingh | 180 | 00:00 | 188 | Zigatola | 68 | 13:00
57 | Ghatail | 78 | 19:00 | 123 | Naogaon | 115 | 00:00
58 | Ghorashal | 12 | 08:00 | 124 | Narail | 53 | 19:30
59 | Ghorashal-230 | 84 | 21:00 | 125 | Narinda | 68 | 13:00
60 | Goalpara | 39 | 23:00 | 126 | Narshingdi | 177 | 19:30
61 | Gollamari | 80 | 13:00 | 127 | Natore | 139 | 19:30
62 | Gopalganj | 98 | 19:00 | 128 | Nawabganj | 54.2 | 22:00
63 | Gulshan | 96 | 13:00 | 129 | Netrakona | 134 | 19:00
64 | Halishahar | 63 | 15:00 | 130 | New | 70.6 | 12:00
65 | HaripurSBU | 165 | 09:00 | 131 | Niamatpur | 66 | 22:00
66 | Hasnabad | 85 | 18:00 | 132 | Noapara | 42 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13485 | 0 |  | 13485
1:00 | 13139 | 0 |  | 13139
2:00 | 12709 | 0 |  | 12709
3:00 | 12291 | 0 |  | 12291
4:00 | 12005 | 0 |  | 12005
5:00 | 11808 | 0 |  | 11808
6:00 | 11278.68 | 0 |  | 11278.68
7:00 | 11313.04 | 0 |  | 11313.04
8:00 | 11182.1 | 0 |  | 11182.1
9:00 | 11342.6 | 0 |  | 11342.6
10:00 | 11062.57 | 0 |  | 11062.57
11:00 | 11465.04 | 0 |  | 11465.04
12:00 | 11741.39 | 0 |  | 11741.39
13:00 | 12245.33 | 0 |  | 12245.33
14:00 | 12173.81 | 0 |  | 12173.81
15:00 | 12230.74 | 0 |  | 12230.74
16:00 | 12129.2 | 0 |  | 12129.2
17:00 | 11726.39 | 0 |  | 11726.39
18:00 | 11948.94 | 0 |  | 11948.94
19:00 | 13548.3 | 0 |  | 13548.3
19:30 | 14280.17 | 0 |  | 14280.17
20:00 | 14201.23 | 0 |  | 14201.23
21:00 | 14112.98 | 0 |  | 14112.98
22:00 | 13972.28 | 0 |  | 13972.28
23:00 | 13995.19 | 0 |  | 13995.19
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6845 | 6640 | 13485 | DAILY GENERATION CURVE
00:30 | 6783 | 6529 | 13312
01:00 | 6721 | 6418 | 13139 | 23-08-2025
01:30 | 6714.5 | 6209.5 | 12924
02:00 | 6708 | 6001 | 12709
02:30 | 6641.5 | 5858.5 | 12500
03:00 | 6575 | 5716 | 12291
03:30 | 6543.5 | 5604.5 | 12148
04:00 | 6512 | 5493 | 12005
04:30 | 6483.5 | 5423 | 11906.5
05:00 | 6455 | 5353 | 11808
05:30 | 6250.67 | 5292.67 | 11543.34
06:00 | 6046.34 | 5232.34 | 11278.68
06:30 | 6011.595 | 5284.265 | 11295.86
07:00 | 5976.85 | 5336.19 | 11313.04
07:30 | 5897.15 | 5350.42 | 11247.57
08:00 | 5817.45 | 5364.65 | 11182.1
08:30 | 5879.685 | 5382.665 | 11262.35
09:00 | 5941.92 | 5400.68 | 11342.6
09:30 | 5832.145 | 5370.44 | 11202.585
10:00 | 5722.37 | 5340.2 | 11062.57
10:30 | 5920.1 | 5343.705 | 11263.805
11:00 | 6117.83 | 5347.21 | 11465.04
11:30 | 6195.525 | 5407.69 | 11603.215
12:00 | 6273.22 | 5468.17 | 11741.39
12:30 | 6400.015 | 5593.345 | 11993.36
13:00 | 6526.81 | 5718.52 | 12245.33
13:30 | 6515.93 | 5693.64 | 12209.57
14:00 | 6505.05 | 5668.76 | 12173.81
14:30 | 6532.255 | 5670.02 | 12202.275
15:00 | 6559.46 | 5671.28 | 12230.74
15:30 | 6545.54 | 5634.43 | 12179.97
16:00 | 6531.62 | 5597.58 | 12129.2
16:30 | 6369.295 | 5558.5 | 11927.795
17:00 | 6206.97 | 5519.42 | 11726.39
17:30 | 6301.02 | 5536.645 | 11837.665
18:00 | 6395.07 | 5553.87 | 11948.94
18:30 | 6826.285 | 5922.335 | 12748.62
19:00 | 7257.5 | 6290.8 | 13548.3
19:30 | 7449.5 | 6830.67 | 14280.17
20:00 | 7423.1 | 6778.13 | 14201.23
20:30 | 7313.3 | 6843.805 | 14157.105 |  | Executive Engineer
21:00 | 7203.5 | 6909.48 | 14112.98 |  | Network Operation Division
21:30 | 7179.25 | 6863.38 | 14042.63
22:00 | 7155 | 6817.28 | 13972.28
22:30 | 7179 | 6804.735 | 13983.735
23:00 | 7203 | 6792.19 | 13995.19

## En-Curve
QF-LDC-12
Date | 23-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3958 | 1920 | 838 | 38 | 44 | 1210 | 221 | 4388 | 0 | 202 | 636 | 0 | 0 | 30 | 0 | DAILY ENERGY CURVE
00:30 | 3939.5 | 1914.5 | 838 | 38 | 43 | 1164 | 221 | 4349.5 | 0 | 168 | 603 | 0 | 0 | 33.5 | 0 | 23-08-2025
01:00 | 3921 | 1909 | 838 | 38 | 42 | 1118 | 221 | 4311 | 0 | 134 | 570 | 0 | 0 | 37 | 0
01:30 | 3929.5 | 1910 | 838 | 38 | 41 | 1065 | 221 | 4187.5 | 0 | 126.5 | 532.5 | 0 | 0 | 35 | 0 | Energy Generated | 299.2096 |  | MKWHr
02:00 | 3938 | 1911 | 838 | 38 | 40 | 1012 | 221 | 4064 | 0 | 119 | 495 | 0 | 0 | 33 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3960.5 | 1912 | 845 | 38 | 40 | 936.5 | 220.5 | 3951 | 0 | 94 | 464.5 | 0 | 0 | 38 | 0 | Total Energy Requirement | 299.2096 |  | MKWHr
03:00 | 3983 | 1913 | 852 | 38 | 40 | 861 | 220 | 3838 | 0 | 69 | 434 | 0 | 0 | 43 | 0
03:30 | 3999 | 1905.5 | 855 | 38 | 39 | 843.5 | 220 | 3747.5 | 0 | 52 | 407 | 0 | 0 | 41.5 | 0
04:00 | 4015 | 1898 | 858 | 38 | 38 | 826 | 220 | 3657 | 0 | 35 | 380 | 0 | 0 | 40 | 0
04:30 | 4002 | 1900 | 858 | 38 | 38 | 826.5 | 220 | 3601.5 | 0 | 35 | 355 | 0 | 0 | 32.5 | 0
05:00 | 3989 | 1902 | 858 | 38 | 38 | 827 | 220 | 3546 | 0 | 35 | 330 | 0 | 0 | 25 | 0
05:30 | 3786 | 1862.5 | 858 | 38 | 37 | 824.5 | 220 | 3530.5 | 5.34 | 26 | 326 | 0 | 0 | 29.5 | 0
06:00 | 3583 | 1823 | 858 | 38 | 36 | 822 | 220 | 3515 | 10.68 | 17 | 322 | 0 | 0 | 34 | 0
06:30 | 3576.5 | 1801.5 | 858 | 38 | 34 | 824 | 220 | 3530 | 59.36 | 25.5 | 295 | 0 | 0 | 34 | 0
07:00 | 3570 | 1780 | 858 | 38 | 32 | 826 | 220 | 3545 | 108.04 | 34 | 268 | 0 | 0 | 34 | 0
07:30 | 3512.5 | 1694.5 | 862.5 | 38 | 31 | 826.775 | 220.5 | 3528.5 | 172.795 | 36.5 | 292 | 0 | 0 | 32 | 0
08:00 | 3455 | 1609 | 867 | 38 | 30 | 827.55 | 221 | 3512 | 237.55 | 39 | 316 | 0 | 0 | 30 | 0
08:30 | 3487 | 1621.9 | 866.5 | 38 | 30 | 824.555 | 221 | 3485 | 275.395 | 48 | 328 | 0 | 0 | 37 | 0
09:00 | 3519 | 1634.8 | 866 | 38 | 30 | 821.56 | 221 | 3458 | 313.24 | 57 | 340 | 0 | 0 | 44 | 0
09:30 | 3402 | 1599.8 | 869 | 38 | 31 | 821.255 | 221 | 3418.5 | 372.98 | 61.5 | 309.55 | 10 | 0 | 48 | 0
10:00 | 3285 | 1564.8 | 872 | 38 | 32 | 820.95 | 221 | 3379 | 432.72 | 66 | 279.1 | 20 | 0 | 52 | 0
10:30 | 3502 | 1638.3 | 872 | 38 | 33 | 821.83 | 221.5 | 3289.5 | 407.275 | 58 | 236.4 | 92.5 | 0 | 53.5 | 0
11:00 | 3719 | 1711.8 | 872 | 38 | 34 | 822.71 | 222 | 3200 | 381.83 | 50 | 193.7 | 165 | 0 | 55 | 0
11:30 | 3790 | 1749.8 | 872 | 38 | 34 | 822.68 | 221.5 | 3201 | 388.885 | 57 | 208.35 | 165 | 0 | 55 | 0
12:00 | 3861 | 1787.8 | 872 | 38 | 34 | 822.65 | 221 | 3202 | 395.94 | 64 | 223 | 165 | 0 | 55 | 0
12:30 | 3889.5 | 1828.8 | 872 | 38 | 33 | 822.56 | 220 | 3323 | 400.65 | 64.5 | 280.35 | 165 | 0 | 56 | 0
13:00 | 3918 | 1869.8 | 872 | 38 | 32 | 822.47 | 219 | 3444 | 405.36 | 65 | 337.7 | 165 | 0 | 57 | 0
13:30 | 3867.5 | 1845.9 | 872 | 38 | 36 | 842.54 | 218 | 3478 | 361.88 | 73.5 | 357.75 | 165 | 0 | 53.5 | 0
14:00 | 3817 | 1822 | 872 | 38 | 40 | 862.61 | 217 | 3512 | 318.4 | 82 | 377.8 | 165 | 0 | 50 | 0
14:30 | 3871 | 1844.5 | 872 | 38 | 39 | 863.75 | 217 | 3512 | 288.125 | 74.5 | 402.4 | 139.5 | 0 | 40.5 | 0
15:00 | 3925 | 1867 | 872 | 38 | 38 | 864.89 | 217 | 3512 | 257.85 | 67 | 427 | 114 | 0 | 31 | 0
15:30 | 3887 | 1867 | 872 | 38 | 36 | 862.675 | 217 | 3493.5 | 233.795 | 67 | 431.5 | 139 | 0 | 35.5 | 0
16:00 | 3849 | 1867 | 872 | 38 | 34 | 860.46 | 217 | 3475 | 209.74 | 67 | 436 | 164 | 0 | 40 | 0
16:30 | 3726 | 1843 | 872.5 | 38 | 33 | 841.11 | 217.5 | 3517 | 144.485 | 67 | 437.2 | 164 | 0 | 27 | 0
17:00 | 3603 | 1819 | 873 | 38 | 32 | 821.76 | 218 | 3559 | 79.23 | 67 | 438.4 | 164 | 0 | 14 | 0
17:30 | 3663.5 | 1832 | 872.5 | 38 | 33 | 824.69 | 218.5 | 3575 | 44.875 | 99 | 447.6 | 165.5 | 0 | 23.5 | 0
18:00 | 3724 | 1845 | 872 | 38 | 34 | 827.62 | 219 | 3591 | 10.52 | 131 | 456.8 | 167 | 0 | 33 | 0
18:30 | 3814.5 | 1886.5 | 871 | 38 | 38 | 890.71 | 219.5 | 3782 | 5.26 | 270 | 731.65 | 165.5 | 0 | 36 | 0
19:00 | 3905 | 1928 | 870 | 38 | 42 | 953.8 | 220 | 3973 | 0 | 409 | 1006.5 | 164 | 0 | 39 | 0
19:30 | 3917 | 1915 | 866 | 38 | 42 | 1120.67 | 220 | 4252 | 0 | 450 | 1286.5 | 165 | 0 | 8 | 0
20:00 | 3926 | 1910 | 865 | 38 | 42 | 1172.13 | 221 | 4356 | 0 | 434 | 1236.1 | 0 | 0 | 1 | 0
20:30 | 3974 | 1937 | 865 | 38 | 42 | 1195.305 | 221 | 4438.5 | 0 | 384 | 1060.3 | 0 | 0 | 2 | 0
21:00 | 4022 | 1964 | 865 | 38 | 42 | 1218.48 | 221 | 4521 | 0 | 334 | 884.5 | 0 | 0 | 3 | 0
21:30 | 4015.5 | 1959 | 865 | 38 | 43 | 1216.38 | 221.5 | 4494 | 0 | 325 | 859.75 | 0 | 0 | 5.5 | 0
22:00 | 4009 | 1954 | 865 | 38 | 44 | 1214.28 | 222 | 4467 | 0 | 316 | 835 | 0 | 0 | 8 | 0
22:30 | 4011 | 1958.5 | 865.5 | 38 | 44 | 1221.735 | 222 | 4457 | 0 | 323.5 | 827 | 0 | 0 | 15.5 | 0
23:00 | 4013 | 1963 | 866 | 38 | 44 | 1229.19 | 222 | 4447 | 0 | 331 | 819 | 0 | 0 | 23 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 7:00 | 375 | 20:00 | Payra | 415 | 07:00 | 409 | 00:00
Ashuganj | 404 | 5:00 | 387 | 12:00 | Rahanpur | 404 | 10:00 | 387 | 21:00
Bhulta | 400 | 05:00 | 383 | 12:00 | Rampal | 406 | 07:00 | 392 | 00:00
Bibiana | 389 | 05:00 | 383 | 00:00
BIPTC | 404 | 07:00 | 396 | 19:30
Bogura | 390 | 10:00 | 369 | 23:00
Gopalganj | 400 | 09:00 | 388 | 21:00
Kaliakoir | 377 | 06:00 | 367 | 21:00
Madunaghat | 394 | 05:00 | 230 | 02:00
Meghnaghat | 388 | 06:00 | 380 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 219 | 15:00 | Keranigonj | 225 | 06:00 | 218 | 13:00
AKSML | 231 | 07:00 | 226 | 01:00 | Khulna(S) | 231 | 09:00 | 220 | 21:00
Aminbazar | 228 | 6:00 | 221 | 22:00 | Madunaghat | 233 | 18:30 | 228 | 00:00
Ashuganj | 231 | 07:00 | 225 | 00:00 | Madunaghat-400 | 234 | 20:00 | 229 | 00:00
Ashuganj-400 | 232 | 7:00 | 224 | 12:00 | Maniknagar | 221 | 6:00 | 215 | 15:00
Baghabari | 235 | 04:00 | 226 | 21:00 | Meghnaghat | 229 | 04:00 | 224 | 14:00
Barapukuria | 229 | 08:00 | 215 | 23:00 | Meghnaghat-400 | 226 | 07:00 | 221 | 12:00
Barapukuria-230 | 229 | 8:00 | 217 | 18:00 | Mirsorai | 228 | 06:00 | 221 | 00:00
Barishal | 231 | 09:00 | 222 | 00:00 | Rajshahi | 231 | 09:00 | 218 | 21:00
Bheramara | 231 | 06:00 | 221 | 21:00 | Rampal | 231 | 08:00 | 221 | 00:00
Bhulta | 231 | 05:00 | 217 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 06:00 | 224 | 00:00 | Rampura | 230 | 06:00 | 22 | 00:00
BIPTC | 234 | 10:00 | 222 | 21:00 | Shikalbaha | 231 | 08:00 | 226 | 00:00
Bogura | 243 | 10:00 | 230 | 21:00 | Shyampur | 224 | 06:00 | 218 | 13:00
Bogura-400 | 243 | 10:00 | 230 | 21:00 | Siddhirganj | 223 | 7:00 | 219 | 20:00
Borhanuddin | 235 | 09:00 | 229 | 00:00 | Sirajgonj | 241 | 06:00 | 235 | 23:00
BSRM | 228 | 18:00 | 224 | 03:00 | Sreepur | 230 | 06:00 | 222 | 21:00
Cumilla(N) | 223 | 05:00 | 217 | 00:00 | Tongi | 225 | 08:00 | 220 | 11:00
Faridpur | 228 | 03:00 | 218 | 21:00
Fenchuganj | 230 | 09:00 | 225 | 00:00
Ghorashal | 230 | 01:00 | 220 | 00:00
Ghorashal-230 | 229 | 06:00 | 218 | 13:00
Gopalganj | 229 | 09:00 | 220 | 21:00
GPH | 230 | 06:00 | 224 | 00:00
Haripur | 223 | 06:00 | 218 | 00:00
Hasnabad | 225 | 08:00 | 219 | 12:00
Hathazari | 231 | 19:30 | 222 | 00:00
Ishurdi | 234 | 08:00 | 224 | 23:00
Jhenaidah | 229 | 10:00 | 220 | 16:00
Kaliakoir | 234 | 06:00 | 227 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 127 | 12:00 | Lalmonirhat | 155 | 16:00 | 118 | 23:00
Agargaon | 134 | 06:00 | 128 | 12:00 | Madanganj | 132 | 07:00 | 125 | 11:00
Agrabad | 132 | 19:30 | 126 | 15:00 | Madaripur | 136 | 10:00 | 130 | 00:00
AKS | 130 | 19:00 | 126 | 00:00 | Madartek | 137 | 03:00 | 127 | 12:00
Aminbazar | 134 | 6:00 | 128 | 22:00 | Madunaghat | 133 | 19:00 | 129 | 00:00
Amnura | 137 | 09:00 | 126 | 21:00 | Magura | 133 | 05:00 | 123 | 19:00
Ashuganj | 141 | 06:00 | 137 | 00:00 | Mahasthangarh | 135 | 10:00 | 125 | 21:00
Bagerhat | 134 | 10:00 | 122 | 23:00 | Maijdee | 120 | 20:00 | 112 | 00:00
Bajitpur | 131 | 10:00 | 124 | 20:00 | Manikganj | 130 | 05:00 | 125 | 00:00
Bakulia | 134 | 20:00 | 127 | 00:00 | Maniknagar | 135 | 04:00 | 130 | 13:00
Banani | 137 | 03:00 | 125 | 13:00 | Matarbari | 122 | 19:30 | 112 | 00:00
Bangabhaban | 135 | 06:00 | 130 | 13:00 | Matuail | 130 | 06:00 | 126 | 11:00
Barapukuria | 140 | 08:00 | 127 | 23:00 | Millgate | 135 | 04:00 | 128 | 12:00
Barguna | 136 | 09:00 | 131 | 00:00 | Mirpur | 133 | 07:00 | 127 | 12:00
Barishal | 136 | 09:00 | 129 | 00:00 | Mirzapur | 129 | 03:00 | 125 | 18:30
Barishal-230 | 136 | 10:00 | 129 | 00:00 | Mithapukur | 133 | 06:00 | 124 | 21:00
Baroaulia | 132 | 05:00 | 128 | 13:00 | MI_Cement | 131 | 06:00 | 125 | 12:00
Baroirhat | 125 | 19:00 | 119 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 03:00 | 127 | 11:00 | Mogbazar | 137 | 02:00 | 127 | 13:00
BashundharaCement | 132 | 07:00 | 125 | 11:00 | Mongla | 134 | 09:00 | 124 | 23:00
Beanibazar | 129 | 09:00 | 123 | 23:00 | Motijheel | 135 | 06:00 | 130 | 13:00
Benapole | 133 | 09:00 | 123 | 21:00 | Muktagacha | 135 | 09:00 | 123 | 21:00
Bhaluka | 130 | 06:00 | 125 | 00:00 | Munshiganj | 130 | 06:00 | 125 | 11:00
Bhandaria | 132 | 11:00 | 123 | 22:00 | Muradnagar | 124 | 06:00 | 119 | 00:00
Bhangura | 134 | 08:00 | 128 | 23:00 | Mymensingh | 135 | 09:00 | 116 | 22:00
Bheramara | 137 | 08:00 | 132 | 21:00 | Naogaon | 132 | 09:00 | 122 | 21:00
Bheramara(GK) | 137 | 08:00 | 132 | 19:00 | Narail | 132 | 09:00 | 121 | 19:30
Bhulta | 125 | 04:00 | 119 | 23:00 | Narinda | 135 | 4:00 | 130 | 13:00
Bog-Sherpur | 135 | 10:00 | 127 | 21:00 | Narshingdi | 135 | 02:00 | 120 | 20:00
Bogura | 137 | 09:00 | 128 | 21:00 | Natore | 134 | 08:00 | 126 | 21:00
Bogura-230 | 138 | 09:00 | 128 | 21:00 | Nawabganj | 136 | 07:00 | 130 | 00:00
Brahmanbaria | 135 | 04:00 | 129 | 20:00 | Netrakona | 128 | 10:00 | 115 | 22:00
Cantonment | 133 | 04:00 | 128 | 12:00 | New | 134 | 07:00 | 129 | 12:00
Chandina | 128 | 19:30 | 123 | 00:00 | Niamatpur | 138 | 08:00 | 130 | 00:00
Chandpur | 129 | 20:00 | 121 | 09:00 | Noapara | 136 | 09:00 | 126 | 23:00
Chandraghona | 132 | 05:00 | 130 | 00:00 | Pabna | 135 | 09:00 | 128 | 23:00
Chapai | 137 | 09:00 | 128 | 23:00 | Palashbari | 132 | 10:00 | 121 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 06:00 | 125 | 13:00 | Panchagarh | 137 | 08:00 | 121 | 05:00
Chauddagram | 125 | 19:30 | 118 | 00:00 | Patiya | 131 | 07:00 | 127 | 00:00
Chhatak | 126 | 06:00 | 120 | 21:00 | Patuakhali | 135 | 08:00 | 131 | 22:00
Chowmuhani | 121 | 20:00 | 113 | 01:00 | Payra | 136 | 04:00 | 133 | 22:00
Chuadanga | 132 | 09:00 | 121 | 23:00 | PHP | 125 | 19:00 | 119 | 01:00
Coxsbazar | 122 | 09:00 | 113 | 00:00 | Postogola | 133 | 06:00 | 129 | 00:00
Cumilla(N) | 128 | 19:30 | 123 | 00:00 | Purbachal | 137 | 03:00 | 127 | 12:00
Cumilla(S) | 132 | 04:00 | 121 | 00:00 | Purbasadipur | 134 | 08:00 | 122 | 05:00
Daganbhuiyan | 123 | 19:00 | 114 | 00:00 | Rahanpur | 138 | 05:00 | 132 | 23:00
Daudkandi | 123 | 06:00 | 117 | 22:00 | Rahanpur-400 | 139 | 08:00 | 133 | 21:00
Dhaka | 137 | 04:00 | 128 | 12:00 | Rahim | 130 | 06:00 | 126 | 13:00
Dhamrai | 134 | 05:00 | 129 | 11:00 | Rajbari | 134 | 09:00 | 126 | 21:00
Dhanmondi | 137 | 03:00 | 128 | 12:00 | Rajendrapur | 131 | 10:00 | 124 | 13:00
Dohazari | 132 | 19:30 | 122 | 00:00 | Rajshahi | 133 | 08:00 | 125 | 21:00
Faridpur | 135 | 07:00 | 129 | 22:00 | Rajshahi-230 | 133 | 09:00 | 121 | 19:00
Fatullah | 132 | 06:00 | 126 | 13:00 | Ramganj | 122 | 18:00 | 116 | 00:00
Fenchuganj | 135 | 06:00 | 132 | 00:00 | Rampur | 131 | 19:00 | 126 | 15:00
Feni | 124 | 19:00 | 117 | 00:00 | Rampura | 137 | 04:00 | 127 | 12:00
Ghatail | 130 | 09:00 | 122 | 19:30 | Rangamati | 132 | 19:30 | 129 | 00:00
Ghorashal | 136 | 05:00 | 131 | 12:00 | Rangpur | 133 | 10:00 | 122 | 07:00
Goalpara | 137 | 08:00 | 129 | 21:00 | Ruppur | 137 | 08:00 | 131 | 23:00
Gollamari | 138 | 09:00 | 130 | 00:00 | Saidpur | 134 | 08:00 | 123 | 21:00
Gopalganj | 136 | 09:00 | 129 | 21:00 | Satkhira | 135 | 09:00 | 124 | 21:00
Gopalganj-400 | 139 | 11:00 | 132 | 00:00 | Satmasjid | 133 | 05:00 | 127 | 13:00
Gulshan | 136 | 05:00 | 127 | 12:00 | Savar | 132 | 19:00 | 126 | 12:00
Halishahar | 134 | 19:30 | 127 | 00:00 | SevenRings | 136 | 06:00 | 131 | 00:00
Haripur | 131 | 06:00 | 127 | 00:00 | ShahCement | 131 | 06:00 | 125 | 13:00
HaripurSBU | 131 | 06:00 | 127 | 00:00 | Shahjadpur | 136 | 05:00 | 133 | 00:00
Hasnabad | 134 | 08:00 | 126 | 00:00 | Shahjibazar | 136 | 06:00 | 129 | 21:00
Hathazari | 134 | 05:00 | 128 | 00:00 | Shahmirpur | 133 | 19:00 | 129 | 12:00
Ishurdi | 138 | 09:00 | 132 | 21:00 | Shariatpur | 136 | 10:00 | 127 | 00:00
Jaldhaka | 133 | 08:00 | 120 | 21:00 | Sherpur | 133 | 09:00 | 116 | 22:00
Jamalpur | 136 | 09:00 | 120 | 21:00 | Shikalbaha | 123 | 20:00 | 117 | 00:00
Jashore | 131 | 06:00 | 122 | 00:00 | Shikalbaha-230 | 134 | 19:00 | 129 | 00:00
Jhenaidah | 135 | 06:00 | 124 | 19:00 | Shitalakhya | 131 | 06:00 | 125 | 12:00
Jhenaidah-230 | 135 | 08:00 | 126 | 21:00 | Sholosohor | 132 | 19:30 | 128 | 00:00
Joydebpur | 135 | 04:00 | 127 | 15:00 | Shyampur | 130 | 01:00 | 127 | 00:00
Joypurhat | 131 | 09:00 | 120 | 23:00 | Shyampur-230 | 132 | 06:00 | 127 | 11:00
Juldah | 134 | 19:30 | 128 | 00:00 | Siddhirganj | 131 | 05:00 | 126 | 23:00
Kabirpur | 132 | 04:00 | 124 | 16:00 | Sirajganj | 134 | 09:00 | 125 | 21:00
Kachua | 128 | 20:00 | 122 | 00:00 | Sonargaon | 128 | 05:00 | 123 | 13:00
Kaliakoir | 133 | 17:00 | 129 | 16:00 | Sreemongol | 134 | 06:00 | 128 | 23:00
Kallyanpur | 133 | 10:00 | 129 | 11:00 | Sreepur | 133 | 05:00 | 128 | 21:00
Kalurghat | 132 | 05:00 | 128 | 00:00 | Srinagar | 136 | 07:00 | 130 | 00:00
Kamrangirchar | 136 | 08:00 | 128 | 00:00 | SSM | 134 | 19:00 | 131 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 06:00 | 119 | 00:00
Kasba | 124 | 18:00 | 118 | 00:00 | Sylhet | 129 | 08:00 | 124 | 21:00
Kazla | 135 | 06:00 | 130 | 13:00 | Sylhet-132 | 128 | 05:00 | 125 | 23:00
Keranigonj | 136 | 06:00 | 130 | 13:00 | Tangail | 127 | 06:00 | 121 | 18:30
Khagrachori | 131 | 06:00 | 128 | 00:00 | Taraganj | 133 | 08:00 | 124 | 05:00
Khulna | 137 | 09:00 | 128 | 22:00 | Thakurgaon | 136 | 08:00 | 118 | 05:00
Khulna(S) | 138 | 09:00 | 129 | 23:00 | TK | 132 | 19:00 | 128 | 00:00
Khulshi | 131 | 19:30 | 127 | 00:00 | Tongi | 133 | 08:00 | 130 | 15:00
Kishoreganj | 130 | 05:00 | 121 | 19:30 | Ullahpara | 134 | 04:00 | 128 | 21:00
Kodda | 130 | 06:00 | 122 | 16:00 | Ullon | 137 | 03:00 | 126 | 12:00
KSRM | 133 | 18:30 | 128 | 12:00 | Uttara | 133 | 06:00 | 127 | 12:00
Kulaura | 134 | 06:00 | 130 | 00:00 | UttaraNew | 133 | 07:00 | 127 | 12:00
Kurigram | 131 | 10:00 | 119 | 23:00 | Zigatola | 136 | 06:00 | 129 | 13:00
Kushtia | 134 | 06:00 | 128 | 19:00
Laksam | 129 | 14:00 | 120 | 12:00
Lakshmipur | 122 | 20:00 | 114 | 00:00
Lalbag | 136 | 06:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division