## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-08-2025 | during | 26-08-2025 | during | 26-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 387 | 323 | 400.75 | 400.75 | 367 | 367 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 320 | 320 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 276 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 102 | 7 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 44.2 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 123 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 42 | 50 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 23 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 89 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 13 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 57 | 145 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 19 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 300 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2001 | 2668.2 | 5827.04 | 5891.04 | 3755.17 | 3819.17
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 217 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 69 | 48 | 64 | 56 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 21 | 2 | 24 | 2 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 87 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.47 | 0 | 4.51 | 0 | 4.51 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1145 | 1125 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 637 | 635 | 690 | 690 | 690 | 690 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2303.47 | 2798 | 3703.23 | 3726.72 | 3535.23 | 3584.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 41 | 46.7 | 46.7 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 42 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 108 | 8 | 195 | 195 | 81 | 81 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 115 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 43 | 166 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 95 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 46 | 51 | 113 | 113 | 50 | 64 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 99 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1392 | 1698 | 2449.56 | 2379.56 | 2231.36 | 2175.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-08-2025 | during | 26-08-2025 | during | 26-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 70 | 86 | 157.5 | 157.5 | 138 | 138 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 76 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 99 | 95 | 103 | 95 | 103 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 28.52 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 6 | 12 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 18 | 18 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 251.52 | 308 | 427.2 | 412 | 355.2 | 346
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 50 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 138 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 15 | 20 | 20 | 16 | 16 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 8 | 25 | 25 | 12 | 12 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 0 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 372 | 313 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1179 | 801 | 1266 | 1266 | 1171 | 1171
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 848 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 275 | 225 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 921 | 1196 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2163 | 2324 | 3639.2 | 3554.2 | 3401 | 3316
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 302 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 960 | 1210 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 249 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1769.5 | 2131 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 57.78 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 200 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 200 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 200 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 407 | 345 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 62 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 820.61 | 1417 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.87 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1994.95 | 2522 | 3159.17 | 2992.87 | 3052.39 | 2886.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 146 | 148 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 176 | 0 | 164.79 | 0 | 164.79 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 390.7 | 422 | 663.39 | 462 | 663.39 | 462
System Total |  |  |  |  | 28823.2 | 27829.875 | 13445.14 | 15672.2 | 23296.79 | 22845.39 | 20311.74 | 19906.34
Forecast Scenario (26-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15110 |  | 0 |  | 15110
|  |  |  | 1:00 | 14480 |  | 0 |  | 14480
|  |  |  | 2:00 | 14090 |  | 0 |  | 14090
|  |  |  | 3:00 | 13680 |  | 0 |  | 13680
|  |  |  | 4:00 | 13470 |  | 0 |  | 13470
|  |  |  | 5:00 | 13190 |  | 0 |  | 13190
|  |  |  | 6:00 | 12860 |  | 0 |  | 12860
|  |  |  | 7:00 | 12820 |  | 0 |  | 12820
|  |  |  | 8:00 | 12800 |  | 0 |  | 12800
|  |  |  | 9:00 | 13120 |  | 0 |  | 13120
|  |  |  | 10:00 | 13340 |  | 0 |  | 13340
|  |  |  | 11:00 | 13660 |  | 0 |  | 13660
|  |  |  | 12:00 | 14040 |  | 0 |  | 14040
|  |  |  | 13:00 | 14440 |  | 0 |  | 14440
|  |  |  | 14:00 | 14490 |  | 0 |  | 14490
|  |  |  | 15:00 | 14460 |  | 0 |  | 14460
|  |  |  | 16:00 | 14270 |  | 0 |  | 14270
|  |  |  | 17:00 | 14130 |  | 0 |  | 14130
|  |  |  | 18:00 | 13760 |  | 0 |  | 13760
|  |  |  | 18:30 | 14600 |  | 0 |  | 14600
|  |  |  | 19:00 | 15880 |  | 0 |  | 15880
|  |  |  | 19:30 | 16100 |  | 0 |  | 16100
|  |  |  | 20:00 | 16220 |  | 0 |  | 16220
|  |  |  | 21:00 | 16180 |  | 0 |  | 16180
|  |  |  | 22:00 | 15900 |  | 0 |  | 15900
|  |  |  | 23:00 | 15800 |  | 0 |  | 15800
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14040.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16220.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16220.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.19 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:14 hrs on 26-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-08-2025 | [28 empty] | Date: | 25-08-2025 | [28 empty] | Date: | 25-08-2025 | [28 empty] | Date: | 25-08-2025 | [28 empty] | Date: | 25-08-2025 | [14 empty] | Date: | 25-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 15 | 17 | 53 | 60 | 0 | 0 | 17 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 51 | 38 | 0 | 12 | 12 | 0 | 222 | 0 | 32 | 625 | 0 | 0 | 12 | 17 | 0 | 223 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 81 | 0 | 356 | 330 | 45 | 194 | 37 | 102 | 70 | 175 | 63 | 19 | 32 | 44 | 25 | 0 | 0 | 310 | 0 | 364 | 0 | 60 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 102 | 78 | 103 | 0 | 0 | 12 | 7500.5 | 876 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 1453.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 169 | 0 | 160 | 0 | 342 | 0 | 0 | 153 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 115 | 220 | 0 | 301 | 1110 | 0 | 7012.2 | 14512.7 | 107.96
01:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 14.7 | 0 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 50 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 32 | 625 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1046 | 0 | 51 | 0 | 81 | 0 | 356 | 330 | 45 | 189 | 37 | 99 | 70 | 167 | 64 | 19 | 29 | 44 | 25 | 0 | 0 | 305 | 0 | 358 | 0 | 60 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 92 | 59 | 103 | 0 | 0 | 6 | 7178.2 | 877 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 1328.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 163 | 0 | 154 | 0 | 335 | 0 | 0 | 152 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 115 | 220 | 0 | 301 | 1100 | 0 | 6707.68 | 13885.88 | 107.95
02:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 26 | 625 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 915 | 0 | 51 | 0 | 81 | 0 | 356 | 330 | 45 | 188 | 37 | 98 | 70 | 167 | 63 | 19 | 30 | 42 | 25 | 0 | 0 | 300 | 0 | 358 | 0 | 60 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 92 | 57 | 103 | 0 | 0 | 6 | 6993 | 876 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 925 | 0 | 1322.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 163 | 0 | 154 | 0 | 333 | 0 | 0 | 153 | 50 | 70 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 115 | 220 | 0 | 301 | 990 | 0 | 6502.99 | 13495.99 | 107.95
03:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 25.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 12 | 0 | 222 | 0 | 30 | 625 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 895 | 0 | 51 | 0 | 81 | 0 | 357 | 330 | 45 | 195 | 37 | 101 | 70 | 158 | 63 | 19 | 29 | 40 | 8 | 0 | 0 | 305 | 0 | 371 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 91 | 57 | 105 | 0 | 0 | 6 | 6885.5 | 876 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 0 | 1113.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 166 | 0 | 157 | 0 | 346 | 0 | 0 | 150 | 50 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 115 | 220 | 0 | 302 | 1000 | 0 | 6202.08 | 13087.58 | 107.94
04:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 25.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 33 | 615 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 893 | 0 | 51 | 0 | 81 | 0 | 357 | 330 | 45 | 194 | 37 | 99 | 70 | 137 | 63 | 19 | 29 | 40 | 0 | 0 | 0 | 300 | 0 | 362 | 0 | 60 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 92 | 57 | 105 | 0 | 0 | 6 | 6792.5 | 876 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 868 | 0 | 1109.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 166 | 0 | 154 | 0 | 342 | 0 | 0 | 150 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 115 | 220 | 0 | 303 | 985 | 0 | 6085.61 | 12878.11 | 107.94
05:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 25.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 37 | 615 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 894 | 0 | 51 | 0 | 81 | 0 | 357 | 330 | 45 | 188 | 37 | 99 | 50 | 100 | 63 | 19 | 0 | 38 | 0 | 0 | 0 | 300 | 0 | 362 | 0 | 60 | 150 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 92 | 57 | 104 | 0 | 0 | 6 | 6664.5 | 876 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 0 | 1047.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 160 | 0 | 154 | 0 | 339 | 0 | 0 | 154 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 115 | 220 | 0 | 302 | 980 | 0 | 5928.8 | 12593.3 | 107.94
06:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 35 | 26 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0.06 | 220 | 0 | 40 | 618 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 878 | 1 | 43 | 0 | 43 | 0 | 357 | 330 | 46 | 189 | 34 | 68 | 50 | 68 | 63 | 19 | 0 | 36 | 0 | 2 | 0 | 295 | 0 | 358 | 0 | 60 | 149 | 6 | 0 | 82 | 30 | 0 | 16 | 166 | 6 | 92 | 57 | 104 | 0 | 0.62 | 6 | 6521.68 | 877 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.9 | 777 | 0 | 1014.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 1.12 | 163 | 0 | 158 | 0 | 152 | 0 | 336 | 0 | 0.09 | 153 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0.02 | 0 | 166 | 115 | 220 | 0 | 303 | 920 | 0 | 5746.44 | 12268.12 | 107.93
07:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 35 | 25 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0.42 | 220 | 0 | 37 | 617 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 890 | 0 | 43 | 0 | 45 | 0 | 357 | 330 | 46 | 193 | 34 | 34 | 50 | 61 | 64 | 19 | 0 | 34 | 0 | 16 | 0 | 300 | 0 | 363 | 0 | 60 | 151 | 6 | 0 | 82 | 30 | 0 | 16 | 165 | 17 | 92 | 57 | 104 | 1 | 2.86 | 2 | 6578.28 | 876 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 790 | 0 | 1015.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.44 | 13 | 0 | 0 | 17.4 | 167 | 0 | 162 | 0 | 155 | 0 | 341 | 0 | 1.08 | 153 | 51 | 0 | 8 | 0 | 0 | 0 | 0 | 1.3 | 21 | 0.12 | 0 | 169 | 115 | 220 | 0 | 302 | 700 | 0 | 5647.9 | 12226.18 | 107.92
08:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 16 | 35 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 1.62 | 222 | 0 | 11 | 618 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 885 | 8 | 43 | 0 | 45 | 0 | 300 | 330 | 45 | 191 | 37 | 32 | 70 | 60 | 63 | 19 | 0 | 34 | 0 | 34 | 0 | 305 | 0 | 359 | 0 | 60 | 143 | 6 | 0 | 82 | 30 | 0 | 16 | 165 | 17 | 92 | 57 | 99 | 1 | 19.34 | 6 | 6537.96 | 876 | 299 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 783 | 0 | 1013.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.02 | 25 | 0 | 0 | 26.2 | 165 | 0 | 158 | 0 | 153 | 0 | 338 | 0 | 2.66 | 150 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 1.4 | 43 | 0.14 | 0 | 169 | 115 | 180 | 0 | 305 | 692 | 0 | 5663.84 | 12201.8 | 107.92
09:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 34 | 30 | 0 | 0 | 16 | 0 | 0 | 300 | 287 | 0 | 0 | 0 | 280 | 0 | 0 | 23 | 35 | 22 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 2.14 | 222 | 0 | 6 | 615 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 900 | 10 | 43 | 0 | 45 | 0 | 300 | 330 | 45 | 201 | 37 | 30 | 70 | 61 | 61 | 19 | 0 | 34 | 0 | 48 | 0 | 310 | 0 | 387 | 0 | 60 | 141 | 6 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 91 | 57 | 92 | 1 | 34.35 | 6 | 6623.49 | 876 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 801 | 0 | 1023.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.06 | 86 | 0 | 0 | 45.2 | 170 | 0 | 161 | 0 | 158 | 0 | 361 | 0 | 3.97 | 152 | 50 | 0 | 26 | 0 | 0 | 0 | 0 | 4.5 | 78 | 0.53 | 0 | 173 | 115 | 180 | 0 | 302 | 700 | 0 | 5902.97 | 12526.46 | 107.91
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 35 | 0 | 0 | 300 | 301 | 0 | 0 | 0 | 280 | 0 | 0 | 31 | 35 | 21 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.54 | 222 | 0 | 2 | 635 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 900 | 18 | 43 | 0 | 73 | 0 | 343 | 330 | 31 | 207 | 34 | 32 | 70 | 34 | 56 | 11 | 0 | 34 | 0 | 59 | 0 | 315 | 0 | 390 | 0 | 60 | 154 | 12 | 0 | 76 | 30 | 0 | 16 | 165 | 0 | 91 | 57 | 81 | 2 | 37.04 | 6 | 6766.58 | 876 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 813 | 0 | 863.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.54 | 73 | 0 | 0 | 59.83 | 177 | 0 | 169 | 0 | 166 | 0 | 382 | 0 | 4.98 | 151 | 49 | 0 | 28 | 0 | 0 | 0 | 0 | 3.1 | 178 | 0.21 | 0 | 173 | 115 | 220 | 0 | 304 | 700 | 0 | 5982.16 | 12748.74 | 107.91
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 50 | 30 | 0 | 0 | 35 | 0 | 12 | 300 | 302 | 0 | 0 | 0 | 280 | 0 | 0 | 33 | 35 | 20 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 4.45 | 222 | 0 | 2 | 667 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1075 | 19 | 43 | 0 | 103 | 0 | 341 | 330 | 18 | 208 | 34 | 34 | 70 | 34 | 52 | 19 | 0 | 36 | 0 | 71 | 0 | 315 | 0 | 390 | 0 | 60 | 158 | 11 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 90 | 56 | 70 | 2 | 46.24 | 6 | 7020.69 | 876 | 283 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95 | 824 | 0 | 822.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.05 | 113 | 0 | 0 | 65.19 | 182 | 0 | 174 | 0 | 171 | 0 | 383 | 0 | 5.55 | 147 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 8 | 131 | 0.75 | 0 | 173 | 115 | 220 | 0 | 302 | 790 | 0 | 6039.32 | 13060.01 | 107.9
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 10 | 19 | 50 | 30 | 0 | 0 | 42 | 57 | 13 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 35 | 35 | 20 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 12 | 20 | 1.47 | 222 | 0 | 6 | 637 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1145 | 10 | 43 | 0 | 108 | 0 | 341 | 330 | 28 | 202 | 37 | 48 | 50 | 43 | 46 | 19 | 0 | 38 | 0 | 59 | 0 | 320 | 0 | 372 | 0 | 30 | 156 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 87 | 57 | 70 | 3 | 28.52 | 6 | 7126.99 | 876 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 921 | 0 | 820.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.78 | 110 | 0 | 0 | 66.87 | 181 | 0 | 175 | 0 | 171 | 0 | 407 | 0 | 5.69 | 146 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 3.7 | 176 | 0.5 | 0 | 171 | 115 | 220 | 0 | 303 | 960 | 0 | 6318.15 | 13445.14 | 107.9
13:00 | 0 | 75 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 28.7 | 35 | 57 | 30 | 0 | 0 | 54 | 65 | 0 | 300 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 34 | 35 | 20 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 12 | 25 | 3.06 | 222 | 0 | 14 | 637 | 0 | 0 | 32 | 0 | 0 | 218 | 0 | 0 | 0 | 1150 | 10 | 43 | 0 | 108 | 0 | 343 | 330 | 41 | 191 | 39 | 90 | 50 | 91 | 42 | 19 | 0 | 42 | 0 | 70 | 0 | 310 | 0 | 389 | 0 | 30 | 154 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 88 | 57 | 70 | 2 | 52.52 | 6 | 7345.28 | 877 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 994 | 0 | 824.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.27 | 116 | 0 | 0 | 58.82 | 173 | 0 | 165 | 0 | 171 | 0 | 409 | 0 | 5.37 | 149 | 49 | 0 | 11 | 0 | 0 | 0 | 0 | 6.5 | 170 | 0.1 | 0 | 172 | 115 | 220 | 0 | 302 | 1090 | 0 | 6497.55 | 13842.83 | 107.89
14:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 32 | 35 | 68 | 30 | 0 | 0 | 55 | 68 | 0 | 300 | 296 | 0 | 0 | 0 | 280 | 0 | 0 | 31 | 70 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 29 | 16 | 0 | 0 | 12 | 25 | 3.14 | 220 | 0 | 9 | 635 | 0 | 0 | 32 | 0 | 0 | 217 | 0 | 0 | 0 | 1150 | 8 | 51 | 0 | 71 | 0 | 338 | 330 | 41 | 169 | 34 | 103 | 70 | 97 | 44 | 19 | 11 | 44 | 0 | 65 | 0 | 305 | 0 | 386 | 0 | 30 | 154 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 88 | 57 | 71 | 2 | 48.23 | 6 | 7378.37 | 876 | 251 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 1001 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.43 | 106 | 0 | 0 | 40.5 | 174 | 0 | 167 | 0 | 176 | 0 | 402 | 0 | 4.92 | 139 | 48 | 0 | 15 | 0 | 0 | 50 | 0 | 6.9 | 190 | 0.07 | 0 | 173 | 115 | 220 | 0 | 303 | 1110 | 0 | 6520.82 | 13899.19 | 107.89
15:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 33.1 | 17 | 68 | 30 | 0 | 0 | 55 | 69 | 0 | 300 | 304 | 0 | 0 | 0 | 280 | 0 | 0 | 26 | 70 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 0 | 12 | 12 | 2.17 | 220 | 0 | 7 | 638 | 0 | 0 | 33 | 0 | 0 | 214 | 0 | 0 | 0 | 1165 | 15 | 51 | 0 | 45 | 0 | 337 | 330 | 41 | 188 | 31 | 106 | 70 | 101 | 42 | 19 | 40 | 44 | 0 | 53 | 0 | 310 | 0 | 382 | 0 | 30 | 154 | 14 | 0 | 78 | 30 | 0 | 15 | 165 | 0 | 87 | 57 | 71 | 2 | 30.51 | 6 | 7370.78 | 875 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 1019 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.05 | 86 | 0 | 0 | 37.76 | 180 | 0 | 182 | 0 | 188 | 0 | 391 | 0 | 2.25 | 142 | 49 | 0 | 19 | 0 | 0 | 140 | 0 | 1.3 | 75 | 0.27 | 0 | 184 | 115 | 220 | 0 | 303 | 1100 | 0 | 6498.63 | 13869.41 | 107.88
16:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 33.8 | 17 | 68 | 30 | 75 | 0 | 55 | 102 | 0 | 300 | 290 | 0 | 0 | 25 | 280 | 0 | 0 | 17 | 70 | 18 | 22 | 0 | 320 | 0 | 0 | 1 | 0 | 5 | 16 | 24 | 0 | 12 | 12 | 2.37 | 220 | 0 | 5 | 638 | 0 | 0 | 33 | 0 | 0 | 215 | 0 | 0 | 0 | 1150 | 10 | 51 | 15 | 8 | 0 | 341 | 330 | 40 | 203 | 34 | 107 | 70 | 132 | 46 | 19 | 47 | 42 | 6 | 35 | 0 | 0 | 0 | 387 | 0 | 30 | 155 | 14 | 0 | 80 | 30 | 0 | 15 | 165 | 0 | 90 | 57 | 70 | 1 | 15.13 | 6 | 7200.3 | 875 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1076 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.28 | 60 | 0 | 0 | 20.66 | 179 | 0 | 176 | 0 | 175 | 0 | 365 | 0 | 1.87 | 143 | 49 | 0 | 20 | 0 | 0 | 178 | 0 | 4.1 | 24 | 0.26 | 0 | 224 | 115 | 220 | 0 | 303 | 1100 | 0 | 6472.17 | 13672.47 | 107.87
17:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 31.6 | 17 | 76 | 30 | 145 | 0 | 55 | 136 | 0 | 300 | 290 | 0 | 0 | 35 | 280 | 0 | 0 | 8 | 70 | 21 | 22 | 0 | 320 | 0 | 0 | 21 | 0 | 0 | 16 | 38 | 0 | 25 | 12 | 0.9 | 219 | 0 | 2 | 635 | 0 | 0 | 33 | 0 | 0 | 215 | 0 | 0 | 0 | 1085 | 2 | 51 | 70 | 8 | 0 | 340 | 330 | 41 | 202 | 37 | 103 | 70 | 128 | 51 | 19 | 47 | 40 | 8 | 8 | 0 | 0 | 0 | 386 | 0 | 30 | 154 | 14 | 0 | 80 | 30 | 0 | 15 | 166 | 2 | 87 | 57 | 70 | 0 | 6.23 | 6 | 7272.73 | 875 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1162 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.41 | 27 | 0 | 0 | 13.03 | 174 | 0 | 171 | 0 | 169 | 0 | 365 | 0 | 1.19 | 143 | 49 | 0 | 9 | 0 | 0 | 70 | 0 | 2.1 | 23 | 0.2 | 0 | 231 | 115 | 220 | 0 | 301 | 1000 | 0 | 6257.93 | 13530.66 | 107.86
18:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 31.6 | 17 | 103 | 45 | 145 | 0 | 55 | 148 | 0 | 300 | 286 | 0 | 0 | 35 | 250 | 0 | 0 | 1 | 70 | 0 | 22 | 0 | 320 | 0 | 0 | 44 | 0 | 0 | 16 | 48 | 0 | 25 | 12 | 0 | 218 | 2 | 13 | 635 | 17 | 0 | 33 | 0 | 3 | 215 | 0 | 0 | 0 | 1005 | 0 | 51 | 80 | 8 | 0 | 300 | 300 | 41 | 197 | 34 | 103 | 70 | 127 | 57 | 19 | 45 | 40 | 8 | 2 | 0 | 0 | 0 | 370 | 0 | 30 | 144 | 8 | 0 | 42 | 30 | 0 | 15 | 166 | 17 | 87 | 74 | 70 | 0 | 1.07 | 12 | 7102.67 | 848 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1025 | 0 | 975 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 1.53 | 3 | 0 | 0 | 0.8 | 163 | 0 | 150 | 0 | 150 | 0 | 348 | 0 | 0.08 | 145 | 49 | 56 | 2 | 33 | 0 | 0 | 0 | 0.3 | 8 | 0.03 | 0 | 201 | 100 | 180 | 0 | 301 | 996 | 0 | 6059.74 | 13162.41 | 107.85
19:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 38.3 | 17 | 110 | 121 | 272 | 12 | 55 | 155 | 0 | 300 | 284 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 320 | 0 | 0 | 78 | 0 | 0 | 66 | 69 | 0 | 25 | 25 | 0 | 219 | 17 | 23 | 632 | 143 | 0 | 33 | 10 | 36 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 98 | 8 | 0 | 343 | 330 | 41 | 199 | 40 | 105 | 70 | 143 | 58 | 19 | 98 | 48 | 26 | 0 | 0 | 0 | 0 | 369 | 0 | 50 | 149 | 8 | 0 | 81 | 30 | 0 | 15 | 166 | 22 | 91 | 74 | 70 | 0 | 0 | 12 | 8236.3 | 848 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1156 | 17 | 1294 | 0 | 20 | 0 | 5 | 1 | 0 | 60 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 165 | 0 | 190 | 0 | 200 | 0 | 404 | 0 | 0 | 145 | 49 | 109 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 220 | 0 | 301 | 1055 | 7 | 7046 | 15282.3 | 107.84
19:30 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 45 | 17 | 149 | 124 | 274 | 30 | 55 | 148 | 0 | 300 | 278 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 108 | 7 | 22 | 0 | 300 | 8 | 0 | 85 | 0 | 0 | 66 | 69 | 0 | 25 | 25 | 0 | 219 | 30 | 19 | 635 | 143 | 0 | 33 | 13 | 51 | 217 | 0 | 0 | 0 | 1130 | 0 | 51 | 115 | 8 | 0 | 347 | 330 | 41 | 189 | 40 | 99 | 70 | 166 | 52 | 19 | 98 | 48 | 52.2 | 0 | 0 | 0 | 0 | 362 | 0 | 50 | 142 | 8 | 0 | 81 | 30 | 0 | 15 | 166 | 35 | 91 | 74 | 70 | 0 | 0 | 12 | 8296.2 | 847 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 17 | 1310 | 0 | 32 | 0 | 35 | 25 | 0 | 62 | 33 | 0 | 0 | 0 | 28 | 0 | 0 | 205 | 0 | 195 | 0 | 200 | 0 | 344 | 0 | 0 | 145 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 115 | 220 | 0 | 302 | 1210 | 35 | 7367 | 15663.2 | 0
20:00 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 44.2 | 17 | 149 | 123 | 294 | 0 | 50 | 145 | 0 | 300 | 276 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 300 | 0 | 0 | 87 | 0 | 0 | 66 | 69 | 0 | 25 | 25 | 0 | 220 | 48 | 21 | 635 | 160 | 0 | 33 | 17 | 50 | 217 | 0 | 0 | 0 | 1125 | 0 | 51 | 115 | 8 | 0 | 348 | 330 | 42 | 192 | 41 | 99 | 70 | 166 | 51 | 19 | 95 | 46 | 25 | 0 | 0 | 0 | 0 | 313 | 0 | 50 | 138 | 8 | 0 | 81 | 30 | 0 | 15 | 166 | 35 | 99 | 76 | 86 | 0 | 0 | 12 | 8273.2 | 848 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 17 | 1417 | 0 | 32 | 0 | 0 | 0 | 0 | 62 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 200 | 0 | 200 | 0 | 200 | 0 | 345 | 0 | 0 | 148 | 49 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 115 | 220 | 0 | 302 | 1210 | 35 | 7399 | 15672.2 | 107.83
21:00 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 44.2 | 17 | 138 | 123 | 294 | 0 | 35 | 141 | 0 | 300 | 283 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 125 | 23.3 | 22 | 0 | 300 | 0 | 0 | 90 | 0 | 0 | 66 | 69 | 0 | 25 | 25 | 0 | 220 | 51 | 16 | 635 | 134 | 0 | 33 | 17 | 45 | 221 | 0 | 0 | 0 | 1113 | 0 | 51 | 80 | 8 | 0 | 348 | 330 | 43 | 186 | 40 | 98 | 70 | 165 | 52 | 19 | 98 | 48 | 25 | 0 | 0 | 0 | 0 | 304 | 0 | 50 | 135 | 8 | 0 | 81 | 30 | 0 | 15 | 165 | 17 | 103 | 77 | 87 | 0 | 0 | 12 | 8127.5 | 848 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 17 | 1455.96 | 0 | 40 | 0 | 0 | 0 | 0 | 78 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 204 | 0 | 198 | 0 | 199 | 0 | 334 | 0 | 0 | 151 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 242 | 115 | 220 | 0 | 300 | 1220 | 17 | 7476.96 | 15604.46 | 107.82
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 46.7 | 17 | 104 | 122 | 145 | 0 | 35 | 108 | 0 | 300 | 305 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 125 | 22.7 | 22 | 0 | 300 | 0 | 0 | 76 | 0 | 0 | 66 | 69 | 0 | 25 | 12 | 0 | 221 | 53 | 21 | 637 | 141 | 0 | 33 | 17 | 49 | 219 | 0 | 0 | 0 | 1175 | 0 | 51 | 30 | 8 | 0 | 343 | 330 | 40 | 214 | 37 | 103 | 70 | 170 | 52 | 19 | 71 | 50 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 50 | 145 | 8 | 0 | 81 | 30 | 0 | 15 | 165 | 17 | 95 | 77 | 87 | 0 | 0 | 12 | 7998.4 | 848 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 17 | 1456.51 | 0 | 40 | 0 | 0 | 0 | 0 | 87 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 150 | 0 | 201 | 0 | 150 | 0 | 414 | 0 | 0 | 149 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 115 | 220 | 0 | 301 | 1120 | 0 | 7303.51 | 15301.91 | 107.81
23:00 | 0 | 93 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 49 | 17 | 68 | 122 | 145 | 0 | 44 | 104 | 0 | 300 | 302 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 66 | 69 | 0 | 25 | 12 | 0 | 221 | 55 | 22 | 635 | 159 | 0 | 33 | 17 | 64 | 220 | 0 | 0 | 0 | 1148 | 0 | 51 | 30 | 40 | 0 | 354 | 330 | 37 | 201 | 40 | 104 | 70 | 176 | 52 | 19 | 50 | 52 | 1 | 0 | 0 | 0 | 0 | 358 | 0 | 50 | 156 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 90 | 77 | 92 | 0 | 0 | 12 | 7950.5 | 848 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 17 | 1446.79 | 0 | 40 | 0 | 0 | 16 | 0 | 87 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 150 | 0 | 196 | 0 | 185 | 0 | 414 | 0 | 0 | 145 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 220 | 0 | 301 | 1160 | 0 | 7380.79 | 15331.29 | 107.8
Total KWH | 0 | 1753920 | 417600 | 0 | 0 | 0 | 0 | 0 | 8607600 | 0 | 0 | 484200 | 323640 | 1596816 | 1224480 | 1580727 | 33488 | 750346 | 1412640 | 24960 | 7577000 | 7091025 | 0 | 0 | 241570 | 6937639 | 0 | 0 | 259523 | 1851600 | 460200 | 498240 | 0 | 8038636.36 | 0 | 0 | 502080 | 0 | 95520 | 730874 | 493733 | 0 | 279360 | 253440 | 24961 | 5308331 | 331200 | 453120 | 15243636.36 | 769455 | 0 | 411360 | 105670.8 | 350436 | 5195898 | 0 | 0 | 0 | 24954543 | 126225 | 1166872 | 630618 | 1288000 | 0 | 8566500 | 7938000 | 972480 | 4761000 | 886464 | 2041920 | 1576090 | 2817600 | 1338960 | 425340 | 758100 | 973440 | 229522 | 523564 | 0 | 4903290 | 0 | 9234000 | 0 | 1143720 | 3605563.64 | 219912 | 0 | 1868160 | 714912 | 0 | 387000 | 4418860 | 173520 | 2188800 | 1495200 | 2004480 | 14100 | 321690 | 189840 | 176573211.16 | 21105454 | 6478560 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 570960 | 23345460 | 103680 | 26072000 | 0 | 191176 | 0 | 24576 | 97152 | 0 | 444576 | 178918 | 0 | 389951 | 853050 | 130931 | 0 | 441752 | 4265455 | 0 | 4367400 | 0 | 4306600 | 0 | 8843709 | 0 | 39600 | 3630000 | 1164218 | 1011599 | 219323 | 1045824 | 0 | 524002.5 | 0 | 47618.04 | 1068000 | 4363 | 27456 | 5018000 | 2735000 | 5358300 | 0 | 7286544 | 24769454.55 | 57600 | 157130262.09 | 333703473.25

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13445.14 | MW | 12:00 Hr. | Energy Generated |  |  | 333.7035 |  | MKWHr.
| Day Peak Demand |  |  | 13445.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.282 |  | MKWHr.
| Evening Peak Generation |  |  | 15672.2 | MW | 20:00 Hr. | Energy Demand |  |  | 333.9855 |  | MKWHr.
| Evening Peak Demand |  |  | 15749.53 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 12201.8 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 982.96 |  | MMCFD
| Maximum Generation of the Day |  |  | 15672.2 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.1312 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.2103 | 0 | 11.696 | 0 | 0 | 0.25952 | 0 | 0 | 51.1659 | Gas | 137.295 | Gas | 492087802.1536
| Chattogram Zone |  |  | 5.649 | 40.1982 | 4.2276 | 0 | 5.3083 | 0.15119 | 0 | 0.09552 | 55.6298 | Coal | 105.4119 | Coal | 623316559.3307
| Cumilla Zone |  |  | 27.5807 | 0 | 7.8167 | 0 | 0 | 0.52356 | 0.97344 | 0 | 36.8945 | HFO | 31.1012 | HFO | 570066279.844
| Mymensingh Zone |  |  | 2.0045 | 0 | 4.0474 | 0 | 0 | 0.33579 | 0 | 0 | 6.3876 | HSD | 0.524 | HSD | 0
| Sylhet Zone |  |  | 26.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.4954 | Hydro | 5.3083 | Hydro | 530833.1
| Khulna Zone |  |  | 6.4786 | 23.3455 | 0.10368 | 0 | 0 | 0.57096 | 22.0175 | 0 | 52.5161 | Solar | 4.9047 | Solar | 72759662.7484
| Barishal Zone |  |  | 8.0933 | 37.074 | 0.085056 | 0 | 0 | 0.004363 | 0 | 0 | 45.2567 | Import | 49.0629 | Import | 285819753.94
| Rajshahi Zone |  |  | 21.7832 | 0 | 1.0673 | 0 | 0 | 1.7244 | 26.072 | 0 | 50.6468 | Wind | 0.09552 | Wind | 1407964.8
| Rangpur Zone |  |  | 0 | 4.7942 | 2.0574 | 0.524 | 0 | 1.3349 | 0 | 0 | 8.7106
| Total |  |  | 137.295 | 105.4119 | 31.1012 | 0.524 | 5.3083 | 4.9047 | 49.0629 | 0.09552 | 333.7035
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 492087802.1536 |  | Hydro | 530833.1
|  |  |  | Coal | 623316559.3307 |  | Solar | 72759662.7484
|  |  |  | HFO | 570066279.844 |  | Import | 285819753.94
|  |  |  | HSD | 0 |  | Wind | 1407964.8
[5 empty] | Total: | 204,59,88,855 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1055 | Peak Hr Flow | 848.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54316145.67 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.072 | Peak Hr Flow | 1417.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2284 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.97344 | Peak Hr Flow | 46.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2586 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.1509 | Peak Hr Flow | 2311.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5345
|  |  |  | Chattogram |  | 0 |  | 1458
|  |  |  | Cumilla |  | 0 |  | 1461
|  |  |  | Mymensingh |  | 74 |  | 1295
|  |  |  | Sylhet |  | 0 |  | 681
|  |  |  | Khulna |  | 0 |  | 1833
|  |  |  | Barishal |  | 0 |  | 458
|  |  |  | Rajshahi |  | 0 |  | 1537
|  |  |  | Rangpur |  | 0 |  | 1057
|  |  |  | Total |  | 74 |  | 15125
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 10:16 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Red hot maintenance (BPBS-2) | [7 empty] | 30.0MW load
interrup.
| 08:03 | 10:15 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Red hot maintenance (BPBS-2) | [7 empty] | 30.0MW load
interrup.
| 08:58 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:-
| 09:01 | 13:28 | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to Line PT
(y-phase) oil leakage maintenance work.
| 09:20 |  | TR-3 Restore at Satkhira Sub-Station.
| 10:42 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
EEGBPS প্রজেক্টের ২৩০ কেভি আমিনবাজার -কালিয়াকৈর সার্কিট -০২ এর LILO অংশে stringing কাজের
জন্য।
| 11:12 | 15:40 | Shyampur-Shyampur(New) 132kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to CB
Timing Test
| 11:23 | 15:13 | Shyampur 230/132kV S/S Bus-1 (132kV) Scheduled S/D Due to CB Timing Test
| 11:36 | 19:23 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Nldc signal list end to end
test
| 12:15 | 13:20 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance
protection 21/2-(Z1, AN) relays Due to N/A
| 12:57 | 16:01 | BIPTC S/S 10CF14 Tripped showing Over current relays Due to Tripped by CPRO4 Fault
| 13:01 | 16:22 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing Simence 7SA87
relays Due to C-G Fault and from Ghorashal 230kV end showing Distance relay-1 & 2 relays
Due to Unknown
| 15:42 | 18:31 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Protection
work
| 15:42 | 16:30 | Khulshi 132/33kV S/S 425T(BSRM) LT Forced S/D Due to Breather change of 33/0.4 kV
Auxiliary Transformer of T-3(BSRM).
| 15:47 | 16:17 | Khulshi 132/33kV S/S 425T(BSRM) HT Forced S/D Due to Breather change of 33/0.4 kV
Auxiliary Transformer of T-3(BSRM).
| 18:13 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- FGMO turned off due to low gas
pressure @ 16:54 hr.
| 20:00 |  | Evening Peak Generation: 15672 MW
| 20:44 | 21:45 | Daudkandi 132/33kV S/S Transformer-3 LT Forced S/D Due to 132/33 kv Transformer-3 | [7 empty] | 28.0MW load
|  |  | Shutdown 33KV load side for PBS -3 | [7 empty] | interrup.
| 22:02 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to DS 641s red hot
|  | 22:15 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT is restored.
| 23:00 |  | BIPTC S/S 10CF14 Tripped showing Over current relays Due to Over current 50 CPRO4 Tripped
| 23:20 |  | Summit Bibiana-2 341MW GT was sync.
| 01:26 |  | Summit Bibiana-2 341MW ST was sync.
| 01:57 | 02:21 | Shahjibazar-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing distance
relay relays Due to shahjibazar circuit-1 tripped showing A and B phase on distance relay
and from Shahjibazar 132/33kV end showing No show relays Due to Heavy rain
| 01:57 | 02:22 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing No show
relays Due to Heavy rain and from Sreemongol 132/33kV end showing distance relay relays
Due to shahjibazar circuit-2 tripped showing A and B phase on distance relay
| 02:56 |  | Summit Bibiana-2 341MW CCPP tripped.
| 05:06 |  | Summit Bibiana-2 341MW GT was sync.
| 05:14 |  | BIPTC S/S 10CF16 Tripped showing 87.1 relays Due to C1 unbalance 60/61 instant L1 Tripped
| 05:51 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Scheduled S/D Due to 132kV breaker loop
maintenance
| 05:51 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Scheduled S/D Due to 132kV breaker loop
maintenance
| 05:54 |  | Rampura 230/132kV S/S 132 kV Busbar-2 Scheduled S/D Due to Bus DS Maintenance
| 06:02 |  | Summit Bibiana-2 341MW ST was sync.
| 06:19 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot maintenance.
| 06:19 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot maintenance
| 06:54 |  | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Due to maintenance of PBS 33kV
feeders.
| 06:54 |  | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Due to maintenance of PBS 33kV
feeders.
| 06:57 |  | Keranigonj 230/132/33kV S/S TR-2 LT Scheduled S/D Due to Due to maintenance of PBS 33kV
feeders.
| 06:58 |  | Keranigonj 230/132/33kV S/S TR-2 HT Scheduled S/D Due to Due to maintenance of PBS 33kV
feeders.
| 07:00 |  | Minimum Generation: 12972 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 323 | 8607600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7577000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 276 | 7091025 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 33488 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 6937639 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.2 | 484200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 1224480 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 50 | 750346 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 241570 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 460200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 498240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 417600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 1580727 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1596816 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 89 | 1753920 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 24960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 1412640 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 259523 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 323640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 8038636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1851600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2668.2 | 51165850.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 105670.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126225 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 411360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5308331 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5195898 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 50 | 350436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 69 | 493733 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 730874 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 279360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 453120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 502080 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 48 | 331200 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 253440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 769455 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1125 | 24954543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 95520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 635 | 15243636.36 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2798 | 55629843.16
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4761000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8566500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7938000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 41 | 886464 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 42 | 972480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1288000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1166872 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 630618 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1576090 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 166 | 2817600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 973440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 229522 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 425340 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 758100 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 51 | 1338960 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 2041920 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 523564 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1698 | 36894470
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 86 | 2004480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 1495200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 2188800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 321690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 189840 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 173520 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 308 | 6387630
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 1143720 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3605563.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714912 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1868160 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4418860 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 387000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 219912 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 4903290 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 313 | 9234000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 801 | 26495417.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 848 | 21105454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 225 | 6478560 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 103680 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 570960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1196 | 23345460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2324 | 52516114
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 302 | 7286544 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 27456 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2735000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 24769454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5358300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 57600 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 249 | 5018000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4363 | -
Barishal Area Total |  |  |  |  | 2236 | 2131 | 45256717.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 389951 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 191176 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 178918 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 200 | 4265455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4367400 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 200 | 4306600 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8843709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 130931 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 62 | 444576 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 97152 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 24576 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1417 | 26072000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 441752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 853050 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | -
Rajshahi Area Total |  |  |  |  | 3518.96 | 2522 | 50646846
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 524002.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1164218 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 148 | 3630000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 1045824 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47618.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1011599 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 219323 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1068000 | -
Rangpur Area Total |  |  |  |  | 950 | 422 | 8710584.54
Eastern Grid Total |  |  |  |  | 17385.715 | 8273.2 | 176573211.16
Western Grid Total |  |  |  |  | 10444.16 | 7399 | 157130262.09
National Grid Total |  |  |  |  | 27829.875 | 15672.2 | 333703473.25
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-08-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10166.51 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4885.5 | MW
i) Dhaka area |  |  | 5345.24 |  | MW | i) Khulna area |  |  |  | 1833 | MW
ii) Chattogram area |  |  | 1458.5 |  | MW | ii) Barishal area |  |  |  | 458.5 | MW
iii) Cumilla area |  |  | 1460.77 |  | MW | iii) Rajshahi area |  |  |  | 1537 | MW
iv) Mymensingh area |  |  | 1221 |  | MW | iv) Rangpur area |  |  |  | 1057 | MW
v) Sylhet area |  |  | 681 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15052.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 79 | 21:00 | 133 | PHP | 8 | 03:00
2 | AKSML | 130 | 07:00 | 68 | Ishurdi | 82 | 19:00 | 134 | Pabna | 132 | 19:00
3 | Aftabnagar | 40 | 18:30 | 69 | Jaldhaka | 92 | 19:30 | 135 | Palashbari | 120 | 19:30
4 | Agargaon | 136 | 13:00 | 70 | Jamalpur | 133 | 23:00 | 136 | Panchagarh | 69 | 19:30
5 | Agrabad | 80 | 19:00 | 71 | Jashore | 142 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 29 | 23:00 | 72 | Jhenaidah | 133 | 19:30 | 138 | Patuakhali | 66.5 | 20:00
7 | Ashuganj | 109 | 20:00 | 73 | Joydebpur | 157 | 19:00 | 139 | Payra | 30 | 21:00
8 | BSRM | 199 | 20:00 | 74 | Joypurhat | 63 | 21:00 | 140 | Postogola | 56 | 13:00
9 | Bagerhat | 83 | 19:00 | 75 | Juldah | 18 | 19:00 | 141 | Purbachal | 22 | 20:00
10 | Bajitpur | 90 | 21:00 | 76 | KSRM | 12 | 11:00 | 142 | Purbasadipur | 127 | 19:30
11 | Bakulia | 93 | 19:30 | 77 | Kabirpur | 249 | 10:00 | 143 | Rahanpur | 39 | 23:00
12 | Banani | 52.8 | 13:00 | 78 | Kachua | 96 | 22:00 | 144 | Rahim | 24 | 13:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 105 | 19:00 | 145 | Rajbari | 87 | 19:00
14 | Barapukuria | 73 | 21:00 | 80 | Kalurghat | 26 | 00:00 | 146 | Rajendrapur | 142 | 23:00
15 | Barguna | 22 | 23:00 | 81 | Kamrangirchar | 79 | 16:00 | 147 | Rajshahi | 122 | 21:00
16 | Barishal | 100 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 90 | 21:00
17 | Barishal-230 | 100 | 19:00 | 83 | Kasba | 38 | 21:00 | 149 | Ramganj | 122 | 22:00
18 | Baroaulia | 64 | 10:00 | 84 | Kazla | 97 | 16:00 | 150 | Rampur | 40 | 18:30
19 | Baroirhat | 63 | 19:30 | 85 | Keranigonj | 82 | 19:00 | 151 | Rangamati | 18 | 18:30
20 | Bashundhara | 201 | 19:00 | 86 | Khagrachori | 38 | 19:00 | 152 | Rangpur | 150 | 20:00
21 | BashundharaCement | 9 | 16:00 | 87 | Khulna | 75 | 13:00 | 153 | Ruppur | 7.8 | 16:00
22 | Beanibazar | 84 | 19:00 | 88 | Khulshi | 178 | 19:30 | 154 | SSM | 16 | 02:00
23 | Benapole | 63 | 20:00 | 89 | Kishoreganj | 144 | 20:00 | 155 | Saidpur | 114 | 19:00
24 | Bhaluka | 164 | 19:00 | 90 | Kodda | 300 | 10:00 | 156 | Satkhira | 122 | 19:00
25 | Bhandaria | 62 | 19:00 | 91 | Kulaura | 61 | 19:00 | 157 | Satmasjid | 100 | 13:00
26 | Bhangura | 40 | 19:00 | 92 | Kurigram | 68 | 19:00 | 158 | Savar | 223 | 12:00
27 | Bheramara(GK) | 69 | 19:30 | 93 | Kushtia | 160 | 19:00 | 159 | SevenRings | 4.49 | 04:00
28 | Bhulta | 214 | 17:00 | 94 | Laksam | 34 | 19:00 | 160 | ShahCement | 13 | 23:00
29 | Bog-Sherpur | 78 | 22:00 | 95 | Lakshmipur | 24.76 | 21:00 | 161 | Shahjadpur | 94 | 19:30
30 | Bogura | 162 | 21:00 | 96 | Lalbag | 62 | 11:00 | 162 | Shahjibazar | 140 | 23:00
31 | Borhanuddin | 93 | 20:00 | 97 | Lalmonirhat | 69 | 19:00 | 163 | Shahmirpur | 56 | 00:00
32 | Brahmanbaria | 140 | 22:00 | 98 | MI_Cement | 16.2 | 21:00 | 164 | Shariatpur | 93 | 22:00
33 | Cantonment | 144 | 14:00 | 99 | Madanganj | 42 | 00:00 | 165 | Sherpur | 152 | 20:00
34 | Chandina | 16.57 | 21:00 | 100 | Madaripur | 114 | 21:00 | 166 | Shikalbaha | 8 | 12:00
35 | Chandpur | 82 | 22:00 | 101 | Madartek | 90 | 21:00 | 167 | Shitalakhya | 73.8 | 11:00
36 | Chandraghona | 37 | 18:30 | 102 | Madunaghat | 55 | 19:00 | 168 | Sholosohor | 43 | 16:00
37 | Chapai | 68 | 22:00 | 103 | Magura | 70 | 19:00 | 169 | Shyampur | 152 | 01:00
38 | Charsaidpur | 42 | 01:00 | 104 | Mahasthangarh | 82 | 23:00 | 170 | Siddhirganj | 118 | 15:00
39 | Chauddagram | 74 | 21:00 | 105 | Maijdee | 15 | 21:00 | 171 | Sirajganj | 118 | 21:00
40 | Chhatak | 42 | 00:00 | 106 | Manikganj | 132 | 21:00 | 172 | Sonargaon | 125 | 22:00
41 | Chowmuhani | 191 | 19:30 | 107 | Maniknagar | 76 | 13:00 | 173 | Sreemongol | 86 | 23:00
42 | Chuadanga | 120 | 19:00 | 108 | Matarbari | 50 | 18:30 | 174 | Sreepur | 103 | 19:30
43 | Coxsbazar | 136 | 18:30 | 109 | Matuail | 72 | 10:00 | 175 | Srinagar | 49.5 | 22:00
44 | Cumilla(N) | 139 | 19:00 | 110 | Millgate | 125 | 10:00 | 176 | Sunamganj | 64 | 21:00
45 | Cumilla(S) | 143 | 18:30 | 111 | Mirpur | 124 | 19:00 | 177 | Sylhet | 55 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 15:00 | 178 | Sylhet-132 | 144 | 18:30
47 | Daudkandi | 144 | 18:30 | 113 | Mirzapur | 44 | 00:00 | 179 | TK | 33 | 19:30
48 | Dhaka | 94 | 13:00 | 114 | Mithapukur | 72 | 19:30 | 180 | Tangail | 184 | 21:00
49 | Dhamrai | 136 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 24 | 19:30
50 | Dhanmondi | 136 | 13:00 | 116 | Mogbazar | 121.2 | 15:00 | 182 | Thakurgaon | 114 | 19:30
51 | Dohazari | 111 | 21:00 | 117 | Mongla | 37 | 19:00 | 183 | Tongi | 104 | 15:00
52 | Faridpur | 175 | 22:00 | 118 | Motijheel | 45 | 13:00 | 184 | Ullahpara | 40 | 20:00
53 | Fatullah | 101 | 10:00 | 119 | Muktagacha | 40 | 19:00 | 185 | Ullon | 46 | 23:00
54 | Fenchuganj | 47 | 23:00 | 120 | Munshiganj | 117 | 23:00 | 186 | Uttara | 82 | 14:00
55 | Feni | 119 | 22:00 | 121 | Muradnagar | 44 | 20:00 | 187 | UttaraNew | 61 | 22:00
56 | GPH | 75 | 06:00 | 122 | Mymensingh | 213 | 20:00 | 188 | Zigatola | 72 | 15:00
57 | Ghatail | 80 | 19:00 | 123 | Naogaon | 133 | 21:00
58 | Ghorashal | 14 | 21:00 | 124 | Narail | 61 | 19:30
59 | Ghorashal-230 | 91 | 22:00 | 125 | Narinda | 74 | 13:00
60 | Goalpara | 39 | 23:00 | 126 | Narshingdi | 186 | 23:00
61 | Gollamari | 94 | 13:00 | 127 | Natore | 149 | 19:30
62 | Gopalganj | 111 | 19:30 | 128 | Nawabganj | 60.8 | 23:00
63 | Gulshan | 126 | 15:00 | 129 | Netrakona | 136 | 00:00
64 | Halishahar | 66 | 11:00 | 130 | New | 74 | 11:00
65 | HaripurSBU | 157 | 11:00 | 131 | Niamatpur | 76 | 22:00
66 | Hasnabad | 88 | 23:00 | 132 | Noapara | 46 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14512.7 | 0 |  | 14512.7
1:00 | 13885.88 | 0 |  | 13885.88
2:00 | 13495.99 | 0 |  | 13495.99
3:00 | 13087.58 | 0 |  | 13087.58
4:00 | 12878.11 | 0 |  | 12878.11
5:00 | 12593.3 | 0 |  | 12593.3
6:00 | 12268.12 | 0 |  | 12268.12
7:00 | 12226.18 | 0 |  | 12226.18
8:00 | 12201.8 | 0 |  | 12201.8
9:00 | 12526.46 | 0 |  | 12526.46
10:00 | 12748.74 | 0 |  | 12748.74
11:00 | 13060.01 | 0 |  | 13060.01
12:00 | 13445.14 | 0 |  | 13445.14
13:00 | 13842.83 | 0 |  | 13842.83
14:00 | 13899.19 | 0 |  | 13899.19
15:00 | 13869.41 | 0 |  | 13869.41
16:00 | 13672.47 | 0 |  | 13672.47
17:00 | 13530.66 | 0 |  | 13530.66
18:00 | 13162.41 | 0 |  | 13162.41
19:00 | 15282.3 | 0 |  | 15282.3
19:30 | 15663.2 | 64 |  | 15730.08
20:00 | 15672.2 | 74 |  | 15749.53
21:00 | 15604.46 | 74 |  | 15681.79
22:00 | 15301.91 | 67 |  | 15371.93
23:00 | 15331.29 | 67 |  | 15401.31
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7500.5 | 7012.2 | 14512.7 | DAILY GENERATION CURVE
00:30 | 7339.35 | 6859.94 | 14199.29
01:00 | 7178.2 | 6707.68 | 13885.88 | 25-08-2025
01:30 | 7085.6 | 6605.335 | 13690.935
02:00 | 6993 | 6502.99 | 13495.99
02:30 | 6939.25 | 6352.535 | 13291.785
03:00 | 6885.5 | 6202.08 | 13087.58
03:30 | 6839 | 6143.845 | 12982.845
04:00 | 6792.5 | 6085.61 | 12878.11
04:30 | 6728.5 | 6007.205 | 12735.705
05:00 | 6664.5 | 5928.8 | 12593.3
05:30 | 6593.09 | 5837.62 | 12430.71
06:00 | 6521.68 | 5746.44 | 12268.12
06:30 | 6549.98 | 5697.17 | 12247.15
07:00 | 6578.28 | 5647.9 | 12226.18
07:30 | 6558.12 | 5655.87 | 12213.99
08:00 | 6537.96 | 5663.84 | 12201.8
08:30 | 6580.725 | 5783.405 | 12364.13
09:00 | 6623.49 | 5902.97 | 12526.46
09:30 | 6695.035 | 5942.565 | 12637.6
10:00 | 6766.58 | 5982.16 | 12748.74
10:30 | 6893.635 | 6010.74 | 12904.375
11:00 | 7020.69 | 6039.32 | 13060.01
11:30 | 7073.84 | 6178.735 | 13252.575
12:00 | 7126.99 | 6318.15 | 13445.14
12:30 | 7236.135 | 6407.85 | 13643.985
13:00 | 7345.28 | 6497.55 | 13842.83
13:30 | 7361.825 | 6509.185 | 13871.01
14:00 | 7378.37 | 6520.82 | 13899.19
14:30 | 7374.575 | 6509.725 | 13884.3
15:00 | 7370.78 | 6498.63 | 13869.41
15:30 | 7285.54 | 6485.4 | 13770.94
16:00 | 7200.3 | 6472.17 | 13672.47
16:30 | 7236.515 | 6365.05 | 13601.565
17:00 | 7272.73 | 6257.93 | 13530.66
17:30 | 7187.7 | 6158.835 | 13346.535
18:00 | 7102.67 | 6059.74 | 13162.41
18:30 | 7669.485 | 6552.87 | 14222.355
19:00 | 8236.3 | 7046 | 15282.3
19:30 | 8296.2 | 7367 | 15663.2
20:00 | 8273.2 | 7399 | 15672.2
20:30 | 8200.35 | 7437.98 | 15638.33 |  | Executive Engineer
21:00 | 8127.5 | 7476.96 | 15604.46 |  | Network Operation Division
21:30 | 8062.95 | 7390.235 | 15453.185
22:00 | 7998.4 | 7303.51 | 15301.91
22:30 | 7974.45 | 7342.15 | 15316.6
23:00 | 7950.5 | 7380.79 | 15331.29

## En-Curve
QF-LDC-12
Date | 25-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3840 | 1991.5 | 876 | 38 | 44 | 1453.2 | 222 | 4759 | 0 | 360 | 927 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3811.5 | 1985.5 | 876.5 | 38 | 44 | 1390.94 | 222 | 4634 | 0 | 325 | 869.85 | 0 | 0 | 2 | 0 | 25-08-2025
01:00 | 3783 | 1979.5 | 877 | 38 | 44 | 1328.68 | 222 | 4509 | 0 | 290 | 812.7 | 0 | 0 | 2 | 0
01:30 | 3781 | 1974.25 | 876.5 | 38 | 43 | 1325.835 | 222 | 4347 | 0 | 280 | 802.35 | 0 | 0 | 1 | 0 | Energy Generated | 333.7035 |  | MKWHr
02:00 | 3779 | 1969 | 876 | 38 | 42 | 1322.99 | 222 | 4185 | 0 | 270 | 792 | 0 | 0 | 0 | 0 | Energy not Served | 0.282 |  | MKWHr
02:30 | 3806 | 1977.75 | 876 | 38 | 41 | 1218.035 | 222 | 4171 | 0 | 228 | 713 | 0 | 0 | 1 | 0 | Total Energy Requirement | 333.9855 |  | MKWHr
03:00 | 3833 | 1986.5 | 876 | 38 | 40 | 1113.08 | 222 | 4157 | 0 | 186 | 634 | 0 | 0 | 2 | 0
03:30 | 3822 | 1983 | 876 | 38 | 40 | 1111.345 | 222 | 4099.5 | 0 | 178.5 | 610 | 0 | 0 | 2.5 | 0
04:00 | 3811 | 1979.5 | 876 | 38 | 40 | 1109.61 | 222 | 4042 | 0 | 171 | 586 | 0 | 0 | 3 | 0
04:30 | 3792 | 1980.5 | 876 | 38 | 39 | 1078.705 | 222 | 4000 | 0 | 152 | 553 | 0 | 0 | 4.5 | 0
05:00 | 3773 | 1981.5 | 876 | 38 | 38 | 1047.8 | 222 | 3958 | 0 | 133 | 520 | 0 | 0 | 6 | 0
05:30 | 3764.5 | 1958.25 | 876.5 | 38 | 37 | 1031.34 | 221 | 3911.5 | 6.12 | 124.5 | 457 | 0 | 0 | 5 | 0
06:00 | 3756 | 1935 | 877 | 38 | 36 | 1014.88 | 220 | 3865 | 12.24 | 116 | 394 | 0 | 0 | 4 | 0
06:30 | 3774 | 1939 | 876.5 | 38 | 35 | 1015.22 | 220 | 3768.5 | 65.93 | 131.5 | 377.5 | 0 | 0 | 6 | 0
07:00 | 3792 | 1943 | 876 | 38 | 34 | 1015.56 | 220 | 3672 | 119.62 | 147 | 361 | 0 | 0 | 8 | 0
07:30 | 3760.5 | 1905.5 | 876 | 38 | 34 | 1014.49 | 221 | 3662 | 189.5 | 147 | 361 | 0 | 0 | 5 | 0
08:00 | 3729 | 1868 | 876 | 38 | 34 | 1013.42 | 222 | 3652 | 259.38 | 147 | 361 | 0 | 0 | 2 | 0
08:30 | 3767.5 | 1861 | 876 | 38 | 34 | 1018.565 | 222 | 3672.5 | 362.565 | 152 | 358.5 | 0 | 0 | 1.5 | 0
09:00 | 3806 | 1854 | 876 | 38 | 34 | 1023.71 | 222 | 3693 | 465.75 | 157 | 356 | 0 | 0 | 1 | 0
09:30 | 3850.5 | 1888.5 | 876 | 38 | 34 | 943.605 | 222 | 3709 | 555.495 | 166.5 | 353.5 | 0 | 0 | 0.5 | 0
10:00 | 3895 | 1923 | 876 | 38 | 34 | 863.5 | 222 | 3725 | 645.24 | 176 | 351 | 0 | 0 | 0 | 0
10:30 | 3900 | 1923 | 876 | 38 | 35 | 843.14 | 222 | 3876.5 | 654.735 | 176 | 360 | 0 | 0 | 0 | 0
11:00 | 3905 | 1923 | 876 | 38 | 36 | 822.78 | 222 | 4028 | 664.23 | 176 | 369 | 0 | 0 | 0 | 0
11:30 | 3878 | 1930.5 | 876 | 38 | 37 | 821.695 | 222 | 4180.5 | 644.88 | 176 | 442.5 | 0 | 0 | 5.5 | 0
12:00 | 3851 | 1938 | 876 | 38 | 38 | 820.61 | 222 | 4333 | 625.53 | 176 | 516 | 0 | 0 | 11 | 0
12:30 | 3832 | 1940 | 876.5 | 38 | 40 | 822.55 | 222 | 4438 | 640.585 | 178.5 | 599.35 | 0 | 0 | 16.5 | 0
13:00 | 3813 | 1942 | 877 | 38 | 42 | 824.49 | 222 | 4543 | 655.64 | 181 | 682.7 | 0 | 0 | 22 | 0
13:30 | 3801 | 1920 | 876.5 | 38 | 43 | 822.745 | 221 | 4551 | 634.915 | 204.5 | 707.85 | 25 | 0 | 25.5 | 0
14:00 | 3789 | 1898 | 876 | 38 | 44 | 821 | 220 | 4559 | 614.19 | 228 | 733 | 50 | 0 | 29 | 0
14:30 | 3811.5 | 1891.5 | 875.5 | 38 | 44 | 822 | 220 | 4579.5 | 518.75 | 227.5 | 735.55 | 95 | 0 | 25.5 | 0
15:00 | 3834 | 1885 | 875 | 38 | 44 | 823 | 220 | 4600 | 423.31 | 227 | 738.1 | 140 | 0 | 22 | 0
15:30 | 3818.5 | 1713.5 | 875 | 38 | 43 | 827 | 220 | 4641.5 | 343.49 | 239.5 | 838.95 | 159 | 0 | 13.5 | 0
16:00 | 3803 | 1542 | 875 | 38 | 42 | 831 | 220 | 4683 | 263.67 | 252 | 939.8 | 178 | 0 | 5 | 0
16:30 | 3787 | 1542 | 875 | 38 | 41 | 826 | 219.5 | 4644.5 | 200.365 | 259 | 1042.7 | 124 | 0 | 2.5 | 0
17:00 | 3771 | 1542 | 875 | 38 | 40 | 821 | 219 | 4606 | 137.06 | 266 | 1145.6 | 70 | 0 | 0 | 0
17:30 | 3650 | 1488 | 861.5 | 38 | 40 | 898 | 218.5 | 4481.5 | 80.435 | 298 | 1257.6 | 35 | 0 | 0 | 0
18:00 | 3529 | 1434 | 848 | 38 | 40 | 975 | 218 | 4357 | 23.81 | 330 | 1369.6 | 0 | 0 | 0 | 0
18:30 | 3717.5 | 1480 | 848 | 38 | 44 | 1134.5 | 218.5 | 4557 | 11.905 | 464.5 | 1708.45 | 0 | 0 | 0 | 0
19:00 | 3906 | 1526 | 848 | 38 | 48 | 1294 | 219 | 4757 | 0 | 599 | 2047.3 | 0 | 0 | 0 | 0
19:30 | 3821 | 1496 | 847 | 38 | 48 | 1310 | 219 | 4930 | 0 | 634 | 2320.2 | 0 | 0 | 0 | 64
20:00 | 3794 | 1509 | 848 | 38 | 46 | 1417 | 220 | 4914 | 0 | 657 | 2229.2 | 0 | 0 | 0 | 74
20:30 | 3779.5 | 1509.15 | 848 | 38 | 47 | 1436.48 | 220 | 4920.5 | 0 | 669.5 | 2170.2 | 0 | 0 | 0 | 74
21:00 | 3765 | 1509.3 | 848 | 38 | 48 | 1455.96 | 220 | 4927 | 0 | 682 | 2111.2 | 0 | 0 | 0 | 74
21:30 | 3814 | 1526 | 848 | 38 | 49 | 1456.235 | 220.5 | 4894 | 0 | 685 | 1922.45 | 0 | 0 | 0 | 70.5
22:00 | 3863 | 1542.7 | 848 | 38 | 50 | 1456.51 | 221 | 4861 | 0 | 688 | 1733.7 | 0 | 0 | 0 | 67
22:30 | 3869 | 1562.1 | 848 | 38 | 51 | 1451.65 | 221 | 4871 | 0 | 690.5 | 1714.35 | 0 | 0 | 0 | 67
23:00 | 3875 | 1581.5 | 848 | 38 | 52 | 1446.79 | 221 | 4881 | 0 | 693 | 1695 | 0 | 0 | 0 | 67
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 07:00 | 371 | 15:00 | Payra | 415 | 07:00 | 407 | 22:00
Ashuganj | 405 | 5:00 | 373 | 14:00 | Rahanpur | 401 | 17:00 | 380 | 22:00
Bhulta | 399 | 05:00 | 370 | 15:00 | Rampal | 408 | 06:00 | 391 | 23:00
Bibiana | 389 | 06:00 | 375 | 16:00
BIPTC | 404 | 05:00 | 391 | 16:00
Bogura | 386 | 11:00 | 361 | 22:00
Gopalganj | 401 | 07:00 | 385 | 23:00
Kaliakoir | 375 | 05:00 | 354 | 08:00
Madunaghat | 394 | 07:00 | 386 | 12:00
Meghnaghat | 389 | 07:00 | 375 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 216 | 13:00 | Keranigonj | 225 | 06:00 | 214 | 13:00
AKSML | 230 | 19:00 | 222 | 13:00 | Khulna(S) | 233 | 08:00 | 218 | 23:00
Aminbazar | 227 | 04:00 | 217 | 11:00 | Madunaghat | 233 | 21:00 | 226 | 13:00
Ashuganj | 231 | 06:00 | 220 | 15:00 | Madunaghat-400 | 233 | 19:00 | 227 | 12:00
Ashuganj-400 | 231 | 06:00 | 220 | 15:00 | Maniknagar | 220 | 05:00 | 212 | 15:00
Baghabari | 235 | 05:00 | 225 | 21:00 | Meghnaghat | 228 | 07:00 | 220 | 02:00
Barapukuria | 224 | 18:00 | 213 | 22:00 | Meghnaghat-400 | 225 | 06:00 | 217 | 12:00
Barapukuria-230 | 224 | 18:00 | 213 | 22:00 | Mirsorai | 231 | 18:00 | 219 | 13:00
Barishal | 229 | 07:00 | 220 | 22:00 | Rajshahi | 232 | 05:00 | 219 | 22:00
Bheramara | 234 | 06:00 | 222 | 22:00 | Rampal | 232 | 06:00 | 220 | 19:00
Bhulta | 230 | 05:00 | 211 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 220 | 16:00 | Rampura | 229 | 06:00 | 208 | 15:00
BIPTC | 236 | 05:00 | 221 | 22:00 | Shikalbaha | 231 | 19:30 | 224 | 11:00
Bogura | 239 | 10:00 | 225 | 22:00 | Shyampur | 224 | 06:00 | 214 | 15:00
Bogura-400 | 239 | 10:00 | 225 | 22:00 | Siddhirganj | 222 | 7:00 | 215 | 12:00
Borhanuddin | 233 | 06:00 | 227 | 19:00 | Sirajgonj | 241 | 05:00 | 233 | 22:00
BSRM | 230 | 19:30 | 218 | 13:00 | Sreepur | 229 | 05:00 | 219 | 22:00
Cumilla(N) | 222 | 06:00 | 214 | 15:00 | Tongi | 226 | 18:00 | 213 | 15:00
Faridpur | 228 | 07:00 | 216 | 22:00
Fenchuganj | 228 | 06:00 | 222 | 23:00
Ghorashal | 235 | 04:00 | 220 | 15:00
Ghorashal-230 | 229 | 06:00 | 211 | 15:00
Gopalganj | 228 | 07:00 | 218 | 23:00
GPH | 229 | 07:00 | 221 | 13:00
Haripur | 222 | 06:00 | 214 | 13:00
Hasnabad | 224 | 06:00 | 214 | 15:00
Hathazari | 230 | 07:00 | 220 | 15:00
Ishurdi | 236 | 06:00 | 224 | 22:00
Jhenaidah | 231 | 08:00 | 217 | 21:00
Kaliakoir | 232 | 05:00 | 221 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 123 | 15:00 | Lalmonirhat | 128 | 18:00 | 116 | 23:00
Agargaon | 134 | 06:00 | 125 | 11:00 | Madanganj | 126 | 07:00 | 123 | 11:00
Agrabad | 131 | 19:30 | 124 | 11:00 | Madaripur | 135 | 06:00 | 128 | 23:00
AKS | 130 | 20:00 | 124 | 11:00 | Madartek | 135 | 01:00 | 122 | 15:00
Aminbazar | 133 | 05:00 | 127 | 11:00 | Madunaghat | 132 | 19:30 | 128 | 11:00
Amnura | 136 | 12:00 | 125 | 23:00 | Magura | 132 | 05:00 | 123 | 22:00
Ashuganj | 140 | 05:00 | 135 | 15:00 | Mahasthangarh | 132 | 18:00 | 121 | 22:00
Bagerhat | 134 | 08:00 | 121 | 22:00 | Maijdee | 123 | 18:00 | 111 | 11:00
Bajitpur | 130 | 06:00 | 121 | 22:00 | Manikganj | 127 | 06:00 | 120 | 15:00
Bakulia | 133 | 18:30 | 126 | 14:00 | Maniknagar | 134 | 05:00 | 127 | 11:00
Banani | 136 | 06:00 | 122 | 15:00 | Matarbari | 119 | 16:00 | 112 | 12:00
Bangabhaban | 134 | 05:00 | 127 | 11:00 | Matuail | 129 | 06:00 | 123 | 15:00
Barapukuria | 136 | 18:00 | 125 | 21:00 | Millgate | 134 | 05:00 | 123 | 15:00
Barguna | 134 | 06:00 | 129 | 23:00 | Mirpur | 132 | 05:00 | 124 | 12:00
Barishal | 135 | 07:00 | 127 | 23:00 | Mirzapur | 129 | 05:00 | 123 | 08:00
Barishal-230 | 135 | 07:00 | 127 | 22:00 | Mithapukur | 130 | 18:00 | 119 | 22:00
Baroaulia | 132 | 19:00 | 126 | 15:00 | MI_Cement | 128 | 04:00 | 123 | 11:00
Baroirhat | 126 | 18:00 | 118 | 11:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 04:00 | 122 | 15:00 | Mogbazar | 135 | 03:00 | 123 | 14:00
BashundharaCement | 126 | 07:00 | 123 | 11:00 | Mongla | 134 | 08:00 | 122 | 19:00
Beanibazar | 127 | 06:00 | 121 | 19:00 | Motijheel | 134 | 05:00 | 127 | 11:00
Benapole | 133 | 08:00 | 122 | 00:00 | Muktagacha | 134 | 06:00 | 126 | 22:00
Bhaluka | 129 | 04:00 | 122 | 22:00 | Munshiganj | 127 | 05:00 | 122 | 10:00
Bhandaria | 130 | 08:00 | 119 | 19:00 | Muradnagar | 124 | 06:00 | 118 | 12:00
Bhangura | 134 | 05:00 | 126 | 22:00 | Mymensingh | 133 | 05:00 | 112 | 22:00
Bheramara | 138 | 06:00 | 131 | 22:00 | Naogaon | 130 | 09:00 | 118 | 22:00
Bheramara(GK) | 138 | 05:00 | 131 | 22:00 | Narail | 132 | 05:00 | 122 | 00:00
Bhulta | 122 | 04:00 | 117 | 14:00 | Narinda | 134 | 05:00 | 127 | 11:00
Bog-Sherpur | 133 | 09:00 | 123 | 22:00 | Narshingdi | 135 | 06:00 | 118 | 12:00
Bogura | 134 | 10:00 | 125 | 22:00 | Natore | 134 | 08:00 | 125 | 22:00
Bogura-230 | 135 | 09:00 | 125 | 22:00 | Nawabganj | 134 | 05:00 | 126 | 13:00
Brahmanbaria | 135 | 04:00 | 126 | 22:00 | Netrakona | 125 | 06:00 | 110 | 22:00
Cantonment | 133 | 05:00 | 124 | 13:00 | New | 134 | 04:00 | 124 | 15:00
Chandina | 127 | 05:00 | 122 | 11:00 | Niamatpur | 136 | 06:00 | 128 | 21:00
Chandpur | 130 | 18:00 | 118 | 11:00 | Noapara | 135 | 07:00 | 125 | 19:00
Chandraghona | 132 | 06:00 | 128 | 15:00 | Pabna | 135 | 06:00 | 126 | 22:00
Chapai | 136 | 18:00 | 127 | 22:00 | Palashbari | 129 | 18:00 | 117 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 05:00 | 123 | 11:00 | Panchagarh | 135 | 18:00 | 121 | 07:00
Chauddagram | 125 | 18:00 | 116 | 13:00 | Patiya | 131 | 19:30 | 126 | 11:00
Chhatak | 126 | 06:00 | 118 | 22:00 | Patuakhali | 134 | 04:00 | 130 | 23:00
Chowmuhani | 124 | 18:00 | 112 | 11:00 | Payra | 136 | 07:00 | 132 | 22:00
Chuadanga | 131 | 09:00 | 122 | 22:00 | PHP | 125 | 18:30 | 116 | 11:00
Coxsbazar | 119 | 07:00 | 113 | 18:30 | Postogola | 137 | 06:00 | 128 | 13:00
Cumilla(N) | 127 | 05:00 | 121 | 14:00 | Purbachal | 136 | 05:00 | 121 | 15:00
Cumilla(S) | 133 | 03:00 | 120 | 11:00 | Purbasadipur | 131 | 18:00 | 119 | 22:00
Daganbhuiyan | 123 | 18:00 | 113 | 11:00 | Rahanpur | 137 | 12:00 | 129 | 22:00
Daudkandi | 121 | 06:00 | 115 | 13:00 | Rahanpur-400 | 138 | 17:00 | 130 | 22:00
Dhaka | 136 | 04:00 | 122 | 15:00 | Rahim | 128 | 04:00 | 124 | 11:00
Dhamrai | 133 | 05:00 | 125 | 11:00 | Rajbari | 134 | 08:00 | 125 | 23:00
Dhanmondi | 136 | 06:00 | 121 | 15:00 | Rajendrapur | 131 | 19:30 | 121 | 23:00
Dohazari | 130 | 20:00 | 122 | 14:00 | Rajshahi | 134 | 05:00 | 125 | 22:00
Faridpur | 135 | 08:00 | 128 | 19:00 | Rajshahi-230 | 134 | 06:00 | 125 | 22:00
Fatullah | 129 | 05:00 | 124 | 11:00 | Ramganj | 125 | 18:00 | 112 | 11:00
Fenchuganj | 135 | 04:00 | 130 | 18:30 | Rampur | 133 | 21:00 | 125 | 11:00
Feni | 125 | 18:30 | 114 | 11:00 | Rampura | 136 | 06:00 | 122 | 15:00
Ghatail | 130 | 04:00 | 121 | 18:30 | Rangamati | 131 | 19:30 | 127 | 14:00
Ghorashal | 136 | 04:00 | 128 | 15:00 | Rangpur | 130 | 18:00 | 121 | 7:00
Goalpara | 138 | 08:00 | 127 | 21:00 | Ruppur | 138 | 04:00 | 130 | 22:00
Gollamari | 137 | 07:00 | 129 | 00:00 | Saidpur | 131 | 18:00 | 120 | 19:00
Gopalganj | 136 | 08:00 | 127 | 19:00 | Satkhira | 135 | 08:00 | 123 | 22:00
Gopalganj-400 | 137 | 07:00 | 130 | 23:00 | Satmasjid | 133 | 05:00 | 124 | 15:00
Gulshan | 136 | 06:00 | 122 | 15:00 | Savar | 133 | 17:00 | 124 | 11:00
Halishahar | 133 | 19:30 | 125 | 11:00 | SevenRings | 137 | 06:00 | 128 | 15:00
Haripur | 129 | 05:00 | 124 | 15:00 | ShahCement | 128 | 05:00 | 123 | 11:00
HaripurSBU | 129 | 05:00 | 125 | 10:00 | Shahjadpur | 136 | 10:00 | 130 | 22:00
Hasnabad | 133 | 05:00 | 129 | 10:00 | Shahjibazar | 135 | 07:00 | 126 | 23:00
Hathazari | 133 | 04:00 | 127 | 15:00 | Shahmirpur | 133 | 20:00 | 127 | 15:00
Ishurdi | 139 | 08:00 | 131 | 22:00 | Shariatpur | 134 | 07:00 | 125 | 23:00
Jaldhaka | 129 | 18:00 | 116 | 22:00 | Sherpur | 132 | 06:00 | 120 | 18:30
Jamalpur | 135 | 06:00 | 125 | 19:00 | Shikalbaha | 123 | 21:00 | 117 | 11:00
Jashore | 131 | 06:00 | 122 | 00:00 | Shikalbaha-230 | 134 | 18:30 | 128 | 11:00
Jhenaidah | 136 | 07:00 | 121 | 22:00 | Shitalakhya | 128 | 04:00 | 123 | 11:00
Jhenaidah-230 | 135 | 06:00 | 125 | 19:00 | Sholosohor | 131 | 07:00 | 127 | 11:00
Joydebpur | 134 | 19:30 | 123 | 09:00 | Shyampur | 129 | 06:00 | 126 | 00:00
Joypurhat | 128 | 08:00 | 115 | 22:00 | Shyampur-230 | 129 | 06:00 | 124 | 15:00
Juldah | 133 | 19:30 | 126 | 11:00 | Siddhirganj | 129 | 04:00 | 124 | 15:00
Kabirpur | 130 | 07:00 | 121 | 16:00 | Sirajganj | 132 | 09:00 | 121 | 22:00
Kachua | 129 | 18:00 | 120 | 10:00 | Sonargaon | 125 | 05:00 | 122 | 10:00
Kaliakoir | 134 | 04:00 | 125 | 08:00 | Sreemongol | 133 | 07:00 | 125 | 22:00
Kallyanpur | 133 | 06:00 | 126 | 11:00 | Sreepur | 132 | 05:00 | 125 | 22:00
Kalurghat | 130 | 00:00 | 129 | 01:00 | Srinagar | 135 | 06:00 | 126 | 13:00
Kamrangirchar | 134 | 05:00 | 126 | 15:00 | SSM | 135 | 19:00 | 130 | 11:00
Kaptai | 134 | 7:00 | 131 | 15:00 | Sunamganj | 123 | 06:00 | 115 | 23:00
Kasba | 123 | 06:00 | 117 | 12:00 | Sylhet | 128 | 06:00 | 123 | 19:30
Kazla | 134 | 07:00 | 127 | 12:00 | Sylhet-132 | 128 | 05:00 | 124 | 22:00
Keranigonj | 135 | 06:00 | 127 | 13:00 | Tangail | 127 | 04:00 | 121 | 22:00
Khagrachori | 130 | 06:00 | 126 | 13:00 | Taraganj | 127 | 05:00 | 119 | 19:00
Khulna | 137 | 08:00 | 128 | 00:00 | Thakurgaon | 134 | 18:00 | 118 | 07:00
Khulna(S) | 138 | 08:00 | 129 | 00:00 | TK | 132 | 19:30 | 127 | 11:00
Khulshi | 131 | 21:00 | 123 | 11:00 | Tongi | 133 | 01:00 | 126 | 15:00
Kishoreganj | 129 | 05:00 | 119 | 22:00 | Ullahpara | 134 | 06:00 | 125 | 22:00
Kodda | 134 | 20:00 | 120 | 08:00 | Ullon | 135 | 04:00 | 122 | 15:00
KSRM | 132 | 18:00 | 126 | 11:00 | Uttara | 132 | 06:00 | 124 | 11:00
Kulaura | 134 | 06:00 | 128 | 23:00 | UttaraNew | 131 | 04:00 | 124 | 11:00
Kurigram | 127 | 18:00 | 115 | 22:00 | Zigatola | 135 | 06:00 | 127 | 12:00
Kushtia | 135 | 05:00 | 126 | 22:00
Laksam | 128 | 18:00 | 118 | 11:00
Lakshmipur | 123.96 | 18:00 | 111 | 11:00
Lalbag | 135 | 07:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division