## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-08-2025 | during | 28-08-2025 | during | 28-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 335 | 333 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 290 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 329 | 335 | 335 | 332 | 332 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 36.6 | 45 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 76 | 119 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21.2 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 297 | 300 | 300 | 300 | 300
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 91 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 140 | 145 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 282 | 288 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2284.6 | 2809.2 | 5808.84 | 5823.84 | 3856.39 | 3871.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 219 | 214 | 214 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 55 | 68 | 48 | 64 | 48 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 16 | 26 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.37 | 0 | 4.43 | 0 | 4.43 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 60 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 88 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1125 | 1150 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 16 | 15 | 25 | 28 | 25 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 635 | 636 | 635 | 635 | 660 | 660 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2345.37 | 2809 | 3677.15 | 3689.72 | 3672.15 | 3684.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 191 | 194 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 342 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 39 | 46.7 | 46.7 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 37 | 38 | 55 | 55 | 42 | 42 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 71 | 195 | 195 | 137 | 137 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 45 | 113 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 30 | 47 | 47 | 47 | 47 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 51 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 173 | 168 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 97 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 42 | 43 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 101 | 98 | 115 | 115 | 103.5 | 103.5 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 77 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1623 | 1774 | 2440.86 | 2370.86 | 2218.16 | 2148.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-08-2025 | during | 28-08-2025 | during | 28-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 67 | 71 | 157.5 | 157.5 | 102 | 102 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 73 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 82 | 109 | 95 | 103 | 95 | 103 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.09 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 22 | 22 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 266.09 | 282 | 433.2 | 412 | 377.7 | 356.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 70 | 0 | 0 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 84 | 84 | 81 | 81 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 166 | 166 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 16 | 16 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 8 | 25 | 25 | 14 | 14 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 351 | 348 | 385 | 385 | 372 | 372 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1108 | 1112 | 1146 | 1146 | 1193 | 1193
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 458 | 842 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 199 | 190 | 410 | 410 | 220 | 220 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 12 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 60 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 20 | 170 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1031 | 1088 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1806 | 2340 | 3634.2 | 3554.2 | 3414 | 3334
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 299 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1092 | 1150 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 165 | 275 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.78 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1892.78 | 2059 | 2162 | 2161 | 2097 | 2096
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.8 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 160 | 214 | 214 | 205 | 205 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 140 | 220 | 220 | 195 | 195 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 140 | 220 | 220 | 193 | 193 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 338 | 345 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 28 | 28 | 28 | 28 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 42 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.18 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1157.67 | 1155.09 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 45.55 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2206.2 | 2276.09 | 3158.47 | 2991.87 | 3054.8 | 2888.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 44 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 149 | 145 | 150 | 150 | 150 | 150 | Machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 143.2 | 0 | 143.2 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 668.8 | 417 | 641.8 | 462 | 641.8 | 462
System Total |  |  |  |  | 28823.2 | 27829.875 | 14200.84 | 15878.29 | 23102.52 | 22611.49 | 20525 | 20033.97
Forecast Scenario (28-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15590 |  | 0 |  | 15590
|  |  |  | 1:00 | 15090 |  | 0 |  | 15090
|  |  |  | 2:00 | 14600 |  | 0 |  | 14600
|  |  |  | 3:00 | 14190 |  | 0 |  | 14190
|  |  |  | 4:00 | 13790 |  | 0 |  | 13790
|  |  |  | 5:00 | 13590 |  | 0 |  | 13590
|  |  |  | 6:00 | 13080 |  | 0 |  | 13080
|  |  |  | 7:00 | 12800 |  | 0 |  | 12800
|  |  |  | 8:00 | 12860 |  | 0 |  | 12860
|  |  |  | 9:00 | 13000 |  | 0 |  | 13000
|  |  |  | 10:00 | 13130 |  | 0 |  | 13130
|  |  |  | 11:00 | 13360 |  | 0 |  | 13360
|  |  |  | 12:00 | 14000 |  | 0 |  | 14000
|  |  |  | 13:00 | 14240 |  | 0 |  | 14240
|  |  |  | 14:00 | 14190 |  | 0 |  | 14190
|  |  |  | 15:00 | 14390 |  | 0 |  | 14390
|  |  |  | 16:00 | 14410 |  | 0 |  | 14410
|  |  |  | 17:00 | 13740 |  | 0 |  | 13740
|  |  |  | 18:00 | 13380 |  | 0 |  | 13380
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 15310 |  | 0 |  | 15310
|  |  |  | 19:30 | 15670 |  | 0 |  | 15670
|  |  |  | 20:00 | 15520 |  | 0 |  | 15520
|  |  |  | 21:00 | 15480 |  | 0 |  | 15480
|  |  |  | 22:00 | 15550 |  | 0 |  | 15550
|  |  |  | 23:00 | 15400 |  | 0 |  | 15400
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 14000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 340.69 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:20 hrs on 28-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-08-2025 | [28 empty] | Date: | 27-08-2025 | [28 empty] | Date: | 27-08-2025 | [28 empty] | Date: | 27-08-2025 | [28 empty] | Date: | 27-08-2025 | [14 empty] | Date: | 27-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 104 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 45.5 | 17 | 149 | 120 | 260 | 15 | 55 | 144 | 0 | 300 | 296 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 125 | 22.8 | 22 | 0 | 280 | 0 | 0 | 51 | 0 | 11 | 66 | 65 | 0 | 12 | 12 | 0 | 222 | 103 | 31 | 635 | 0 | 0 | 19 | 17 | 94 | 218 | 0 | 0 | 0 | 1135 | 0 | 51 | 135 | 26 | 0 | 352 | 330 | 36 | 191 | 39 | 99 | 70 | 171 | 61 | 18 | 97 | 54 | 43 | 0 | 30 | 305 | 0 | 363 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 99 | 77 | 83 | 0 | 0 | 12 | 8578.3 | 868 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 17 | 1156 | 0 | 0 | 0 | 0 | 33 | 0 | 87 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 396 | 0 | 0 | 154 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 300 | 1225 | 119 | 7171 | 15749.3 | 107.64
01:00 | 0 | 104 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 46 | 0 | 133 | 120 | 75 | 0 | 55 | 147 | 0 | 300 | 299 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 287 | 0 | 0 | 28 | 0 | 10 | 66 | 52 | 0 | 12 | 12 | 0 | 222 | 85 | 35 | 635 | 0 | 0 | 19 | 17 | 93 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 50 | 26 | 0 | 351 | 330 | 36 | 195 | 36 | 100 | 70 | 168 | 48 | 18 | 97 | 50 | 43 | 0 | 30 | 305 | 0 | 364 | 0 | 60 | 153 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 57 | 83 | 0 | 0 | 12 | 8156 | 848 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 17 | 1149 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 405 | 0 | 0 | 155 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 300 | 1225 | 118 | 7093 | 15249 | 107.67
02:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 45.5 | 0 | 103 | 105 | 0 | 0 | 50 | 146 | 0 | 300 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 290 | 0 | 0 | 0 | 0 | 9 | 66 | 52 | 0 | 12 | 12 | 0 | 222 | 51 | 37 | 635 | 0 | 0 | 19 | 0 | 96 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 26 | 0 | 352 | 330 | 37 | 194 | 36 | 101 | 70 | 168 | 49 | 18 | 97 | 48 | 43 | 0 | 30 | 305 | 0 | 367 | 0 | 60 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 57 | 97 | 0 | 0 | 12 | 7859.5 | 847 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 17 | 1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 406 | 0 | 0 | 154 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 300 | 1225 | 47 | 6944 | 14803.5 | 107.7
03:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 16.5 | 0 | 68 | 91 | 0 | 0 | 17 | 72 | 0 | 300 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 24.7 | 22 | 0 | 281 | 0 | 0 | 0 | 0 | 11 | 61 | 52 | 0 | 12 | 12 | 0 | 220 | 20 | 37 | 635 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 26 | 0 | 353 | 330 | 37 | 193 | 36 | 101 | 70 | 175 | 52 | 17 | 97 | 48 | 31 | 0 | 30 | 310 | 0 | 356 | 0 | 60 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 57 | 97 | 0 | 0 | 12 | 7511.2 | 848 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 17 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 403 | 0 | 0 | 155 | 47 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 300 | 1225 | 0 | 6881 | 14392.2 | 107.73
04:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 15 | 0 | 51 | 91 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 24.7 | 22 | 0 | 288 | 0 | 0 | 0 | 0 | 16 | 33 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 37 | 635 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 26 | 0 | 352 | 330 | 38 | 194 | 36 | 100 | 70 | 172 | 51 | 17 | 88 | 46 | 25 | 0 | 30 | 305 | 0 | 354 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 24 | 97 | 0 | 0 | 8 | 7193.7 | 848 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 17 | 1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 407 | 0 | 0 | 155 | 45 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 300 | 1225 | 0 | 6800 | 13993.7 | 107.76
05:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 51 | 91 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 24.7 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 38 | 635 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1132 | 0 | 51 | 0 | 26 | 0 | 356 | 330 | 38 | 188 | 37 | 98 | 70 | 170 | 52 | 17 | 88 | 46 | 0 | 0 | 30 | 305 | 0 | 350 | 0 | 60 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 24 | 97 | 0 | 0 | 0 | 7083.7 | 848 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1189 | 17 | 1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 160 | 0 | 160 | 0 | 339 | 0 | 0 | 156 | 46 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 300 | 1225 | 0 | 6709 | 13792.7 | 107.79
06:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 51 | 76 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 52 | 24.7 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 12 | 12 | 0.08 | 219 | 0 | 42 | 635 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1012 | 0 | 51 | 0 | 26 | 0 | 352 | 330 | 38 | 184 | 37 | 99 | 70 | 169 | 52 | 17 | 70 | 40 | 0 | 2 | 30 | 310 | 0 | 339 | 0 | 60 | 136 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 24 | 97 | 0 | 0.47 | 0 | 6880.25 | 848 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1128 | 17 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0 | 0 | 0 | 0.62 | 170 | 0 | 160 | 0 | 160 | 0 | 328 | 0 | 0.05 | 156 | 44 | 50 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 160 | 115 | 220 | 0 | 300 | 1100 | 0 | 6408.55 | 13288.8 | 107.82
07:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 51 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 0 | 0 | 0 | 335 | 0 | 0 | 7 | 52 | 25 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 16 | 0 | 0 | 12 | 12 | 0.97 | 220 | 0 | 40 | 635 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1063 | 3 | 43 | 0 | 20 | 0 | 351 | 330 | 38 | 202 | 37 | 103 | 70 | 170 | 45 | 17 | 34 | 38 | 0 | 21 | 30 | 310 | 0 | 391 | 0 | 60 | 146 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 90 | 30 | 83 | 0 | 8.85 | 0 | 6989.82 | 526 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 1025 | 17 | 1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.54 | 12 | 0 | 0 | 8.55 | 170 | 0 | 160 | 0 | 160 | 0 | 414 | 0 | 0.69 | 153 | 48 | 35 | 2 | 34 | 0 | 0 | 0 | 1.5 | 6 | 0.18 | 0 | 173 | 115 | 220 | 0 | 300 | 1010 | 0 | 6014.46 | 13004.28 | 107.85
08:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 51 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 23.5 | 22 | 0 | 290 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 2.06 | 219 | 0 | 13 | 635 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1050 | 5 | 43 | 0 | 30 | 0 | 353 | 330 | 39 | 194 | 33 | 101 | 70 | 173 | 44 | 17 | 17 | 38 | 0 | 39 | 30 | 310 | 0 | 386 | 0 | 60 | 155 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 91 | 54 | 67 | 1 | 9.46 | 0 | 6949.02 | 526 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 8 | 0 | 0 | 55 | 1002 | 0 | 1160.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.94 | 18 | 0 | 0 | 17.78 | 170 | 0 | 160 | 0 | 160 | 0 | 407 | 0 | 1.99 | 151 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 2.5 | 14 | 0.45 | 0 | 172 | 115 | 220 | 0 | 301 | 1080 | 0 | 6111.73 | 13060.75 | 107.88
09:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 51 | 76 | 0 | 0 | 7 | 0 | 0 | 300 | 290 | 0 | 0 | 0 | 333 | 0 | 0 | 14 | 52 | 21.5 | 22 | 0 | 289 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 12 | 3.16 | 220 | 0 | 14 | 635 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1055 | 13 | 43 | 0 | 26 | 0 | 351 | 330 | 38 | 194 | 32 | 100 | 70 | 171 | 44 | 17 | 17 | 38 | 0 | 56 | 30 | 315 | 0 | 345 | 0 | 60 | 150 | 6 | 0 | 77 | 30 | 0 | 16 | 100 | 0 | 92 | 57 | 67 | 2 | 12.1 | 4 | 6979.76 | 474 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 19 | 0 | 0 | 87 | 996 | 0 | 1150.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.38 | 80 | 0 | 0 | 16.26 | 170 | 0 | 160 | 0 | 160 | 0 | 390 | 0 | 1.2 | 145 | 48 | 35 | 8 | 34 | 0 | 0 | 0 | 2.3 | 103 | 0.59 | 0 | 171 | 115 | 220 | 0 | 301 | 1090 | 0 | 6229.62 | 13209.38 | 107.89
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 10.4 | 0 | 51 | 76 | 15 | 0 | 35 | 46 | 0 | 300 | 283 | 0 | 0 | 17 | 332 | 0 | 0 | 18 | 52 | 20 | 15 | 0 | 281 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 2.58 | 220 | 0 | 14 | 635 | 0 | 0 | 4 | 0 | 0 | 218 | 0 | 0 | 0 | 1110 | 18 | 43 | 0 | 26 | 0 | 347 | 330 | 38 | 188 | 37 | 99 | 50 | 170 | 43 | 17 | 17 | 36 | 0 | 68 | 30 | 305 | 0 | 292 | 0 | 60 | 138 | 6 | 0 | 76 | 30 | 0 | 16 | 100 | 0 | 92 | 57 | 67 | 2 | 33.4 | 6 | 7055.38 | 458 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 990 | 0 | 1153.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.24 | 108 | 0 | 0 | 58.69 | 170 | 0 | 160 | 0 | 160 | 0 | 338 | 0 | 5.7 | 146 | 48 | 35 | 15 | 34 | 0 | 0 | 0 | 4.6 | 150 | 0.41 | 0 | 166 | 115 | 220 | 0 | 300 | 1088 | 0 | 6280.59 | 13335.97 | 107.9
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 30.9 | 6 | 86 | 76 | 15 | 0 | 35 | 45 | 0 | 300 | 289 | 0 | 0 | 17 | 330 | 0 | 0 | 24 | 52 | 20 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 3.13 | 221 | 0 | 14 | 635 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 1150 | 7 | 43 | 2 | 26 | 0 | 300 | 330 | 38 | 196 | 37 | 100 | 50 | 170 | 43 | 17 | 17 | 40 | 0 | 72 | 36 | 310 | 0 | 351 | 0 | 60 | 142 | 6 | 0 | 78 | 30 | 0 | 16 | 100 | 0 | 83 | 57 | 67 | 2 | 51.88 | 6 | 7254.91 | 458 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 992 | 0 | 1154.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.91 | 56 | 0 | 0 | 45.55 | 170 | 0 | 160 | 0 | 160 | 0 | 350 | 0 | 4.49 | 146 | 46 | 35 | 13 | 34 | 0 | 0 | 0 | 3.1 | 191 | 0.07 | 0 | 172 | 115 | 220 | 0 | 300 | 1090 | 0 | 6305.64 | 13560.55 | 107.91
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 36.6 | 0 | 91 | 76 | 95 | 4 | 50 | 140 | 0 | 300 | 286 | 0 | 0 | 35 | 330 | 0 | 0 | 35 | 52 | 20 | 22 | 0 | 282 | 0 | 0 | 0 | 0 | 16 | 0 | 55 | 0 | 12 | 12 | 3.37 | 221 | 0 | 16 | 635 | 0 | 0 | 30 | 0 | 0 | 218 | 0 | 0 | 0 | 1125 | 2 | 43 | 45 | 26 | 0 | 342 | 330 | 37 | 191 | 37 | 101 | 70 | 173 | 42 | 17 | 17 | 40 | 0 | 77 | 35 | 305 | 0 | 351 | 0 | 60 | 154 | 12 | 0 | 80 | 30 | 0 | 16 | 100 | 0 | 82 | 57 | 67 | 1 | 53.09 | 6 | 7627.06 | 458 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 20 | 0 | 0 | 60 | 1031 | 0 | 1157.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.8 | 115 | 0 | 0 | 45.55 | 170 | 0 | 160 | 0 | 160 | 0 | 338 | 0 | 5.18 | 149 | 46 | 35 | 35 | 34 | 0 | 160 | 0 | 5.8 | 204 | 0.78 | 0 | 165 | 115 | 220 | 0 | 300 | 1092 | 0 | 6573.78 | 14200.84 | 107.92
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 47.1 | 0 | 141 | 75 | 95 | 15 | 37 | 150 | 0 | 300 | 289 | 0 | 0 | 35 | 325 | 0 | 0 | 35 | 70 | 20 | 22 | 0 | 280 | 0 | 0 | 20 | 0 | 21 | 0 | 55 | 0 | 12 | 12 | 2.19 | 222 | 0 | 19 | 639 | 0 | 0 | 40 | 0 | 0 | 216 | 0 | 0 | 0 | 1125 | 9 | 43 | 86 | 53 | 0 | 340 | 280 | 36 | 192 | 36 | 99 | 70 | 170 | 42 | 17 | 17 | 44 | 0 | 51 | 35 | 310 | 0 | 352 | 0 | 58 | 142 | 8 | 0 | 80 | 30 | 0 | 16 | 100 | 0 | 73 | 63 | 67 | 2 | 50.95 | 6 | 7724.24 | 559 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 20 | 0 | 0 | 104 | 1097 | 0 | 1155.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.99 | 98 | 0 | 0 | 65.55 | 170 | 0 | 160 | 0 | 160 | 0 | 343 | 0 | 5.75 | 148 | 47 | 35 | 30 | 34 | 0 | 164 | 0 | 3.1 | 171 | 0.34 | 0 | 166 | 115 | 220 | 0 | 300 | 1090 | 0 | 6722.17 | 14446.41 | 107.92
14:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 45.3 | 0 | 149 | 75 | 95 | 15 | 36 | 146 | 0 | 300 | 297 | 0 | 0 | 35 | 280 | 0 | 0 | 32 | 90 | 20.8 | 22 | 0 | 318 | 0 | 0 | 30 | 0 | 39 | 0 | 55 | 0 | 12 | 12 | 1.64 | 222 | 0 | 14 | 638 | 0 | 0 | 40 | 0 | 0 | 219 | 0 | 0 | 0 | 1145 | 11 | 43 | 103 | 53 | 0 | 300 | 280 | 36 | 201 | 38 | 99 | 70 | 170 | 42 | 18 | 17 | 42 | 0 | 37 | 35 | 305 | 0 | 351 | 0 | 60 | 138 | 8 | 0 | 80 | 30 | 0 | 16 | 100 | 0 | 73 | 63 | 66 | 1 | 45.4 | 6 | 7743.14 | 843 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 20 | 0 | 0 | 37 | 1027 | 0 | 1007.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.27 | 109 | 0 | 0 | 58.29 | 170 | 0 | 160 | 0 | 160 | 0 | 355 | 0 | 5.23 | 152 | 45 | 35 | 22 | 34 | 0 | 164 | 0 | 3.6 | 189 | 0.25 | 0 | 169 | 115 | 180 | 0 | 299 | 1000 | 0 | 6650.51 | 14393.65 | 107.92
15:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 49.6 | 0 | 149 | 75 | 95 | 15 | 55 | 158 | 0 | 300 | 294 | 0 | 0 | 35 | 318 | 0 | 0 | 26 | 90 | 20 | 22 | 0 | 300 | 0 | 0 | 30 | 0 | 56 | 0 | 56 | 0 | 12 | 12 | 1.03 | 221 | 0 | 10 | 636 | 0 | 0 | 40 | 10 | 0 | 217 | 0 | 0 | 0 | 1150 | 6 | 51 | 110 | 53 | 0 | 300 | 330 | 37 | 202 | 35 | 105 | 70 | 177 | 42 | 18 | 17 | 42 | 0 | 41 | 28 | 320 | 0 | 375 | 0 | 50 | 155 | 8 | 0 | 80 | 30 | 0 | 16 | 100 | 2 | 73 | 66 | 66 | 2 | 28.69 | 6 | 7936.32 | 843 | 191 | 0 | 0 | 0 | 38 | 0 | 0 | 63 | 0 | 0 | 58 | 1018 | 0 | 967.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.34 | 80 | 0 | 0 | 46.61 | 170 | 0 | 160 | 0 | 160 | 0 | 368 | 0 | 4.19 | 148 | 44 | 35 | 18 | 34 | 0 | 127 | 0 | 2.9 | 162 | 0.7 | 0 | 170 | 115 | 220 | 0 | 300 | 1065 | 0 | 6653.68 | 14590 | 107.93
16:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 48.5 | 0 | 149 | 75 | 240 | 21 | 55 | 155 | 0 | 300 | 285 | 0 | 0 | 55 | 324 | 0 | 0 | 19 | 90 | 19.3 | 22 | 0 | 282 | 0 | 0 | 30 | 0 | 36 | 4 | 55 | 0 | 12 | 12 | 0.66 | 220 | 0 | 11 | 636 | 0 | 0 | 40 | 17 | 0 | 219 | 0 | 0 | 0 | 1120 | 4 | 51 | 98 | 53 | 0 | 338 | 330 | 36 | 188 | 37 | 103 | 70 | 179 | 42 | 18 | 97 | 40 | 0 | 17 | 28 | 310 | 0 | 361 | 0 | 50 | 154 | 14 | 0 | 82 | 30 | 0 | 16 | 100 | 17 | 73 | 64 | 66 | 1 | 24.95 | 6 | 8087.41 | 844 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 99 | 0 | 0 | 52 | 1076 | 0 | 965.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.49 | 61 | 0 | 0 | 22.64 | 170 | 0 | 160 | 0 | 160 | 0 | 386 | 0 | 1.54 | 147 | 44 | 35 | 8 | 34 | 0 | 100 | 0 | 1.4 | 45 | 0.33 | 0 | 165 | 115 | 220 | 0 | 300 | 1100 | 0 | 6527.46 | 14614.87 | 107.93
17:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 43.5 | 5 | 134 | 75 | 294 | 55 | 55 | 140 | 0 | 300 | 288 | 0 | 0 | 55 | 270 | 0 | 0 | 1 | 90 | 0 | 22 | 0 | 277 | 0 | 0 | 30 | 0 | 42 | 16 | 61 | 0 | 25 | 12 | 0.25 | 220 | 0 | 22 | 636 | 0 | 0 | 40 | 17 | 0 | 219 | 0 | 0 | 0 | 1000 | 0 | 51 | 105 | 53 | 0 | 300 | 280 | 36 | 188 | 38 | 96 | 70 | 164 | 35 | 18 | 97 | 36 | 0 | 12 | 28 | 300 | 0 | 328 | 0 | 50 | 133 | 14 | 0 | 82 | 30 | 0 | 16 | 100 | 17 | 78 | 64 | 71 | 0 | 9.93 | 6 | 7759.68 | 843 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 114 | 0 | 0 | 16 | 1070 | 0 | 967.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.85 | 13 | 0 | 0 | 11.41 | 140 | 0 | 140 | 0 | 140 | 0 | 332 | 0 | 1 | 145 | 44 | 35 | 8 | 34 | 0 | 93 | 0 | 0.1 | 44 | 0.12 | 0 | 164 | 115 | 180 | 0 | 300 | 1000 | 0 | 6183.14 | 13942.82 | 107.93
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 43.4 | 34.92 | 134 | 75 | 294 | 55 | 55 | 138 | 0 | 300 | 278 | 0 | 0 | 55 | 270 | 0 | 0 | 1 | 125 | 19.8 | 22 | 0 | 272 | 0 | 0 | 32 | 0 | 56 | 16 | 68 | 0 | 25 | 12 | 0.02 | 219 | 0 | 25 | 636 | 0 | 0 | 40 | 17 | 0 | 185 | 0 | 0 | 0 | 980 | 0 | 51 | 98 | 70 | 0 | 300 | 280 | 37 | 155 | 38 | 96 | 70 | 160 | 43 | 18 | 97 | 34 | 0 | 1 | 29 | 300 | 0 | 321 | 0 | 70 | 133 | 8 | 0 | 82 | 20 | 0 | 16 | 100 | 17 | 99 | 73 | 71 | 0 | 0.76 | 6 | 7775.9 | 842 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 126 | 0 | 0 | 3 | 988 | 0 | 971.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1.03 | 1 | 0 | 0 | 1.13 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0.12 | 143 | 44 | 35 | 1 | 34 | 0 | 0 | 0 | 0.1 | 10 | 0.02 | 0 | 156 | 115 | 180 | 0 | 299 | 900 | 0 | 5809.05 | 13584.95 | 107.93
19:00 | 24 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 46.6 | 35 | 149 | 119 | 295 | 55 | 55 | 150 | 0 | 320 | 286 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 125 | 20.5 | 22 | 0 | 280 | 0 | 0 | 50 | 0 | 36 | 66 | 68 | 0 | 25 | 12 | 0 | 220 | 15 | 25 | 634 | 80 | 0 | 40 | 17 | 42 | 219 | 0 | 0 | 0 | 1120 | 0 | 51 | 102 | 71 | 0 | 344 | 330 | 38 | 188 | 39 | 101 | 50 | 176 | 43 | 19 | 97 | 42 | 43 | 0 | 30 | 310 | 0 | 359 | 0 | 70 | 147 | 8 | 0 | 83 | 30 | 0 | 16 | 100 | 17 | 108 | 73 | 72 | 0 | 0 | 11 | 8658.1 | 842 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 150 | 0 | 0 | 0 | 1077 | 12 | 1117.98 | 0 | 22 | 0 | 50 | 30 | 0 | 82 | 0 | 52.2 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 391 | 0 | 0 | 145 | 44 | 110 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 299 | 980 | 0 | 6799.18 | 15457.28 | 107.93
19:30 | 16 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 45 | 35 | 149 | 119 | 297 | 55 | 55 | 145 | 0 | 300 | 290 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 125 | 21.2 | 22 | 0 | 288 | 15 | 0 | 50 | 0 | 15 | 66 | 68 | 17 | 25 | 12 | 0 | 220 | 60 | 26 | 636 | 88 | 0 | 40 | 17 | 85 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 113 | 71 | 0 | 345 | 330 | 38 | 194 | 39 | 98 | 51 | 168 | 43 | 19 | 97 | 44 | 43 | 0 | 30 | 310 | 0 | 348 | 0 | 70 | 147 | 8 | 0 | 83 | 30 | 0 | 16 | 100 | 17 | 109 | 73 | 71 | 0 | 0 | 12 | 8786.2 | 842 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 170 | 0 | 0 | 0 | 1088 | 12 | 1155.09 | 0 | 31 | 0 | 70 | 80 | 0 | 86 | 0 | 42 | 0 | 0 | 27 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 345 | 0 | 0 | 145 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 299 | 1150 | 0 | 7092.09 | 15878.29 | 107.93
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 43.9 | 35 | 149 | 120 | 297 | 15 | 55 | 141 | 0 | 300 | 286 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 108 | 21.5 | 22 | 0 | 283 | 28 | 0 | 51 | 0 | 24 | 66 | 68 | 0 | 25 | 12 | 0 | 221 | 67 | 29 | 636 | 53 | 0 | 40 | 17 | 98 | 219 | 0 | 0 | 0 | 1122 | 0 | 51 | 113 | 71 | 0 | 348 | 330 | 39 | 187 | 40 | 91 | 50 | 165 | 44 | 19 | 97 | 44 | 43 | 0 | 35 | 305 | 0 | 332 | 0 | 70 | 137 | 8 | 0 | 83 | 30 | 0 | 16 | 100 | 17 | 109 | 75 | 71 | 0 | 0 | 12 | 8605.4 | 842 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 200 | 0 | 0 | 0 | 1105 | 12 | 1152.46 | 0 | 45 | 0 | 50 | 105 | 0 | 86 | 0 | 24 | 0 | 0 | 27 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 334 | 0 | 0 | 145 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 220 | 0 | 299 | 1150 | 0 | 7120.46 | 15725.86 | 107.93
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 44.9 | 35 | 149 | 121 | 297 | 15 | 55 | 143 | 0 | 300 | 280 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 327 | 0 | 0 | 50 | 0 | 53 | 66 | 68 | 0 | 25 | 12 | 0 | 221 | 66 | 32 | 636 | 45 | 0 | 40 | 17 | 92 | 220 | 0 | 0 | 0 | 1132 | 0 | 51 | 113 | 71 | 0 | 350 | 0 | 39 | 190 | 40 | 92 | 50 | 170 | 54 | 19 | 97 | 46 | 43 | 0 | 37 | 305 | 0 | 336 | 0 | 70 | 137 | 8 | 0 | 84 | 30 | 0 | 16 | 100 | 17 | 109 | 75 | 71 | 0 | 0 | 12 | 8347.9 | 842 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 364 | 0 | 0 | 0 | 1120 | 12 | 1152.62 | 0 | 41 | 0 | 50 | 50 | 0 | 86 | 0 | 24 | 0 | 0 | 27 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 385 | 0 | 0 | 143 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 299 | 1150 | 0 | 7295.62 | 15643.52 | 107.93
22:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 44.9 | 17 | 149 | 91 | 297 | 15 | 55 | 144 | 0 | 300 | 286 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 125 | 21.4 | 22 | 0 | 370 | 0 | 0 | 50 | 0 | 16 | 66 | 68 | 0 | 25 | 12 | 0 | 222 | 68 | 36 | 637 | 45 | 0 | 20 | 17 | 94 | 219 | 0 | 0 | 0 | 1139 | 0 | 51 | 118 | 162 | 0 | 350 | 0 | 42 | 193 | 40 | 98 | 70 | 169 | 54 | 19 | 97 | 46 | 43 | 0 | 37 | 300 | 0 | 328 | 0 | 70 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 100 | 17 | 108 | 75 | 72 | 0 | 0 | 12 | 8458.3 | 843 | 195 | 0 | 0 | 0 | 38 | 0 | 0 | 341 | 0 | 0 | 0 | 1121 | 12 | 1151.07 | 0 | 41 | 0 | 50 | 50 | 0 | 86 | 0 | 24 | 0 | 0 | 27 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 402 | 0 | 0 | 140 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 299 | 1150 | 0 | 7292.07 | 15750.37 | 107.92
23:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 46 | 17 | 149 | 60 | 297 | 15 | 55 | 145 | 0 | 300 | 292 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 380 | 0 | 0 | 51 | 0 | 12 | 66 | 68 | 0 | 25 | 12 | 0 | 222 | 68 | 38 | 636 | 48 | 0 | 19 | 17 | 93 | 211 | 0 | 0 | 0 | 1157 | 0 | 51 | 107 | 173 | 0 | 351 | 0 | 42 | 198 | 37 | 98 | 70 | 171 | 56 | 19 | 97 | 44 | 43 | 0 | 37 | 310 | 0 | 346 | 0 | 70 | 153 | 8 | 0 | 84 | 30 | 0 | 16 | 100 | 17 | 108 | 75 | 73 | 0 | 0 | 12 | 8476 | 842 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 343 | 0 | 0 | 0 | 1123 | 15 | 1137.18 | 0 | 41 | 0 | 50 | 50 | 0 | 86 | 0 | 24 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 409 | 0 | 0 | 142 | 47 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 300 | 1150 | 0 | 7289.18 | 15765.18 | 107.92
Total KWH | 34992 | 1804800 | 466560 | 0 | 0 | 0 | 0 | 0 | 8240400 | 0 | 0 | 772200 | 222120 | 2606112 | 2036160 | 3028473 | 355510 | 893385 | 2355840 | 0 | 7584000 | 7068945 | 0 | 0 | 697465 | 7729258 | 0 | 0 | 225146 | 1957200 | 513000 | 516600 | 0 | 7877272.73 | 41400 | 0 | 512640 | 0 | 573120 | 714753 | 904656 | 10922 | 378240 | 298560 | 22461 | 5304342 | 623924 | 641280 | 15440000 | 284364 | 0 | 570720 | 179173.8 | 792873 | 5244094 | 0 | 0 | 0 | 26809088 | 81810 | 1161104 | 1433527 | 1338182 | 0 | 8447800 | 6752000 | 912960 | 4735000 | 900216 | 2399040 | 1561300 | 4108320 | 1129800 | 412980 | 1581180 | 1008960 | 404506 | 519800 | 753408 | 7492500 | 0 | 8788000 | 0 | 1368000 | 3534054.54 | 175176 | 0 | 1948800 | 692448 | 0 | 395000 | 2403950 | 162000 | 2152800 | 1408800 | 1763520 | 13450 | 335030 | 179760 | 188787231.07 | 18819636 | 4682592 | 0 | 0 | 0 | 192000 | 0 | 0 | 1846774.55 | 0 | 0 | 537120 | 26014540 | 218880 | 26743637 | 0 | 206665 | 0 | 349056 | 402624 | 0 | 515920 | 0 | 179707 | 394393 | 748740 | 170200 | 0 | 425256 | 4096091 | 0 | 3945064 | 0 | 3972973 | 0 | 9072872 | 0 | 37440 | 3662000 | 1073890 | 1653628 | 145033 | 1661232 | 0 | 770332.5 | 0 | 30682.8 | 1218240 | 3688 | 0 | 5280000 | 2763000 | 5338490 | 0 | 7221096 | 27179636.36 | 212400 | 161785529.21 | 350572760.28

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14200.84 | MW | 12:00 Hr. | Energy Generated |  |  | 350.5728 |  | MKWHr.
| Day Peak Demand |  |  | 14200.84 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.275 |  | MKWHr.
| Evening Peak Generation |  |  | 15878.29 | MW | 19:30 Hr. | Energy Demand |  |  | 350.8478 |  | MKWHr.
| Evening Peak Demand |  |  | 15878.29 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 13004.28 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 981.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 15878.29 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.6843 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.5295 | 0 | 17.2308 | 0 | 0 | 0.22515 | 0 | 0 | 56.9854 | Gas | 134.0689 | Gas | 481355172.4955
| Chattogram Zone |  |  | 5.8854 | 42.2491 | 5.3122 | 0 | 5.3043 | 0.10427 | 0 | 0.57312 | 59.4284 | Coal | 112.6803 | Coal | 670572218.0452
| Cumilla Zone |  |  | 26.2215 | 0 | 11.8098 | 0 | 0 | 0.5198 | 1.009 | 0 | 39.5601 | HFO | 43.8265 | HFO | 804932080.934
| Mymensingh Zone |  |  | 1.7635 | 0 | 3.9034 | 0 | 0 | 0.34848 | 0 | 0 | 6.0154 | HSD | 2.6171 | HSD | 33112667.6815
| Sylhet Zone |  |  | 26.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7979 | Hydro | 5.3043 | Hydro | 530434.2
| Khulna Zone |  |  | 4.6826 | 26.0145 | 0.21888 | 1.8468 | 0 | 0.53712 | 19.0116 | 0 | 52.3115 | Solar | 4.7383 | Solar | 70280909.608
| Barishal Zone |  |  | 8.1015 | 39.6807 | 0.2124 | 0 | 0 | 0.003688 | 0 | 0 | 47.9983 | Import | 46.7642 | Import | 274108345.57
| Rajshahi Zone |  |  | 21.087 | 0 | 1.8242 | 0 | 0 | 1.6058 | 26.7436 | 0 | 51.2606 | Wind | 0.57312 | Wind | 8447788.8
| Rangpur Zone |  |  | 0 | 4.7359 | 3.3149 | 0.77033 | 0 | 1.394 | 0 | 0 | 10.215
| Total |  |  | 134.0689 | 112.6803 | 43.8265 | 2.6171 | 5.3043 | 4.7383 | 46.7642 | 0.57312 | 350.5728
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 481355172.4955 |  | Hydro | 530434.2
|  |  |  | Coal | 670572218.0452 |  | Solar | 70280909.608
|  |  |  | HFO | 804932080.934 |  | Import | 274108345.57
|  |  |  | HSD | 33112667.6815 |  | Wind | 8447788.8
[5 empty] | Total: | 234,33,39,617 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.8196 | Peak Hr Flow | 842.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47228643.7 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.7436 | Peak Hr Flow | 1155.09 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2014 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.009 | Peak Hr Flow | 44.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2532 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.5722 | Peak Hr Flow | 2041.09 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5500
|  |  |  | Chattogram |  | 0 |  | 1465
|  |  |  | Cumilla |  | 0 |  | 1433
|  |  |  | Mymensingh |  | 0 |  | 1261
|  |  |  | Sylhet |  | 0 |  | 642
|  |  |  | Khulna |  | 0 |  | 1855
|  |  |  | Barishal |  | 0 |  | 430
|  |  |  | Rajshahi |  | 0 |  | 1585
|  |  |  | Rangpur |  | 0 |  | 1090
|  |  |  | Total |  | 0 |  | 15261
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:30 | 18:34 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project work.
| 08:50 | 11:06 | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Red hot maintenance | [7 empty] | 35.0MW load
interrup.
| 08:51 | 11:07 | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D | [7 empty] | 35.0MW load
interrup.
|  | 09:25 | Meghnaghat 400/230kV S/S 400 kV Bus -02 is restored.
| 09:26 |  | Khulna 330MW GT was forced shutdown due to GT exhaust leakage.
| 09:27 |  | Khulna 330 MW P/S de synchronize due to GT exhaust leakage. | [7 empty] | 19MW generation
interrup.
| 09:55 | 11:57 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end. | [7 empty] | 40.0MW load
interrup. Tongi
230/132/33kV end
| 10:06 | 13:12 | KSRM 132/33kV S/S Transformer-01 LT Scheduled S/D Due to for checking oil leakage of CT
| 11:05 | 18:58 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D Due to DS QB-02(132KV ATR-02 side)
Magnatic contact change
| 11:06 | 18:57 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D Due to DS QB-02 (132 KV ATR-02 Side)
Magnatic contact change
| 11:18 | 17:19 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Scheduled S/D Due to OLTC oil change.
| 11:29 |  | Siadpur 150 MW GT was synch.
| 11:45 |  | Khulna 330 MW CCPP GT was synch.
| 11:45 |  | Khulna 330 MW P/S synchronize for Final Acceptance test.
| 12:00 |  | Day Peak Gen. 14200 MW
| 12:40 |  | From NLDC: Bheramara HVDC Pole-1 restored
|  | 12:40 | BIPTC S/S 21T01 HT is restored.
| 14:12 | 14:22 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 51.0MW load
interrup.
| 14:12 | 14:35 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 44.0MW load
interrup.
| 14:25 | 18:29 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to Hot
spot maintenance and from Gopalganj 400/132kVend.
| 14:33 | 15:53 | Bheramara P/S-Kustia 132 kV Ckt-1 Forced S/D from Kushtia 132/33kV end Due to Earthing
Wire Connection and from Bheramara 230/132kVend.
| 15:10 | 17:55 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to Distance
Relay Failure Maintenance
| 15:21 | 18:00 | Chowmuhani-Ramganj 132 kV Ckt-1 Project Work S/D from Ramganj 132/33kV end Due to project
work
| 16:01 | 18:46 | Bheramara P/S-Kustia 132 kV Ckt-2 Forced S/D from Kushtia 132/33kV end. and from
Bheramara 230/132kVend.
|  | 17:59 | BIPTC S/S 20DF24 is restored.
| 19:36 | 19:48 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Lockout. relays Due to 33 kV T-4 Post | [7 empty] | 45.0MW load
|  |  | insulator crack. | [7 empty] | interrup.
| 19:47 | 21:04 | Lakshmipur 132/33kV S/S Transformer-1 HT Scheduled S/D
| 20:52 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- Plant
| 20:52 |  | Ashuganj South 360 MW CCPP tripped due to the tripping of the Natural Gas controller
system.
| 23:45 | 01:13 | Juldah-Shahmirpur 132kV Ckt-2 Forced S/D from Juldah 132/33kV end Due to Due to having
continuous Flashing at LA counter Connection point of 132 KV julda-shahmirpur circuit-2
| 06:37 |  | Ashuganj South 360 MW CCPP GT was sync.
| 06:37 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 07:05 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to High
temperature maintenace.
| 07:05 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to High
temperature maintenace.
| 07:20 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to 33kV Kaligong LA Fault
Maintenance under 132kV T-1 Transformer.
| 07:20 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kv Kaligong feeder LA Fault
under 132kV T1
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 333 | 8240400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7584000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7068945 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 355510 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7729258 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 34992 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 772200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 119 | 2036160 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 893385 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 697465 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.2 | 513000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 516600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 466560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 297 | 3028473 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2606112 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1804800 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 2355840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 225146 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 222120 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 288 | 7877272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1957200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2809.2 | 56985438.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 179173.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 81810 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 570720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5304342 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5244094 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 792873 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 904656 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 714753 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 378240 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 641280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 512640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22461 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 10922 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 60 | 623924 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 298560 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 41400 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 88 | 284364 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 26809088 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 15 | 573120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 636 | 15440000 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2809 | 59428420.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 194 | 4735000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8447800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 6752000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 900216 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 38 | 912960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 71 | 1338182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1161104 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 113 | 1433527 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 753408 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1561300 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 168 | 4108320 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 44 | 1008960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 404506 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 412980 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1581180 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 43 | 1129800 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 98 | 2399040 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 519800 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1774 | 39560083
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1763520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 73 | 1408800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 109 | 2152800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 335030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 179760 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 162000 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 282 | 6015360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 70 | 1368000 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3534054.54 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 692448 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1948800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 395000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 175176 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7492500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8788000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1112 | 26797928.54
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 842 | 18819636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 190 | 4682592 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 12 | 218880 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 537120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 170 | 1846774.55 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1088 | 26014540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 192000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2340 | 52311542.55
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 299 | 7221096 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2763000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1150 | 27179636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5338490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 212400 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 5280000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3688 | -
Barishal Area Total |  |  |  |  | 2236 | 2059 | 47998310.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 394393 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 206665 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4096091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3945064 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3972973 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 9072872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 170200 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 42 | 179707 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 515920 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 402624 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 349056 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1155.09 | 26743637 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 425256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 748740 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | -
Rajshahi Area Total |  |  |  |  | 3518.96 | 2276.09 | 51260638
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 770332.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 44 | 1073890 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 145 | 3662000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1661232 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30682.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1653628 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 145033 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1218240 | -
Rangpur Area Total |  |  |  |  | 950 | 417 | 10215038.3
Eastern Grid Total |  |  |  |  | 17385.715 | 8786.2 | 188787231.07
Western Grid Total |  |  |  |  | 10444.16 | 7092.09 | 161785529.21
National Grid Total |  |  |  |  | 27829.875 | 15878.29 | 350572760.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10300.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4960 | MW
i) Dhaka area |  |  | 5500.07 |  | MW | i) Khulna area |  |  |  | 1855 | MW
ii) Chattogram area |  |  | 1465 |  | MW | ii) Barishal area |  |  |  | 430 | MW
iii) Cumilla area |  |  | 1432.51 |  | MW | iii) Rajshahi area |  |  |  | 1585 | MW
iv) Mymensingh area |  |  | 1261 |  | MW | iv) Rangpur area |  |  |  | 1090 | MW
v) Sylhet area |  |  | 642 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15260.58 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 84 | 19:00 | 133 | PHP | 3 | 08:00
2 | AKSML | 158 | 09:00 | 68 | Ishurdi | 85 | 19:00 | 134 | Pabna | 133 | 19:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 85 | 00:00 | 135 | Palashbari | 130 | 19:00
4 | Agargaon | 139 | 15:00 | 70 | Jamalpur | 128 | 20:00 | 136 | Panchagarh | 63 | 19:00
5 | Agrabad | 82 | 12:00 | 71 | Jashore | 142 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 35 | 19:00 | 72 | Jhenaidah | 130 | 21:00 | 138 | Patuakhali | 71.7 | 00:00
7 | Ashuganj | 88 | 01:00 | 73 | Joydebpur | 163 | 18:30 | 139 | Payra | 32 | 00:00
8 | BSRM | 196 | 20:00 | 74 | Joypurhat | 68 | 21:00 | 140 | Postogola | 57 | 13:00
9 | Bagerhat | 83 | 19:00 | 75 | Juldah | 18 | 23:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 92 | 19:30 | 76 | KSRM | 15 | 03:00 | 142 | Purbasadipur | 132 | 00:00
11 | Bakulia | 94 | 19:30 | 77 | Kabirpur | 256 | 09:00 | 143 | Rahanpur | 42 | 22:00
12 | Banani | 56 | 13:00 | 78 | Kachua | 96 | 00:00 | 144 | Rahim | 40 | 18:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 90 | 19:00
14 | Barapukuria | 72 | 19:00 | 80 | Kalurghat | 40 | 13:00 | 146 | Rajendrapur | 142 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 80 | 12:00 | 147 | Rajshahi | 118 | 00:00
16 | Barishal | 110 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 94 | 13:00
17 | Barishal-230 | 110 | 21:00 | 83 | Kasba | 38 | 22:00 | 149 | Ramganj | 118 | 00:00
18 | Baroaulia | 72 | 11:00 | 84 | Kazla | 106 | 17:00 | 150 | Rampur | 41 | 00:00
19 | Baroirhat | 64 | 21:00 | 85 | Keranigonj | 85 | 19:00 | 151 | Rangamati | 14 | 13:00
20 | Bashundhara | 206 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Rangpur | 154 | 20:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 68 | 19:30 | 153 | Ruppur | 7.2 | 16:00
22 | Beanibazar | 84 | 00:00 | 88 | Khulshi | 195 | 15:00 | 154 | SSM | 14 | 00:00
23 | Benapole | 62 | 00:00 | 89 | Kishoreganj | 140 | 21:00 | 155 | Saidpur | 118 | 19:00
24 | Bhaluka | 161 | 20:00 | 90 | Kodda | 297 | 11:00 | 156 | Satkhira | 128 | 19:00
25 | Bhandaria | 54 | 00:00 | 91 | Kulaura | 56 | 21:00 | 157 | Satmasjid | 104 | 16:00
26 | Bhangura | 40 | 19:00 | 92 | Kurigram | 70 | 20:00 | 158 | Savar | 247 | 12:00
27 | Bheramara(GK) | 69 | 00:00 | 93 | Kushtia | 165 | 19:30 | 159 | SevenRings | 18.17 | 21:00
28 | Bhulta | 211 | 19:00 | 94 | Laksam | 36 | 23:00 | 160 | ShahCement | 26 | 11:00
29 | Bog-Sherpur | 82 | 01:00 | 95 | Lakshmipur | 34 | 22:00 | 161 | Shahjadpur | 92 | 20:00
30 | Bogura | 176 | 00:00 | 96 | Lalbag | 64 | 13:00 | 162 | Shahjibazar | 139 | 22:00
31 | Borhanuddin | 93 | 20:00 | 97 | Lalmonirhat | 73 | 19:30 | 163 | Shahmirpur | 65 | 00:00
32 | Brahmanbaria | 141 | 00:00 | 98 | MI_Cement | 16.6 | 10:00 | 164 | Shariatpur | 94 | 22:00
33 | Cantonment | 150 | 13:00 | 99 | Madanganj | 44 | 00:00 | 165 | Sherpur | 158 | 22:00
34 | Chandina | 17.05 | 22:00 | 100 | Madaripur | 117 | 23:00 | 166 | Shikalbaha | 13 | 17:00
35 | Chandpur | 83 | 00:00 | 101 | Madartek | 100 | 00:00 | 167 | Shitalakhya | 76.8 | 16:00
36 | Chandraghona | 35 | 18:30 | 102 | Madunaghat | 56 | 21:00 | 168 | Sholosohor | 46 | 10:00
37 | Chapai | 71 | 00:00 | 103 | Magura | 71 | 19:00 | 169 | Shyampur | 174 | 08:00
38 | Charsaidpur | 30 | 11:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 122 | 11:00
39 | Chauddagram | 73 | 00:00 | 105 | Maijdee | 41 | 18:30 | 171 | Sirajganj | 126 | 19:30
40 | Chhatak | 45 | 19:00 | 106 | Manikganj | 136 | 00:00 | 172 | Sonargaon | 137 | 23:00
41 | Chowmuhani | 189 | 21:00 | 107 | Maniknagar | 80 | 13:00 | 173 | Sreemongol | 88 | 19:00
42 | Chuadanga | 121 | 00:00 | 108 | Matarbari | 132 | 12:00 | 174 | Sreepur | 106 | 19:00
43 | Coxsbazar | 124 | 00:00 | 109 | Matuail | 74 | 00:00 | 175 | Srinagar | 50.26 | 23:00
44 | Cumilla(N) | 153 | 00:00 | 110 | Millgate | 135 | 15:00 | 176 | Sunamganj | 65 | 00:00
45 | Cumilla(S) | 150 | 00:00 | 111 | Mirpur | 130 | 16:00 | 177 | Sylhet | 52 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 09:00 | 178 | Sylhet-132 | 139 | 17:00
47 | Daudkandi | 151 | 00:00 | 113 | Mirzapur | 48 | 19:30 | 179 | TK | 35 | 22:00
48 | Dhaka | 98 | 13:00 | 114 | Mithapukur | 76 | 23:00 | 180 | Tangail | 184 | 00:00
49 | Dhamrai | 136 | 21:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 23:00
50 | Dhanmondi | 147 | 12:00 | 116 | Mogbazar | 126.4 | 16:00 | 182 | Thakurgaon | 116 | 19:30
51 | Dohazari | 107 | 21:00 | 117 | Mongla | 51 | 12:00 | 183 | Tongi | 111 | 17:00
52 | Faridpur | 176 | 23:00 | 118 | Motijheel | 49 | 17:00 | 184 | Ullahpara | 42 | 21:00
53 | Fatullah | 112 | 16:00 | 119 | Muktagacha | 40 | 00:00 | 185 | Ullon | 50 | 00:00
54 | Fenchuganj | 50 | 19:30 | 120 | Munshiganj | 116 | 00:00 | 186 | Uttara | 86 | 11:00
55 | Feni | 119 | 19:00 | 121 | Muradnagar | 43 | 20:00 | 187 | UttaraNew | 63 | 00:00
56 | GPH | 73 | 20:00 | 122 | Mymensingh | 217 | 19:00 | 188 | Zigatola | 76 | 18:30
57 | Ghatail | 82 | 20:00 | 123 | Naogaon | 144 | 22:00
58 | Ghorashal | 15 | 12:00 | 124 | Narail | 62 | 19:30
59 | Ghorashal-230 | 95 | 22:00 | 125 | Narinda | 80 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 193 | 00:00
61 | Gollamari | 94 | 00:00 | 127 | Natore | 159 | 00:00
62 | Gopalganj | 112 | 00:00 | 128 | Nawabganj | 64 | 22:00
63 | Gulshan | 132 | 12:00 | 129 | Netrakona | 149 | 00:00
64 | Halishahar | 63.5 | 15:00 | 130 | New | 78 | 12:00
65 | HaripurSBU | 160 | 11:00 | 131 | Niamatpur | 80 | 00:00
66 | Hasnabad | 92 | 23:00 | 132 | Noapara | 45 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15749.3 | 45 |  | 15796.3
1:00 | 15249 | 39 |  | 15290
2:00 | 14803.5 | 0 |  | 14803.5
3:00 | 14392.2 | 0 |  | 14392.2
4:00 | 13993.7 | 0 |  | 13993.7
5:00 | 13792.7 | 0 |  | 13792.7
6:00 | 13288.8 | 0 |  | 13288.8
7:00 | 13004.28 | 0 |  | 13004.28
8:00 | 13060.75 | 0 |  | 13060.75
9:00 | 13209.38 | 0 |  | 13209.38
10:00 | 13335.97 | 0 |  | 13335.97
11:00 | 13560.55 | 0 |  | 13560.55
12:00 | 14200.84 | 0 |  | 14200.84
13:00 | 14446.41 | 0 |  | 14446.41
14:00 | 14393.65 | 0 |  | 14393.65
15:00 | 14590 | 0 |  | 14590
16:00 | 14614.87 | 0 |  | 14614.87
17:00 | 13942.82 | 0 |  | 13942.82
18:00 | 13584.95 | 0 |  | 13584.95
19:00 | 15457.28 | 53 |  | 15512.28
19:30 | 15878.29 | 0 |  | 15878.29
20:00 | 15725.86 | 0 |  | 15725.86
21:00 | 15643.52 | 36 |  | 15681.14
22:00 | 15750.37 | 49 |  | 15801.37
23:00 | 15765.18 | 53 |  | 15820.18
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8578.3 | 7171 | 15749.3 | DAILY GENERATION CURVE
00:30 | 8367.15 | 7132 | 15499.15
01:00 | 8156 | 7093 | 15249 | 27-08-2025
01:30 | 8007.75 | 7018.5 | 15026.25
02:00 | 7859.5 | 6944 | 14803.5
02:30 | 7685.35 | 6912.5 | 14597.85
03:00 | 7511.2 | 6881 | 14392.2
03:30 | 7352.45 | 6840.5 | 14192.95
04:00 | 7193.7 | 6800 | 13993.7
04:30 | 7138.7 | 6754.5 | 13893.2
05:00 | 7083.7 | 6709 | 13792.7
05:30 | 6981.975 | 6558.775 | 13540.75
06:00 | 6880.25 | 6408.55 | 13288.8
06:30 | 6935.035 | 6211.505 | 13146.54
07:00 | 6989.82 | 6014.46 | 13004.28
07:30 | 6969.42 | 6063.095 | 13032.515
08:00 | 6949.02 | 6111.73 | 13060.75
08:30 | 6964.39 | 6170.675 | 13135.065
09:00 | 6979.76 | 6229.62 | 13209.38
09:30 | 7017.57 | 6255.105 | 13272.675
10:00 | 7055.38 | 6280.59 | 13335.97
10:30 | 7155.145 | 6293.115 | 13448.26
11:00 | 7254.91 | 6305.64 | 13560.55
11:30 | 7440.985 | 6439.71 | 13880.695
12:00 | 7627.06 | 6573.78 | 14200.84
12:30 | 7675.65 | 6647.975 | 14323.625
13:00 | 7724.24 | 6722.17 | 14446.41
13:30 | 7733.69 | 6686.34 | 14420.03
14:00 | 7743.14 | 6650.51 | 14393.65
14:30 | 7839.73 | 6652.095 | 14491.825
15:00 | 7936.32 | 6653.68 | 14590
15:30 | 8011.865 | 6590.57 | 14602.435
16:00 | 8087.41 | 6527.46 | 14614.87
16:30 | 7923.545 | 6355.3 | 14278.845
17:00 | 7759.68 | 6183.14 | 13942.82
17:30 | 7767.79 | 5996.095 | 13763.885
18:00 | 7775.9 | 5809.05 | 13584.95
18:30 | 8217 | 6304.115 | 14521.115
19:00 | 8658.1 | 6799.18 | 15457.28
19:30 | 8786.2 | 7092.09 | 15878.29
20:00 | 8605.4 | 7120.46 | 15725.86
20:30 | 8476.65 | 7208.04 | 15684.69 |  | Executive Engineer
21:00 | 8347.9 | 7295.62 | 15643.52 |  | Network Operation Division
21:30 | 8403.1 | 7293.845 | 15696.945
22:00 | 8458.3 | 7292.07 | 15750.37
22:30 | 8467.15 | 7290.625 | 15757.775
23:00 | 8476 | 7289.18 | 15765.18

## En-Curve
QF-LDC-12
Date | 27-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3705 | 1848.8 | 868 | 38 | 54 | 1156 | 222 | 4960 | 0 | 647 | 2239.5 | 0 | 0 | 11 | 45 | DAILY ENERGY CURVE
00:30 | 3721.5 | 1856.4 | 858 | 38 | 52 | 1152.5 | 222 | 4973.5 | 0 | 611.5 | 2003.25 | 0 | 0 | 10.5 | 42 | 27-08-2025
01:00 | 3738 | 1864 | 848 | 38 | 50 | 1149 | 222 | 4987 | 0 | 576 | 1767 | 0 | 0 | 10 | 39
01:30 | 3750 | 1868.5 | 847.5 | 38 | 49 | 1150 | 222 | 4984 | 0 | 502.5 | 1605.25 | 0 | 0 | 9.5 | 19.5 | Energy Generated | 350.5728 |  | MKWHr
02:00 | 3762 | 1873 | 847 | 38 | 48 | 1151 | 222 | 4981 | 0 | 429 | 1443.5 | 0 | 0 | 9 | 0 | Energy not Served | 0.275 |  | MKWHr
02:30 | 3757 | 1870.35 | 847.5 | 38 | 48 | 1152 | 221 | 4980.5 | 0 | 396.5 | 1277 | 0 | 0 | 10 | 0 | Total Energy Requirement | 350.8478 |  | MKWHr
03:00 | 3752 | 1867.7 | 848 | 38 | 48 | 1153 | 220 | 4980 | 0 | 364 | 1110.5 | 0 | 0 | 11 | 0
03:30 | 3751 | 1867.7 | 848 | 38 | 47 | 1148.5 | 219 | 4978.5 | 0 | 324 | 957.75 | 0 | 0 | 13.5 | 0
04:00 | 3750 | 1867.7 | 848 | 38 | 46 | 1144 | 218 | 4977 | 0 | 284 | 805 | 0 | 0 | 16 | 0
04:30 | 3708.5 | 1862.7 | 848 | 38 | 46 | 1144.5 | 218 | 4966 | 0 | 275.5 | 769.5 | 0 | 0 | 16.5 | 0
05:00 | 3667 | 1857.7 | 848 | 38 | 46 | 1145 | 218 | 4955 | 0 | 267 | 734 | 0 | 0 | 17 | 0
05:30 | 3640.5 | 1849.2 | 848 | 38 | 43 | 1149 | 218.5 | 4745 | 3.55 | 259.5 | 724.5 | 0 | 0 | 22 | 0
06:00 | 3614 | 1840.7 | 848 | 38 | 40 | 1153 | 219 | 4535 | 7.1 | 252 | 715 | 0 | 0 | 27 | 0
06:30 | 3701.5 | 1845.35 | 687 | 38 | 39 | 1151 | 219.5 | 4471 | 56.19 | 244 | 674 | 0 | 0 | 20 | 0
07:00 | 3789 | 1850 | 526 | 38 | 38 | 1149 | 220 | 4407 | 105.28 | 236 | 633 | 0 | 0 | 13 | 0
07:30 | 3777 | 1840.75 | 526 | 38 | 38 | 1154.535 | 219.5 | 4423 | 141.73 | 228 | 628.5 | 4 | 0 | 13.5 | 0
08:00 | 3765 | 1831.5 | 526 | 38 | 38 | 1160.07 | 219 | 4439 | 178.18 | 220 | 624 | 8 | 0 | 14 | 0
08:30 | 3727.5 | 1830 | 500 | 38 | 38 | 1155.48 | 219.5 | 4440 | 296.585 | 228 | 630 | 13.5 | 0 | 18.5 | 0
09:00 | 3690 | 1828.5 | 474 | 38 | 38 | 1150.89 | 220 | 4441 | 414.99 | 236 | 636 | 19 | 0 | 23 | 0
09:30 | 3612.5 | 1805.25 | 466 | 38 | 37 | 1152.42 | 220 | 4462 | 509.305 | 244.5 | 695.7 | 9.5 | 0 | 20.5 | 0
10:00 | 3535 | 1782 | 458 | 38 | 36 | 1153.95 | 220 | 4483 | 603.62 | 253 | 755.4 | 0 | 0 | 18 | 0
10:30 | 3550.5 | 1800 | 458 | 38 | 38 | 1154.235 | 220.5 | 4507 | 614.875 | 256 | 790.15 | 0 | 0 | 21 | 0
11:00 | 3566 | 1818 | 458 | 38 | 40 | 1154.52 | 221 | 4531 | 626.13 | 259 | 824.9 | 0 | 0 | 24 | 0
11:30 | 3592.5 | 1819 | 458 | 38 | 40 | 1156.095 | 221 | 4537 | 661.85 | 286 | 961.25 | 90 | 0 | 20 | 0
12:00 | 3619 | 1820 | 458 | 38 | 40 | 1157.67 | 221 | 4543 | 697.57 | 313 | 1097.6 | 180 | 0 | 16 | 0
12:30 | 3588.5 | 1829.5 | 508.5 | 38 | 42 | 1156.555 | 221.5 | 4577.5 | 676.22 | 321.5 | 1163.35 | 182 | 0 | 18.5 | 0
13:00 | 3558 | 1839 | 559 | 38 | 44 | 1155.44 | 222 | 4612 | 654.87 | 330 | 1229.1 | 184 | 0 | 21 | 0
13:30 | 3525 | 1835.9 | 701 | 38 | 43 | 1081.655 | 222 | 4543.5 | 632.775 | 340 | 1243.2 | 184 | 0 | 30 | 0
14:00 | 3492 | 1832.8 | 843 | 38 | 42 | 1007.87 | 222 | 4475 | 610.68 | 350 | 1257.3 | 184 | 0 | 39 | 0
14:30 | 3556 | 1860.4 | 843 | 38 | 42 | 987.905 | 221.5 | 4503 | 566.07 | 347 | 1292.45 | 187 | 0 | 47.5 | 0
15:00 | 3620 | 1888 | 843 | 38 | 42 | 967.94 | 221 | 4531 | 521.46 | 344 | 1327.6 | 190 | 0 | 56 | 0
15:30 | 3618.5 | 1872.65 | 843.5 | 38 | 41 | 966.5 | 220.5 | 4559.5 | 401.235 | 345.5 | 1455.05 | 194.5 | 0 | 46 | 0
16:00 | 3617 | 1857.3 | 844 | 38 | 40 | 965.06 | 220 | 4588 | 281.01 | 347 | 1582.5 | 199 | 0 | 36 | 0
16:30 | 3470 | 1816.65 | 843.5 | 38 | 38 | 966.36 | 220 | 4473.5 | 205.335 | 356 | 1609.5 | 203 | 0 | 39 | 0
17:00 | 3323 | 1776 | 843 | 38 | 36 | 967.66 | 220 | 4359 | 129.66 | 365 | 1636.5 | 207 | 0 | 42 | 0
17:30 | 3271 | 1785.9 | 842.5 | 38 | 35 | 969.655 | 219.5 | 4252.5 | 74.92 | 386.5 | 1672.91 | 166.5 | 0 | 49 | 0
18:00 | 3219 | 1795.8 | 842 | 38 | 34 | 971.65 | 219 | 4146 | 20.18 | 408 | 1709.32 | 126 | 0 | 56 | 0
18:30 | 3411 | 1848.15 | 842 | 38 | 38 | 1044.815 | 219.5 | 4360.5 | 10.09 | 528.5 | 1996.56 | 138 | 0 | 46 | 26.5
19:00 | 3603 | 1900.5 | 842 | 38 | 42 | 1117.98 | 220 | 4575 | 0 | 649 | 2283.8 | 150 | 0 | 36 | 53
19:30 | 3565 | 1894.2 | 842 | 38 | 44 | 1155.09 | 220 | 4787 | 0 | 682 | 2466 | 170 | 0 | 15 | 0
20:00 | 3525 | 1874.5 | 842 | 38 | 44 | 1152.46 | 221 | 4770 | 0 | 668 | 2366.9 | 200 | 0 | 24 | 0
20:30 | 3392 | 1895.75 | 842 | 38 | 45 | 1152.54 | 221 | 4783.5 | 0 | 667.5 | 2326.9 | 282 | 0 | 38.5 | 18
21:00 | 3259 | 1917 | 842 | 38 | 46 | 1152.62 | 221 | 4797 | 0 | 667 | 2286.9 | 364 | 0 | 53 | 36
21:30 | 3279 | 1995.2 | 842.5 | 38 | 46 | 1151.845 | 221.5 | 4801 | 0 | 660 | 2274.9 | 352.5 | 0 | 34.5 | 42.5
22:00 | 3299 | 2073.4 | 843 | 38 | 46 | 1151.07 | 222 | 4805 | 0 | 653 | 2262.9 | 341 | 0 | 16 | 49
22:30 | 3310.5 | 2094.2 | 842.5 | 38 | 45 | 1144.125 | 222 | 4818 | 0 | 628 | 2259.45 | 342 | 0 | 14 | 51
23:00 | 3322 | 2115 | 842 | 38 | 44 | 1137.18 | 222 | 4831 | 0 | 603 | 2256 | 343 | 0 | 12 | 53
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 06:00 | 371 | 12:00 | Payra | 412 | 18:00 | 408 | 02:00
Ashuganj | 406 | 07:00 | 388 | 00:00 | Rahanpur | 398 | 09:00 | 390 | 00:00
Bhulta | 400 | 06:00 | 373 | 15:00 | Rampal | 404 | 18:00 | 390 | 00:00
Bibiana | 387 | 18:00 | 377 | 15:00
BIPTC | 406 | 07:00 | 388 | 00:00
Bogura | 379 | 09:00 | 368 | 00:00
Gopalganj | 397 | 18:00 | 385 | 00:00
Kaliakoir | 373 | 18:00 | 361 | 15:00
Madunaghat | 392 | 18:00 | 387 | 13:00
Meghnaghat | 385 | 18:00 | 376 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 18:00 | 216 | 11:00 | Keranigonj | 222 | 18:00 | 215 | 11:00
AKSML | 230 | 18:00 | 224 | 11:00 | Khulna(S) | 231 | 18:00 | 218 | 00:00
Aminbazar | 225 | 17:00 | 216 | 15:00 | Madunaghat | 233 | 19:00 | 226 | 13:00
Ashuganj | 231 | 06:00 | 223 | 11:00 | Madunaghat-400 | 234 | 21:00 | 227 | 12:00
Ashuganj-400 | 231 | 06:00 | 223 | 11:00 | Maniknagar | 218 | 05:00 | 211 | 15:00
Baghabari | 233 | 05:00 | 226 | 21:00 | Meghnaghat | 226 | 18:00 | 220 | 12:00
Barapukuria | 224 | 12:00 | 216 | 00:00 | Meghnaghat-400 | 223 | 06:00 | 217 | 15:00
Barapukuria-230 | 224 | 12:00 | 216 | 00:00 | Mirsorai | 229 | 19:00 | 220 | 13:00
Barishal | 227 | 18:00 | 219 | 00:00 | Rajshahi | 230 | 06:00 | 219 | 15:00
Bheramara | 233 | 06:00 | 222 | 15:00 | Rampal | 230 | 06:00 | 218 | 00:00
Bhulta | 231 | 06:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 04:00 | 221 | 15:00 | Rampura | 230 | 06:00 | 211 | 15:00
BIPTC | 236 | 06:00 | 222 | 19:00 | Shikalbaha | 232 | 19:00 | 225 | 09:00
Bogura | 237 | 10:00 | 229 | 00:00 | Shyampur | 221 | 18:00 | 214 | 15:00
Bogura-400 | 239 | 18:00 | 229 | 00:00 | Siddhirganj | 219 | 19:00 | 214 | 12:00
Borhanuddin | 231 | 06:00 | 226 | 00:00 | Sirajgonj | 239 | 05:00 | 235 | 23:00
BSRM | 227 | 18:00 | 220 | 15:00 | Sreepur | 228 | 06:00 | 220 | 23:00
Cumilla(N) | 224 | 18:00 | 215 | 15:00 | Tongi | 226 | 19:30 | 212 | 16:00
Faridpur | 225 | 18:00 | 216 | 00:00
Fenchuganj | 229 | 06:00 | 224 | 13:00
Ghorashal | 230 | 00:00 | 220 | 14:00
Ghorashal-230 | 228 | 06:00 | 215 | 13:00
Gopalganj | 226 | 18:00 | 218 | 00:00
GPH | 228 | 00:00 | 224 | 05:00
Haripur | 220 | 06:00 | 214 | 12:00
Hasnabad | 222 | 18:00 | 214 | 15:00
Hathazari | 229 | 18:30 | 223 | 11:00
Ishurdi | 234 | 06:00 | 224 | 23:00
Jhenaidah | 231 | 06:00 | 218 | 00:00
Kaliakoir | 232 | 06:00 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 122 | 15:00 | Lalmonirhat | 128 | 10:00 | 120 | 00:00
Agargaon | 131 | 06:00 | 125 | 11:00 | Madanganj | 128 | 18:00 | 123 | 10:00
Agrabad | 131 | 18:30 | 126 | 11:00 | Madaripur | 134 | 18:00 | 128 | 00:00
AKS | 130 | 19:30 | 125 | 07:00 | Madartek | 137 | 06:00 | 124 | 15:00
Aminbazar | 138 | 20:00 | 127 | 08:00 | Madunaghat | 132 | 19:00 | 128 | 15:00
Amnura | 135 | 18:00 | 126 | 15:00 | Magura | 135 | 06:00 | 124 | 19:00
Ashuganj | 141 | 18:00 | 135 | 21:00 | Mahasthangarh | 132 | 10:00 | 123 | 01:00
Bagerhat | 132 | 18:00 | 121 | 00:00 | Maijdee | 125 | 18:00 | 114 | 15:00
Bajitpur | 130 | 06:00 | 121 | 22:00 | Manikganj | 127 | 06:00 | 120 | 16:00
Bakulia | 133 | 21:00 | 127 | 11:00 | Maniknagar | 132 | 05:00 | 125 | 16:00
Banani | 137 | 06:00 | 122 | 15:00 | Matarbari | 122 | 21:00 | 112 | 00:00
Bangabhaban | 132 | 06:00 | 126 | 13:00 | Matuail | 128 | 18:00 | 123 | 16:00
Barapukuria | 136 | 10:00 | 127 | 00:00 | Millgate | 133 | 06:00 | 124 | 15:00
Barguna | 136 | 00:00 | 130 | 23:00 | Mirpur | 130 | 06:00 | 126 | 09:00
Barishal | 133 | 07:00 | 128 | 00:00 | Mirzapur | 129 | 06:00 | 124 | 01:00
Barishal-230 | 134 | 18:00 | 127 | 00:00 | Mithapukur | 130 | 09:00 | 122 | 00:00
Baroaulia | 132 | 18:00 | 126 | 11:00 | MI_Cement | 128 | 18:00 | 123 | 11:00
Baroirhat | 128 | 18:00 | 119 | 15:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 137 | 06:00 | 122 | 15:00 | Mogbazar | 137 | 04:00 | 125 | 13:00
BashundharaCement | 128 | 18:00 | 123 | 10:00 | Mongla | 133 | 06:00 | 124 | 00:00
Beanibazar | 128 | 07:00 | 121 | 19:30 | Motijheel | 132 | 06:00 | 126 | 13:00
Benapole | 132 | 07:00 | 120 | 00:00 | Muktagacha | 131 | 17:00 | 124 | 15:00
Bhaluka | 130 | 18:00 | 120 | 23:00 | Munshiganj | 127 | 18:00 | 122 | 09:00
Bhandaria | 130 | 18:00 | 119 | 00:00 | Muradnagar | 126 | 18:00 | 117 | 22:00
Bhangura | 133 | 08:00 | 127 | 21:00 | Mymensingh | 134 | 05:00 | 110 | 22:00
Bheramara | 138 | 09:00 | 131 | 00:00 | Naogaon | 129 | 09:00 | 120 | 00:00
Bheramara(GK) | 138 | 09:00 | 131 | 00:00 | Narail | 136 | 09:00 | 124 | 00:00
Bhulta | 123 | 17:00 | 120 | 00:00 | Narinda | 132 | 05:00 | 125 | 16:00
Bog-Sherpur | 132 | 10:00 | 126 | 00:00 | Narshingdi | 137 | 18:00 | 118 | 00:00
Bogura | 134 | 10:00 | 127 | 00:00 | Natore | 133 | 09:00 | 125 | 01:00
Bogura-230 | 134 | 10:00 | 128 | 01:00 | Nawabganj | 132 | 06:00 | 127 | 11:00
Brahmanbaria | 135 | 06:00 | 127 | 23:00 | Netrakona | 122 | 05:00 | 109 | 23:00
Cantonment | 130 | 05:00 | 123 | 15:00 | New | 133 | 04:00 | 124 | 15:00
Chandina | 129 | 18:00 | 123 | 15:00 | Niamatpur | 136 | 10:00 | 131 | 23:00
Chandpur | 134 | 18:00 | 125 | 00:00 | Noapara | 135 | 18:00 | 125 | 00:00
Chandraghona | 132 | 17:00 | 129 | 15:00 | Pabna | 134 | 06:00 | 128 | 00:00
Chapai | 135 | 09:00 | 131 | 00:00 | Palashbari | 129 | 09:00 | 120 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:00 | 123 | 12:00 | Panchagarh | 135 | 18:30 | 125 | 01:00
Chauddagram | 127 | 18:00 | 12 | 07:00 | Patiya | 132 | 21:00 | 126 | 12:00
Chhatak | 128 | 06:00 | 118 | 18:30 | Patuakhali | 136 | 00:00 | 131 | 12:00
Chowmuhani | 125 | 18:00 | 112 | 15:00 | Payra | 135 | 00:00 | 133 | 03:00
Chuadanga | 137 | 07:00 | 121 | 23:00 | PHP | 127 | 18:00 | 117 | 15:00
Coxsbazar | 119 | 08:00 | 112 | 00:00 | Postogola | 133 | 05:00 | 129 | 11:00
Cumilla(N) | 129 | 18:00 | 122 | 15:00 | Purbachal | 138 | 06:00 | 122 | 15:00
Cumilla(S) | 132 | 05:00 | 121 | 15:00 | Purbasadipur | 130 | 10:00 | 122 | 19:00
Daganbhuiyan | 126 | 18:00 | 115 | 15:00 | Rahanpur | 136 | 07:00 | 132 | 00:00
Daudkandi | 123 | 18:00 | 114 | 22:00 | Rahanpur-400 | 137 | 09:00 | 133 | 00:00
Dhaka | 137 | 06:00 | 124 | 15:00 | Rahim | 127 | 04:00 | 124 | 11:00
Dhamrai | 131 | 06:00 | 124 | 15:00 | Rajbari | 132 | 18:00 | 124 | 00:00
Dhanmondi | 137 | 06:00 | 123 | 13:00 | Rajendrapur | 135 | 18:00 | 121 | 22:00
Dohazari | 129 | 20:00 | 123 | 11:00 | Rajshahi | 132 | 02:00 | 125 | 00:00
Faridpur | 132 | 06:00 | 127 | 00:00 | Rajshahi-230 | 132 | 06:00 | 126 | 00:00
Fatullah | 128 | 06:00 | 123 | 15:00 | Ramganj | 128 | 18:00 | 118 | 00:00
Fenchuganj | 135 | 06:00 | 131 | 13:00 | Rampur | 131 | 19:30 | 126 | 10:00
Feni | 125 | 18:00 | 116 | 15:00 | Rampura | 137 | 06:00 | 123 | 15:00
Ghatail | 130 | 06:00 | 120 | 02:00 | Rangamati | 131 | 18:00 | 128 | 12:00
Ghorashal | 137 | 18:30 | 130 | 14:00 | Rangpur | 131 | 10:00 | 123 | 00:00
Goalpara | 138 | 18:00 | 127 | 00:00 | Ruppur | 137 | 05:00 | 131 | 00:00
Gollamari | 137 | 06:00 | 128 | 00:00 | Saidpur | 130 | 09:00 | 122 | 19:00
Gopalganj | 134 | 06:00 | 126 | 00:00 | Satkhira | 135 | 18:00 | 122 | 00:00
Gopalganj-400 | 136 | 18:00 | 130 | 00:00 | Satmasjid | 130 | 06:00 | 124 | 13:00
Gulshan | 137 | 06:00 | 124 | 13:00 | Savar | 132 | 18:00 | 125 | 08:00
Halishahar | 133 | 21:00 | 126 | 11:00 | SevenRings | 137 | 18:00 | 131 | 11:00
Haripur | 128 | 06:00 | 125 | 09:00 | ShahCement | 129 | 18:00 | 123 | 12:00
HaripurSBU | 128 | 06:00 | 125 | 09:00 | Shahjadpur | 137 | 04:00 | 132 | 00:00
Hasnabad | 132 | 02:00 | 128 | 15:00 | Shahjibazar | 135 | 18:00 | 127 | 22:00
Hathazari | 134 | 18:00 | 129 | 09:00 | Shahmirpur | 133 | 21:00 | 128 | 11:00
Ishurdi | 138 | 06:00 | 131 | 00:00 | Shariatpur | 132 | 06:00 | 124 | 00:00
Jaldhaka | 129 | 10:00 | 119 | 00:00 | Sherpur | 134 | 06:00 | 118 | 01:00
Jamalpur | 137 | 05:00 | 125 | 01:00 | Shikalbaha | 122 | 19:00 | 118 | 10:00
Jashore | 135 | 06:00 | 124 | 00:00 | Shikalbaha-230 | 134 | 19:00 | 129 | 09:00
Jhenaidah | 136 | 05:00 | 120 | 15:00 | Shitalakhya | 128 | 18:00 | 123 | 11:00
Jhenaidah-230 | 138 | 06:00 | 128 | 00:00 | Sholosohor | 132 | 18:00 | 128 | 10:00
Joydebpur | 140 | 18:00 | 126 | 10:00 | Shyampur | 129 | 18:00 | 124 | 11:00
Joypurhat | 127 | 09:00 | 117 | 00:00 | Shyampur-230 | 129 | 18:00 | 124 | 11:00
Juldah | 133 | 19:30 | 128 | 12:00 | Siddhirganj | 128 | 06:00 | 124 | 15:00
Kabirpur | 131 | 00:00 | 121 | 15:00 | Sirajganj | 130 | 10:00 | 124 | 00:00
Kachua | 132 | 18:00 | 123 | 22:00 | Sonargaon | 125 | 22:00 | 120 | 15:00
Kaliakoir | 134 | 18:00 | 128 | 11:00 | Sreemongol | 133 | 05:00 | 126 | 22:00
Kallyanpur | 132 | 18:00 | 127 | 08:00 | Sreepur | 132 | 06:00 | 125 | 23:00
Kalurghat | 132 | 18:00 | 128 | 11:00 | Srinagar | 132 | 06:00 | 126 | 15:00
Kamrangirchar | 132 | 05:00 | 126 | 13:00 | SSM | 134 | 22:00 | 130 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 07:00 | 116 | 00:00
Kasba | 125 | 18:00 | 117 | 22:00 | Sylhet | 129 | 07:00 | 123 | 19:00
Kazla | 131 | 08:00 | 126 | 13:00 | Sylhet-132 | 128 | 06:00 | 124 | 15:00
Keranigonj | 133 | 06:00 | 127 | 12:00 | Tangail | 128 | 06:00 | 121 | 01:00
Khagrachori | 130 | 06:00 | 127 | 12:00 | Taraganj | 130 | 10:00 | 121 | 01:00
Khulna | 136 | 06:00 | 127 | 00:00 | Thakurgaon | 133 | 18:30 | 124 | 19:00
Khulna(S) | 138 | 18:00 | 128 | 00:00 | TK | 132 | 19:00 | 128 | 10:00
Khulshi | 130 | 18:00 | 125 | 11:00 | Tongi | 132 | 18:30 | 128 | 11:00
Kishoreganj | 129 | 18:00 | 119 | 23:00 | Ullahpara | 132 | 10:00 | 127 | 00:00
Kodda | 132 | 19:00 | 124 | 14:00 | Ullon | 137 | 06:00 | 122 | 15:00
KSRM | 132 | 18:00 | 127 | 11:00 | Uttara | 130 | 02:00 | 124 | 11:00
Kulaura | 134 | 06:00 | 129 | 15:00 | UttaraNew | 130 | 02:00 | 124 | 11:00
Kurigram | 130 | 01:00 | 116 | 19:00 | Zigatola | 132 | 06:00 | 126 | 16:00
Kushtia | 135 | 09:00 | 123 | 15:00
Laksam | 131 | 18:00 | 122 | 00:00
Lakshmipur | 126 | 18:00 | 114 | 23:00
Lalbag | 132 | 06:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division