## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-08-2025 | during | 29-08-2025 | during | 29-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 346 | 316 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 286 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 49.2 | 47.8 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 119 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 36 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21.2 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 105 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 130 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 102 | 142 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 300 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 115 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2350.2 | 2766 | 5808.84 | 5780.84 | 4394.17 | 4366.17
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 48 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 219 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 15 | 43 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 22 | 68 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 20 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 33 | 97 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.23 | 0 | 3.85 | 0 | 3.85 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 15 | 45 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 90 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1050 | 1065 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 16 | 17 | 20 | 9 | 20 | 9 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 635 | 630 | 635 | 635 | 660 | 660 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2326.23 | 2684 | 3704.57 | 3696.72 | 3523.57 | 3541.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 185 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 40 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 46.7 | 46.7 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 44 | 55 | 55 | 42 | 42 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 150 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 66 | 120 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 37 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 115 | 160 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 98 | 114 | 114 | 102.6 | 102.6 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 56 | 46 | 113 | 113 | 50 | 64 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 84 | 79 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 13 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1411 | 1866 | 2440.86 | 2370.86 | 2202.26 | 2146.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-08-2025 | during | 29-08-2025 | during | 29-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 68 | 73 | 157.5 | 157.5 | 103 | 103 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 76 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 81 | 110 | 108 | 108 | 108 | 108 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 26.1 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 6 | 12 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 239.1 | 288 | 440.2 | 417 | 332.2 | 315
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 70 | 70 | 70 | 70 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 81 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 103 | 103 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 16 | 16 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 14 | 14 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 355 | 385 | 385 | 372 | 372 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1155 | 1119 | 1218 | 1218 | 1130 | 1130
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 866 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 190 | 222 | 410 | 410 | 226 | 226 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 15 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 962 | 1047 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2141 | 2213 | 3622.2 | 3552.2 | 2664 | 2594
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 299 | 301 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1070 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 268 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1854.69 | 1934 | 2162 | 2161 | 2097 | 2096
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 23.54 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 140 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 160 | 160 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 330 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.15 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1153 | 1142.45 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.7 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2071.39 | 2220.45 | 3158.47 | 2991.87 | 2995.8 | 2829.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 148 | 147 | 150 | 150 | 150 | 150 | Machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 4 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 105 | 0 | 117.5 | 0 | 117.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 316 | 416 | 616.1 | 462 | 582.1 | 428
System Total |  |  |  |  | 28823.2 | 27829.875 | 13864.61 | 15506.45 | 23171.24 | 22650.49 | 19921.1 | 19446.35
Forecast Scenario (29-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14870 |  | 0 |  | 14870
|  |  |  | 1:00 | 14350 |  | 0 |  | 14350
|  |  |  | 2:00 | 14130 |  | 0 |  | 14130
|  |  |  | 3:00 | 13840 |  | 0 |  | 13840
|  |  |  | 4:00 | 13530 |  | 0 |  | 13530
|  |  |  | 5:00 | 13260 |  | 0 |  | 13260
|  |  |  | 6:00 | 12310 |  | 0 |  | 12310
|  |  |  | 7:00 | 12110 |  | 0 |  | 12110
|  |  |  | 8:00 | 11980 |  | 0 |  | 11980
|  |  |  | 9:00 | 11470 |  | 0 |  | 11470
|  |  |  | 10:00 | 11480 |  | 0 |  | 11480
|  |  |  | 11:00 | 11880 |  | 0 |  | 11880
|  |  |  | 12:00 | 12460 |  | 0 |  | 12460
|  |  |  | 13:00 | 12980 |  | 0 |  | 12980
|  |  |  | 14:00 | 12520 |  | 0 |  | 12520
|  |  |  | 15:00 | 12800 |  | 0 |  | 12800
|  |  |  | 16:00 | 12280 |  | 0 |  | 12280
|  |  |  | 17:00 | 12170 |  | 0 |  | 12170
|  |  |  | 18:00 | 11550 |  | 0 |  | 11550
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13460 |  | 0 |  | 13460
|  |  |  | 19:30 | 14400 |  | 0 |  | 14400
|  |  |  | 20:00 | 14570 |  | 0 |  | 14570
|  |  |  | 21:00 | 14790 |  | 0 |  | 14790
|  |  |  | 22:00 | 14810 |  | 0 |  | 14810
|  |  |  | 23:00 | 14910 |  | 0 |  | 14910
Probable Maximum Temperature: |  |  | 31.20°C
Probable Maximum Demand at Day Peak: |  |  | 12460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14790.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14790.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 314.51 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:40 hrs on 29-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-08-2025 | [28 empty] | Date: | 28-08-2025 | [28 empty] | Date: | 28-08-2025 | [28 empty] | Date: | 28-08-2025 | [28 empty] | Date: | 28-08-2025 | [14 empty] | Date: | 28-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 77 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 47 | 17 | 132 | 46 | 295 | 15 | 55 | 150 | 0 | 300 | 283 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 108 | 23 | 23 | 0 | 365 | 0 | 0 | 50 | 0 | 22 | 66 | 68 | 0 | 12 | 12 | 0 | 222 | 82 | 38 | 635 | 46 | 0 | 24 | 17 | 97 | 211 | 0 | 0 | 0 | 1131 | 0 | 51 | 108 | 172 | 0 | 352 | 0 | 43 | 190 | 37 | 102 | 70 | 176 | 55 | 19 | 97 | 48 | 43 | 0 | 37 | 310 | 0 | 360 | 0 | 70 | 155 | 8 | 0 | 84 | 30 | 0 | 16 | 101 | 17 | 108 | 76 | 98 | 0 | 0 | 12 | 8460 | 843 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 188 | 0 | 0 | 0 | 1174 | 17 | 1148.97 | 0 | 41 | 0 | 50 | 67 | 0 | 86 | 0 | 24 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 399 | 0 | 0 | 146 | 48 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 299 | 1225 | 0 | 7281.97 | 15741.97 | 107.92
01:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 43.8 | 0 | 133 | 30 | 245 | 0 | 55 | 140 | 0 | 300 | 283 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 363 | 0 | 0 | 0 | 0 | 15 | 66 | 68 | 0 | 12 | 12 | 0 | 222 | 110 | 38 | 635 | 0 | 0 | 33 | 17 | 88 | 221 | 0 | 0 | 0 | 1127 | 0 | 51 | 108 | 172 | 0 | 354 | 0 | 44 | 188 | 37 | 90 | 70 | 164 | 49 | 19 | 97 | 46 | 43 | 0 | 37 | 300 | 0 | 359 | 0 | 70 | 149 | 8 | 0 | 84 | 30 | 0 | 16 | 104 | 0 | 91 | 56 | 98 | 0 | 0 | 12 | 8170.8 | 843 | 195 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 14 | 1152.57 | 0 | 41 | 0 | 0 | 35 | 0 | 86 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 395 | 0 | 0 | 148 | 48 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 299 | 1222 | 38 | 7008.57 | 15179.37 | 107.92
02:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 44.5 | 0 | 149 | 30 | 95 | 0 | 55 | 143 | 0 | 300 | 285 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 24 | 22 | 0 | 365 | 0 | 0 | 0 | 0 | 15 | 66 | 40 | 0 | 12 | 12 | 0 | 222 | 101 | 38 | 635 | 0 | 0 | 19 | 17 | 92 | 221 | 0 | 0 | 0 | 1127 | 0 | 51 | 50 | 172 | 0 | 354 | 0 | 44 | 190 | 37 | 90 | 70 | 164 | 56 | 18 | 97 | 44 | 16 | 0 | 37 | 300 | 0 | 359 | 0 | 70 | 150 | 8 | 0 | 84 | 30 | 0 | 16 | 105 | 0 | 91 | 56 | 103 | 0 | 0 | 12 | 7907.5 | 843 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 1148.12 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 397 | 0 | 0 | 149 | 47 | 50 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 299 | 1120 | 45 | 6727.12 | 14634.62 | 107.92
03:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 44 | 0 | 149 | 30 | 0 | 0 | 51 | 141 | 0 | 300 | 283 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 25.5 | 22 | 0 | 362 | 0 | 0 | 0 | 0 | 20 | 49 | 0 | 0 | 12 | 12 | 0 | 220 | 98 | 39 | 635 | 0 | 0 | 0 | 17 | 90 | 221 | 0 | 0 | 0 | 1137 | 0 | 51 | 10 | 172 | 0 | 355 | 0 | 44 | 189 | 37 | 99 | 70 | 165 | 56 | 19 | 97 | 42 | 16 | 0 | 37 | 305 | 0 | 366 | 0 | 70 | 150 | 8 | 0 | 84 | 30 | 0 | 16 | 104 | 0 | 91 | 57 | 103 | 0 | 0 | 1 | 7692.5 | 843 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 0 | 1157.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 398 | 0 | 0 | 147 | 45 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 299 | 1105 | 15 | 6582.53 | 14275.03 | 107.92
04:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 44 | 0 | 104 | 30 | 0 | 0 | 55 | 144 | 0 | 300 | 284 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 26 | 22 | 0 | 362 | 0 | 0 | 0 | 0 | 32 | 33 | 0 | 0 | 12 | 12 | 0 | 219 | 40 | 39 | 635 | 0 | 0 | 0 | 0 | 93 | 221 | 0 | 0 | 0 | 1149 | 0 | 51 | 0 | 180 | 0 | 354 | 0 | 45 | 190 | 34 | 80 | 50 | 166 | 56 | 19 | 30 | 42 | 16 | 0 | 37 | 305 | 0 | 333 | 0 | 70 | 142 | 8 | 0 | 84 | 30 | 0 | 16 | 104 | 0 | 91 | 57 | 103 | 0 | 0 | 0 | 7388 | 843 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 0 | 1150.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 338 | 0 | 0 | 152 | 46 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 299 | 1100 | 0 | 6459.97 | 13847.97 | 107.92
05:00 | 0 | 86 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 34 | 0 | 77 | 30 | 0 | 0 | 55 | 17 | 0 | 300 | 299 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 70 | 26 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 12 | 0 | 218 | 0 | 40 | 635 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 182 | 0 | 350 | 0 | 45 | 199 | 34 | 83 | 50 | 170 | 56 | 19 | 16 | 40 | 0 | 0 | 37 | 310 | 0 | 335 | 0 | 70 | 142 | 8 | 0 | 84 | 30 | 0 | 16 | 103 | 0 | 91 | 57 | 103 | 0 | 0 | 0 | 6992 | 857 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 1154.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 140 | 0 | 368 | 0 | 0 | 151 | 46 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 299 | 1100 | 0 | 6489.22 | 13481.22 | 107.92
06:00 | 0 | 86 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 77 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 70 | 26 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.08 | 218 | 0 | 40 | 635 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1085 | 0 | 51 | 0 | 182 | 0 | 349 | 0 | 45 | 201 | 34 | 82 | 50 | 100 | 57 | 19 | 0 | 36 | 0 | 0 | 37 | 315 | 0 | 336 | 0 | 70 | 141 | 8 | 0 | 84 | 30 | 0 | 16 | 103 | 0 | 91 | 57 | 103 | 0 | 0.19 | 0 | 6704.27 | 865 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1176 | 0 | 1169.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 0.1 | 160 | 0 | 140 | 0 | 140 | 0 | 367 | 0 | 0.01 | 150 | 47 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 3 | 0.01 | 0 | 194 | 115 | 220 | 0 | 300 | 1100 | 0 | 6427.4 | 13131.67 | 107.92
07:00 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 77 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 290 | 0 | 0 | 0 | 300 | 0 | 0 | 6 | 70 | 24.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.45 | 218 | 0 | 37 | 635 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1040 | 2 | 51 | 0 | 182 | 0 | 356 | 18 | 45 | 195 | 34 | 85 | 70 | 100 | 57 | 19 | 0 | 36 | 0 | 14 | 37 | 310 | 0 | 384 | 0 | 70 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 103 | 0 | 91 | 57 | 96 | 0 | 3.07 | 0 | 6774.02 | 866 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 1063 | 0 | 1152.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.52 | 17 | 0 | 0 | 8.12 | 160 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 0.73 | 148 | 46 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 13 | 0.03 | 0 | 169 | 115 | 220 | 0 | 300 | 1096 | 0 | 6346.28 | 13120.3 | 107.92
08:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 77 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 52 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.14 | 219 | 0 | 17 | 635 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 1004 | 9 | 51 | 0 | 185 | 0 | 325 | 51 | 45 | 197 | 34 | 68 | 70 | 51 | 57 | 19 | 0 | 32 | 0 | 12 | 37 | 300 | 0 | 346 | 0 | 70 | 148 | 8 | 0 | 82 | 30 | 0 | 16 | 103 | 0 | 91 | 56 | 67 | 1 | 10.26 | 0 | 6523.4 | 866 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 994 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.21 | 47 | 0 | 0 | 25.52 | 160 | 0 | 140 | 0 | 140 | 0 | 357 | 0 | 2.54 | 146 | 44 | 0 | 5 | 0 | 0 | 0 | 0 | 2.3 | 55 | 0.08 | 0 | 169 | 100 | 180 | 0 | 301 | 1110 | 0 | 6336.65 | 12860.05 | 107.92
09:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 10 | 0 | 77 | 30 | 0 | 0 | 13 | 40 | 0 | 300 | 288 | 0 | 0 | 0 | 280 | 0 | 0 | 18 | 70 | 21.5 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 1.9 | 220 | 0 | 12 | 635 | 0 | 0 | 1 | 0 | 0 | 198 | 0 | 0 | 0 | 998 | 12 | 51 | 0 | 185 | 0 | 349 | 80 | 45 | 189 | 37 | 70 | 70 | 50 | 57 | 19 | 0 | 28 | 0 | 29 | 37 | 315 | 0 | 312 | 0 | 70 | 150 | 8 | 0 | 82 | 30 | 0 | 16 | 103 | 0 | 91 | 56 | 68 | 1 | 16.06 | 0 | 6668.46 | 866 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 932 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.72 | 55 | 0 | 0 | 30.67 | 160 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 1.58 | 147 | 47 | 0 | 18 | 0 | 0 | 0 | 0 | 2.9 | 117 | 0.2 | 0 | 167 | 115 | 220 | 0 | 299 | 1108 | 0 | 6414.07 | 13082.53 | 107.92
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 15 | 0 | 77 | 30 | 0 | 0 | 54 | 60 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 22 | 70 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 2.45 | 220 | 0 | 12 | 635 | 0 | 0 | 22 | 0 | 0 | 218 | 0 | 0 | 0 | 1007 | 7 | 51 | 0 | 185 | 0 | 347 | 44 | 42 | 200 | 39 | 76 | 70 | 73 | 57 | 19 | 0 | 30 | 0 | 43 | 37 | 310 | 0 | 330 | 0 | 70 | 139 | 0 | 0 | 81 | 30 | 0 | 16 | 103 | 0 | 91 | 56 | 68 | 1 | 17.37 | 6 | 6810.82 | 866 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 983 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.71 | 58 | 0 | 0 | 23.48 | 160 | 0 | 140 | 0 | 140 | 0 | 362 | 0 | 1.72 | 146 | 49 | 0 | 22 | 0 | 0 | 0 | 0 | 3.8 | 64 | 0.83 | 0 | 170 | 115 | 220 | 0 | 299 | 1110 | 0 | 6395.54 | 13206.36 | 107.92
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 35 | 8 | 82 | 30 | 35 | 0 | 38 | 100 | 0 | 300 | 291 | 0 | 0 | 17 | 280 | 0 | 0 | 35 | 70 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 12 | 3.64 | 221 | 0 | 12 | 635 | 0 | 0 | 32 | 1 | 0 | 217 | 0 | 0 | 0 | 1034 | 4 | 51 | 4 | 185 | 0 | 348 | 22 | 40 | 196 | 40 | 83 | 70 | 90 | 56 | 12 | 4 | 30 | 0 | 11 | 37 | 310 | 0 | 334 | 0 | 70 | 142 | 6 | 0 | 83 | 30 | 0 | 16 | 103 | 0 | 81 | 56 | 68 | 2 | 20.48 | 6 | 6959.12 | 867 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 978 | 0 | 1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.31 | 80 | 0 | 0 | 53.57 | 140 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 1.88 | 147 | 50 | 0 | 36 | 0 | 0 | 0 | 0 | 5.6 | 205 | 0.83 | 0 | 169 | 115 | 220 | 0 | 299 | 1050 | 0 | 6516.19 | 13475.31 | 107.92
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 49.2 | 17 | 130 | 30 | 105 | 0 | 36 | 102 | 0 | 300 | 300 | 0 | 0 | 17 | 327 | 0 | 0 | 34 | 70 | 20 | 22 | 0 | 350 | 0 | 0 | 33 | 0 | 16 | 0 | 22 | 0 | 12 | 12 | 4.23 | 222 | 15 | 12 | 635 | 0 | 0 | 48 | 8 | 15 | 216 | 0 | 0 | 0 | 1050 | 6 | 51 | 66 | 185 | 0 | 341 | 40 | 40 | 202 | 40 | 84 | 50 | 115 | 56 | 12 | 32 | 32 | 16 | 13 | 36 | 315 | 0 | 385 | 0 | 70 | 148 | 6 | 0 | 82 | 30 | 0 | 16 | 103 | 0 | 81 | 56 | 68 | 2 | 26.1 | 6 | 7481.53 | 866 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 962 | 0 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.54 | 92 | 0 | 0 | 7.7 | 140 | 0 | 140 | 0 | 140 | 0 | 374 | 0 | 1.15 | 148 | 51 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 105 | 0.69 | 0 | 170 | 115 | 220 | 0 | 299 | 1050 | 0 | 6383.08 | 13864.61 | 107.92
13:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 46 | 17 | 133 | 30 | 145 | 0 | 36 | 142 | 0 | 300 | 274 | 0 | 0 | 17 | 331 | 0 | 0 | 23 | 70 | 20 | 22 | 0 | 350 | 0 | 0 | 40 | 0 | 26 | 33 | 37 | 0 | 12 | 12 | 3.29 | 222 | 15 | 21 | 631 | 0 | 0 | 50 | 8 | 15 | 216 | 0 | 0 | 0 | 1024 | 11 | 51 | 100 | 184 | 0 | 346 | 77 | 42 | 199 | 40 | 82 | 50 | 132 | 56 | 12 | 30 | 34 | 16 | 7 | 36 | 305 | 0 | 360 | 0 | 70 | 159 | 8 | 0 | 83 | 30 | 0 | 16 | 103 | 0 | 99 | 56 | 70 | 3 | 16.5 | 4 | 7691.79 | 866 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 97 | 946 | 0 | 1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.66 | 77 | 0 | 0 | 35.97 | 140 | 0 | 140 | 0 | 140 | 0 | 337 | 0 | 3.57 | 145 | 51 | 0 | 15 | 0 | 0 | 0 | 0 | 6.4 | 210 | 0.32 | 0 | 167 | 115 | 220 | 0 | 301 | 1090 | 0 | 6545.92 | 14237.71 | 107.92
14:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 44.5 | 17 | 133 | 30 | 145 | 0 | 36 | 143 | 0 | 300 | 297 | 0 | 0 | 17 | 328 | 0 | 0 | 30 | 70 | 21.2 | 22 | 0 | 300 | 0 | 0 | 46 | 0 | 10 | 33 | 37 | 0 | 12 | 12 | 0.72 | 222 | 15 | 18 | 635 | 0 | 0 | 50 | 8 | 15 | 216 | 0 | 0 | 0 | 1033 | 15 | 51 | 100 | 185 | 0 | 310 | 92 | 42 | 196 | 37 | 80 | 50 | 139 | 48 | 12 | 32 | 34 | 16 | 23 | 36 | 305 | 0 | 360 | 0 | 70 | 151 | 8 | 0 | 83 | 30 | 0 | 16 | 103 | 0 | 99 | 56 | 70 | 1 | 24.39 | 3 | 7648.81 | 874 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 942 | 0 | 1146.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.4 | 37 | 0 | 0 | 5.91 | 140 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 1.3 | 145 | 50 | 0 | 25 | 0 | 0 | 0 | 0 | 4.8 | 127 | 0.2 | 0 | 169 | 115 | 220 | 0 | 301 | 1050 | 0 | 6346.26 | 13995.07 | 107.92
15:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 48.8 | 17 | 141 | 30 | 145 | 0 | 28 | 155 | 0 | 300 | 300 | 0 | 0 | 17 | 331 | 0 | 0 | 18 | 70 | 20.2 | 15 | 0 | 320 | 0 | 0 | 44 | 0 | 14 | 33 | 37 | 0 | 12 | 12 | 1.45 | 222 | 15 | 10 | 635 | 0 | 0 | 50 | 8 | 16 | 217 | 0 | 0 | 0 | 1047 | 13 | 51 | 100 | 185 | 0 | 340 | 147 | 42 | 205 | 37 | 87 | 70 | 148 | 49 | 12 | 33 | 38 | 16 | 13 | 36 | 315 | 0 | 365 | 0 | 70 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 0 | 99 | 56 | 70 | 1 | 20.7 | 6 | 7816.15 | 874 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 889 | 0 | 1149.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.02 | 12 | 0 | 0 | 14.35 | 140 | 0 | 140 | 0 | 140 | 0 | 377 | 0 | 2.15 | 144 | 50 | 0 | 25 | 0 | 0 | 0 | 0 | 3.1 | 66 | 0.09 | 0 | 171 | 115 | 220 | 0 | 301 | 1051 | 0 | 6268.39 | 14084.54 | 107.92
16:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 47 | 17 | 149 | 30 | 95 | 0 | 17 | 151 | 0 | 300 | 290 | 0 | 0 | 17 | 334 | 0 | 0 | 9 | 70 | 20 | 18 | 0 | 320 | 0 | 0 | 47 | 0 | 15 | 33 | 37 | 0 | 12 | 12 | 1.18 | 222 | 15 | 13 | 635 | 0 | 0 | 50 | 8 | 15 | 217 | 0 | 0 | 0 | 1043 | 6 | 51 | 100 | 185 | 0 | 348 | 210 | 42 | 195 | 37 | 82 | 70 | 143 | 51 | 19 | 29 | 36 | 16 | 17 | 36 | 305 | 0 | 371 | 0 | 70 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 0 | 99 | 57 | 70 | 0 | 14.57 | 6 | 7776.75 | 879 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32.68 | 850 | 0 | 1140.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.37 | 26 | 0 | 0 | 12.18 | 140 | 0 | 140 | 0 | 140 | 0 | 405 | 0 | 1.63 | 144 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 4.1 | 54 | 0.08 | 0 | 167 | 115 | 220 | 0 | 301 | 963 | 0 | 6079.83 | 13856.58 | 107.92
17:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 44.5 | 17 | 149 | 30 | 45 | 0 | 17 | 144 | 0 | 300 | 287 | 0 | 0 | 17 | 300 | 0 | 0 | 9 | 70 | 20 | 22 | 0 | 300 | 0 | 0 | 45 | 0 | 14 | 33 | 37 | 0 | 25 | 12 | 0.45 | 220 | 14 | 14 | 590 | 0 | 0 | 50 | 8 | 15 | 217 | 0 | 0 | 0 | 1020 | 1 | 51 | 100 | 185 | 0 | 300 | 300 | 42 | 190 | 40 | 81 | 70 | 138 | 60 | 19 | 27 | 30 | 16 | 9 | 36 | 310 | 0 | 361 | 0 | 70 | 140 | 8 | 0 | 83 | 30 | 0 | 16 | 103 | 0 | 107 | 57 | 71 | 0 | 1.33 | 6 | 7593.28 | 886 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.5 | 835 | 0 | 1150.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 6.23 | 27 | 0 | 0 | 10.06 | 140 | 0 | 140 | 0 | 140 | 0 | 395 | 0 | 0.99 | 144 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 1.4 | 23 | 0.12 | 0 | 166 | 100 | 180 | 0 | 301 | 942 | 0 | 5933.2 | 13526.48 | 107.93
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 43.8 | 17 | 140 | 30 | 15 | 0 | 35 | 140 | 0 | 300 | 290 | 0 | 0 | 17 | 250 | 0 | 0 | 1 | 70 | 20 | 22 | 0 | 320 | 0 | 0 | 44 | 0 | 35 | 34 | 51 | 0 | 25 | 12 | 0 | 220 | 14 | 18 | 635 | 0 | 0 | 50 | 8 | 15 | 217 | 0 | 0 | 0 | 1013 | 0 | 51 | 100 | 137 | 0 | 270 | 280 | 31 | 141 | 40 | 79 | 70 | 134 | 54 | 19 | 27 | 36 | 16 | 1 | 37 | 300 | 0 | 372 | 0 | 70 | 135 | 8 | 0 | 42 | 30 | 0 | 16 | 103 | 0 | 110 | 75 | 73 | 0 | 1.02 | 6 | 7428.82 | 890 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 806 | 0 | 1064.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 1.81 | 2 | 0 | 0 | 1.39 | 140 | 0 | 140 | 0 | 140 | 0 | 345 | 0 | 0.12 | 144 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.01 | 0 | 168 | 100 | 180 | 0 | 301 | 848 | 0 | 5607.06 | 13035.88 | 107.93
19:00 | 14 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 47.8 | 20 | 141 | 80 | 195 | 18 | 55 | 153 | 0 | 300 | 285 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 21.2 | 22 | 0 | 300 | 0 | 0 | 50 | 0 | 18 | 66 | 57 | 0 | 25 | 12 | 0 | 220 | 23 | 19 | 630 | 74 | 0 | 50 | 10 | 27 | 218 | 0 | 0 | 0 | 1057 | 0 | 51 | 113 | 147 | 0 | 352 | 320 | 27 | 186 | 40 | 84 | 70 | 162 | 53 | 19 | 99 | 42 | 35 | 0 | 37 | 315 | 0 | 350 | 0 | 70 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 3 | 110 | 75 | 73 | 0 | 0 | 12 | 8354 | 891 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 10 | 1143.09 | 0 | 0 | 0 | 60 | 35 | 0 | 96 | 37 | 25 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 391 | 0 | 0 | 147 | 50 | 109 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 115 | 220 | 0 | 301 | 935 | 0 | 6639.09 | 14993.09 | 107.93
19:30 | 16 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 47.8 | 35 | 149 | 119 | 294 | 55 | 55 | 142 | 0 | 300 | 286 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 115 | 21.2 | 15 | 0 | 300 | 0 | 0 | 97 | 0 | 17 | 66 | 68 | 0 | 25 | 12 | 0 | 220 | 45 | 20 | 630 | 90 | 0 | 50 | 17 | 43 | 219 | 0 | 0 | 0 | 1065 | 0 | 51 | 120 | 150 | 0 | 352 | 330 | 44 | 185 | 40 | 79 | 70 | 160 | 46 | 19 | 98 | 42 | 43 | 0 | 37 | 305 | 0 | 355 | 0 | 70 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 17 | 110 | 76 | 73 | 0 | 0 | 12 | 8723 | 891 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 15 | 1142.45 | 0 | 0 | 0 | 100 | 50 | 0 | 96 | 37 | 25 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 330 | 0 | 0 | 147 | 50 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 180 | 0 | 301 | 1070 | 0 | 6783.45 | 15506.45
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 43.1 | 35 | 149 | 122 | 294 | 38 | 55 | 140 | 0 | 300 | 286 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 125 | 21.2 | 15 | 0 | 300 | 0 | 0 | 93 | 0 | 10 | 66 | 70 | 0 | 25 | 12 | 0 | 219 | 25 | 21 | 630 | 45 | 0 | 50 | 17 | 17 | 221 | 0 | 0 | 0 | 1085 | 0 | 51 | 120 | 156 | 0 | 352 | 330 | 43 | 188 | 40 | 80 | 70 | 173 | 48 | 19 | 97 | 42 | 43 | 0 | 31 | 305 | 0 | 350 | 0 | 70 | 148 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 17 | 110 | 76 | 73 | 0 | 0 | 12 | 8611.3 | 823 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 17 | 1146.96 | 0 | 0 | 0 | 0 | 50 | 0 | 96 | 39 | 0 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 336 | 0 | 0 | 149 | 50 | 115 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 180 | 0 | 307 | 1074 | 0 | 6667.96 | 15279.26 | 107.93
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 43.4 | 19 | 149 | 92 | 195 | 15 | 55 | 143 | 0 | 300 | 281 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 125 | 21.8 | 15 | 0 | 280 | 0 | 0 | 102 | 0 | 12 | 66 | 70 | 0 | 25 | 12 | 0 | 219 | 14 | 24 | 630 | 45 | 0 | 50 | 17 | 15 | 221 | 0 | 0 | 0 | 1088 | 0 | 43 | 132 | 92 | 0 | 355 | 330 | 44 | 187 | 41 | 78 | 70 | 200 | 53 | 19 | 97 | 44 | 43 | 0 | 37 | 305 | 0 | 371 | 0 | 70 | 149 | 8 | 0 | 83 | 30 | 0 | 16 | 103 | 17 | 110 | 76 | 73 | 0 | 0 | 12 | 8446.2 | 823 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1145.09 | 0 | 0 | 0 | 0 | 35 | 0 | 96 | 39 | 0 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 333 | 0 | 0 | 150 | 50 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 180 | 0 | 302 | 1081 | 0 | 6798.29 | 15244.49 | 107.93
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 45.5 | 17 | 149 | 92 | 45 | 0 | 55 | 147 | 0 | 300 | 300 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 21.8 | 14 | 0 | 302 | 0 | 0 | 85 | 0 | 6 | 66 | 70 | 0 | 25 | 12 | 0 | 220 | 0 | 28 | 631 | 16 | 0 | 50 | 8 | 0 | 222 | 0 | 0 | 0 | 1134 | 0 | 43 | 135 | 95 | 0 | 349 | 330 | 44 | 179 | 41 | 82 | 70 | 200 | 54 | 19 | 97 | 44 | 43 | 0 | 37 | 310 | 0 | 385 | 0 | 60 | 156 | 8 | 0 | 81 | 30 | 0 | 16 | 103 | 0 | 110 | 77 | 73 | 0 | 0 | 12 | 8283.3 | 824 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1141.84 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 39 | 0 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 366 | 0 | 0 | 151 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 302 | 1090 | 0 | 6836.04 | 15119.34 | 107.93
23:00 | 0 | 102 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 51.1 | 17 | 149 | 92 | 45 | 0 | 55 | 160 | 0 | 300 | 306 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 21.8 | 22 | 0 | 308 | 0 | 0 | 50 | 0 | 19 | 66 | 70 | 0 | 25 | 12 | 0 | 222 | 0 | 31 | 631 | 17 | 0 | 50 | 8 | 0 | 221 | 0 | 0 | 0 | 1156 | 0 | 51 | 125 | 86 | 0 | 348 | 330 | 44 | 159 | 41 | 90 | 50 | 200 | 53 | 19 | 98 | 44 | 43 | 0 | 37 | 320 | 0 | 395 | 0 | 60 | 161 | 8 | 0 | 81 | 30 | 0 | 16 | 105 | 0 | 111 | 77 | 73 | 0 | 0 | 12 | 8321.9 | 895 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1142.63 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 142 | 0 | 140 | 0 | 140 | 0 | 407 | 0 | 0 | 152 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 302 | 1098 | 0 | 6920.83 | 15242.73 | 107.93
Total KWH | 22032 | 2169600 | 551520 | 0 | 0 | 0 | 0 | 0 | 8078400 | 0 | 0 | 877320 | 252000 | 2968992 | 1088160 | 2132727 | 106238 | 932246 | 2704320 | 0 | 7578000 | 7017425 | 0 | 0 | 441492 | 7568049 | 0 | 0 | 190193 | 2108400 | 534600 | 495360 | 0 | 8228181.82 | 0 | 0 | 734400 | 0 | 411360 | 797654 | 752688 | 0 | 330240 | 261120 | 18480 | 5333271 | 642324 | 613440 | 15243636.36 | 225818 | 0 | 768000 | 190454.4 | 628945 | 5076486 | 0 | 0 | 0 | 25805452 | 83025 | 1164908 | 1704509 | 3930909 | 0 | 8527700 | 3226000 | 1008000 | 4606000 | 923040 | 2001600 | 1515810 | 3473760 | 1313760 | 408450 | 1169640 | 907200 | 459763 | 204700 | 885680 | 7517000 | 0 | 8928000 | 0 | 1677600 | 3579218.18 | 169128 | 0 | 1925760 | 720192 | 0 | 393000 | 2476150 | 59400 | 2312400 | 1492800 | 1864320 | 11000 | 207250 | 151680 | 184878376.76 | 20879272 | 5310720 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 454320 | 25127270 | 60480 | 27496909 | 0 | 41031 | 0 | 141696 | 270240 | 0 | 711792 | 147253 | 41846 | 315808 | 561262 | 135061 | 0 | 270000 | 3813818 | 0 | 3641382 | 0 | 3645882 | 0 | 8959127 | 0 | 23760 | 3634000 | 1344872 | 967343 | 170014 | 1052649 | 0 | 0 | 0 | 30682.8 | 1035360 | 2604 | 0 | 5314000 | 2715000 | 5306280 | 0 | 7213824 | 26433454.55 | 111600 | 158292612.35 | 343170989.11

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13864.61 | MW | 12:00 Hr. | Energy Generated |  |  | 343.171 |  | MKWHr.
| Day Peak Demand |  |  | 13902.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.287 |  | MKWHr.
| Evening Peak Generation |  |  | 15506.45 | MW | 19:30 Hr. | Energy Demand |  |  | 343.458 |  | MKWHr.
| Evening Peak Demand |  |  | 15506.45 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 12860.05 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 996.6 |  | MMCFD
| Maximum Generation of the Day |  |  | 15741.97 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.4928 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.5 | 0 | 16.355 | 0 | 0 | 0.19019 | 0 | 0 | 56.0453 | Gas | 133.1433 | Gas | 479992293.3632
| Chattogram Zone |  |  | 5.6899 | 41.0491 | 5.3316 | 0 | 5.3333 | 0.1015 | 0 | 0.41136 | 57.9168 | Coal | 110.1165 | Coal | 654559248.0707
| Cumilla Zone |  |  | 25.3108 | 0 | 11.0087 | 0 | 0 | 0.2047 | 0.9072 | 0 | 37.4314 | HFO | 40.3927 | HFO | 739182391.882
| Mymensingh Zone |  |  | 1.8643 | 0 | 4.0163 | 0 | 0 | 0.21825 | 0 | 0 | 6.0988 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.386 | Hydro | 5.3333 | Hydro | 533327.1
| Khulna Zone |  |  | 5.3107 | 25.1273 | 0.06048 | 0 | 0 | 0.45432 | 21.7913 | 0 | 52.7441 | Solar | 3.5785 | Solar | 54358474.908
| Barishal Zone |  |  | 8.0213 | 38.9613 | 0.1116 | 0 | 0 | 0.002604 | 0 | 0 | 47.0968 | Import | 50.1954 | Import | 293447034.89
| Rajshahi Zone |  |  | 20.0602 | 0 | 1.4889 | 0 | 0 | 1.1708 | 27.4969 | 0 | 50.2169 | Wind | 0.41136 | Wind | 6063446.4
| Rangpur Zone |  |  | 0 | 4.9789 | 2.02 | 0 | 0 | 1.2361 | 0 | 0 | 8.2349
| Total |  |  | 133.1433 | 110.1165 | 40.3927 | 0 | 5.3333 | 3.5785 | 50.1954 | 0.41136 | 343.171
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 479992293.3632 |  | Hydro | 533327.1
|  |  |  | Coal | 654559248.0707 |  | Solar | 54358474.908
|  |  |  | HFO | 739182391.882 |  | Import | 293447034.89
|  |  |  | HSD | 0 |  | Wind | 6063446.4
[5 empty] | Total: | 222,81,36,216 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8793 | Peak Hr Flow | 891.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46499610.99 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.4969 | Peak Hr Flow | 1142.45 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1742 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9072 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2720 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.2834 | Peak Hr Flow | 2075.45 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5452
|  |  |  | Chattogram |  | 0 |  | 1452
|  |  |  | Cumilla |  | 0 |  | 1376
|  |  |  | Mymensingh |  | 0 |  | 1206
|  |  |  | Sylhet |  | 0 |  | 608
|  |  |  | Khulna |  | 0 |  | 1782
|  |  |  | Barishal |  | 0 |  | 432
|  |  |  | Rajshahi |  | 0 |  | 1534
|  |  |  | Rangpur |  | 0 |  | 1055
|  |  |  | Total |  | 0 |  | 14897
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 09:03 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
|  | 09:04 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
|  | 09:36 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT is restored.
|  | 09:36 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
| 09:40 | 17:30 | Hathazari 230/132/33kV S/S 230KV MAIN BUS-01 Project Work S/D Due to G2G CCCE Progect
work
| 10:34 | 15:57 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end. and from
Faridpur 132/33kV end Due to Hot spot maintenance at Gopalgonj 400kV SS end.
| 11:05 | 15:47 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to Distance
Relay Maintenance (Ramgonj Ckt-) and from Ramganj 132/33kV end Due to Project Work
| 12:00 |  | Day Peak Gen. 13862 MW
| 13:26 | 13:42 | Tangail 132/33kV S/S Tr-3 LT Tripped showing REF 630 relays Due to 33kV feeder Fault | [7 empty] | 30.0MW load
interrup.
| 13:26 | 13:42 | Tangail 132/33kV S/S Tr-3 HT Tripped showing RET 650 (Main-2 Protection) relays Due to | [7 empty] | 30.0MW load
|  |  | 33kV feeder Fault | [7 empty] | interrup.
| 13:33 |  | Ashugonj (S) STG synch
| 13:33 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 15:16 | 17:32 | Bagerhat-Mongla 132 kV Ckt-1 Scheduled S/D from Mongla 132/33kV end Due to Breaker
maintenance at bagerhat end.
| 16:05 | 16:40 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to 33 kv T4 feeder post insulator | [7 empty] | 15.0MW load
|  |  | repair | [7 empty] | interrup.
| 16:06 | 16:39 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to 33kv T4 feeder post insulator | [7 empty] | 15.0MW load
|  |  | repair. | [7 empty] | interrup.
| 16:38 |  | Baghabari -Ishurdi 132 KV Ckt-3 Sync (Baghabari 352A CB Closed)
| 19:30 |  | Evening Peak Generation 15505 MW.
| 06:15 |  | Maniknagar 132/33kV S/S Transformer GT-1 LT Scheduled S/D Due to GT-1 bushing maintenance
due to red hot
| 06:22 |  | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to GT-1 Bushing maintenance
due to red hot.
| 06:34 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Scheduled S/D Due to LT bushing red
hot maintenance work.
| 06:35 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Scheduled S/D Due to LT bushing red
hot maintenance work.
| 06:43 | 07:20 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Project work
| 06:44 | 07:19 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to Project work
| 07:00 |  | Minimum Generation 11992 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 316 | 8078400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7578000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 7017425 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 106238 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7568049 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 22032 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.8 | 877320 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 119 | 1088160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 932246 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 441492 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.2 | 534600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 495360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 551520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2132727 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2968992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2169600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 142 | 2704320 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 190193 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 252000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 8228181.82 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 115 | 2108400 | -
Dhaka Area Total |  |  |  |  | 6657.724 | 2766 | 56045255.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 190454.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 83025 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 768000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5333271 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5076486 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 43 | 628945 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 752688 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 797654 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 330240 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 613440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 734400 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 45 | 642324 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 261120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 90 | 225818 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1065 | 25805452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 17 | 411360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 630 | 15243636.36 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2684 | 57916793.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 185 | 4606000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8527700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 3226000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 923040 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1008000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 150 | 3930909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1164908 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 1704509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 885680 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1515810 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 3473760 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 42 | 907200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 459763 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 408450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1169640 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 1313760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 79 | 2001600 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 204700 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1866 | 37431429
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 1864320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 1492800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 110 | 2312400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 207250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 151680 | 06 MW for 17 hrs and 12 MW for 7 for fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 59400 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 288 | 6098850
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 70 | 1677600 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3579218.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720192 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1925760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 103 | 2476150 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 393000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 169128 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7517000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 8928000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1119 | 27386048.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 20879272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 222 | 5310720 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 15 | 60480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 454320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1047 | 25127270 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2213 | 52744062
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7213824 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2715000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1070 | 26433454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5306280 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 111600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5314000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2604 | -
Barishal Area Total |  |  |  |  | 2236 | 1934 | 47096762.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 315808 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 41031 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 147253 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3813818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3641382 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3645882 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 330 | 8959127 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 135061 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 41846 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 711792 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 270240 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 100 | 141696 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1142.45 | 27496909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 270000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 561262 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2220.45 | 50216867
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1344872 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 147 | 3634000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1052649 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30682.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 967343 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170014 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1035360 | -
Rangpur Area Total |  |  |  |  | 950 | 416 | 8234920.8
Eastern Grid Total |  |  |  |  | 17385.715 | 8723 | 184878376.76
Western Grid Total |  |  |  |  | 10444.16 | 6783.45 | 158292612.35
National Grid Total |  |  |  |  | 27829.875 | 15506.45 | 343170989.11
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10093.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4802.8 | MW
i) Dhaka area |  |  | 5451.5 |  | MW | i) Khulna area |  |  |  | 1781.5 | MW
ii) Chattogram area |  |  | 1451.8 |  | MW | ii) Barishal area |  |  |  | 432.3 | MW
iii) Cumilla area |  |  | 1375.99 |  | MW | iii) Rajshahi area |  |  |  | 1534 | MW
iv) Mymensingh area |  |  | 1206 |  | MW | iv) Rangpur area |  |  |  | 1055 | MW
v) Sylhet area |  |  | 608 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14896.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 81 | 19:00 | 133 | PHP | 4 | 17:00
2 | AKSML | 147 | 02:00 | 68 | Ishurdi | 80 | 20:00 | 134 | Pabna | 125 | 19:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 86 | 19:30 | 135 | Palashbari | 130 | 00:00
4 | Agargaon | 142 | 13:00 | 70 | Jamalpur | 134 | 19:30 | 136 | Panchagarh | 64 | 19:00
5 | Agrabad | 96 | 18:30 | 71 | Jashore | 137 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 134 | 19:00 | 138 | Patuakhali | 67 | 00:00
7 | Ashuganj | 87 | 00:00 | 73 | Joydebpur | 158 | 12:00 | 139 | Payra | 34 | 23:00
8 | BSRM | 187 | 07:00 | 74 | Joypurhat | 68 | 00:00 | 140 | Postogola | 56 | 00:00
9 | Bagerhat | 80 | 00:00 | 75 | Juldah | 19.5 | 16:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 93 | 20:00 | 76 | KSRM | 12 | 18:00 | 142 | Purbasadipur | 128 | 00:00
11 | Bakulia | 94 | 19:30 | 77 | Kabirpur | 266 | 12:00 | 143 | Rahanpur | 40 | 00:00
12 | Banani | 56 | 13:00 | 78 | Kachua | 92 | 00:00 | 144 | Rahim | 45 | 07:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 108 | 00:00 | 145 | Rajbari | 84 | 00:00
14 | Barapukuria | 67 | 00:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajendrapur | 138 | 21:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 79 | 13:00 | 147 | Rajshahi | 116 | 00:00
16 | Barishal | 97 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 93 | 00:00
17 | Barishal-230 | 100 | 22:00 | 83 | Kasba | 36 | 00:00 | 149 | Ramganj | 118 | 00:00
18 | Baroaulia | 61 | 12:00 | 84 | Kazla | 106 | 13:00 | 150 | Rampur | 40 | 00:00
19 | Baroirhat | 60 | 20:00 | 85 | Keranigonj | 83 | 00:00 | 151 | Rangamati | 16 | 18:30
20 | Bashundhara | 212 | 12:00 | 86 | Khagrachori | 30 | 18:30 | 152 | Rangpur | 154 | 19:00
21 | BashundharaCement | 9 | 12:00 | 87 | Khulna | 64 | 13:00 | 153 | Ruppur | 7.2 | 10:00
22 | Beanibazar | 70 | 00:00 | 88 | Khulshi | 188 | 15:00 | 154 | SSM | 15 | 00:00
23 | Benapole | 62 | 19:00 | 89 | Kishoreganj | 134 | 00:00 | 155 | Saidpur | 110 | 19:00
24 | Bhaluka | 151 | 15:00 | 90 | Kodda | 324 | 18:30 | 156 | Satkhira | 123 | 22:00
25 | Bhandaria | 54 | 21:00 | 91 | Kulaura | 51 | 00:00 | 157 | Satmasjid | 99 | 13:00
26 | Bhangura | 38 | 00:00 | 92 | Kurigram | 70 | 19:00 | 158 | Savar | 234 | 12:00
27 | Bheramara(GK) | 69 | 19:00 | 93 | Kushtia | 155 | 19:00 | 159 | SevenRings | 16.77 | 02:00
28 | Bhulta | 224 | 23:00 | 94 | Laksam | 35 | 00:00 | 160 | ShahCement | 29 | 08:00
29 | Bog-Sherpur | 76 | 00:00 | 95 | Lakshmipur | 32 | 00:00 | 161 | Shahjadpur | 83 | 19:30
30 | Bogura | 168 | 23:00 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 131 | 21:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 68 | 18:30 | 163 | Shahmirpur | 65 | 00:00
32 | Brahmanbaria | 138 | 22:00 | 98 | MI_Cement | 12.4 | 07:00 | 164 | Shariatpur | 91 | 00:00
33 | Cantonment | 145 | 13:00 | 99 | Madanganj | 42 | 13:00 | 165 | Sherpur | 142 | 22:00
34 | Chandina | 15.7 | 23:00 | 100 | Madaripur | 116 | 00:00 | 166 | Shikalbaha | 14 | 12:00
35 | Chandpur | 78 | 00:00 | 101 | Madartek | 98.7 | 00:00 | 167 | Shitalakhya | 75.9 | 12:00
36 | Chandraghona | 34 | 18:30 | 102 | Madunaghat | 56 | 19:00 | 168 | Sholosohor | 44 | 12:00
37 | Chapai | 70 | 00:00 | 103 | Magura | 64 | 20:00 | 169 | Shyampur | 172 | 13:00
38 | Charsaidpur | 39 | 02:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 120 | 14:00
39 | Chauddagram | 71 | 00:00 | 105 | Maijdee | 15 | 01:00 | 171 | Sirajganj | 114 | 20:00
40 | Chhatak | 43 | 00:00 | 106 | Manikganj | 131 | 00:00 | 172 | Sonargaon | 127 | 19:30
41 | Chowmuhani | 182 | 00:00 | 107 | Maniknagar | 80 | 13:00 | 173 | Sreemongol | 89 | 19:00
42 | Chuadanga | 119 | 23:00 | 108 | Matarbari | 50 | 23:00 | 174 | Sreepur | 102 | 19:30
43 | Coxsbazar | 129 | 19:00 | 109 | Matuail | 72 | 00:00 | 175 | Srinagar | 48.71 | 22:00
44 | Cumilla(N) | 157 | 00:00 | 110 | Millgate | 134 | 15:00 | 176 | Sunamganj | 62 | 00:00
45 | Cumilla(S) | 143 | 00:00 | 111 | Mirpur | 122 | 12:00 | 177 | Sylhet | 50 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 11:00 | 178 | Sylhet-132 | 122 | 13:00
47 | Daudkandi | 149 | 19:00 | 113 | Mirzapur | 48 | 21:00 | 179 | TK | 35 | 18:30
48 | Dhaka | 96 | 12:00 | 114 | Mithapukur | 76 | 01:00 | 180 | Tangail | 182 | 21:00
49 | Dhamrai | 138 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 00:00
50 | Dhanmondi | 140 | 13:00 | 116 | Mogbazar | 120.6 | 14:00 | 182 | Thakurgaon | 114 | 19:30
51 | Dohazari | 108 | 19:00 | 117 | Mongla | 43 | 00:00 | 183 | Tongi | 108 | 16:00
52 | Faridpur | 172 | 00:00 | 118 | Motijheel | 47 | 13:00 | 184 | Ullahpara | 46 | 19:00
53 | Fatullah | 106 | 12:00 | 119 | Muktagacha | 40 | 21:00 | 185 | Ullon | 57 | 22:00
54 | Fenchuganj | 50 | 00:00 | 120 | Munshiganj | 125 | 00:00 | 186 | Uttara | 87 | 12:00
55 | Feni | 114 | 19:00 | 121 | Muradnagar | 42 | 20:00 | 187 | UttaraNew | 65 | 00:00
56 | GPH | 70 | 00:00 | 122 | Mymensingh | 206 | 00:00 | 188 | Zigatola | 74 | 13:00
57 | Ghatail | 88 | 19:30 | 123 | Naogaon | 141 | 00:00
58 | Ghorashal | 14 | 00:00 | 124 | Narail | 57.5 | 19:30
59 | Ghorashal-230 | 93 | 01:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 186 | 00:00
61 | Gollamari | 94 | 00:00 | 127 | Natore | 159 | 21:00
62 | Gopalganj | 106 | 18:30 | 128 | Nawabganj | 60 | 00:00
63 | Gulshan | 130 | 13:00 | 129 | Netrakona | 142 | 00:00
64 | Halishahar | 60 | 14:00 | 130 | New | 77.8 | 12:00
65 | HaripurSBU | 166 | 12:00 | 131 | Niamatpur | 80 | 22:00
66 | Hasnabad | 92 | 00:00 | 132 | Noapara | 45 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15741.97 | 75 |  | 15820.35
1:00 | 15179.37 | 0 |  | 15179.37
2:00 | 14634.62 | 0 |  | 14634.62
3:00 | 14275.03 | 0 |  | 14275.03
4:00 | 13847.97 | 0 |  | 13847.97
5:00 | 13481.22 | 0 |  | 13481.22
6:00 | 13131.67 | 0 |  | 13131.67
7:00 | 13120.3 | 0 |  | 13120.3
8:00 | 12860.05 | 0 |  | 12860.05
9:00 | 13082.53 | 59 |  | 13144.53
10:00 | 13206.36 | 46 |  | 13254.36
11:00 | 13475.31 | 37 |  | 13514.31
12:00 | 13864.61 | 36 |  | 13902.61
13:00 | 14237.71 | 34 |  | 14273.71
14:00 | 13995.07 | 0 |  | 13995.07
15:00 | 14084.54 | 0 |  | 14084.54
16:00 | 13856.58 | 0 |  | 13856.58
17:00 | 13526.48 | 0 |  | 13526.48
18:00 | 13035.88 | 0 |  | 13035.88
19:00 | 14993.09 | 0 |  | 14993.09
19:30 | 15506.45 | 0 |  | 15506.45
20:00 | 15279.26 | 0 |  | 15279.26
21:00 | 15244.49 | 0 |  | 15244.49
22:00 | 15119.34 | 0 |  | 15119.34
23:00 | 15242.73 | 0 |  | 15242.73
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8460 | 7281.97 | 15741.97 | DAILY GENERATION CURVE
00:30 | 8315.4 | 7145.27 | 15460.67
01:00 | 8170.8 | 7008.57 | 15179.37 | 28-08-2025
01:30 | 8039.15 | 6867.845 | 14906.995
02:00 | 7907.5 | 6727.12 | 14634.62
02:30 | 7800 | 6654.825 | 14454.825
03:00 | 7692.5 | 6582.53 | 14275.03
03:30 | 7540.25 | 6521.25 | 14061.5
04:00 | 7388 | 6459.97 | 13847.97
04:30 | 7190 | 6474.595 | 13664.595
05:00 | 6992 | 6489.22 | 13481.22
05:30 | 6848.135 | 6458.31 | 13306.445
06:00 | 6704.27 | 6427.4 | 13131.67
06:30 | 6739.145 | 6386.84 | 13125.985
07:00 | 6774.02 | 6346.28 | 13120.3
07:30 | 6648.71 | 6341.465 | 12990.175
08:00 | 6523.4 | 6336.65 | 12860.05
08:30 | 6595.93 | 6375.36 | 12971.29
09:00 | 6668.46 | 6414.07 | 13082.53
09:30 | 6739.64 | 6404.805 | 13144.445
10:00 | 6810.82 | 6395.54 | 13206.36
10:30 | 6884.97 | 6455.865 | 13340.835
11:00 | 6959.12 | 6516.19 | 13475.31
11:30 | 7220.325 | 6449.635 | 13669.96
12:00 | 7481.53 | 6383.08 | 13864.61
12:30 | 7586.66 | 6464.5 | 14051.16
13:00 | 7691.79 | 6545.92 | 14237.71
13:30 | 7670.3 | 6446.09 | 14116.39
14:00 | 7648.81 | 6346.26 | 13995.07
14:30 | 7732.48 | 6307.325 | 14039.805
15:00 | 7816.15 | 6268.39 | 14084.54
15:30 | 7796.45 | 6174.11 | 13970.56
16:00 | 7776.75 | 6079.83 | 13856.58
16:30 | 7685.015 | 6006.515 | 13691.53
17:00 | 7593.28 | 5933.2 | 13526.48
17:30 | 7511.05 | 5770.13 | 13281.18
18:00 | 7428.82 | 5607.06 | 13035.88
18:30 | 7891.41 | 6123.075 | 14014.485
19:00 | 8354 | 6639.09 | 14993.09
19:30 | 8723 | 6783.45 | 15506.45
20:00 | 8611.3 | 6667.96 | 15279.26
20:30 | 8528.75 | 6733.125 | 15261.875 |  | Executive Engineer
21:00 | 8446.2 | 6798.29 | 15244.49 |  | Network Operation Division
21:30 | 8364.75 | 6817.165 | 15181.915
22:00 | 8283.3 | 6836.04 | 15119.34
22:30 | 8302.6 | 6878.435 | 15181.035
23:00 | 8321.9 | 6920.83 | 15242.73

## En-Curve
QF-LDC-12
Date | 28-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3349 | 2094 | 843 | 38 | 48 | 1148.97 | 222 | 4929 | 0 | 580 | 2280 | 188 | 0 | 22 | 75 | DAILY ENERGY CURVE
00:30 | 3344.5 | 2085.5 | 843 | 38 | 47 | 1150.77 | 222 | 4920 | 0 | 576.5 | 2120.9 | 94 | 0 | 18.5 | 37.5 | 28-08-2025
01:00 | 3340 | 2077 | 843 | 38 | 46 | 1152.57 | 222 | 4911 | 0 | 573 | 1961.8 | 0 | 0 | 15 | 0
01:30 | 3346 | 2079 | 843 | 38 | 45 | 1150.345 | 222 | 4864.5 | 0 | 534 | 1770.15 | 0 | 0 | 15 | 0 | Energy Generated | 343.171 |  | MKWHr
02:00 | 3352 | 2081 | 843 | 38 | 44 | 1148.12 | 222 | 4818 | 0 | 495 | 1578.5 | 0 | 0 | 15 | 0 | Energy not Served | 0.287 |  | MKWHr
02:30 | 3357.5 | 2082.75 | 843 | 38 | 43 | 1152.825 | 221 | 4816 | 0 | 423.5 | 1459.75 | 0 | 0 | 17.5 | 0 | Total Energy Requirement | 343.458 |  | MKWHr
03:00 | 3363 | 2084.5 | 843 | 38 | 42 | 1157.53 | 220 | 4814 | 0 | 352 | 1341 | 0 | 0 | 20 | 0
03:30 | 3309 | 2085.75 | 843 | 38 | 42 | 1154.25 | 219.5 | 4822.5 | 0 | 316.5 | 1205 | 0 | 0 | 26 | 0
04:00 | 3255 | 2087 | 843 | 38 | 42 | 1150.97 | 219 | 4831 | 0 | 281 | 1069 | 0 | 0 | 32 | 0
04:30 | 3261.5 | 2092.5 | 850 | 38 | 41 | 1152.595 | 218.5 | 4838 | 0 | 256 | 885.5 | 0 | 0 | 31 | 0
05:00 | 3268 | 2098 | 857 | 38 | 40 | 1154.22 | 218 | 4845 | 0 | 231 | 702 | 0 | 0 | 30 | 0
05:30 | 3269.5 | 2099 | 861 | 38 | 38 | 1161.835 | 218 | 4766 | 3.11 | 231 | 600 | 0 | 0 | 21 | 0
06:00 | 3271 | 2100 | 865 | 38 | 36 | 1169.45 | 218 | 4687 | 6.22 | 231 | 498 | 0 | 0 | 12 | 0
06:30 | 3347 | 2097.25 | 865.5 | 38 | 36 | 1160.865 | 218 | 4592 | 46.87 | 235 | 482.5 | 0 | 0 | 7 | 0
07:00 | 3423 | 2094.5 | 866 | 38 | 36 | 1152.28 | 218 | 4497 | 87.52 | 239 | 467 | 0 | 0 | 2 | 0
07:30 | 3324 | 2058.25 | 866 | 38 | 34 | 1154.64 | 218.5 | 4450 | 173.285 | 234.5 | 433.5 | 0 | 0 | 5.5 | 0
08:00 | 3225 | 2022 | 866 | 38 | 32 | 1157 | 219 | 4403 | 259.05 | 230 | 400 | 0 | 0 | 9 | 0
08:30 | 3252.5 | 2035.25 | 866 | 38 | 30 | 1158 | 219.5 | 4368 | 319.54 | 231 | 444.5 | 0 | 0 | 9 | 29.5
09:00 | 3280 | 2048.5 | 866 | 38 | 28 | 1159 | 220 | 4333 | 380.03 | 232 | 489 | 0 | 0 | 9 | 59
09:30 | 3282.5 | 2049.25 | 866 | 38 | 29 | 1153.5 | 220 | 4366 | 348.195 | 232 | 550 | 0 | 0 | 10 | 52.5
10:00 | 3285 | 2050 | 866 | 38 | 30 | 1148 | 220 | 4399 | 316.36 | 232 | 611 | 0 | 0 | 11 | 46
10:30 | 3263 | 2047.5 | 866.5 | 38 | 30 | 1140.5 | 220.5 | 4380.5 | 423.835 | 232 | 681.5 | 0 | 0 | 17 | 41.5
11:00 | 3241 | 2045 | 867 | 38 | 30 | 1133 | 221 | 4362 | 531.31 | 232 | 752 | 0 | 0 | 23 | 37
11:30 | 3287 | 2054 | 866.5 | 38 | 31 | 1143 | 221.5 | 4363.5 | 471.86 | 242.5 | 931.6 | 0 | 0 | 19.5 | 36.5
12:00 | 3333 | 2063 | 866 | 38 | 32 | 1153 | 222 | 4365 | 412.41 | 253 | 1111.2 | 0 | 0 | 16 | 36
12:30 | 3343 | 2057 | 866 | 38 | 33 | 1149 | 222 | 4360 | 480.56 | 294.5 | 1187.1 | 0 | 0 | 21 | 35
13:00 | 3353 | 2051 | 866 | 38 | 34 | 1145 | 222 | 4355 | 548.71 | 336 | 1263 | 0 | 0 | 26 | 34
13:30 | 3343 | 2033.1 | 870 | 38 | 34 | 1145.825 | 222 | 4340 | 471.715 | 336 | 1264.75 | 0 | 0 | 18 | 17
14:00 | 3333 | 2015.2 | 874 | 38 | 34 | 1146.65 | 222 | 4325 | 394.72 | 336 | 1266.5 | 0 | 0 | 10 | 0
14:30 | 3406.5 | 2023.2 | 874 | 38 | 36 | 1148.165 | 222 | 4306.5 | 352.79 | 336 | 1284.65 | 0 | 0 | 12 | 0
15:00 | 3480 | 2031.2 | 874 | 38 | 38 | 1149.68 | 222 | 4288 | 310.86 | 336 | 1302.8 | 0 | 0 | 14 | 0
15:30 | 3521.5 | 2028.6 | 876.5 | 38 | 37 | 1145.235 | 222 | 4220.5 | 261.825 | 336 | 1268.9 | 0 | 0 | 14.5 | 0
16:00 | 3563 | 2026 | 879 | 38 | 36 | 1140.79 | 222 | 4153 | 212.79 | 336 | 1235 | 0 | 0 | 15 | 0
16:30 | 3544 | 1993.5 | 882.5 | 38 | 33 | 1145.845 | 221 | 4100.5 | 163.435 | 340.5 | 1214.75 | 0 | 0 | 14.5 | 0
17:00 | 3525 | 1961 | 886 | 38 | 30 | 1150.9 | 220 | 4048 | 114.08 | 345 | 1194.5 | 0 | 0 | 14 | 0
17:30 | 3438 | 1917 | 888 | 38 | 33 | 1107.765 | 220 | 4006.5 | 66.265 | 356.5 | 1185.65 | 0 | 0 | 24.5 | 0
18:00 | 3351 | 1873 | 890 | 38 | 36 | 1064.63 | 220 | 3965 | 18.45 | 368 | 1176.8 | 0 | 0 | 35 | 0
18:30 | 3484 | 1918.6 | 890.5 | 38 | 39 | 1103.86 | 220 | 4202 | 9.225 | 499.5 | 1583.3 | 0 | 0 | 26.5 | 0
19:00 | 3617 | 1964.2 | 891 | 38 | 42 | 1143.09 | 220 | 4439 | 0 | 631 | 1989.8 | 0 | 0 | 18 | 0
19:30 | 3581 | 1931.2 | 891 | 38 | 42 | 1142.45 | 220 | 4578 | 0 | 688 | 2377.8 | 0 | 0 | 17 | 0
20:00 | 3571 | 1934.2 | 823 | 38 | 42 | 1146.96 | 219 | 4662 | 0 | 699 | 2134.1 | 0 | 0 | 10 | 0
20:30 | 3588.5 | 1889.5 | 823 | 38 | 43 | 1146.025 | 219 | 4734.1 | 0 | 687 | 2082.75 | 0 | 0 | 11 | 0
21:00 | 3606 | 1844.8 | 823 | 38 | 44 | 1145.09 | 219 | 4806.2 | 0 | 675 | 2031.4 | 0 | 0 | 12 | 0
21:30 | 3628 | 1893.3 | 823.5 | 38 | 44 | 1143.465 | 219.5 | 4837.2 | 0 | 666.5 | 1879.45 | 0 | 0 | 9 | 0
22:00 | 3650 | 1941.8 | 824 | 38 | 44 | 1141.84 | 220 | 4868.2 | 0 | 658 | 1727.5 | 0 | 0 | 6 | 0
22:30 | 3663.5 | 1960.3 | 859.5 | 38 | 44 | 1142.235 | 221 | 4883.7 | 0 | 637 | 1719.3 | 0 | 0 | 12.5 | 0
23:00 | 3677 | 1978.8 | 895 | 38 | 44 | 1142.63 | 222 | 4899.2 | 0 | 616 | 1711.1 | 0 | 0 | 19 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 18:00 | 372 | 10:00 | Payra | 412 | 18:00 | 408 | 10:00
Ashuganj | 403 | 20:00 | 377 | 11:00 | Rahanpur | 399 | 18:30 | 390 | 02:00
Bhulta | 399 | 20:00 | 374 | 11:00 | Rampal | 405 | 18:00 | 393 | 00:00
Bibiana | 386 | 19:30 | 379 | 04:00
BIPTC | 399 | 04:00 | 388 | 19:30
Bogura | 380 | 18:30 | 369 | 03:00
Gopalganj | 397 | 18:00 | 386 | 01:00
Kaliakoir | 374 | 19:30 | 359 | 10:00
Madunaghat | 392 | 18:00 | 388 | 06:00
Meghnaghat | 383 | 18:00 | 376 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 18:00 | 215 | 12:00 | Keranigonj | 221 | 18:00 | 214 | 10:00
AKSML | 232 | 18:30 | 224 | 05:00 | Khulna(S) | 232 | 18:00 | 220 | 01:00
Aminbazar | 224 | 18:30 | 216 | 10:00 | Madunaghat | 234 | 19:30 | 228 | 10:00
Ashuganj | 233 | 20:00 | 220 | 11:00 | Madunaghat-400 | 233 | 20:00 | 228 | 06:00
Ashuganj-400 | 232 | 20:00 | 221 | 11:00 | Maniknagar | 218 | 19:30 | 212 | 10:00
Baghabari | 234 | 18:00 | 226 | 01:00 | Meghnaghat | 226 | 18:00 | 220 | 10:00
Barapukuria | 222 | 18:00 | 210 | 05:00 | Meghnaghat-400 | 222 | 18:00 | 217 | 10:00
Barapukuria-230 | 222 | 18:00 | 211 | 5:00 | Mirsorai | 230 | 19:00 | 220 | 12:00
Barishal | 228 | 18:00 | 220 | 00:00 | Rajshahi | 230 | 18:00 | 220 | 01:00
Bheramara | 231 | 18:00 | 224 | 00:00 | Rampal | 231 | 18:00 | 220 | 01:00
Bhulta | 230 | 20:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 17:00 | 222 | 00:00 | Rampura | 229 | 21:00 | 210 | 11:00
BIPTC | 233 | 08:00 | 224 | 00:00 | Shikalbaha | 231 | 19:00 | 225 | 09:00
Bogura | 238 | 18:30 | 230 | 02:00 | Shyampur | 221 | 18:00 | 214 | 10:00
Bogura-400 | 237 | 18:30 | 230 | 02:00 | Siddhirganj | 220 | 18:00 | 215 | 09:00
Borhanuddin | 233 | 18:00 | 227 | 00:00 | Sirajgonj | 240 | 18:30 | 235 | 01:00
BSRM | 230 | 19:00 | 220 | 11:00 | Sreepur | 228 | 18:00 | 221 | 00:00
Cumilla(N) | 223 | 18:00 | 215 | 10:00 | Tongi | 227 | 18:30 | 216 | 11:00
Faridpur | 225 | 18:00 | 217 | 00:00
Fenchuganj | 229 | 07:00 | 224 | 00:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 228 | 20:00 | 213 | 10:00
Gopalganj | 226 | 18:00 | 219 | 00:00
GPH | 229 | 19:30 | 224 | 12:00
Haripur | 219 | 18:00 | 214 | 10:00
Hasnabad | 221 | 17:00 | 215 | 11:00
Hathazari | 229 | 00:00 | 223 | 15:00
Ishurdi | 233 | 18:00 | 225 | 00:00
Jhenaidah | 231 | 18:00 | 219 | 22:00
Kaliakoir | 233 | 19:30 | 221 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 21:00 | 124 | 10:00 | Lalmonirhat | 124 | 08:00 | 120 | 10:00
Agargaon | 130 | 01:00 | 124 | 12:00 | Madanganj | 128 | 19:30 | 123 | 11:00
Agrabad | 131 | 18:00 | 127 | 08:00 | Madaripur | 135 | 18:00 | 129 | 00:00
AKS | 129 | 18:30 | 125 | 06:00 | Madartek | 134 | 05:00 | 122 | 11:00
Aminbazar | 133 | 22:00 | 127 | 07:00 | Madunaghat | 133 | 19:30 | 129 | 11:00
Amnura | 136 | 18:00 | 127 | 02:00 | Magura | 136 | 18:00 | 126 | 00:00
Ashuganj | 140 | 08:00 | 135 | 00:00 | Mahasthangarh | 132 | 18:30 | 124 | 22:00
Bagerhat | 133 | 18:00 | 121 | 22:00 | Maijdee | 123 | 18:00 | 113 | 00:00
Bajitpur | 130 | 04:00 | 123 | 00:00 | Manikganj | 127 | 20:00 | 120 | 10:00
Bakulia | 133 | 19:30 | 128 | 10:00 | Maniknagar | 131 | 02:00 | 126 | 13:00
Banani | 134 | 02:00 | 122 | 11:00 | Matarbari | 120 | 18:00 | 113 | 18:30
Bangabhaban | 131 | 04:00 | 126 | 12:00 | Matuail | 128 | 19:00 | 124 | 12:00
Barapukuria | 135 | 18:30 | 127 | 07:00 | Millgate | 133 | 20:00 | 122 | 10:00
Barguna | 134 | 18:00 | 130 | 22:00 | Mirpur | 131 | 18:00 | 125 | 11:00
Barishal | 134 | 18:00 | 128 | 00:00 | Mirzapur | 129 | 18:00 | 124 | 10:00
Barishal-230 | 134 | 18:00 | 128 | 00:00 | Mithapukur | 129 | 18:30 | 123 | 07:00
Baroaulia | 132 | 00:00 | 128 | 08:00 | MI_Cement | 128 | 19:00 | 123 | 10:00
Baroirhat | 125 | 18:00 | 119 | 05:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 03:00 | 122 | 11:00 | Mogbazar | 135 | 01:00 | 124 | 11:00
BashundharaCement | 128 | 19:30 | 123 | 11:00 | Mongla | 133 | 18:00 | 122 | 23:00
Beanibazar | 128 | 07:00 | 122 | 00:00 | Motijheel | 131 | 04:00 | 126 | 12:00
Benapole | 133 | 18:00 | 121 | 23:00 | Muktagacha | 134 | 16:00 | 124 | 07:00
Bhaluka | 130 | 18:00 | 122 | 00:00 | Munshiganj | 127 | 17:00 | 121 | 10:00
Bhandaria | 130 | 18:00 | 119 | 23:00 | Muradnagar | 124 | 18:00 | 117 | 00:00
Bhangura | 133 | 18:00 | 127 | 23:00 | Mymensingh | 136 | 17:00 | 111 | 00:00
Bheramara | 136 | 08:00 | 133 | 00:00 | Naogaon | 130 | 18:30 | 121 | 22:00
Bheramara(GK) | 136 | 17:00 | 132 | 00:00 | Narail | 137 | 18:00 | 125 | 22:00
Bhulta | 123 | 18:30 | 119 | 00:00 | Narinda | 131 | 2:00 | 126 | 13:00
Bog-Sherpur | 133 | 18:30 | 126 | 01:00 | Narshingdi | 138 | 20:00 | 119 | 00:00
Bogura | 135 | 18:30 | 128 | 22:00 | Natore | 133 | 18:30 | 126 | 23:00
Bogura-230 | 135 | 18:30 | 128 | 02:00 | Nawabganj | 132 | 04:00 | 126 | 10:00
Brahmanbaria | 134 | 17:00 | 129 | 00:00 | Netrakona | 125 | 17:00 | 109 | 00:00
Cantonment | 130 | 02:00 | 124 | 10:00 | New | 133 | 19:30 | 124 | 10:00
Chandina | 128 | 18:00 | 123 | 00:00 | Niamatpur | 135 | 18:00 | 131 | 01:00
Chandpur | 131 | 18:00 | 124 | 05:00 | Noapara | 136 | 18:00 | 125 | 22:00
Chandraghona | 133 | 19:00 | 130 | 05:00 | Pabna | 134 | 18:00 | 129 | 00:00
Chapai | 134 | 17:00 | 131 | 23:00 | Palashbari | 128 | 18:30 | 120 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:30 | 123 | 10:00 | Panchagarh | 135 | 01:00 | 120 | 13:00
Chauddagram | 125 | 18:00 | 118 | 06:00 | Patiya | 131 | 17:00 | 127 | 05:00
Chhatak | 127 | 07:00 | 118 | 00:00 | Patuakhali | 133 | 07:00 | 131 | 00:00
Chowmuhani | 122 | 18:00 | 115 | 00:00 | Payra | 136 | 18:00 | 133 | 00:00
Chuadanga | 133 | 18:00 | 121 | 00:00 | PHP | 125 | 18:00 | 118 | 05:00
Coxsbazar | 118 | 04:00 | 112 | 18:30 | Postogola | 133 | 18:00 | 128 | 10:00
Cumilla(N) | 128 | 18:00 | 123 | 00:00 | Purbachal | 134 | 05:00 | 123 | 10:00
Cumilla(S) | 132 | 03:00 | 122 | 00:00 | Purbasadipur | 130 | 01:00 | 119 | 13:00
Daganbhuiyan | 123 | 18:00 | 116 | 01:00 | Rahanpur | 137 | 18:00 | 133 | 00:00
Daudkandi | 121 | 18:00 | 114 | 00:00 | Rahanpur-400 | 137 | 18:00 | 134 | 00:00
Dhaka | 135 | 03:00 | 123 | 11:00 | Rahim | 128 | 19:00 | 124 | 10:00
Dhamrai | 131 | 19:30 | 124 | 10:00 | Rajbari | 132 | 18:00 | 125 | 00:00
Dhanmondi | 136 | 20:00 | 124 | 12:00 | Rajendrapur | 136 | 19:30 | 122 | 10:00
Dohazari | 128 | 17:00 | 123 | 06:00 | Rajshahi | 133 | 18:00 | 127 | 00:00
Faridpur | 133 | 18:00 | 128 | 00:00 | Rajshahi-230 | 132 | 18:00 | 126 | 01:00
Fatullah | 128 | 18:00 | 123 | 10:00 | Ramganj | 125 | 18:00 | 117 | 00:00
Fenchuganj | 134 | 07:00 | 131 | 00:00 | Rampur | 131 | 19:30 | 126 | 11:00
Feni | 124 | 17:00 | 119 | 00:00 | Rampura | 135 | 07:00 | 123 | 11:00
Ghatail | 129 | 17:00 | 120 | 07:00 | Rangamati | 132 | 19:30 | 129 | 07:00
Ghorashal | 137 | 19:30 | 129 | 11:00 | Rangpur | 129 | 18:30 | 123 | 07:00
Goalpara | 138 | 18:00 | 128 | 00:00 | Ruppur | 136 | 05:00 | 132 | 00:00
Gollamari | 137 | 09:00 | 128 | 01:00 | Saidpur | 131 | 18:30 | 122 | 07:00
Gopalganj | 135 | 18:00 | 128 | 00:00 | Satkhira | 135 | 18:00 | 123 | 22:00
Gopalganj-400 | 136 | 18:00 | 131 | 00:00 | Satmasjid | 130 | 03:00 | 124 | 10:00
Gulshan | 135 | 07:00 | 124 | 11:00 | Savar | 131 | 18:00 | 123 | 08:00
Halishahar | 133 | 19:30 | 128 | 05:00 | SevenRings | 138 | 19:00 | 128 | 10:00
Haripur | 128 | 18:00 | 124 | 10:00 | ShahCement | 128 | 18:30 | 123 | 10:00
HaripurSBU | 128 | 18:00 | 124 | 10:00 | Shahjadpur | 134 | 15:00 | 132 | 12:00
Hasnabad | 133 | 18:00 | 129 | 09:00 | Shahjibazar | 134 | 17:00 | 128 | 00:00
Hathazari | 134 | 21:00 | 130 | 01:00 | Shahmirpur | 133 | 19:30 | 129 | 05:00
Ishurdi | 137 | 18:00 | 132 | 00:00 | Shariatpur | 133 | 18:00 | 126 | 00:00
Jaldhaka | 128 | 18:30 | 120 | 15:00 | Sherpur | 135 | 17:00 | 118 | 05:00
Jamalpur | 138 | 17:00 | 124 | 07:00 | Shikalbaha | 123 | 19:30 | 118 | 06:00
Jashore | 136 | 18:00 | 120 | 02:00 | Shikalbaha-230 | 134 | 21:00 | 129 | 05:00
Jhenaidah | 138 | 18:00 | 123 | 00:00 | Shitalakhya | 128 | 19:00 | 123 | 10:00
Jhenaidah-230 | 138 | 18:00 | 128 | 23:00 | Sholosohor | 131 | 00:00 | 128 | 05:00
Joydebpur | 140 | 02:00 | 126 | 10:00 | Shyampur | 128 | 18:00 | 123 | 10:00
Joypurhat | 128 | 18:30 | 118 | 22:00 | Shyampur-230 | 131 | 18:00 | 124 | 10:00
Juldah | 133 | 19:30 | 128 | 06:00 | Siddhirganj | 128 | 18:00 | 124 | 10:00
Kabirpur | 133 | 19:30 | 120 | 11:00 | Sirajganj | 132 | 18:30 | 124 | 02:00
Kachua | 130 | 18:00 | 123 | 00:00 | Sonargaon | 127 | 19:00 | 122 | 10:00
Kaliakoir | 134 | 19:00 | 126 | 10:00 | Sreemongol | 132 | 06:00 | 127 | 00:00
Kallyanpur | 133 | 18:00 | 126 | 10:00 | Sreepur | 132 | 18:00 | 126 | 00:00
Kalurghat | 132 | 18:00 | 128 | 06:00 | Srinagar | 131 | 02:00 | 126 | 10:00
Kamrangirchar | 132 | 04:00 | 126 | 11:00 | SSM | 135 | 19:30 | 130 | 06:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 07:00 | 118 | 00:00
Kasba | 124 | 18:00 | 116 | 00:00 | Sylhet | 128 | 07:00 | 123 | 00:00
Kazla | 131 | 04:00 | 126 | 11:00 | Sylhet-132 | 128 | 07:00 | 125 | 00:00
Keranigonj | 132 | 03:00 | 127 | 11:00 | Tangail | 127 | 18:00 | 121 | 07:00
Khagrachori | 130 | 01:00 | 128 | 05:00 | Taraganj | 128 | 19:00 | 122 | 15:00
Khulna | 137 | 18:00 | 128 | 01:00 | Thakurgaon | 133 | 01:00 | 118 | 13:00
Khulna(S) | 138 | 18:00 | 129 | 22:00 | TK | 132 | 17:00 | 129 | 03:00
Khulshi | 130 | 18:00 | 126 | 11:00 | Tongi | 133 | 04:00 | 127 | 11:00
Kishoreganj | 129 | 17:00 | 120 | 00:00 | Ullahpara | 134 | 18:30 | 128 | 01:00
Kodda | 137 | 19:30 | 122 | 10:00 | Ullon | 135 | 21:00 | 123 | 11:00
KSRM | 132 | 04:00 | 128 | 08:00 | Uttara | 132 | 04:00 | 125 | 10:00
Kulaura | 133 | 08:00 | 129 | 00:00 | UttaraNew | 131 | 18:00 | 125 | 10:00
Kurigram | 125 | 09:00 | 117 | 19:00 | Zigatola | 131 | 03:00 | 127 | 11:00
Kushtia | 133 | 07:00 | 127 | 00:00
Laksam | 129 | 18:30 | 122 | 00:00
Lakshmipur | 123 | 18:00 | 114 | 00:00
Lalbag | 131 | 03:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division