## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-08-2025 | [28 empty] | Date: | 31-08-2025 | [28 empty] | Date: | 31-08-2025 | [28 empty] | Date: | 31-08-2025 | [28 empty] | Date: | 31-08-2025 | [14 empty] | Date: | 31-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 49.6 | 0 | 131 | 60 | 145 | 0 | 0 | 157 | 0 | 350 | 300 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 350 | 0 | 0 | 50 | 0 | 4 | 66 | 68 | 0 | 12 | 12 | 0 | 222 | 51 | 6 | 635 | 0 | 0 | 39 | 0 | 100 | 220 | 0 | 0 | 0 | 852 | 0 | 51 | 127 | 8 | 0 | 352 | 330 | 45 | 200 | 36 | 78 | 50 | 182 | 12 | 19 | 114 | 46 | 43 | 0 | 38 | 315 | 0 | 385 | 0 | 60 | 158 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 17 | 111 | 77 | 99 | 0 | 0 | 0 | 7962.6 | 916 | 308 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1179 | 17 | 1153 | 0 | 41 | 0 | 0 | 0 | 0 | 87 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 197 | 0 | 190 | 0 | 189 | 0 | 414 | 0 | 0 | 153 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 302 | 1225 | 0 | 7314 | 15276.6 | 107.88
01:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 47.1 | 0 | 131 | 60 | 145 | 0 | 0 | 125 | 0 | 350 | 286 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 332 | 0 | 0 | 42 | 0 | 0 | 66 | 68 | 0 | 12 | 12 | 0 | 222 | 51 | 28 | 635 | 0 | 0 | 0 | 0 | 96 | 222 | 0 | 0 | 0 | 831 | 0 | 51 | 130 | 8 | 0 | 355 | 330 | 45 | 190 | 36 | 83 | 70 | 177 | 9 | 19 | 114 | 46 | 43 | 0 | 38 | 310 | 0 | 360 | 0 | 60 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 17 | 112 | 58 | 99 | 0 | 0 | 0 | 7824.1 | 915 | 299 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1169 | 17 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 36 | 0 | 0 | 0 | 28 | 0 | 0 | 190 | 0 | 186 | 0 | 187 | 0 | 401 | 0 | 0 | 152 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 302 | 1120 | 0 | 7114 | 14938.1 | 107.88
02:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 44.2 | 0 | 124 | 30 | 0 | 0 | 0 | 112 | 0 | 350 | 287 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 333 | 0 | 0 | 24 | 0 | 0 | 66 | 68 | 0 | 12 | 12 | 0 | 222 | 45 | 37 | 635 | 0 | 0 | 19 | 0 | 91 | 224 | 0 | 0 | 0 | 832 | 0 | 51 | 50 | 8 | 0 | 355 | 330 | 45 | 190 | 34 | 74 | 70 | 168 | 9 | 19 | 114 | 44 | 43 | 0 | 38 | 305 | 0 | 360 | 0 | 60 | 150 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 112 | 58 | 103 | 0 | 0 | 0 | 7476.2 | 915 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 180 | 0 | 181 | 0 | 399 | 0 | 0 | 155 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 302 | 1092 | 0 | 6864 | 14340.2 | 107.88
03:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 18.1 | 0 | 82 | 30 | 0 | 0 | 0 | 88 | 0 | 350 | 289 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 66 | 37 | 0 | 12 | 12 | 0 | 222 | 17 | 37 | 635 | 0 | 0 | 0 | 0 | 47 | 187 | 0 | 0 | 0 | 837 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 45 | 191 | 34 | 75 | 70 | 167 | 9 | 19 | 114 | 42 | 43 | 0 | 38 | 305 | 0 | 365 | 0 | 60 | 149 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 112 | 58 | 103 | 0 | 0 | 0 | 7164.1 | 915 | 293 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 0 | 1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 180 | 0 | 181 | 0 | 400 | 0 | 0 | 152 | 0 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 302 | 1092 | 0 | 6803 | 13967.1 | 107.88
04:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 14.2 | 0 | 68 | 30 | 0 | 0 | 0 | 16 | 0 | 300 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 66 | 15 | 0 | 12 | 12 | 0 | 220 | 0 | 38 | 635 | 0 | 0 | 0 | 0 | 15 | 220 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 45 | 191 | 34 | 87 | 70 | 164 | 9 | 19 | 114 | 42 | 43 | 0 | 38 | 310 | 0 | 370 | 0 | 60 | 149 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 111 | 58 | 103 | 0 | 0 | 0 | 6989.2 | 916 | 289 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 178 | 0 | 179 | 0 | 404 | 0 | 0 | 153 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 115 | 220 | 0 | 302 | 1090 | 0 | 6611 | 13600.2 | 107.88
05:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 14.8 | 0 | 68 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 23 | 22 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 66 | 15 | 0 | 12 | 12 | 0 | 220 | 0 | 38 | 636 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 853 | 0 | 51 | 0 | 8 | 0 | 353 | 330 | 45 | 195 | 34 | 93 | 70 | 172 | 9 | 19 | 61 | 38 | 43 | 0 | 38 | 310 | 0 | 383 | 0 | 60 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 111 | 57 | 103 | 0 | 0 | 0 | 6951.8 | 916 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 0 | 1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 184 | 0 | 186 | 0 | 414 | 0 | 0 | 153 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 220 | 0 | 302 | 1100 | 0 | 6486 | 13437.8 | 107.88
06:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 15 | 0 | 63 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 52 | 23.5 | 22 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.09 | 220 | 0 | 39 | 633 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 847 | 0 | 51 | 0 | 21 | 0 | 355 | 330 | 45 | 193 | 34 | 92 | 70 | 170 | 8 | 19 | 59 | 38 | 25 | 3 | 38 | 310 | 0 | 385 | 0 | 60 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 112 | 57 | 104 | 0 | 1.14 | 0 | 6749.73 | 916 | 283 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 980 | 0 | 1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 0 | 0 | 0 | 183 | 0 | 184 | 0 | 185 | 0 | 406 | 0 | 0 | 152 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.2 | 3 | 0 | 0 | 168 | 115 | 220 | 0 | 302 | 970 | 0 | 6268.54 | 13018.27 | 107.88
07:00 | 0 | 51 | 2 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 15.2 | 0 | 51 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 250 | 0 | 0 | 5 | 52 | 16 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 25 | 636 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 859 | 0 | 51 | 0 | 26 | 0 | 353 | 330 | 45 | 199 | 34 | 93 | 50 | 136 | 9 | 19 | 43 | 36 | 8 | 25 | 38 | 315 | 0 | 385 | 0 | 60 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 112 | 57 | 105 | 0 | 11.51 | 0 | 6724.71 | 915 | 280 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 961 | 0 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.38 | 3 | 0 | 0 | 16.38 | 187 | 0 | 188 | 0 | 189 | 0 | 414 | 0 | 0.82 | 148 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.6 | 32 | 0.04 | 0 | 170 | 115 | 220 | 0 | 300 | 936 | 0 | 6301.22 | 13025.93 | 107.88
08:00 | 0 | 68 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 14.7 | 0 | 51 | 45 | 0 | 0 | 7 | 0 | 0 | 300 | 290 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 70 | 26.5 | 22 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.03 | 218 | 0 | 13 | 635 | 0 | 0 | 5 | 0 | 0 | 220 | 0 | 0 | 0 | 852 | 10 | 51 | 0 | 26 | 0 | 352 | 330 | 45 | 193 | 34 | 68 | 50 | 100 | 9 | 19 | 47 | 34 | 8 | 33 | 37 | 305 | 0 | 375 | 0 | 60 | 151 | 0 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 111 | 57 | 93 | 1 | 25.71 | 0 | 6769.94 | 916 | 271 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 918 | 0 | 1147.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.41 | 10 | 0 | 0 | 25 | 181 | 0 | 182 | 0 | 186 | 0 | 406 | 0 | 1.56 | 147 | 0 | 35 | 11 | 0 | 0 | 0 | 0 | 2 | 110 | 0.14 | 0 | 169 | 115 | 180 | 0 | 299 | 902 | 0 | 6305.16 | 13075.1 | 107.86
09:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15.4 | 0 | 59 | 45 | 0 | 0 | 18 | 0 | 0 | 300 | 304 | 0 | 0 | 0 | 330 | 0 | 0 | 18 | 52 | 25 | 22 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.08 | 219 | 0 | 4 | 635 | 0 | 0 | 18 | 0 | 0 | 219 | 0 | 0 | 0 | 854 | 13 | 51 | 0 | 26 | 0 | 345 | 330 | 45 | 203 | 38 | 68 | 70 | 95 | 9 | 20 | 47 | 34 | 8 | 54 | 36 | 310 | 0 | 390 | 0 | 60 | 155 | 0 | 0 | 81 | 30 | 0 | 18 | 100 | 0 | 109 | 57 | 92 | 2 | 25.89 | 0 | 6893.37 | 915 | 268 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 907 | 0 | 1113.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.45 | 31 | 0 | 0 | 22 | 186 | 0 | 187 | 0 | 191 | 0 | 414 | 0 | 1.95 | 147 | 0 | 35 | 18 | 0 | 0 | 0 | 0 | 3.9 | 162 | 0.2 | 0 | 169 | 115 | 180 | 0 | 301 | 906 | 0 | 6408.33 | 13301.7 | 107.86
10:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 15.4 | 0 | 86 | 45 | 0 | 0 | 40 | 145 | 0 | 300 | 294 | 0 | 0 | 0 | 327 | 0 | 0 | 31 | 60 | 24.5 | 22 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 4.02 | 220 | 0 | 6 | 635 | 0 | 0 | 30 | 0 | 69 | 219 | 0 | 0 | 0 | 853 | 16 | 51 | 0 | 26 | 0 | 344 | 330 | 43 | 198 | 35 | 89 | 70 | 96 | 9 | 20 | 47 | 38 | 8 | 56 | 36 | 310 | 0 | 390 | 0 | 60 | 155 | 0 | 0 | 81 | 30 | 0 | 18 | 100 | 0 | 109 | 57 | 81 | 1 | 28.35 | 0 | 7181.27 | 916 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 906 | 0 | 894.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.04 | 60 | 0 | 0 | 51.15 | 186 | 0 | 191 | 0 | 200 | 0 | 414 | 0 | 3.73 | 144 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 4.8 | 178 | 0.4 | 0 | 170 | 115 | 180 | 0 | 299 | 980 | 0 | 6321.35 | 13502.62 | 107.89
11:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 40 | 14 | 87 | 45 | 0 | 0 | 55 | 154 | 0 | 300 | 288 | 0 | 0 | 40 | 327 | 0 | 0 | 25 | 70 | 23.5 | 22 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 4.37 | 220 | 0 | 6 | 635 | 0 | 0 | 50 | 0 | 105 | 218 | 0 | 0 | 0 | 880 | 16 | 51 | 6 | 26 | 0 | 347 | 330 | 40 | 192 | 35 | 93 | 70 | 108 | 8 | 20 | 50 | 40 | 8 | 50 | 35 | 320 | 0 | 389 | 0 | 60 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 90 | 57 | 82 | 2 | 19.56 | 0 | 7309.43 | 916 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 941 | 0 | 858.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.98 | 83 | 0 | 0 | 62.52 | 195 | 0 | 186 | 0 | 200 | 0 | 402 | 0 | 5.47 | 144 | 0 | 35 | 27 | 0 | 0 | 100 | 0 | 6.5 | 160 | 0.43 | 0 | 166 | 115 | 220 | 0 | 297 | 1000 | 0 | 6541.61 | 13851.04 | 107.89
12:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 44.8 | 54 | 112 | 75 | 248 | 16 | 55 | 144 | 0 | 300 | 298 | 0 | 0 | 55 | 327 | 0 | 0 | 6 | 70 | 22.8 | 22 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 16 | 39 | 0 | 12 | 12 | 2.14 | 220 | 0 | 7 | 630 | 0 | 0 | 50 | 0 | 94 | 216 | 0 | 0 | 0 | 887 | 13 | 51 | 76 | 26 | 0 | 348 | 330 | 43 | 192 | 34 | 92 | 50 | 140 | 9 | 20 | 52 | 42 | 43 | 75 | 35 | 305 | 0 | 357 | 0 | 58 | 152 | 0 | 0 | 84 | 30 | 0 | 18 | 100 | 0 | 91 | 56 | 70 | 1 | 15.87 | 2 | 7759.61 | 916 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 103 | 994 | 0 | 845.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.44 | 52 | 0 | 0 | 60.82 | 184 | 0 | 168 | 0 | 191 | 0 | 386 | 0 | 2.26 | 137 | 0 | 0 | 22 | 0 | 0 | 50 | 0 | 4.3 | 187 | 0.42 | 0 | 168 | 115 | 220 | 0 | 300 | 1030 | 0 | 6447.84 | 14207.45 | 107.89
13:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 47.7 | 23 | 128 | 75 | 280 | 55 | 54 | 153 | 0 | 300 | 299 | 0 | 0 | 55 | 329 | 0 | 0 | 35 | 70 | 21.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 16 | 53 | 0 | 12 | 12 | 0 | 221 | 0 | 16 | 633 | 0 | 0 | 50 | 0 | 34 | 214 | 0 | 0 | 0 | 860 | 0 | 51 | 110 | 26 | 0 | 345 | 330 | 44 | 193 | 33 | 92 | 50 | 145 | 15 | 20 | 49 | 46 | 43 | 65 | 35 | 315 | 0 | 317 | 0 | 60 | 145 | 0 | 0 | 83 | 30 | 0 | 16 | 30 | 0 | 90 | 56 | 70 | 2 | 50 | 6 | 7762.9 | 915 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1076 | 0 | 865.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.58 | 75 | 0 | 0 | 23.35 | 172 | 0 | 175 | 0 | 173 | 0 | 351 | 0 | 2.29 | 138 | 0 | 35 | 11 | 0 | 0 | 0 | 0 | 7.6 | 144 | 0.21 | 0 | 242 | 115 | 220 | 0 | 300 | 1047 | 0 | 6473.66 | 14236.56 | 107.89
14:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 46 | 17 | 130 | 60 | 225 | 15 | 55 | 146 | 0 | 300 | 300 | 0 | 0 | 55 | 325 | 0 | 0 | 29 | 70 | 23 | 22 | 0 | 315 | 0 | 0 | 0 | 0 | 2 | 16 | 51 | 0 | 12 | 12 | 3.95 | 221 | 0 | 10 | 632 | 0 | 0 | 50 | 0 | 34 | 214 | 0 | 0 | 0 | 900 | 0 | 51 | 115 | 26 | 0 | 341 | 330 | 44 | 201 | 34 | 90 | 50 | 142 | 9 | 19 | 47 | 48 | 43 | 65 | 35 | 310 | 0 | 338 | 0 | 58 | 140 | 0 | 0 | 83 | 30 | 0 | 16 | 30 | 0 | 99 | 56 | 70 | 1 | 48.06 | 6 | 7691.01 | 915 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 93 | 1142 | 0 | 867.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.88 | 67 | 0 | 0 | 28.89 | 166 | 0 | 171 | 0 | 167 | 0 | 372 | 0 | 3.4 | 137 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 6.9 | 108 | 0.71 | 0 | 277 | 115 | 220 | 0 | 300 | 1044 | 0 | 6596.3 | 14287.31 | 107.89
15:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 49.2 | 17 | 130 | 60 | 225 | 15 | 46 | 153 | 0 | 300 | 300 | 0 | 0 | 55 | 326 | 0 | 0 | 10 | 70 | 23 | 22 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 16 | 51 | 0 | 12 | 12 | 2.95 | 222 | 0 | 5 | 632 | 0 | 0 | 50 | 0 | 34 | 213 | 0 | 0 | 0 | 875 | 14 | 51 | 108 | 41 | 0 | 343 | 330 | 43 | 200 | 35 | 90 | 70 | 149 | 8 | 19 | 78 | 46 | 43 | 52 | 35 | 315 | 0 | 362 | 0 | 58 | 149 | 0 | 0 | 83 | 30 | 0 | 16 | 30 | 0 | 100 | 56 | 70 | 1 | 43.88 | 6 | 7732.03 | 915 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75 | 1226 | 0 | 873.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.35 | 65 | 0 | 0 | 45.97 | 171 | 0 | 181 | 0 | 195 | 0 | 405 | 0 | 4.2 | 167 | 0 | 35 | 7 | 0 | 0 | 100 | 0 | 1.9 | 124 | 0.25 | 0 | 276 | 115 | 220 | 0 | 300 | 1042 | 0 | 6814.26 | 14546.29 | 107.89
16:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 47 | 17 | 104 | 60 | 225 | 15 | 55 | 148 | 0 | 300 | 301 | 0 | 0 | 55 | 280 | 0 | 0 | 6 | 70 | 21 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 3 | 16 | 51 | 0 | 12 | 12 | 2.09 | 220 | 0 | 6 | 631 | 0 | 0 | 0 | 0 | 30 | 213 | 0 | 0 | 0 | 900 | 11 | 51 | 108 | 53 | 0 | 320 | 330 | 42 | 200 | 37 | 92 | 70 | 144 | 8 | 19 | 97 | 48 | 42 | 35 | 35 | 310 | 0 | 336 | 0 | 58 | 152 | 0 | 0 | 83 | 30 | 0 | 16 | 66 | 0 | 99 | 56 | 70 | 0 | 26.68 | 3 | 7575.77 | 915 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 1204 | 0 | 887.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.75 | 39 | 0 | 0 | 3.59 | 173 | 0 | 192 | 0 | 191 | 0 | 358 | 0 | 0.76 | 160 | 0 | 35 | 12 | 0 | 0 | 100 | 0 | 2.1 | 94 | 0.15 | 0 | 277 | 115 | 220 | 0 | 300 | 1042 | 0 | 6658.63 | 14234.4 | 107.89
17:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 47.8 | 17 | 95 | 60 | 195 | 15 | 55 | 151 | 0 | 300 | 291 | 0 | 0 | 55 | 280 | 0 | 0 | 2 | 90 | 0 | 22 | 0 | 290 | 0 | 0 | 13 | 0 | 0 | 16 | 51 | 0 | 25 | 12 | 0.94 | 220 | 0 | 6 | 630 | 0 | 0 | 0 | 6 | 33 | 214 | 0 | 0 | 0 | 885 | 3 | 51 | 108 | 53 | 0 | 320 | 330 | 42 | 192 | 37 | 90 | 70 | 147 | 9 | 19 | 100 | 46 | 42 | 14 | 35 | 310 | 0 | 303 | 0 | 58 | 153 | 0 | 0 | 83 | 30 | 0 | 16 | 66 | 0 | 108 | 56 | 70 | 0 | 3.98 | 0 | 7454.72 | 916 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 1183 | 0 | 880.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.75 | 25 | 0 | 0 | 3.87 | 178 | 0 | 192 | 0 | 192 | 0 | 342 | 0 | 0.36 | 149 | 0 | 35 | 8 | 0 | 0 | 100 | 0 | 1.4 | 51 | 0.12 | 0 | 273 | 115 | 220 | 0 | 300 | 1030 | 0 | 6486.46 | 13941.18 | 107.89
18:00 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 26.8 | 17 | 85 | 60 | 195 | 15 | 28 | 102 | 0 | 300 | 300 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 3 | 22 | 0 | 295 | 0 | 0 | 50 | 0 | 0 | 61 | 64 | 0 | 25 | 12 | 0.01 | 219 | 0 | 6 | 632 | 0 | 0 | 0 | 17 | 30 | 214 | 0 | 0 | 0 | 901 | 0 | 51 | 90 | 53 | 0 | 280 | 280 | 42 | 200 | 35 | 82 | 50 | 138 | 8 | 19 | 80 | 44 | 28 | 1 | 35 | 305 | 0 | 336 | 0 | 59 | 143 | 0 | 0 | 83 | 30 | 0 | 16 | 72 | 0 | 109 | 75 | 71 | 0 | 0.66 | 0 | 7306.47 | 916 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1129 | 0 | 888.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0.77 | 3 | 0 | 0 | 0.22 | 160 | 0 | 160 | 0 | 160 | 0 | 364 | 0 | 0.03 | 148 | 0 | 35 | 1 | 0 | 0 | 165 | 0 | 0.3 | 4 | 0.01 | 0 | 198 | 115 | 180 | 0 | 300 | 950 | 0 | 6139.89 | 13446.36 | 107.9
19:00 | 8 | 88 | 17 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 35 | 17 | 125 | 121 | 298 | 30 | 38 | 140 | 0 | 300 | 284 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 290 | 10 | 10 | 78 | 0 | 0 | 66 | 64 | 0 | 25 | 12 | 0 | 219 | 13 | 21 | 632 | 92 | 0 | 0 | 17 | 51 | 214 | 0 | 0 | 0 | 935 | 0 | 51 | 100 | 80 | 0 | 343 | 330 | 43 | 193 | 37 | 91 | 70 | 156 | 8 | 19 | 114 | 52 | 32 | 0 | 29 | 315 | 0 | 364 | 0 | 59 | 152 | 0 | 0 | 83 | 30 | 0 | 18 | 87 | 10 | 109 | 76 | 71 | 0 | 0 | 0 | 8181 | 915 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 17 | 855.67 | 0 | 0 | 0 | 70 | 38 | 0 | 96 | 33 | 43 | 0 | 0 | 28 | 0 | 0 | 183 | 0 | 177 | 0 | 192 | 0 | 406 | 0 | 0 | 148 | 0 | 95 | 0 | 103 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 300 | 982 | 29 | 6881.67 | 15062.67 | 107.9
19:30 | 16 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 43 | 17 | 149 | 124 | 298 | 55 | 55 | 143 | 0 | 330 | 284 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 108 | 22 | 22 | 0 | 290 | 25 | 15 | 95 | 0 | 0 | 66 | 64 | 0 | 25 | 12 | 0 | 180 | 48 | 25 | 632 | 88 | 0 | 1 | 17 | 90 | 214 | 0 | 0 | 0 | 925 | 0 | 51 | 108 | 80 | 0 | 330 | 330 | 43 | 184 | 37 | 93 | 70 | 183 | 0 | 19 | 114 | 52 | 43 | 0 | 29 | 310 | 0 | 362 | 0 | 60 | 144 | 0 | 0 | 83 | 30 | 0 | 18 | 97 | 35 | 110 | 76 | 71 | 0 | 0 | 0 | 8393 | 915 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1154 | 17 | 1132.87 | 0 | 35 | 0 | 108 | 70 | 0 | 96 | 35 | 52.2 | 0 | 0 | 28 | 0 | 0 | 205 | 0 | 192 | 0 | 190 | 0 | 335 | 0 | 0 | 148 | 0 | 114 | 0 | 108 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 266 | 115 | 180 | 0 | 300 | 1030 | 81 | 7319.07 | 15712.07
20:00 | 0 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 44.1 | 17 | 149 | 123 | 298 | 30 | 55 | 143 | 0 | 330 | 289 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 295 | 38 | 0 | 94 | 0 | 0 | 66 | 64 | 0 | 25 | 12 | 0 | 180 | 50 | 29 | 632 | 46 | 0 | 3 | 17 | 90 | 214 | 0 | 0 | 0 | 927 | 0 | 51 | 108 | 81 | 0 | 320 | 330 | 43 | 193 | 37 | 92 | 70 | 181 | 0 | 19 | 114 | 52 | 43 | 0 | 30 | 300 | 0 | 370 | 0 | 60 | 140 | 0 | 0 | 83 | 30 | 0 | 18 | 97 | 35 | 101 | 76 | 71 | 0 | 0 | 0 | 8335.1 | 915 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 17 | 1134.11 | 0 | 40 | 0 | 35 | 70 | 0 | 96 | 39 | 25 | 0 | 0 | 28 | 0 | 0 | 205 | 0 | 191 | 0 | 191 | 0 | 343 | 0 | 0 | 149 | 0 | 114 | 0 | 108 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 274 | 115 | 180 | 0 | 301 | 1020 | 81 | 7256.11 | 15591.21 | 107.9
21:00 | 0 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 46 | 17 | 149 | 123 | 298 | 15 | 55 | 145 | 0 | 360 | 292 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 294 | 0 | 0 | 92 | 0 | 0 | 55 | 64 | 0 | 25 | 12 | 0 | 179 | 49 | 0 | 632 | 17 | 0 | 0 | 17 | 96 | 214 | 0 | 0 | 0 | 940 | 0 | 51 | 118 | 132 | 0 | 345 | 330 | 43 | 196 | 38 | 94 | 70 | 185 | 0 | 19 | 114 | 50 | 43 | 0 | 28 | 305 | 0 | 383 | 0 | 60 | 147 | 0 | 0 | 83 | 30 | 0 | 18 | 112 | 35 | 110 | 76 | 82 | 0 | 0 | 0 | 8434 | 915 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 17 | 1126.26 | 0 | 40 | 0 | 0 | 70 | 0 | 96 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 205 | 0 | 191 | 0 | 190 | 0 | 407 | 0 | 0 | 150 | 0 | 114 | 0 | 110 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 301 | 1042 | 100 | 7341.26 | 15775.26 | 107.9
22:00 | 0 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 46 | 17 | 149 | 123 | 298 | 15 | 55 | 147 | 0 | 360 | 289 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 293 | 0 | 0 | 70 | 0 | 0 | 66 | 66 | 0 | 25 | 12 | 0 | 219 | 48 | 34 | 632 | 15 | 0 | 1 | 17 | 95 | 218 | 0 | 0 | 0 | 920 | 0 | 51 | 123 | 137 | 0 | 347 | 330 | 44 | 194 | 38 | 93 | 50 | 181 | 0 | 19 | 114 | 48 | 43 | 0 | 35 | 310 | 0 | 364 | 0 | 60 | 152 | 0 | 0 | 84 | 30 | 0 | 18 | 131 | 31 | 110 | 76 | 82 | 0 | 0 | 0 | 8469 | 916 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 17 | 1133.82 | 0 | 40 | 0 | 0 | 70 | 0 | 96 | 38 | 0 | 0 | 0 | 28 | 0 | 0 | 202 | 0 | 186 | 0 | 189 | 0 | 401 | 0 | 0 | 152 | 0 | 114 | 0 | 106 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 301 | 1042 | 118 | 7339.82 | 15808.82 | 107.91
23:00 | 0 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 45.3 | 17 | 149 | 123 | 297 | 15 | 55 | 146 | 0 | 360 | 296 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 306 | 0 | 0 | 69 | 0 | 0 | 66 | 60 | 0 | 25 | 12 | 0 | 219 | 50 | 34 | 630 | 17 | 0 | 24 | 17 | 93 | 218 | 0 | 0 | 0 | 942 | 0 | 51 | 117 | 8 | 0 | 345 | 330 | 44 | 205 | 38 | 92 | 70 | 181 | 0 | 19 | 114 | 48 | 43 | 0 | 35 | 310 | 0 | 392 | 0 | 60 | 153 | 0 | 0 | 84 | 30 | 0 | 18 | 140 | 17 | 110 | 76 | 80 | 0 | 0 | 0 | 8442.3 | 916 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1183 | 17 | 1133.31 | 0 | 40 | 0 | 0 | 70 | 0 | 96 | 38 | 0 | 0 | 0 | 27 | 0 | 0 | 200 | 0 | 184 | 0 | 188 | 0 | 414 | 0 | 0 | 152 | 0 | 114 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 301 | 1042 | 140 | 7315.31 | 15757.61 | 107.91
Total KWH | 21146 | 1687680 | 444000 | 0 | 0 | 0 | 0 | 0 | 8391600 | 0 | 0 | 829908 | 291600 | 2555856 | 1587840 | 3483371 | 314127 | 794631 | 2550240 | 0 | 7931000 | 7105076 | 0 | 0 | 665453 | 7230576 | 0 | 0 | 182634 | 2072400 | 499800 | 493920 | 0 | 7871818.18 | 87818 | 20073 | 565440 | 0 | 6720 | 869436 | 923724 | 0 | 376320 | 298560 | 23762 | 5225933 | 412300 | 459840 | 15316363.67 | 204073 | 0 | 467520 | 127152 | 1344036 | 5217811 | 0 | 0 | 0 | 21174543 | 98280 | 1199352 | 1657672 | 903272 | 0 | 8548100 | 7954000 | 1046400 | 4773000 | 854208 | 2110080 | 1458300 | 3645600 | 177240 | 444640 | 2032620 | 1043520 | 821928 | 515827 | 848384 | 7544000 | 0 | 9149000 | 0 | 1399120 | 3630027 | 53232 | 0 | 1996800 | 712896 | 0 | 445000 | 2866070 | 170640 | 2533200 | 1495200 | 1956480 | 12800 | 299940 | 24240 | 184547168.85 | 22176727 | 5992416 | 0 | 0 | 0 | 916000 | 0 | 0 | 0 | 0 | 0 | 681120 | 26189090 | 120000 | 24919463 | 0 | 243526 | 0 | 163296 | 434496 | 0 | 622752 | 230962 | 64282 | 289837 | 514649 | 176340 | 0 | 317248 | 4520545 | 0 | 4606045 | 0 | 4722909 | 0 | 9464290 | 0 | 26580 | 3664000 | 0 | 1467567 | 205140 | 1065561 | 0 | 1366785 | 0 | 44258.16 | 1392480 | 3667 | 20928 | 5651000 | 2759000 | 5324980 | 0 | 7199280 | 24949818.18 | 578400 | 163085437.34 | 347632606.19

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-08-2025 | during | 01-09-2025 | during | 01-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 326 | 335 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 360 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 292 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 16 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 44.8 | 46 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 75 | 123 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.8 | 23 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 248 | 298 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 68 | 103 | 105 | 105 | 70 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 144 | 145 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 17 | 55 | 55 | 35 | 35 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 295 | 294 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2563.6 | 2745 | 5815.84 | 5780.84 | 3853.92 | 3818.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 179 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 214 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 94 | 96 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 39 | 64 | 48 | 70 | 48 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 55 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 0 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 92 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.14 | 0 | 1.34 | 0 | 1.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 49 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 887 | 940 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 20 | 1 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 630 | 632 | 635 | 635 | 635 | 635 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2198.14 | 2392 | 3648.06 | 3697.72 | 3472.06 | 3534.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 192 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 348 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 38 | 46.7 | 46.7 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 43 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 132 | 195 | 195 | 157 | 157 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 76 | 118 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 28 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 140 | 185 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 50 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 92 | 94 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 75 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1658 | 1856 | 2435.86 | 2370.86 | 2143.66 | 2078.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-08-2025 | during | 01-09-2025 | during | 01-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 70 | 82 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 76 | 55 | 75 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 91 | 110 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.87 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 2 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 235.87 | 303 | 450.2 | 418 | 396.7 | 364.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 60 | 70 | 70 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 83 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 112 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 383 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1104 | 1138 | 1218 | 1218 | 1113 | 1113
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 236 | 204 | 410 | 410 | 394 | 394 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 103 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 994 | 1184 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2287 | 2358 | 3644.2 | 3552.2 | 3450.2 | 3358.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 301 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1030 | 1042 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 168 | 275 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.42 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1833.42 | 2053 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 37.44 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 184 | 205 | 214 | 214 | 195 | 195 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 191 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 386 | 407 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.26 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 845.6 | 1126.26 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.82 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 52 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1927.12 | 2391.26 | 3190.47 | 3023.87 | 3097.68 | 2931.08
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 50 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 137 | 150 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.3 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 187 | 0 | 182.71 | 0 | 182.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 400.3 | 539 | 631.31 | 412 | 631.31 | 412
System Total |  |  |  |  | 28823.2 | 27829.875 | 14207.45 | 15775.26 | 23195.94 | 22634.49 | 20305.53 | 19757.08
Forecast Scenario (01-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15670 |  | 0 |  | 15670
|  |  |  | 1:00 | 15330 |  | 0 |  | 15330
|  |  |  | 2:00 | 14740 |  | 0 |  | 14740
|  |  |  | 3:00 | 14360 |  | 0 |  | 14360
|  |  |  | 4:00 | 14000 |  | 0 |  | 14000
|  |  |  | 5:00 | 13830 |  | 0 |  | 13830
|  |  |  | 6:00 | 13410 |  | 0 |  | 13410
|  |  |  | 7:00 | 13420 |  | 0 |  | 13420
|  |  |  | 8:00 | 13470 |  | 0 |  | 13470
|  |  |  | 9:00 | 13700 |  | 0 |  | 13700
|  |  |  | 10:00 | 13900 |  | 0 |  | 13900
|  |  |  | 11:00 | 14250 |  | 0 |  | 14250
|  |  |  | 12:00 | 14600 |  | 0 |  | 14600
|  |  |  | 13:00 | 14630 |  | 0 |  | 14630
|  |  |  | 14:00 | 14680 |  | 0 |  | 14680
|  |  |  | 15:00 | 14940 |  | 0 |  | 14940
|  |  |  | 16:00 | 14630 |  | 0 |  | 14630
|  |  |  | 17:00 | 14340 |  | 0 |  | 14340
|  |  |  | 18:00 | 13840 |  | 0 |  | 13840
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15580 |  | 0 |  | 15580
|  |  |  | 19:30 | 16200 |  | 0 |  | 16200
|  |  |  | 20:00 | 16040 |  | 0 |  | 16040
|  |  |  | 21:00 | 16220 |  | 0 |  | 16220
|  |  |  | 22:00 | 16200 |  | 0 |  | 16200
|  |  |  | 23:00 | 16100 |  | 0 |  | 16100
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 14600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16220.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16220.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 351.88 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:08 hrs on 01-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14207.45 | MW | 12:00 Hr. | Energy Generated |  |  | 347.6326 |  | MKWHr.
| Day Peak Demand |  |  | 14207.45 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.294 |  | MKWHr.
| Evening Peak Generation |  |  | 15775.26 | MW | 21:00 Hr. | Energy Demand |  |  | 347.9266 |  | MKWHr.
| Evening Peak Demand |  |  | 15825.42 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 13018.27 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1006.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 15808.82 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.5406 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.5238 | 0 | 17.2983 | 0 | 0 | 0.18263 | 0 | 0 | 57.0047 | Gas | 139.5255 | Gas | 501385252.8406
| Chattogram Zone |  |  | 5.6777 | 36.4909 | 5.6965 | 0 | 5.2259 | 0.12204 | 0 | 0.00672 | 53.2197 | Coal | 104.1441 | Coal | 615036738.141
| Cumilla Zone |  |  | 27.1813 | 0 | 11.2935 | 0 | 0 | 0.51583 | 1.0435 | 0 | 40.0341 | HFO | 43.6996 | HFO | 801514498.72
| Mymensingh Zone |  |  | 1.9565 | 0 | 4.2233 | 0 | 0 | 0.31274 | 0 | 0 | 6.4925 | HSD | 1.3668 | HSD | 0
| Sylhet Zone |  |  | 27.7961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7961 | Hydro | 5.2259 | Hydro | 522593.3
| Khulna Zone |  |  | 5.9924 | 26.1891 | 0.12 | 0 | 0 | 0.68112 | 23.0927 | 0 | 56.0754 | Solar | 4.6082 | Solar | 71150413.9236
| Barishal Zone |  |  | 8.084 | 37.8001 | 0.59933 | 0 | 0 | 0.003667 | 0 | 0 | 46.4871 | Import | 49.0557 | Import | 284018362.36
| Rajshahi Zone |  |  | 23.3138 | 0 | 1.9357 | 0 | 0 | 1.1483 | 24.9195 | 0 | 51.3172 | Wind | 0.00672 | Wind | 99052.8
| Rangpur Zone |  |  | 0 | 3.664 | 2.5331 | 1.3668 | 0 | 1.6419 | 0 | 0 | 9.2058
| Total |  |  | 139.5255 | 104.1441 | 43.6996 | 1.3668 | 5.2259 | 4.6082 | 49.0557 | 0.00672 | 347.6326
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 501385252.8406 |  | Hydro | 522593.3
|  |  |  | Coal | 615036738.141 |  | Solar | 71150413.9236
|  |  |  | HFO | 801514498.72 |  | Import | 284018362.36
|  |  |  | HSD | 0 |  | Wind | 99052.8
[5 empty] | Total: | 227,37,26,912 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1767 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48047127.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.9195 | Peak Hr Flow | 1126.26 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2066 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0435 | Peak Hr Flow | 50.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2642 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.1397 | Peak Hr Flow | 2091.26 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 7 |  | 5267
|  |  |  | Chattogram |  | 0 |  | 1440
|  |  |  | Cumilla |  | 11 |  | 1477
|  |  |  | Mymensingh |  | 30 |  | 1267
|  |  |  | Sylhet |  | 0 |  | 705
|  |  |  | Khulna |  | 0 |  | 1925
|  |  |  | Barishal |  | 0 |  | 458
|  |  |  | Rajshahi |  | 0 |  | 1594
|  |  |  | Rangpur |  | 0 |  | 1093
|  |  |  | Total |  | 48 |  | 15226
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Chowmuhani 113 MW |  |  | 113
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 513
|  |  |  | Total Unavailable Capacity |  |  |  | 813
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:32 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
|  | 08:33 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
| 08:35 | 09:40 | BIPTC S/S 10CF26 Forced S/D Due to Shutdown is taken for emergency maintenance work
|  | 08:45 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt is restored.
| 09:10 | 23:48 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to Distance
Relay Maintenance
|  | 09:34 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 09:35 | Khulna (C) S/S TR-1 425T LT is restored.
| 10:26 | 20:10 | BIPTC S/S Baharampur-4 Forced S/D Due to Shutdown is taken from Baharampur end
|  | 10:34 | Gopalganj 132/33kV S/S T2 HT is restored.
|  | 10:35 | Gopalganj 132/33kV S/S T2 LT is restored.
| 11:15 | 13:15 | Khulna (C) S/S Tr-3 405T LT Forced S/D Due to Wz work purpose
| 11:16 | 13:12 | Khulna (C) S/S Tr-3 405T HT Forced S/D Due to Wz work purpose
| 13:13 | 13:36 | Chowmuhani-Feni 132 kV Ckt-2 Tripped from Feni 132/33kV end showing Alstom relays. and
from Chowmuhani 132/33kV end showing Distance Relay Trip A,B,C Distance Relay Trip
3PH Zone-2 Fault relays Due to Distance Relay Trip A,B,C Distance Relay Trip
3PH Zone-2 Fault
| 14:01 |  | system normal, shift charge received
| 14:13 | 14:28 | Chowmuhani-Feni 132 kV Ckt-2 Tripped from Chowmuhani 132/33kV end showing Distance Relay
Trip relays Due to Distance Relay Tripped
| 14:29 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Due to low gas pressure.
| 15:24 | 16:34 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 18:09 | 19:56 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Red Hot maintenance of TR-3 33 kV | [7 empty] | 20.0MW load
|  |  | Bus section loop point | [7 empty] | interrup.
| 18:09 | 19:57 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Red Hot maintenance of TR-3, 33 kV | [7 empty] | 20.0MW load
|  |  | Bus section loop point | [7 empty] | interrup.
| 18:10 | 19:55 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Red Hot maintenance of TR-3,33 kV | [7 empty] | 50.0MW load
|  |  | Bus section loop point. | [7 empty] | interrup.
| 18:10 | 19:55 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Red Hot maintenance of TR-3, 33 kV | [7 empty] | 50.0MW load
|  |  | Bus section loop point | [7 empty] | interrup.
| 20:24 | 21:36 | Coxsbazar 132/33kV S/S 405T-T1 LT Tripped showing MCGG relays Due to Over current | [7 empty] | 36.0MW load
interrup.
| 21:00 |  | Evening peak Generation is 15775 MW
| 05:44 |  | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to For red hot at 33 kV isolator (DS).
| 05:45 | 08:00 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to for red hot at 33kV isolator (DS).
| 06:00 |  | Minimum Generation: 13384 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 335 | 8391600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 7931000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 292 | 7105076 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 314127 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7230576 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 21146 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46 | 829908 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 1587840 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 794631 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 665453 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 499800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 493920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 444000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 298 | 3483371 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2555856 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 103 | 1687680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 2550240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 182634 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 291600 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 294 | 7871818.18 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2072400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2745 | 57004676.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 127152 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 98280 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 467520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 179 | 5225933 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5217811 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 96 | 1344036 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 64 | 923724 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 55 | 869436 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 376320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 459840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 565440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 20073 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 412300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 298560 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 87818 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 204073 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 940 | 21174543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 6720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 632 | 15316363.67 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2392 | 53219704.67
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4773000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8548100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7954000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 854208 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 1046400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 132 | 903272 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1199352 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 118 | 1657672 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 848384 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1458300 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 185 | 3645600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 50 | 1043520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 821928 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 444640 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2032620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 177240 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 2110080 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 515827 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1856 | 40034143
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 82 | 1956480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 1495200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 110 | 2533200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 299940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 24240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 170640 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 303 | 6492500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1399120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3630027 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 712896 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1996800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 112 | 2866070 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 445000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 53232 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7544000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 9149000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1138 | 27796145
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 22176727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 204 | 5992416 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 120000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 681120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1184 | 26189090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 916000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2358 | 56075353
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7199280 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 20928 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2759000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1042 | 24949818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5324980 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 578400 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 5651000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3667 | -
Barishal Area Total |  |  |  |  | 2236 | 2053 | 46487073.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 289837 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 243526 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 230962 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 205 | 4520545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4606045 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4722909 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 407 | 9464290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 176340 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 64282 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 622752 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 434496 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 163296 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1126.26 | 24919463 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 317248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 514649 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2391.26 | 51317220
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 165 | 1366785 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3664000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 1065561 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44258.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1467567 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 205140 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1392480 | -
Rangpur Area Total |  |  |  |  | 950 | 539 | 9205791.16
Eastern Grid Total |  |  |  |  | 17385.715 | 8434 | 184547168.85
Western Grid Total |  |  |  |  | 10444.16 | 7341.26 | 163085437.34
National Grid Total |  |  |  |  | 27829.875 | 15775.26 | 347632606.19
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-08-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10108.49 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5069.9 | MW
i) Dhaka area |  |  | 5260.22 |  | MW | i) Khulna area |  |  |  | 1925 | MW
ii) Chattogram area |  |  | 1440.5 |  | MW | ii) Barishal area |  |  |  | 457.5 | MW
iii) Cumilla area |  |  | 1465.77 |  | MW | iii) Rajshahi area |  |  |  | 1594.4 | MW
iv) Mymensingh area |  |  | 1237 |  | MW | iv) Rangpur area |  |  |  | 1093 | MW
v) Sylhet area |  |  | 705 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15178.39 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 87 | 19:00 | 133 | PHP | 8 | 04:00
2 | AKSML | 118 | 14:00 | 68 | Ishurdi | 84 | 19:30 | 134 | Pabna | 133 | 19:30
3 | Aftabnagar | 40 | 18:30 | 69 | Jaldhaka | 94 | 19:00 | 135 | Palashbari | 130 | 19:00
4 | Agargaon | 132 | 11:00 | 70 | Jamalpur | 132 | 07:00 | 136 | Panchagarh | 68 | 19:00
5 | Agrabad | 98 | 17:00 | 71 | Jashore | 152 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 142 | 19:00 | 138 | Patuakhali | 72 | 22:00
7 | Ashuganj | 80 | 14:00 | 73 | Joydebpur | 158 | 12:00 | 139 | Payra | 34 | 00:00
8 | BSRM | 189 | 03:00 | 74 | Joypurhat | 66 | 21:00 | 140 | Postogola | 56 | 13:00
9 | Bagerhat | 86 | 19:00 | 75 | Juldah | 18 | 18:30 | 141 | Purbachal | 22 | 23:00
10 | Bajitpur | 96 | 18:30 | 76 | KSRM | 24 | 19:30 | 142 | Purbasadipur | 127 | 19:30
11 | Bakulia | 98 | 19:00 | 77 | Kabirpur | 262 | 12:00 | 143 | Rahanpur | 40 | 00:00
12 | Banani | 51.6 | 11:00 | 78 | Kachua | 102 | 22:00 | 144 | Rahim | 44 | 14:00
13 | Bangabhaban | 25 | 10:00 | 79 | Kallyanpur | 102 | 20:00 | 145 | Rajbari | 88 | 19:00
14 | Barapukuria | 68 | 21:00 | 80 | Kalurghat | 42 | 11:00 | 146 | Rajendrapur | 140 | 19:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 75 | 18:30 | 147 | Rajshahi | 112 | 00:00
16 | Barishal | 102 | 23:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 98 | 00:00
17 | Barishal-230 | 102 | 19:30 | 83 | Kasba | 39 | 21:00 | 149 | Ramganj | 120 | 18:30
18 | Baroaulia | 73 | 14:00 | 84 | Kazla | 92 | 00:00 | 150 | Rampur | 43 | 23:00
19 | Baroirhat | 67 | 18:30 | 85 | Keranigonj | 83 | 19:00 | 151 | Rangamati | 18 | 18:30
20 | Bashundhara | 203 | 12:00 | 86 | Khagrachori | 34 | 18:30 | 152 | Rangpur | 159 | 19:30
21 | BashundharaCement | 3 | 10:00 | 87 | Khulna | 69 | 19:00 | 153 | Ruppur | 8.2 | 10:00
22 | Beanibazar | 82 | 20:00 | 88 | Khulshi | 188 | 14:00 | 154 | SSM | 1 | 23:00
23 | Benapole | 68 | 22:00 | 89 | Kishoreganj | 136 | 21:00 | 155 | Saidpur | 113 | 19:00
24 | Bhaluka | 154 | 16:00 | 90 | Kodda | 305 | 16:00 | 156 | Satkhira | 133 | 22:00
25 | Bhandaria | 62 | 00:00 | 91 | Kulaura | 58 | 18:00 | 157 | Satmasjid | 98 | 19:00
26 | Bhangura | 40 | 18:30 | 92 | Kurigram | 74 | 19:00 | 158 | Savar | 223 | 11:00
27 | Bheramara(GK) | 72 | 22:00 | 93 | Kushtia | 168 | 19:00 | 159 | SevenRings | 9.13 | 16:00
28 | Bhulta | 209 | 12:00 | 94 | Laksam | 36 | 22:00 | 160 | ShahCement | 37 | 00:00
29 | Bog-Sherpur | 80 | 00:00 | 95 | Lakshmipur | 33 | 00:00 | 161 | Shahjadpur | 91 | 20:00
30 | Bogura | 173 | 20:00 | 96 | Lalbag | 61 | 13:00 | 162 | Shahjibazar | 142 | 22:00
31 | Borhanuddin | 93 | 23:00 | 97 | Lalmonirhat | 74 | 19:00 | 163 | Shahmirpur | 69 | 00:00
32 | Brahmanbaria | 145 | 20:00 | 98 | MI_Cement | 16.7 | 11:00 | 164 | Shariatpur | 95 | 22:00
33 | Cantonment | 136 | 13:00 | 99 | Madanganj | 32 | 00:00 | 165 | Sherpur | 154 | 20:00
34 | Chandina | 16.94 | 20:00 | 100 | Madaripur | 127 | 22:00 | 166 | Shikalbaha | 14 | 01:00
35 | Chandpur | 100 | 05:00 | 101 | Madartek | 97.01 | 23:00 | 167 | Shitalakhya | 77.8 | 12:00
36 | Chandraghona | 38 | 19:00 | 102 | Madunaghat | 57 | 19:30 | 168 | Sholosohor | 46 | 18:30
37 | Chapai | 69 | 22:00 | 103 | Magura | 72 | 19:30 | 169 | Shyampur | 162 | 09:00
38 | Charsaidpur | 40 | 19:00 | 104 | Mahasthangarh | 82 | 00:00 | 170 | Siddhirganj | 124 | 12:00
39 | Chauddagram | 78 | 22:00 | 105 | Maijdee | 21 | 00:00 | 171 | Sirajganj | 120 | 19:00
40 | Chhatak | 43 | 21:00 | 106 | Manikganj | 131 | 22:00 | 172 | Sonargaon | 138 | 00:00
41 | Chowmuhani | 176 | 19:00 | 107 | Maniknagar | 40 | 00:00 | 173 | Sreemongol | 91 | 22:00
42 | Chuadanga | 126 | 19:00 | 108 | Matarbari | 55 | 19:00 | 174 | Sreepur | 99 | 16:00
43 | Coxsbazar | 132 | 18:30 | 109 | Matuail | 73 | 12:00 | 175 | Srinagar | 48 | 22:00
44 | Cumilla(N) | 147 | 00:00 | 110 | Millgate | 131 | 12:00 | 176 | Sunamganj | 64 | 21:00
45 | Cumilla(S) | 159 | 18:30 | 111 | Mirpur | 123 | 12:00 | 177 | Sylhet | 60 | 18:30
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 11:00 | 178 | Sylhet-132 | 127 | 18:30
47 | Daudkandi | 159 | 21:00 | 113 | Mirzapur | 48 | 01:00 | 179 | TK | 36 | 19:00
48 | Dhaka | 112 | 11:00 | 114 | Mithapukur | 80 | 19:00 | 180 | Tangail | 170 | 18:30
49 | Dhamrai | 128 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:00
50 | Dhanmondi | 131 | 14:00 | 116 | Mogbazar | 107.7 | 11:00 | 182 | Thakurgaon | 118 | 19:30
51 | Dohazari | 119 | 19:00 | 117 | Mongla | 51 | 12:00 | 183 | Tongi | 109 | 11:00
52 | Faridpur | 182 | 22:00 | 118 | Motijheel | 44 | 11:00 | 184 | Ullahpara | 42 | 19:00
53 | Fatullah | 106 | 15:00 | 119 | Muktagacha | 38 | 20:00 | 185 | Ullon | 58 | 20:00
54 | Fenchuganj | 53 | 20:00 | 120 | Munshiganj | 115 | 00:00 | 186 | Uttara | 83 | 13:00
55 | Feni | 124 | 19:30 | 121 | Muradnagar | 39 | 00:00 | 187 | UttaraNew | 62 | 23:00
56 | GPH | 79 | 18:00 | 122 | Mymensingh | 217 | 20:00 | 188 | Zigatola | 70 | 14:00
57 | Ghatail | 86 | 22:00 | 123 | Naogaon | 144 | 23:00
58 | Ghorashal | 14 | 00:00 | 124 | Narail | 65 | 19:00
59 | Ghorashal-230 | 97 | 21:00 | 125 | Narinda | 74 | 17:00
60 | Goalpara | 42 | 00:00 | 126 | Narshingdi | 190 | 00:00
61 | Gollamari | 102 | 13:00 | 127 | Natore | 156 | 19:00
62 | Gopalganj | 116 | 22:00 | 128 | Nawabganj | 61.2 | 22:00
63 | Gulshan | 124 | 11:00 | 129 | Netrakona | 148 | 22:00
64 | Halishahar | 71 | 15:00 | 130 | New | 76 | 12:00
65 | HaripurSBU | 164 | 15:00 | 131 | Niamatpur | 80 | 21:00
66 | Hasnabad | 86 | 12:00 | 132 | Noapara | 47 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15276.6 | 0 |  | 15276.6
1:00 | 14938.1 | 0 |  | 14938.1
2:00 | 14340.2 | 0 |  | 14340.2
3:00 | 13967.1 | 0 |  | 13967.1
4:00 | 13600.2 | 0 |  | 13600.2
5:00 | 13437.8 | 0 |  | 13437.8
6:00 | 13018.27 | 0 |  | 13018.27
7:00 | 13025.93 | 0 |  | 13025.93
8:00 | 13075.1 | 0 |  | 13075.1
9:00 | 13301.7 | 0 |  | 13301.7
10:00 | 13502.62 | 0 |  | 13502.62
11:00 | 13851.04 | 0 |  | 13851.04
12:00 | 14207.45 | 0 |  | 14207.45
13:00 | 14236.56 | 0 |  | 14236.56
14:00 | 14287.31 | 0 |  | 14287.31
15:00 | 14546.29 | 0 |  | 14546.29
16:00 | 14234.4 | 0 |  | 14234.4
17:00 | 13941.18 | 0 |  | 13941.18
18:00 | 13446.36 | 0 |  | 13446.36
19:00 | 15062.67 | 113 |  | 15180.76
19:30 | 15712.07 | 90 |  | 15806.12
20:00 | 15591.21 | 52 |  | 15645.55
21:00 | 15775.26 | 48 |  | 15825.42
22:00 | 15808.82 | 40 |  | 15850.82
23:00 | 15757.61 | 41 |  | 15800.61
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7962.6 | 7314 | 15276.6 | DAILY GENERATION CURVE
00:30 | 7893.35 | 7214 | 15107.35
01:00 | 7824.1 | 7114 | 14938.1 | 31-08-2025
01:30 | 7650.15 | 6989 | 14639.15
02:00 | 7476.2 | 6864 | 14340.2
02:30 | 7320.15 | 6833.5 | 14153.65
03:00 | 7164.1 | 6803 | 13967.1
03:30 | 7076.65 | 6707 | 13783.65
04:00 | 6989.2 | 6611 | 13600.2
04:30 | 6970.5 | 6548.5 | 13519
05:00 | 6951.8 | 6486 | 13437.8
05:30 | 6850.765 | 6377.27 | 13228.035
06:00 | 6749.73 | 6268.54 | 13018.27
06:30 | 6737.22 | 6284.88 | 13022.1
07:00 | 6724.71 | 6301.22 | 13025.93
07:30 | 6747.325 | 6303.19 | 13050.515
08:00 | 6769.94 | 6305.16 | 13075.1
08:30 | 6831.655 | 6356.745 | 13188.4
09:00 | 6893.37 | 6408.33 | 13301.7
09:30 | 7037.32 | 6364.84 | 13402.16
10:00 | 7181.27 | 6321.35 | 13502.62
10:30 | 7245.35 | 6431.48 | 13676.83
11:00 | 7309.43 | 6541.61 | 13851.04
11:30 | 7534.52 | 6494.725 | 14029.245
12:00 | 7759.61 | 6447.84 | 14207.45
12:30 | 7761.255 | 6460.75 | 14222.005
13:00 | 7762.9 | 6473.66 | 14236.56
13:30 | 7726.955 | 6534.98 | 14261.935
14:00 | 7691.01 | 6596.3 | 14287.31
14:30 | 7711.52 | 6705.28 | 14416.8
15:00 | 7732.03 | 6814.26 | 14546.29
15:30 | 7653.9 | 6736.445 | 14390.345
16:00 | 7575.77 | 6658.63 | 14234.4
16:30 | 7515.245 | 6572.545 | 14087.79
17:00 | 7454.72 | 6486.46 | 13941.18
17:30 | 7380.595 | 6313.175 | 13693.77
18:00 | 7306.47 | 6139.89 | 13446.36
18:30 | 7743.735 | 6510.78 | 14254.515
19:00 | 8181 | 6881.67 | 15062.67
19:30 | 8393 | 7319.07 | 15712.07
20:00 | 8335.1 | 7256.11 | 15591.21
20:30 | 8384.55 | 7298.685 | 15683.235 |  | Executive Engineer
21:00 | 8434 | 7341.26 | 15775.26 |  | Network Operation Division
21:30 | 8451.5 | 7340.54 | 15792.04
22:00 | 8469 | 7339.82 | 15808.82
22:30 | 8455.65 | 7327.565 | 15783.215
23:00 | 8442.3 | 7315.31 | 15757.61

## En-Curve
QF-LDC-12
Date | 31-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3901 | 1958 | 916 | 38 | 46 | 1153 | 222 | 4623 | 0 | 664 | 1751.6 | 0 | 0 | 4 | 0 | DAILY ENERGY CURVE
00:30 | 3906 | 1949 | 915.5 | 38 | 46 | 1153.5 | 222 | 4551.5 | 0 | 624 | 1699.85 | 0 | 0 | 2 | 0 | 31-08-2025
01:00 | 3911 | 1940 | 915 | 38 | 46 | 1154 | 222 | 4480 | 0 | 584 | 1648.1 | 0 | 0 | 0 | 0
01:30 | 3905.5 | 1941 | 915 | 38 | 45 | 1146 | 222 | 4461.5 | 0 | 472 | 1493.15 | 0 | 0 | 0 | 0 | Energy Generated | 347.6326 |  | MKWHr
02:00 | 3900 | 1942 | 915 | 38 | 44 | 1138 | 222 | 4443 | 0 | 360 | 1338.2 | 0 | 0 | 0 | 0 | Energy not Served | 0.294 |  | MKWHr
02:30 | 3884.5 | 1943.5 | 915 | 38 | 43 | 1141.5 | 222 | 4445.5 | 0 | 344.5 | 1176.15 | 0 | 0 | 0 | 0 | Total Energy Requirement | 347.9266 |  | MKWHr
03:00 | 3869 | 1945 | 915 | 38 | 42 | 1145 | 222 | 4448 | 0 | 329 | 1014.1 | 0 | 0 | 0 | 0
03:30 | 3884 | 1920 | 915.5 | 38 | 42 | 1146.5 | 221 | 4404.5 | 0 | 309 | 903.15 | 0 | 0 | 0 | 0
04:00 | 3899 | 1895 | 916 | 38 | 42 | 1148 | 220 | 4361 | 0 | 289 | 792.2 | 0 | 0 | 0 | 0
04:30 | 3927.5 | 1905 | 916 | 38 | 40 | 1145.5 | 220 | 4291 | 0 | 279 | 757 | 0 | 0 | 0 | 0
05:00 | 3956 | 1915 | 916 | 38 | 38 | 1143 | 220 | 4221 | 0 | 269 | 721.8 | 0 | 0 | 0 | 0
05:30 | 3907.5 | 1922.25 | 916 | 38 | 38 | 1144.5 | 220 | 4136.5 | 4.385 | 219.5 | 681.4 | 0 | 0 | 0 | 0
06:00 | 3859 | 1929.5 | 916 | 38 | 38 | 1146 | 220 | 4052 | 8.77 | 170 | 641 | 0 | 0 | 0 | 0
06:30 | 3865.5 | 1924.25 | 915.5 | 38 | 37 | 1149.5 | 219 | 4031 | 68.75 | 179 | 594.6 | 0 | 0 | 0 | 0
07:00 | 3872 | 1919 | 915 | 38 | 36 | 1153 | 218 | 4010 | 128.73 | 188 | 548.2 | 0 | 0 | 0 | 0
07:30 | 3874 | 1884.25 | 915.5 | 38 | 35 | 1150.025 | 218 | 3966 | 215.29 | 212 | 542.45 | 0 | 0 | 0 | 0
08:00 | 3876 | 1849.5 | 916 | 38 | 34 | 1147.05 | 218 | 3922 | 301.85 | 236 | 536.7 | 0 | 0 | 0 | 0
08:30 | 3911 | 1863.75 | 915.5 | 38 | 34 | 1130.44 | 218.5 | 3920.5 | 376.16 | 231 | 549.55 | 0 | 0 | 0 | 0
09:00 | 3946 | 1878 | 915 | 38 | 34 | 1113.83 | 219 | 3919 | 450.47 | 226 | 562.4 | 0 | 0 | 0 | 0
09:30 | 3928.5 | 1867.75 | 915.5 | 38 | 36 | 1004.03 | 219.5 | 3953 | 498.98 | 230 | 710.9 | 0 | 0 | 0 | 0
10:00 | 3911 | 1857.5 | 916 | 38 | 38 | 894.23 | 220 | 3987 | 547.49 | 234 | 859.4 | 0 | 0 | 0 | 0
10:30 | 3897 | 1854.5 | 916 | 38 | 39 | 876.47 | 220 | 4025 | 580.66 | 238.5 | 941.7 | 50 | 0 | 0 | 0
11:00 | 3883 | 1851.5 | 916 | 38 | 40 | 858.71 | 220 | 4063 | 613.83 | 243 | 1024 | 100 | 0 | 0 | 0
11:30 | 3809.5 | 1848.65 | 916 | 38 | 41 | 852.155 | 220 | 4104.5 | 598.04 | 285.5 | 1240.9 | 75 | 0 | 0 | 0
12:00 | 3736 | 1845.8 | 916 | 38 | 42 | 845.6 | 220 | 4146 | 582.25 | 328 | 1457.8 | 50 | 0 | 0 | 0
12:30 | 3651 | 1854 | 915.5 | 38 | 44 | 855.615 | 220.5 | 4221 | 561.14 | 335 | 1501.25 | 25 | 0 | 0 | 0
13:00 | 3566 | 1862.2 | 915 | 38 | 46 | 865.63 | 221 | 4296 | 540.03 | 342 | 1544.7 | 0 | 0 | 0 | 0
13:30 | 3578.5 | 1862.6 | 915 | 38 | 47 | 866.575 | 221 | 4364 | 542.91 | 333.5 | 1491.85 | 0 | 0 | 1 | 0
14:00 | 3591 | 1863 | 915 | 38 | 48 | 867.52 | 221 | 4432 | 545.79 | 325 | 1439 | 0 | 0 | 2 | 0
14:30 | 3653 | 1864.5 | 915 | 38 | 47 | 870.555 | 221.5 | 4475 | 501.145 | 325 | 1455.1 | 50 | 0 | 1 | 0
15:00 | 3715 | 1866 | 915 | 38 | 46 | 873.59 | 222 | 4518 | 456.5 | 325 | 1471.2 | 100 | 0 | 0 | 0
15:30 | 3662.5 | 1862 | 915 | 38 | 47 | 880.435 | 221 | 4516 | 384.31 | 325 | 1437.6 | 100 | 0 | 1.5 | 0
16:00 | 3610 | 1858 | 915 | 38 | 48 | 887.28 | 220 | 4514 | 312.12 | 325 | 1404 | 100 | 0 | 3 | 0
16:30 | 3583.5 | 1849 | 915.5 | 38 | 47 | 884.12 | 220 | 4482 | 231.77 | 326 | 1409.4 | 100 | 0 | 1.5 | 0
17:00 | 3557 | 1840 | 916 | 38 | 46 | 880.96 | 220 | 4450 | 151.42 | 327 | 1414.8 | 100 | 0 | 0 | 0
17:30 | 3494.5 | 1821 | 916 | 38 | 45 | 884.76 | 219.5 | 4354 | 82.71 | 366 | 1339.8 | 132.5 | 0 | 0 | 0
18:00 | 3432 | 1802 | 916 | 38 | 44 | 888.56 | 219 | 4258 | 14 | 405 | 1264.8 | 165 | 0 | 0 | 0
18:30 | 3567 | 1852 | 915.5 | 38 | 48 | 872.115 | 219 | 4338.5 | 7 | 527.5 | 1704.9 | 165 | 0 | 0 | 56.5
19:00 | 3702 | 1902 | 915 | 38 | 52 | 855.67 | 219 | 4419 | 0 | 650 | 2145 | 165 | 0 | 0 | 113
19:30 | 3639 | 1883 | 915 | 38 | 52 | 1132.87 | 180 | 4455 | 0 | 713 | 2539.2 | 165 | 0 | 0 | 90
20:00 | 3653 | 1885 | 915 | 38 | 52 | 1134.11 | 180 | 4465 | 0 | 722 | 2382.1 | 165 | 0 | 0 | 52
20:30 | 3729 | 1938 | 915 | 38 | 51 | 1130.185 | 179.5 | 4494.5 | 0 | 715 | 2328.05 | 165 | 0 | 0 | 50
21:00 | 3805 | 1991 | 915 | 38 | 50 | 1126.26 | 179 | 4524 | 0 | 708 | 2274 | 165 | 0 | 0 | 48
21:30 | 3782.5 | 2014.5 | 915.5 | 38 | 49 | 1130.04 | 199 | 4513 | 0 | 718 | 2267.5 | 165 | 0 | 0 | 44
22:00 | 3760 | 2038 | 916 | 38 | 48 | 1133.82 | 219 | 4502 | 0 | 728 | 2261 | 165 | 0 | 0 | 40
22:30 | 3797.5 | 1984 | 916 | 38 | 48 | 1133.565 | 219 | 4514.5 | 0 | 724.5 | 2275.65 | 132.5 | 0 | 0 | 40.5
23:00 | 3835 | 1930 | 916 | 38 | 48 | 1133.31 | 219 | 4527 | 0 | 721 | 2290.3 | 100 | 0 | 0 | 41
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 372 | 11:00 | Payra | 412 | 08:00 | 407 | 00:00
Ashuganj | 399 | 6:00 | 380 | 11:00 | Rahanpur | 400 | 11:00 | 389 | 00:00
Bhulta | 396 | 06:00 | 377 | 11:00 | Rampal | 403 | 08:00 | 392 | 0:00
Bibiana | 385 | 06:00 | 380 | 02:00
BIPTC | 402 | 06:00 | 389 | 20:00
Bogura | 382 | 18:00 | 370 | 00:00
Gopalganj | 395 | 08:00 | 385 | 23:00
Kaliakoir | 374 | 19:00 | 363 | 11:00
Madunaghat | 392 | 20:00 | 386 | 16:00
Meghnaghat | 381 | 06:00 | 375 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 217 | 09:00 | Keranigonj | 221 | 06:00 | 215 | 11:00
AKSML | 229 | 20:00 | 224 | 08:00 | Khulna(S) | 230 | 08:00 | 217 | 23:00
Aminbazar | 223 | 05:00 | 218 | 11:00 | Madunaghat | 232 | 18:30 | 227 | 14:00
Ashuganj | 229 | 01:00 | 222 | 10:00 | Madunaghat-400 | 232 | 20:00 | 227 | 15:00
Ashuganj-400 | 229 | 01:00 | 222 | 10:00 | Maniknagar | 217 | 05:00 | 213 | 11:00
Baghabari | 234 | 09:00 | 228 | 21:00 | Meghnaghat | 228 | 03:00 | 220 | 13:00
Barapukuria | 225 | 17:00 | 216 | 07:00 | Meghnaghat-400 | 222 | 06:00 | 217 | 16:00
Barapukuria-230 | 225 | 17:00 | 216 | 07:00 | Mirsorai | 230 | 19:30 | 220 | 16:00
Barishal | 227 | 08:00 | 220 | 00:00 | Rajshahi | 230 | 18:00 | 221 | 23:00
Bheramara | 232 | 10:00 | 223 | 23:00 | Rampal | 230 | 08:00 | 219 | 23:00
Bhulta | 228 | 06:00 | 214 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 18:00 | 222 | 00:00 | Rampura | 227 | 01:00 | 212 | 11:00
BIPTC | 235 | 18:00 | 224 | 23:00 | Shikalbaha | 231 | 20:00 | 224 | 16:00
Bogura | 238 | 11:00 | 230 | 00:00 | Shyampur | 220 | 06:00 | 216 | 00:00
Bogura-400 | 238 | 18:00 | 230 | 00:00 | Siddhirganj | 219 | 03:00 | 216 | 14:00
Borhanuddin | 232 | 08:00 | 226 | 23:00 | Sirajgonj | 245 | 22:00 | 236 | 23:00
BSRM | 228 | 19:30 | 220 | 09:00 | Sreepur | 227 | 07:00 | 222 | 09:00
Cumilla(N) | 222 | 18:00 | 217 | 15:00 | Tongi | 228 | 18:30 | 217 | 11:00
Faridpur | 224 | 08:00 | 216 | 00:00
Fenchuganj | 228 | 05:00 | 223 | 00:00
Ghorashal | 230 | 00:00 | 225 | 09:00
Ghorashal-230 | 228 | 22:00 | 216 | 11:00
Gopalganj | 225 | 08:00 | 218 | 00:00
GPH | 230 | 19:30 | 223 | 16:00
Haripur | 219 | 05:00 | 215 | 10:00
Hasnabad | 221 | 07:00 | 216 | 10:00
Hathazari | 226 | 00:00 | 220 | 15:00
Ishurdi | 233 | 06:00 | 226 | 23:00
Jhenaidah | 229 | 06:00 | 217 | 23:00
Kaliakoir | 233 | 19:00 | 224 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 01:00 | 123 | 11:00 | Lalmonirhat | 128 | 11:00 | 121 | 07:00
Agargaon | 130 | 06:00 | 126 | 11:00 | Madanganj | 127 | 19:00 | 123 | 09:00
Agrabad | 130 | 19:30 | 125 | 16:00 | Madaripur | 133 | 06:00 | 127 | 22:00
AKS | 128 | 19:00 | 125 | 08:00 | Madartek | 136 | 03:00 | 123 | 11:00
Aminbazar | 132 | 13:00 | 128 | 08:00 | Madunaghat | 131 | 04:00 | 128 | 14:00
Amnura | 136 | 18:00 | 130 | 00:00 | Magura | 134 | 10:00 | 122 | 23:00
Ashuganj | 139 | 13:00 | 137 | 00:00 | Mahasthangarh | 131 | 10:00 | 125 | 00:00
Bagerhat | 131 | 07:00 | 119 | 23:00 | Maijdee | 117 | 18:00 | 108 | 14:00
Bajitpur | 130 | 18:00 | 123 | 23:00 | Manikganj | 128 | 04:00 | 122 | 11:00
Bakulia | 131 | 18:00 | 126 | 15:00 | Maniknagar | 132 | 03:00 | 128 | 11:00
Banani | 135 | 01:00 | 125 | 11:00 | Matarbari | 118 | 08:00 | 111 | 18:30
Bangabhaban | 132 | 03:00 | 128 | 10:00 | Matuail | 127.6 | 06:00 | 124 | 11:00
Barapukuria | 138 | 18:30 | 128 | 07:00 | Millgate | 132 | 05:00 | 123 | 11:00
Barguna | 137 | 22:00 | 131 | 00:00 | Mirpur | 130 | 13:00 | 125 | 09:00
Barishal | 133 | 18:00 | 128 | 00:00 | Mirzapur | 131 | 19:30 | 124 | 11:00
Barishal-230 | 133 | 08:00 | 127 | 00:00 | Mithapukur | 130 | 11:00 | 124 | 07:00
Baroaulia | 131 | 23:00 | 127 | 09:00 | MI_Cement | 127 | 06:00 | 123.3 | 10:00
Baroirhat | 122 | 04:00 | 118 | 15:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 134 | 04:00 | 123 | 11:00 | Mogbazar | 135 | 00:00 | 125 | 11:00
BashundharaCement | 127 | 19:00 | 123 | 10:00 | Mongla | 131 | 08:00 | 120 | 23:00
Beanibazar | 127 | 07:00 | 121 | 22:00 | Motijheel | 132 | 03:00 | 128 | 10:00
Benapole | 132 | 18:00 | 118 | 23:00 | Muktagacha | 132 | 08:00 | 125 | 18:30
Bhaluka | 128 | 12:00 | 123 | 19:00 | Munshiganj | 126 | 04:00 | 123 | 08:00
Bhandaria | 128 | 18:00 | 117 | 00:00 | Muradnagar | 124 | 06:00 | 119 | 00:00
Bhangura | 132 | 06:00 | 129 | 00:00 | Mymensingh | 134 | 08:00 | 113 | 18:30
Bheramara | 137 | 10:00 | 132 | 23:00 | Naogaon | 130 | 18:30 | 121 | 00:00
Bheramara(GK) | 137 | 06:00 | 132 | 23:00 | Narail | 135 | 06:00 | 121 | 23:00
Bhulta | 125 | 06:00 | 120 | 01:00 | Narinda | 132 | 03:00 | 128 | 11:00
Bog-Sherpur | 133 | 18:00 | 127 | 00:00 | Narshingdi | 136 | 19:00 | 118 | 00:00
Bogura | 134 | 18:00 | 127 | 02:00 | Natore | 133 | 10:00 | 127 | 23:00
Bogura-230 | 135 | 18:30 | 129 | 00:00 | Nawabganj | 132 | 05:00 | 128 | 00:00
Brahmanbaria | 133 | 06:00 | 129 | 18:30 | Netrakona | 121 | 18:00 | 110 | 18:30
Cantonment | 130 | 03:00 | 126 | 09:00 | New | 133 | 04:00 | 125 | 11:00
Chandina | 127 | 06:00 | 123 | 15:00 | Niamatpur | 136 | 17:00 | 130 | 00:00
Chandpur | 156 | 02:00 | 120 | 08:00 | Noapara | 136 | 11:00 | 123 | 23:00
Chandraghona | 131 | 01:00 | 129 | 15:00 | Pabna | 134 | 10:00 | 128 | 23:00
Chapai | 136 | 18:00 | 129 | 00:00 | Palashbari | 129 | 18:30 | 121 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 05:00 | 123 | 10:00 | Panchagarh | 136 | 18:30 | 122 | 07:00
Chauddagram | 123 | 18:00 | 118 | 14:00 | Patiya | 130 | 00:00 | 125 | 16:00
Chhatak | 125 | 06:00 | 118 | 21:00 | Patuakhali | 138 | 22:00 | 130 | 00:00
Chowmuhani | 117 | 18:00 | 110 | 22:00 | Payra | 136 | 22:00 | 132 | 00:00
Chuadanga | 133 | 06:00 | 119 | 23:00 | PHP | 121 | 06:00 | 116 | 14:00
Coxsbazar | 119 | 05:00 | 113 | 16:00 | Postogola | 133 | 05:00 | 130 | 00:00
Cumilla(N) | 127 | 06:00 | 123 | 15:00 | Purbachal | 135 | 05:00 | 123 | 11:00
Cumilla(S) | 133 | 05:00 | 122 | 00:00 | Purbasadipur | 132 | 18:00 | 122 | 06:00
Daganbhuiyan | 119 | 18:00 | 112 | 14:00 | Rahanpur | 137 | 10:00 | 133 | 00:00
Daudkandi | 121 | 05:00 | 116 | 00:00 | Rahanpur-400 | 137 | 10:00 | 133 | 00:00
Dhaka | 135 | 03:00 | 124 | 11:00 | Rahim | 128 | 06:00 | 124 | 10:00
Dhamrai | 133 | 13:00 | 125 | 11:00 | Rajbari | 132 | 06:00 | 125 | 22:00
Dhanmondi | 135 | 01:00 | 125 | 11:00 | Rajendrapur | 136 | 00:00 | 124 | 00:00
Dohazari | 127 | 18:00 | 123 | 14:00 | Rajshahi | 133 | 18:00 | 127 | 00:00
Faridpur | 133 | 06:00 | 127 | 21:00 | Rajshahi-230 | 132 | 11:00 | 127 | 23:00
Fatullah | 128 | 19:30 | 124 | 10:00 | Ramganj | 123 | 18:00 | 115 | 00:00
Fenchuganj | 134 | 06:00 | 131 | 00:00 | Rampur | 131 | 19:30 | 125 | 16:00
Feni | 121 | 01:00 | 116 | 14:00 | Rampura | 135 | 01:00 | 124 | 11:00
Ghatail | 128 | 07:00 | 121 | 22:00 | Rangamati | 130 | 00:00 | 128 | 14:00
Ghorashal | 136 | 13:00 | 131 | 09:00 | Rangpur | 131 | 11:00 | 125 | 14:00
Goalpara | 136 | 08:00 | 125 | 23:00 | Ruppur | 137 | 18:00 | 132 | 23:00
Gollamari | 137 | 08:00 | 127 | 23:00 | Saidpur | 134 | 18:30 | 122 | 07:00
Gopalganj | 134 | 08:00 | 126 | 23:00 | Satkhira | 139 | 13:00 | 119 | 23:00
Gopalganj-400 | 135 | 08:00 | 130 | 22:00 | Satmasjid | 131 | 06:00 | 126 | 10:00
Gulshan | 135 | 01:00 | 124 | 11:00 | Savar | 132 | 17:00 | 126 | 09:00
Halishahar | 132 | 20:00 | 124 | 16:00 | SevenRings | 136 | 01:00 | 129 | 11:00
Haripur | 128 | 05:00 | 125 | 00:00 | ShahCement | 127 | 05:00 | 123 | 10:00
HaripurSBU | 127 | 18:00 | 113 | 01:00 | Shahjadpur | 136 | 03:00 | 132 | 23:00
Hasnabad | 132 | 05:00 | 129 | 10:00 | Shahjibazar | 133 | 08:00 | 127 | 23:00
Hathazari | 131 | 00:00 | 127 | 16:00 | Shahmirpur | 132 | 04:00 | 127 | 16:00
Ishurdi | 137 | 06:00 | 133 | 00:00 | Shariatpur | 132 | 08:00 | 125 | 22:00
Jaldhaka | 131 | 11:00 | 122 | 13:00 | Sherpur | 132 | 07:00 | 121 | 18:30
Jamalpur | 136 | 08:00 | 126 | 01:00 | Shikalbaha | 122 | 19:30 | 116 | 16:00
Jashore | 135 | 10:00 | 121 | 19:00 | Shikalbaha-230 | 133 | 18:00 | 128 | 14:00
Jhenaidah | 137 | 09:00 | 121 | 22:00 | Shitalakhya | 127.2 | 18:30 | 123.2 | 11:00
Jhenaidah-230 | 136 | 06:00 | 126 | 23:00 | Sholosohor | 131 | 19:30 | 127 | 16:00
Joydebpur | 136 | 22:00 | 125 | 10:00 | Shyampur | 128 | 19:30 | 126 | 11:00
Joypurhat | 128 | 18:00 | 119 | 00:00 | Shyampur-230 | 128 | 06:00 | 125 | 01:00
Juldah | 132 | 19:00 | 127 | 15:00 | Siddhirganj | 128 | 05:00 | 125 | 11:00
Kabirpur | 136 | 20:00 | 122 | 11:00 | Sirajganj | 131 | 10:00 | 125 | 00:00
Kachua | 128 | 18:00 | 121 | 23:00 | Sonargaon | 125 | 02:00 | 122 | 10:00
Kaliakoir | 136 | 19:00 | 127 | 11:00 | Sreemongol | 132 | 07:00 | 127 | 00:00
Kallyanpur | 134 | 02:00 | 127 | 09:00 | Sreepur | 131 | 18:00 | 127 | 09:00
Kalurghat | 132 | 19:30 | 128 | 09:00 | Srinagar | 132 | 05:00 | 128 | 10:00
Kamrangirchar | 132 | 05:00 | 127 | 11:00 | SSM | 134 | 01:00 | 132 | 00:00
Kaptai | 134 | 1:00 | 132 | 9:00 | Sunamganj | 123 | 07:00 | 115 | 20:00
Kasba | 124 | 06:00 | 118 | 15:00 | Sylhet | 128 | 08:00 | 123 | 00:00
Kazla | 132 | 05:00 | 128 | 10:00 | Sylhet-132 | 128 | 08:00 | 124 | 15:00
Keranigonj | 132 | 05:00 | 128 | 11:00 | Tangail | 128 | 19:30 | 121 | 23:00
Khagrachori | 130 | 01:00 | 126 | 16:00 | Taraganj | 132 | 18:30 | 122 | 07:00
Khulna | 135 | 08:00 | 125 | 23:00 | Thakurgaon | 134 | 18:30 | 119 | 07:00
Khulna(S) | 137 | 08:00 | 127 | 23:00 | TK | 132 | 19:30 | 128 | 16:00
Khulshi | 129 | 19:30 | 124 | 16:00 | Tongi | 134 | 03:00 | 128 | 08:00
Kishoreganj | 128 | 18:00 | 121 | 00:00 | Ullahpara | 132 | 06:00 | 129 | 00:00
Kodda | 136 | 19:30 | 123 | 11:00 | Ullon | 134 | 01:00 | 124 | 11:00
KSRM | 131 | 03:00 | 127 | 14:00 | Uttara | 130 | 13:00 | 125 | 9:00
Kulaura | 133 | 06:00 | 129 | 00:00 | UttaraNew | 130 | 13:00 | 125 | 08:00
Kurigram | 128 | 11:00 | 119 | 07:00 | Zigatola | 132 | 05:00 | 128 | 10:00
Kushtia | 133 | 05:00 | 127 | 19:00
Laksam | 127 | 07:00 | 120 | 22:00
Lakshmipur | 118 | 18:00 | 110 | 14:00
Lalbag | 132 | 06:00 | 127 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division