## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: July 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-07-02 |  | 2025-06-01 |  | 2024-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16794 | 2025-07-23 | 15691.42 | 2025-06-21 | 15223 | 2024-07-28 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 9799.07 | 2025-07-25 | 8827.15 | 2025-06-03 | 10542 | 2024-07-23 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16794 | 2025-07-23 | 15691.42 | 2025-06-21 | 15223 | 2024-07-28 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 14859 | 2025-07-23 | 14156.82 | 2025-06-24 | 13868 | 2024-07-28 | 14859 | 2025-07-23
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 17099.14 | 2025-07-23 | 15720.68 | 2025-06-21 | 16000 | 2024-07-30 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14953.5771 |  | 14578.408 |  | 14431 |  | - | -
7 | Average Generation (MW) at Day Peak | 13322.5084 |  | 12594.8343 |  | 12793.5806 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 976 | 2025-07-01 | 981 | 2025-06-20 | 970 | 2024-07-06 | 970 | 2024-07-06
|  |  | 15:00 |  | 2:00 |  | 14:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 64 | 2025-07-13 | 55 | 2025-06-15 | 106 | 2024-07-18 | 194 | 12/06/19
|  |  | 20:00 |  | 21:15 |  | 15:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 812 | 2025-07-21 | 110 | 2025-06-13 | 1341 | 2024-07-10 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15152.08 | 2025-07-21 | 15175.2 | 2025-06-13 | 14096 | 45483 | 14965 | 2024-05-16
|  |  | 21:00 |  | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-07-04 | 0 | 2025-06-01 | 0 | 45478 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13879 | 2025-07-04 | 13631.03 | 2025-06-01 | 13229 | 2024-07-05 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 190 | 2025-07-23 | 39 | 2025-06-20 | 1795 | 45484 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 14859 | 2025-07-23 | 11715.34 | 2025-06-20 | 12870 | 45484 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-07-04 | 0 | 2025-06-01 | 0 | 45478 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 12021 | 2025-07-04 | 12880.09 | 2025-06-01 | 11167 | 45478 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 24 |  | 14 |  | 29 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 4 |  | 2 |  | 17 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1285.2058 |  | 1336.914 |  | 1553.74 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 42.7752 |  | 51.8734 |  | 63.1342 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1242.4306 |  | 1285.0406 |  | 1490.6058 |  | - | -
23 | Net Generation of IPP (MKWH) | 3008.2106 |  | 3779.248 |  | 3471.59 |  | - | -
23b | Net Generation by Generation Companies | 4093.7217 |  | 2803.8877 |  | 2904.26
24 | Net Generation of REB (MKWH) | 48.2102 |  | 39.5405 |  | 72.09 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 135.6626 |  | 113.4342 |  | 224.06 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 8528.2357 |  | 8021.151 |  | 8162.6058 |  | - | -
26 | Energy Generation by Gas (MKWH) | 4241.0786 |  | 4276.4107 |  | 3966.4454 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 0.018 |  | 2.4799 |  | 18.1087 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 1124.286 |  | 923.0317 |  | 1371.0357 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 148.0037 |  | 119.0818 |  | 138.7193 |  | - | -
30 | Energy Generation by Solar (MKWH) | 99.5917 |  | 111.712 |  | 93.2904 |  | - | -
30b | Energy Generation by Wind (MKWH) | 14.5906 |  | 14.0246 |  | 16.4786 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2943.4421 |  | 2626.2838 |  | 2621.6684 |  | - | -
32 | Enegry Import from India (MKWH) | 1545.2637 |  | 1378.3078 |  | 739.9666 |  | - | -
33 | Monthly Load Factor (%) | 80.9643 |  | 83.6562 |  | 81.3292 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: July 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16794 | 2025-07-23 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5814.5
| Chattogram | MW | 1556.5
| Cumilla | MW | 1484.25
| Mymensingh | MW | 1254
| Sylhet | MW | 631
a) | Total supply in East zone | MW | 10740.25
| Khulna | MW | 2001.9
| Barisal | MW | 518
| Rajshahi | MW | 1806
| Rangpur | MW | 978
b) | Total supply in West zone | MW | 5303.9
c) | Total supply in both zone ( a+b) | MW | 16044.15
Ref: | 27.21.0000.603.16.087.20.928 | Date: 16/08/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | -76 | 2025-07-24 | 5:00
| b) Ishurdi end | MW | 374 | 2025-07-01 | 11:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1016 | 2025-07-01 | 11:00
| b) Ishurdi end | MW | -38 | 2025-07-24 | 5:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0
| b) Ishurdi end | MKWH | 167.4935
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 162.4687
| b) Ishurdi end | MKWH | 0
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 220 | 2025-07-13 | 6:00
| b)Serajganj end | MW | 750 | 2025-07-21 | 21:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2025-07-29 | 9:00
| b)Sirajganj end | MW | -34 | 2025-07-13 | 6:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 373.888
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 362.5995
30 | Transmission loss of EWI /NO-2 | % | 3.02%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2840 | 2025-07-14 | 11:00
|  | MW | 1760
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2824 | 2025-07-14 | 11:00
|  | MW | 1759
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 38651 | 2025-07-14 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 38601 | 2025-07-14
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 888.538
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 886.719
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.205%
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 132kV Transformer-1 (405T1) | 2025-07-18 23:58 | 2025-07-19 02:36 | 0.10972 | T | Prd trip 86 | 40 | 105.3333 | Power interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-07-24 03:18 | 2025-07-24 07:05 | 0.15764 | T | Over current flow REC650 | 60 | 227 | Power interruption
Bajitpur 132/33kV | Tr-2(414T) | 2025-07-24 03:18 | 2025-07-24 07:06 | 0.15833 | T | Over current flow REC650 | 15 | 57 | Power interruption
Jamalpur 132/33kV | T-4 | 2025-07-14 03:20 | 2025-07-14 04:14 | 0.0375 | T | 33kv Switching -2 feeder faulty. O/C & E/F | 24 | 21.6 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-07-09 09:25 | 2025-07-09 10:14 | 0.034028 | T | Single line to ground Fault MiCom P 127 | 70 | 57.1667 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-07-24 23:14 | 2025-07-24 23:25 | 0.0076389 | T | over current siprotec | 42 | 7.7 | Power interruption
Tangail 132/33kV | Tr-4 | 2025-07-27 10:50 | 2025-07-27 11:19 | 0.020139 | T | 33kv kachuadanga feeder fault.(BPDB) N/A | 12 | 5.8 | Power interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-07-29 14:51 | 2025-07-29 16:04 | 0.050694 | E/O | 33kV bus section-1 insulator broken maintenance. | 40 | 48.6667 | Power interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 | 2025-07-21 23:05 | 2025-07-22 01:16 | 0.090972 | E/O | red hot ds maintenance | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-07-16 22:18 | 2025-07-17 00:00 | 0.070833 | E/O | Tr-01 S/D taken due to red hot at 33 kV side B-phase. | 26 | 44.2 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-07-03 13:29 | 2025-07-03 13:55 | 0.018056 | E/O | jaek bus Repair | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2025-07-25 20:10 | 2025-07-25 22:18 | 0.088889 | E/O | due to 33kv bus section DS red hot.(BPDB) | 30 | 64 | Power interruption
Tangail 132/33kV | Tr-1 | 2025-07-27 07:37 | 2025-07-27 09:35 | 0.081944 | E/O | Due 33kv Betka Feeder red hot(BPDB) | 50 | 98.3333 | Power interruption
|  |  | Total : | 0.92639 |  | Unserved Energy: |  | 736.8
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2025-07-25 12:33 | 2025-07-25 21:04 | 0.35486 | T | 33 KV feeder Fault VAJ | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-07-24 05:33 | 2025-07-24 09:47 | 0.17639 | T | Dir O/C Trip, 51, MVAJM, Trip 25 | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 | 2025-07-16 17:55 | 2025-07-16 19:55 | 0.083333 | T | O/E fault relay | 8 | 16 | Power interruption
Madanganj 132/33kV | GT-2 | 2025-07-16 17:55 | 2025-07-16 20:50 | 0.12153 | T | O/E fault | 30 | 87.5 | Power interruption
Madanganj 132/33kV | GT-2 | 2025-07-25 18:35 | 2025-07-25 18:35 | 0 | T | Back up protection relay | 30 | 0 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2025-07-15 14:37 | 2025-07-15 14:57 | 0.013889 | T | DIR E/F Trip | 41 | 13.6667 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2025-07-15 14:37 | 2025-07-15 14:37 | 0 | T | None DIR E/F Trip | 0 | 0 | Power interruption
Narshingdi 132/33kV | T-4 | 2025-07-06 12:37 | 2025-07-06 13:13 | 0.025 | T | 33 kV Shibpur feeder fault Lockout operated | 23 | 13.8 | Power interruption
Narshingdi 132/33kV | T-4 | 2025-07-10 07:24 | 2025-07-10 07:30 | 0.0041667 | T | df/dt fault Lockout operated | 7 | 0.7 | Power interruption
Siddhirganj 230/132kV | MTR 1 | 2025-07-11 05:39 | 2025-07-11 14:11 | 0.35556 | T | PRV Trip ETR Main 1 protection unit RET 670 | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2025-07-25 11:50 | 2025-07-25 12:18 | 0.019444 | T | Due to Pbs Anandabazar and Astha feeder. DIR O/C | 65 | 30.3333 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-07-25 15:16 | 2025-07-25 16:15 | 0.040972 | E/O | Emergencey Repear of Incommer-2 CT B Phase icoming clamp conncetor | 52 | 51.1333 | Power interruption
Hasnabad 132/33kV | 132kV Main Bus | 2025-07-29 11:45 | 2025-07-29 11:45 | 0 | E/O | Red hot maintenance work. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-07-08 11:03 | 2025-07-08 19:29 | 0.35139 | E/O | DPDC 33kV S/S Side CB Flashing Maintenence work | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-07-08 19:55 | 2025-07-09 19:45 | 0.066667 | E/O | DPDC 33kV side Faulty | 7 | 11.2 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-07-18 02:11 | 2025-07-18 03:36 | 0.10417 | E/O | 33 kv langalband underground feeder loop out | 50 | 125 | Power interruption
|  |  | Total : | 1899-12-31 17:13 |  | Unserved Energy: |  | 349.3333
Chattogram Grid Circle :
Coxsbazar 132/33kV | T3 | 2025-07-22 14:53 | 2025-07-22 17:24 | 0.10486 | T | T-3 Tripped due 33 kV over current Auxiliary Station Transformar Dropout fuse flashing. differential(87T) I-Differential Pickup. | 58 | 145.9667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-07-10 11:47 | 2025-07-10 12:07 | 0.013889 | T | Due to B.Ban 33 KV feeder . General trip, Phase (R Y B) LV-OC trip | 46 | 15.3333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-07-28 19:24 | 2025-07-28 19:42 | 0.0125 | T | Due to Lohaghara & Banshkhali 33 kv feeder (O/C & E/F) Over current pro. trip, Lockout Relay K861 trip, Lockout Relay K862 trip, | 70 | 21 | Power interruption
Khulshi 132/33kV | 415T (T2) | 2025-07-09 05:10 | 2025-07-09 05:57 | 0.032639 | T | 33kV Isphani line fault MVJM25 | 30 | 23.5 | Power interruption
Bakulia 132/33kV | T-4 (432T) | 2025-07-17 09:59 | 2025-07-17 10:35 | 0.025 | E/O | Oil Leakage checking. | 0 | 0 | No interruption
Baroaulia 132/33kV | 132kv Main Bus | 2025-07-02 05:08 | 2025-07-02 06:44 | 0.066667 | E/O | 132kv Main BUS DS Y-phase Redhot work. | 24 | 38.4 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-07-04 14:18 | 2025-07-05 14:38 | 1899-12-31 00:20 | E/O | routine maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-02 | 2025-07-20 12:10 | 2025-07-20 12:10 | 0 | E/O | Oil Acidity high. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-04 | 2025-07-28 20:22 | 2025-07-28 21:40 | 0.054167 | E/O | Red hot maintainance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-07-02 19:20 | 2025-07-02 20:21 | 0.042361 | E/O | T-02(33kV) Bus shutdown due to Ononna feeder maintenance. | 3 | 3.05 | Power interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-07-03 17:51 | 2025-07-03 18:58 | 0.046528 | E/O | Insolator Maintenance of Ononna Feder. Shut Down by PDB. | 3 | 3.35 | Power interruption
|  |  | Total : | 1899-12-31 09:54 |  | Unserved Energy: |  | 250.6
Cumilla Grid Circle :
Ashuganj 230/132/33kV | TR-OAT-11 | 2025-07-31 19:00 | 2025-07-31 19:06 | 0.0041667 | T | Over Current, No.2 Master Trip Relay | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 402T | 2025-07-26 16:51 | 2025-07-26 17:00 | 0.00625 | T | Due to PBS fault OC/EF | 50 | 7.5 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-07-28 13:45 | 2025-07-28 14:04 | 0.013194 | T | Due to PBS fault OC/EF | 50 | 15.8333 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-07-28 17:42 | 2025-07-28 17:58 | 0.011111 | T | O/C & E/F Relay | 20 | 5.3333 | Power interruption
Chandpur 132/33kV | 422T | 2025-07-24 20:53 | 2025-07-24 21:43 | 0.034722 | T | Due to Cdr3 breaker fail and under voltage relay and tcsr relay O/c and E/f and | 40 | 33.3333 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-04 | 2025-07-03 16:52 | 2025-07-03 19:28 | 0.10833 | T | 33 KV Summit Jungalia Feeder DS loop blast Overcurrent relay | 40 | 104 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-07-03 16:52 | 2025-07-03 17:35 | 0.029861 | T | Overcurrent relay | 40 | 28.6667 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-07-05 15:56 | 2025-07-05 16:09 | 0.0090278 | T | 33KV Laksam REB Feeder Fault RET 650 REF 615 | 40 | 8.6667 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-07-18 12:53 | 2025-07-18 13:13 | 0.013889 | T | 33KV palpara feeder fult REF 615 | 28 | 9.3333 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-07-18 17:48 | 2025-07-18 17:57 | 0.00625 | T | 1.RET670 2.REF615 | 24 | 3.6 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-07-20 07:03 | 2025-07-20 07:16 | 0.0090278 | T | 33 KV Kaliyajuri feeder Fault RET 650 REF 615 | 26 | 5.6333 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-07-20 11:40 | 2025-07-20 11:51 | 0.0076389 | T | REF 615 RET 650 | 24 | 4.4 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-07-24 09:01 | 2025-07-24 09:14 | 0.0090278 | T | 33Kv Kaliyajhori feeder Fault 132kv-RET 650 33Kv-REF 615 | 44 | 9.5333 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-07-25 09:12 | 2025-07-25 09:51 | 0.027083 | T | 33KV laksham REB feeder fult by O/C,E/F 33kv side REF615,132kv side RET 650 | 25 | 16.25 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-07-26 15:07 | 2025-07-26 15:15 | 0.0055556 | T | 33 KV Kotbari feeder fault. REF 615 | 26 | 3.4667 | Power interruption
Daudkandi 132/33kV | Transformer-1 | 2025-07-05 09:32 | 2025-07-05 09:57 | 0.017361 | T | Total substation dead because main busbar fault . differential protection relay | 25 | 10.4167 | Power interruption
Daudkandi 132/33kV | Transformer-2 | 2025-07-05 09:32 | 2025-07-05 09:57 | 0.017361 | T | Total substation dead because main busbar fault . differential protection relay | 25 | 10.4167 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2025-07-05 09:32 | 2025-07-05 09:58 | 0.018056 | T | Total substation dead because main busbar fault . differential protection relay | 20 | 8.6667 | Power interruption
Feni 132/33kV | T-1(405T) | 2025-07-19 07:28 | 2025-07-19 07:55 | 0.01875 | T | Transformer T-1 33kV side trip for Chowmuhani 33kV ckt-1 trip. Y phase bus loop out SIEMENS | 34 | 15.3 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-06 08:20 | 2025-07-06 08:47 | 0.01875 | T | N/A lockout relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-08 02:28 | 2025-07-08 02:54 | 0.018056 | T | N/A INSTT. Over Current | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-08 04:56 | 2025-07-08 09:43 | 0.19931 | T | N/A Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-08 21:25 | 2025-07-08 23:24 | 0.082639 | T | Bad Weather Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-12 14:27 | 2025-07-12 17:29 | 0.12639 | T | Micom Relay,SRT, MicomRelay, SRT,Lockout Realy | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-31 18:58 | 2025-08-02 00:08 | 1899-12-31 05:10 | T | Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-07-31 18:58 | 2025-08-02 19:12 | 1900-01-01 00:14 | T | 33 kv habiganj feeder breaker burn Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-07-31 18:58 | 2025-08-01 08:50 | 0.57778 | T | 33 kv habiganj feeder breaker burn No Relay | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-07-09 03:02 | 2025-07-09 03:39 | 0.025694 | T | 33 kv IC-2 Feeder red phase CT brust OC (Inst.)E/F (inst.) | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-07-09 03:02 | 2025-07-09 03:39 | 0.025694 | T | 33 kv IC-2 Feeder red phase CT brust general trip, OC trip | 20 | 12.3333 | Power interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-07-17 15:57 | 2025-07-17 16:59 | 0.043056 | E/O | To fix Red Hot in 33kv Kanaighat feeder Isolator | 35 | 36.1667 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-07-17 17:29 | 2025-07-17 18:14 | 0.03125 | E/O | To fix Red Hot in 33kv Alinagor feeder Isolator | 30 | 22.5 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-07-27 04:57 | 2025-07-27 07:30 | 0.10625 | E/O | Fenchugonj line red-hot maintenance work | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-07-27 04:57 | 2025-07-27 07:45 | 0.11667 | E/O | Fenchugonj line shutdown for hed-hot maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-07-29 07:15 | 2025-07-29 09:15 | 0.083333 | E/O | Incommer 2 DS RED HOT Maintenance. | 13 | 26 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-07-01 14:06 | 2025-07-01 14:41 | 0.024306 | E/O |  | 50 | 29.1667 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-07-11 09:50 | 2025-07-11 10:26 | 0.025 | E/O | Emergency maintenance work | 33 | 19.8 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-07-11 15:14 | 2025-07-11 16:35 | 0.05625 | E/O | Emergency maintenance work | 45 | 60.75 | Power interruption
Chandpur 132/33kV | 402T | 2025-07-28 18:30 | 2025-07-28 18:30 | 0 | E/O | LT side S/D by the permission of higher authorities. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-07-12 10:04 | 2025-07-12 13:21 | 0.13681 | E/O | 132kv T-3 transformer shutdown required for the 132kv GCB hydraulic oil leakage problem. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR3-435T | 2025-07-04 22:30 | 2025-07-04 23:45 | 0.052083 | E/O | 33 KV Dotterhat Feeder Red Hot Maintenence | 50 | 62.5 | Power interruption
Chowmuhani 132/33kV | TR3-435T | 2025-07-25 03:08 | 2025-07-25 04:49 | 0.070139 | E/O | 33KV PDB Datterhat Feeder BUBBAR end Red hot maintenance. | 50 | 84.1667 | Power interruption
Chowmuhani 132/33kV | TR2-425T | 2025-07-29 22:41 | 2025-07-29 23:48 | 0.046528 | E/O | 33KV REB Sadar Incoming DS Y Phase (red hot) Loop Maintenance | 30 | 33.5 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-07-29 22:42 | 2025-07-30 00:02 | 0.055556 | E/O | 33KV Maijdee Incoming DS Y Phase (red hot) Loop Maintenance | 30 | 40 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-07-23 10:00 | 2025-07-24 00:16 | 0.59444 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-07-10 15:34 | 2025-07-10 17:02 | 0.061111 | E/O | PBS feeder Red hot maintenance | 30 | 44 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-07-26 09:57 | 2025-07-26 10:20 | 0.015972 | E/O | PDB Red hot maintenance | 9 | 3.45 | Power interruption
Maijdee 132/33kV | Tr-02 | 2025-07-21 21:58 | 2025-07-21 23:56 | 0.081944 | E/O | 33kv sudharam feeder red Hot maintenance | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-07-12 07:23 | 2025-07-12 09:28 | 0.086806 | E/O | IC-2 Breaker and CT Replacement work purpose. | 19 | 39.5833 | Power interruption
|  |  | Total : | 1900-01-05 08:29 |  | Unserved Energy: |  | 814.2667
Khulna Grid Circle :
Barishal 132/33kV | T-1 (405T) | 2025-07-02 08:10 | 2025-07-02 08:22 | 0.0083333 | T | 33 kv polaspur feeder fault O/C | 50 | 10 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-07-03 14:14 | 2025-07-03 14:32 | 0.0125 | T | Dopdopia 2 33kV feeder fault. O/C , E/F | 45 | 13.5 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-07-14 01:36 | 2025-07-14 01:47 | 0.0076389 | T | WZPDCL 33kV Jhalokathi feeder fault-(over current) Over current, Earth Fault | 50 | 9.1667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-07-19 10:43 | 2025-07-19 10:49 | 0.0041667 | T | Kashipur 33 kV feeder fault. O/C, E/F | 42 | 4.2 | Power interruption
Barishal 230/132kV | T-5 | 2025-07-13 12:54 | 2025-07-13 13:25 | 0.021528 | T | Sawrupkathi-1 33 kV feeder fault. Micom P142 | 28.5 | 14.725 | Power interruption
Barishal 230/132kV | T-4 | 2025-07-13 12:54 | 2025-07-13 13:25 | 0.021528 | T | Sawrupkathi-1 33 kV feeder fault. Micom P142 | 28.5 | 14.725 | Power interruption
Barishal 230/132kV | T-4 | 2025-07-20 09:46 | 2025-07-20 10:08 | 0.015278 | T | 33kv nabagram feeder Micom p142 | 45 | 16.5 | Power interruption
Barishal 230/132kV | T-5 | 2025-07-20 09:46 | 2025-07-20 10:08 | 0.015278 | T | Nabagram 33kv feeder Micom p142 | 45 | 16.5 | Power interruption
Barishal 230/132kV | ATR-2 | 2025-07-25 23:05 | 2025-07-26 01:55 | 0.11806 | T | Oltc prd trip No operate 132 kv relay.only 230kv relay operate | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 | 2025-07-26 02:22 | 2025-07-26 14:51 | 0.52014 | T | Oltc prd trip No operate 132 kv relay.only 230kv relay operate | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2025-07-21 08:25 | 2025-07-21 09:46 | 0.05625 | T | Trip for Bagerhat line trip Protection relay 81 U/F Under voltage blocking | 34 | 45.9 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-07-04 20:30 | 2025-07-04 20:53 | 0.015972 | T | 33kV khalil Mondol hat & Vanga-2 PBS Feeder fault. 33kV Over current | 66 | 25.3 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-07-04 20:30 | 2025-07-04 20:55 | 0.017361 | T | 33kV khalil Mondol hat & Vanga-2 PBS Feeder fault. 33kV Over current | 66 | 27.5 | Power interruption
Goalpara 132/33kV | T1 | 2025-07-05 02:52 | 2025-07-05 10:32 | 0.31944 | T | Rain differential | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2025-07-15 11:58 | 2025-07-15 12:39 | 0.028472 | T | due to Khulna Sadar (PBS) Feeder fault. Backup relay 1 | 32 | 21.8667 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-07-15 11:58 | 2025-07-15 12:40 | 0.029167 | T | Due to Khulna sadar (PBS) Backup protection-1 relay | 32 | 22.4 | Power interruption
Gopalganj 132/33kV | T1 | 2025-07-16 08:18 | 2025-07-16 08:48 | 0.020833 | T | Bpbs-1+REB-8 feeder fault O/c+u/f | 35 | 17.5 | Power interruption
Khulna (C) | Tr-2 415 T | 2025-07-14 12:56 | 2025-07-14 14:41 | 0.072917 | T | Due to 33kv Shiromoni-2 Faulty 50G ( inst E/F) But Not Trip | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-07-25 18:25 | 2025-07-25 18:50 | 0.017361 | T | 33kv pbs feeder faulty OC/EF | 24 | 10 | Power interruption
Khulna (C) | Tr-2 415 T | 2025-07-25 18:25 | 2025-07-25 18:46 | 0.014583 | T | 33kv pbs feeder faulty OC/EF | 24 | 8.4 | Power interruption
Madaripur 132/33kV | T3-426T | 2025-07-04 01:53 | 2025-07-04 08:52 | 0.29097 | T | PRD trip PRD | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-07-11 11:41 | 2025-07-11 12:00 | 0.013194 | T | O/C,E/F O/C and E/F Relay | 48 | 15.2 | Power interruption
Madaripur 132/33kV | T2-415T | 2025-07-11 11:41 | 2025-07-11 12:02 | 0.014583 | T | O/C,E/F O/C and E/F Relay | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-07-01 22:54 | 2025-07-01 23:02 | 0.0055556 | T | Due to Reb-01 Feeder fault. SIEMENS 7SJ81 | 22.5 | 3 | Power interruption
Noapara 132/33kV | T-2 | 2025-07-01 22:54 | 2025-07-01 23:02 | 0.0055556 | T | Due to Reb-01 Feeder fault. SIEMENS 7SJ81 | 22.5 | 3 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-07-01 15:29 | 2025-07-01 15:38 | 0.00625 | T | Due to 33kV Tala & 33kV Ashasuni feeder fault. Over current relay & Earth fault relay. | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-07-07 14:46 | 2025-07-07 14:52 | 0.0041667 | E/O | Parallel opretion | 28 | 2.8 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-07-16 09:27 | 2025-07-16 10:02 | 0.024306 | E/O | 33 kV Incoming Meter Replacement work by EAUD, BPDB Barishal. | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2025-07-16 10:20 | 2025-07-16 11:05 | 0.03125 | E/O | 33 kV Incoming Meter Replacement work by EAUD, BPDB Barishal. | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2025-07-29 16:04 | 2025-07-29 17:23 | 0.054861 | E/O | Fault of 33kv Pbs feeder. | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-07-15 10:31 | 2025-07-15 12:42 | 0.090972 | E/O | Due to 33 kv seromoni-2 feeder faulty | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-07-26 10:47 | 2025-07-26 12:03 | 0.052778 | E/O | 33kv bus section-2 Bus DS red-hot maintenance. | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-07-11 14:10 | 2025-07-11 19:10 | 0.20833 | E/O | 33KV incoming -01(B-Phase CT Fault) | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-07-03 15:47 | 2025-07-03 16:48 | 0.042361 | E/O | T-1 TTB change by BPDB. | 7.5 | 7.625 | Power interruption
Mongla 132/33kV | T-1 | 2025-07-11 16:34 | 2025-07-11 18:07 | 0.064583 | E/O | WZ 33 KV Section DS Red Hot. | 4 | 6.2 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-07-28 07:21 | 2025-07-28 08:26 | 0.045139 | E/O | Auxiliary fuse change | 50 | 54.1667 | Power interruption
|  |  | Total : | 1900-01-01 07:00 |  | Unserved Energy: |  | 370.175
HVDC Grid Circle :
Bheramara(GK) 132/33kV | TR-1 | 2025-07-13 18:21 | 2025-07-13 19:25 | 0.044444 | T | 33kV Feeder Fault OC/EF | 25 | 26.6667 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-07-13 18:21 | 2025-07-13 19:25 | 0.044444 | T | 33kV Feeder Fault OC/EF | 25 | 26.6667 | Power interruption
Bheramara(GK) 132/33kV | TR-1 | 2025-07-21 11:58 | 2025-07-21 12:11 | 0.0090278 | T | Taragunia 33kV PBS Feeder & Pragpur 33kV PBS Feeder Fault OC/EF | 17 | 3.6833 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-07-21 11:58 | 2025-07-21 12:11 | 0.0090278 | T | Taragunia 33kV PBS Feeder & Pragpur 33kV PBS Feeder Fault OC/EF | 17 | 3.6833 | Power interruption
Bheramara(GK) 132/33kV | TR-1 | 2025-07-25 15:55 | 2025-07-25 16:22 | 0.01875 | T | 33 kV Feeder Fault OC/EF | 11 | 4.95 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-07-25 15:55 | 2025-07-25 16:20 | 0.017361 | T | 33 kV Feeder Fault OC/EF | 22 | 9.1667 | Power interruption
Jashore 132/33kV | T-1 | 2025-07-14 15:25 | 2025-07-14 18:36 | 0.13264 | T | Trip O/C, E/F | 0 | 0 | No interruption
Magura 132/33kV | T-3 (425T) | 2025-07-03 10:54 | 2025-07-03 11:09 | 0.010417 | T | PBS Rawtara 33kV over current earth fault. Non directional earth fault & general trip. | 32 | 8 | Power interruption
Magura 132/33kV | T-3 (425T) | 2025-07-05 07:50 | 2025-07-05 08:19 | 0.020139 | T | Pbs 33kV Rawtara feeder trip. 51/51N | 30 | 14.5 | Power interruption
BIPTC | 20DF12 | 2025-07-01 16:18 | 2025-07-01 17:43 | 0.059028 | T | Tripped | 0 | 0 | No interruption
BIPTC | 10CF23 | 2025-07-09 19:46 | 2025-07-10 11:08 | 0.64028 | T | SF6 Protection operated (T1 CT) | 0 | 0 | No interruption
BIPTC | 20DF21 | 2025-07-24 05:10 | 2025-07-24 13:16 | 0.3375 | T | tripped by unbalanced 60/61 instant trip. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-07-25 05:44 | 2025-07-25 18:15 | 0.52153 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF42 | 2025-07-29 18:33 | 2025-07-30 10:07 | 0.64861 | T | Tripped by Capacitor unbalance | 0 | 0 | No interruption
BIPTC | 10CF23 | 2025-07-10 09:28 | 2025-07-10 11:08 | 0.069444 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-07-25 15:25 | 2025-07-25 18:15 | 0.11806 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 20DF42 | 2025-07-30 08:51 | 2025-07-30 10:07 | 0.052778 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 20DF42 | 2025-07-30 08:51 | 2025-07-30 10:07 | 0.052778 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 | 2025-07-30 20:52 | 2025-07-30 23:16 | 0.1 | E/O | Red hot Maintenance work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-07-10 07:20 | 2025-07-10 08:35 | 0.052083 | E/O | Red hot maintenance work | 12 | 15 | Power interruption
Kushtia 132/33kV | T2 | 2025-07-20 21:03 | 2025-07-21 00:17 | 0.13472 | E/O | T2A 33kV side CT load side Y phase Red Hot maintenance | 10 | 32.3333 | Power interruption
Shahjadpur 132/33kV | T-1(405T) | 2025-07-07 09:50 | 2025-07-07 13:45 | 0.16319 | E/O | Red-hot Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 06:09 |  | Unserved Energy: |  | 144.65
Bogura Grid Circle:
Bogura 230/132kV | T-01 | 2025-07-16 12:29 | 2025-07-16 12:44 | 0.010417 | T | N/A | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2025-07-15 13:15 | 2025-07-15 14:04 | 0.034028 | T | Finding… (আবহাওয়া জনিত কারনে T-3, ৩৩ কেভি বাসে সংযুক্ত পবিস Rajshahi-2, ফিডার Relay তে O/C, E/F DMT Signal দেখায় কিন্তু তাদের ব্রেকার ট্রিপ না করে গ্রিড এর 33kV Breaker (T-3 transformer) ট্রিপ করে।) OC/ EF & OPTD | 6 | 4.9 | Power interruption
Palashbari 132/33kV | TR1-414T | 2025-07-14 08:42 | 2025-07-14 08:48 | 0.0041667 | T | ডুগডুগি ৩৩ কেভি ফিডার চালু করার সময় T-1 & T-2 ৩৩ কেভি ইনকামার-১ এবং ইনকামার-২ ট্রিপ করে। MiCOM P142 | 46 | 4.6 | Power interruption
Palashbari 132/33kV | TR2-404T | 2025-07-14 08:42 | 2025-07-14 08:48 | 0.0041667 | T | ডুগডুগি ৩৩ কেভি ফিডার চালু করার সময় T-1 & T-2 ৩৩ কেভি ইনকামার-১ এবং ইনকামার-২ ট্রিপ করে। MiCOM P142 | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-07-16 08:54 | 2025-07-16 09:18 | 0.016667 | T | ALSTOM (MCGG) | 6 | 2.4 | Power interruption
Rahanpur 400/132kV | HV 400 KV BUS | 2025-07-07 05:46 | 2025-07-07 16:23 | 0.44236 | T | Bus Zone 2 Trip.Fault Distance 0.3km Bus Protection Relay | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-07-07 05:46 | 2025-07-07 21:14 | 0.64444 | T | Connected with Busbar-2 Protection Relay | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2025-07-14 20:20 | 2025-07-15 00:13 | 0.16181 | E/O | Red hot maintenance. | 0 | 0 | No interruption
Chapai 132/33kV | T-3 (425T) | 2025-07-18 10:22 | 2025-07-18 12:30 | 0.088889 | E/O | Red hot Remove | 15 | 32 | Power interruption
Chapai 132/33kV | T-1 (405T) | 2025-07-19 11:11 | 2025-07-19 12:48 | 0.067361 | E/O | Forced Shut down | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2025-07-03 22:02 | 2025-07-03 23:45 | 0.071528 | E/O | 33KV BUS section-01 shutdown for PBS Dimla 33KV Feeder Red hot maintenance work. | 40 | 68.6667 | Power interruption
Jaldhaka 132/33kV | 406T-1 | 2025-07-14 21:50 | 2025-07-14 23:03 | 0.050694 | E/O | 33 kv Domar-2 feeder red hot maintenance work. | 25 | 30.4167 | Power interruption
Jaldhaka 132/33kV | 406T-1 | 2025-07-19 10:24 | 2025-07-19 12:44 | 0.097222 | E/O | Red hot at B phase in jaldhaka 33kv feeder | 32 | 74.6667 | Power interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2025-07-03 11:07 | 2025-07-03 12:10 | 0.04375 | E/O | due to tempareture high at 132kv CT PT and 33kv CT,PT,DS | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2025-07-24 11:10 | 2025-07-24 11:35 | 0.017361 | E/O | Tr-01,, 33kv bushing Red hot remove R-Phase | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-07-22 20:15 | 2025-07-22 20:56 | 0.028472 | E/O | Due to source blade maintenance of 33 kV Pirob feeder. | 40 | 27.3333 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2025-07-21 10:17 | 2025-07-21 12:13 | 0.080556 | E/O | Red hot work. | 25 | 48.3333 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-07-23 09:01 | 2025-07-23 10:17 | 0.052778 | E/O | By PBS for 33kv mirpur feeder bus DS R-ph emergency red hot maintenance work. | 10 | 12.6667 | Power interruption
Mithapukur 132/33kV | BUS SECTION-2 (33KV) | 2025-07-23 09:18 | 2025-07-23 10:17 | 0.040972 | E/O | By PBS for 33kv mirpur feeder bus DS R-ph emergency red hot maintenance work. | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-1(404T) | 2025-07-25 15:45 | 2025-07-25 15:45 | 0 | E/O | Red hot maintanence | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-07-26 12:13 | 2025-07-26 13:06 | 0.036806 | E/O | T1 LT CB clamp hoigh temperature | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2025-07-27 12:45 | 2025-07-27 13:58 | 0.050694 | E/O | For tightening work at the connector of GCB of 132/33 Kv Tr-2 transformer to minimize high temperature. | 0 | 0 | No interruption
Rajshahi 132/33kV | Station Aux. Transformer-1 | 2025-07-28 16:49 | 2025-07-28 19:00 | 0.090972 | E/O | High temperature maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-07-28 16:52 | 2025-07-28 18:50 | 0.081944 | E/O | High temperature maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | T-1(414T) | 2025-07-02 06:30 | 2025-07-02 08:20 | 0.076389 | E/O | 33kV Lalbagh-2 under 33kV BUS Section-1 D/S raiser Red Hot rectification work. | 25 | 45.8333 | Power interruption
Saidpur 132/33kV | TR-4 (414T) | 2025-07-07 16:37 | 2025-07-07 17:28 | 0.035417 | E/O | Emergency maint.work | 20 | 17 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2025-07-19 21:57 | 2025-07-19 23:09 | 0.05 | E/O | Sirajgonj PBS-2 has been taken shut down for emergency Redhot maintenance at Kazipur 33kv CT R-Phase | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 09:07 |  | Unserved Energy: |  | 368.8167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-17 08:06 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: july 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-07-24 04:00 | 2025-07-24 05:20 | 0.055556 | T | Trip main-2 internal relay fail | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Mirpur-01 | 2025-07-24 04:00 | 2025-07-24 07:10 | 0.13194 | T | Trip main-1 diff E/F | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2025-07-17 07:25 | 2025-07-17 07:49 | 0.016667 | T | Bad weather. | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2025-07-17 07:25 | 2025-07-17 07:50 | 0.017361 | T | Bad weather | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-07-09 09:25 | 2025-07-09 09:55 | 0.020833 | T | Over current A& C Phase | 75 | 37.5 | Power interruption | 22.5 | 0:30 | 0.2 | 4.5
Kabirpur 132/33kV | Tongi-2 | 2025-07-09 10:40 | 2025-07-09 11:20 | 0.027778 | T | Over current A & C Phase | 35 | 23.3333 | Power interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2025-07-16 16:07 | 2025-07-16 16:53 | 0.031944 | T | Extreme weather | 12 | 9.2 | Power interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-07-24 04:05 | 2025-07-24 05:28 | 0.057639 | T | Thundering & rain . | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-24 04:05 | 2025-07-24 05:33 | 0.061111 | T | Thundering & rain . | 50 | 73.3333 | Power interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-07-25 10:06 | 2025-07-25 10:22 | 0.011111 | T | E/F | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-25 10:08 | 2025-07-25 10:08 | 0 | T | No | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-07-25 12:46 | 2025-07-25 12:48 | 0.0013889 | T | NA | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-25 12:46 | 2025-07-25 12:48 | 0.0013889 | T | Unknown | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2025-07-17 07:26 | 2025-07-17 07:50 | 0.016667 | T | Due to Heavy Thunderstorm | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2025-07-17 07:26 | 2025-07-17 07:50 | 0.016667 | T | Due to heavy thunderstorm | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2025-07-24 23:38 | 2025-07-25 01:05 | 0.060417 | T | Due to heavy thunderstorm | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2025-07-24 23:38 | 2025-07-25 01:05 | 0.060417 | T | Due to heavy thunderstorm | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-07-16 16:21 | 2025-07-16 16:53 | 0.022222 | T | Earth fault at R-Phase shown at Kodda end , there is no relay/breaker operated at Rajendrapur end. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-07-09 09:25 | 2025-07-09 09:56 | 0.021528 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-07-09 10:40 | 2025-07-09 11:12 | 0.022222 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-07-09 11:13 | 2025-07-09 15:28 | 0.17708 | T | Bad weather | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-07-07 12:24 | 2025-07-08 03:10 | 0.61528 | E/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-07-08 07:40 | 2025-07-08 17:45 | 0.42014 | E/O | By NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Tongi 80 MW PS | 2025-07-27 11:42 | 2025-07-27 13:25 | 0.071528 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 22:32 |  | Unserved Energy: |  | 143.3667
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Madanganj | 2025-07-24 03:40 | 2025-07-24 05:25 | 0.072917 | T | Due to bad weather | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-07-12 22:55 | 2025-07-12 23:35 | 0.027778 | T | Raining & Thundering, | 13 | 8.6667 | Power interruption
Haripur 230/132kV | Madanganj-1 | 2025-07-24 03:37 | 2025-07-24 04:57 | 0.055556 | T | Raining & Thundering. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-07-25 11:01 | 2025-07-25 11:43 | 0.029167 | T | Tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2025-07-07 11:33 | 2025-07-07 12:30 | 0.039583 | T | Motor fault in their mail section | 7 | 6.65 | Power interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2025-07-16 18:01 | 2025-07-16 22:21 | 0.18056 | T | Tripped | 6 | 26 | Power interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-07-24 03:40 | 2025-07-24 04:50 | 0.048611 | T | Tripped | 40 | 46.6667 | Power interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2025-07-24 03:40 | 2025-07-24 04:50 | 0.048611 | T | Tripped | 60 | 70 | Power interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-2 | 2025-07-24 03:40 | 2025-07-24 04:50 | 0.048611 | T | Tripped | 28 | 32.6667 | Power interruption
Maniknagar 132/33kV | Motijheel Ckt-2 | 2025-07-24 10:21 | 2025-07-24 10:21 | 0 | T | TT Para underground cable fault . | 0 | 0 | No interruption
Narshingdi 132/33kV | Ghorasal-01 | 2025-07-18 09:21 | 2025-07-18 09:40 | 0.013194 | T | Dis. Fault | 105 | 33.25 | No interruption
Siddhirganj 132/33kV | 132kV MTR 1 | 2025-07-11 05:39 | 2025-07-11 14:13 | 0.35694 | T | PRV Alarm 230 Kv side | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-07-05 09:32 | 2025-07-05 09:58 | 0.018056 | T | Due to Daudkandi end trip and their bus fault. simultaneously sonargaon end trip. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-07-05 09:32 | 2025-07-05 10:00 | 0.019444 | T | Due to Daudkandi end trip and their bus fault. simultaneously sonargaon end trip. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-07-24 03:03 | 2025-07-24 04:34 | 0.063194 | T | Bad weather | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-07-29 11:24 | 2025-07-29 13:50 | 0.10139 | E/O | Red hot maintenance work. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 1 | 2025-07-11 07:10 | 2025-07-11 14:13 | 0.29375 | E/O | MTR-1 Trip (PRV) | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-07-29 09:54 | 2025-07-29 14:26 | 0.18889 | E/O | According to the direction of NLDC | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-07-29 09:54 | 2025-07-29 14:26 | 0.18889 | E/O | According to the direction of NLDC-299724 | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 19:05 |  | Unserved Energy: |  | 223.9
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2025-07-26 13:15 | 2025-07-27 17:52 | 1899-12-31 04:37 | T | 3Phase fault | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2025-07-24 12:58 | 2025-07-24 13:09 | 0.0076389 | T | Distance trip | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-07-13 17:41 | 2025-07-13 18:05 | 0.016667 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-01 | 2025-07-07 22:37 | 2025-07-08 14:49 | 0.675 | T | Tripped | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2025-07-13 18:43 | 2025-07-13 19:11 | 0.019444 | T | due to thundering | 0 | 0 | No interruption
Baroirhat 132/33kV | PHP | 2025-07-16 08:45 | 2025-07-16 17:41 | 0.37222 | E/O | PHP SS S/D | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 06:48 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chowmuhani 132/33kV | Ramganj line-01 | 2025-07-23 00:59 | 2025-07-24 00:14 | 0.96875 | T | Over Thundering | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-02 | 2025-07-23 23:59 | 2025-07-24 00:15 | 0.011111 | T | Over Thundering | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2025-07-24 02:14 | 2025-07-24 11:49 | 0.39931 | T | None | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2025-07-05 09:32 | 2025-07-05 09:57 | 0.017361 | T | Total substation dead because main busbar fault . | 25 | 10.4167 | Power interruption
Daudkandi 132/33kV | Sonargaon-2 | 2025-07-05 09:32 | 2025-07-05 10:02 | 0.020833 | T | Total substation dead because main busbar fault . | 25 | 12.5 | Power interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-07-05 09:32 | 2025-07-05 10:13 | 0.028472 | T | Total substation dead because main busbar fault . | 10 | 6.8333 | Power interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2025-07-05 09:32 | 2025-07-05 10:14 | 0.029167 | T | Total substation dead because main busbar fault . | 10 | 7 | Power interruption
Daudkandi 132/33kV | Titas 50 MW Power Plant Line | 2025-07-05 09:32 | 2025-07-05 09:58 | 0.018056 | T | Total substation dead because main busbar fault . | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-07-08 02:28 | 2025-07-08 02:54 | 0.018056 | T | N/A | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-07-12 17:58 | 2025-07-12 18:07 | 0.00625 | T | Tripped | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Shahajibazar 132 kV Ckt-3 | 2025-07-31 19:06 | 2025-07-31 19:52 | 0.031944 | E/O | Asper instruction of NLDC | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-07-27 04:56 | 2025-07-27 07:25 | 0.10347 | E/O | Fenchugonj line shutdown for redhot | 70 | 173.8333 | Power interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-07-01 07:35 | 2025-07-01 08:42 | 0.046528 | E/O | Red Hot Maintenance in Ramgonj Substation . | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 16:47 |  | Unserved Energy: |  | 210.5833
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-07-11 01:51 | 2025-07-11 09:10 | 0.30486 | T | Unknown | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-07-21 08:20 | 2025-07-21 08:36 | 0.011111 | T | None | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-07-21 08:47 | 2025-07-21 14:50 | 0.25208 | T | Tripped | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-07-25 15:19 | 2025-07-25 15:31 | 0.0083333 | T | Unknown | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2025-07-25 12:09 | 2025-07-25 14:32 | 0.099306 | T | Tree broken. | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2025-07-25 12:09 | 2025-07-25 14:33 | 0.1 | T | b to c phase to phase fault | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-07-25 16:04 | 2025-07-25 18:18 | 0.093056 | T | Tripped | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-07-11 01:51 | 2025-07-11 09:10 | 0.30486 | T | line-1 tripped at 1:51 Distance Realy Showed 10.84 km | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-07-25 15:19 | 2025-07-26 15:33 | 1899-12-31 00:14 | T | B phase or Y phase tear at 30 no tower. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-07-26 08:57 | 2025-07-26 09:50 | 0.036806 | T | Distance Relay Trip | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-07-21 08:25 | 2025-07-21 09:43 | 0.054167 | E/O | Red hot Maintenance at Barishal Sub-Station End. | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2025-07-22 15:40 | 2025-07-22 17:24 | 0.072222 | E/O | Ordered by ALDC khulna. | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2025-07-26 09:54 | 2025-07-26 16:03 | 0.25625 | E/O | Emergency maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2025-07-26 09:54 | 2025-07-26 16:03 | 0.25625 | E/O | Emergency maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-07-07 12:57 | 2025-07-07 13:07 | 0.0069444 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-07-26 08:57 | 2025-07-26 15:33 | 0.275 | E/O | B phase Conductor tear at 30 no tower. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 03:23 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jashore 132/33kV | JH-2(L1) | 2025-07-13 14:41 | 2025-07-13 18:15 | 0.14861 | T | Trip | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-07-22 13:27 | 2025-07-22 13:44 | 0.011806 | T | Phase A, Trip ABC | 128 | 36.2667 | Power interruption
Jashore 132/33kV | Cap. Bank-1 | 2025-07-22 13:27 | 2025-07-22 14:02 | 0.024306 | T | Trip | 0 | 0 | No interruption
Jashore 132/33kV | NOA-1(L3) | 2025-07-26 08:58 | 2025-07-26 09:50 | 0.036111 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-07-13 14:41 | 2025-07-13 18:13 | 0.14722 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2025-07-22 13:26 | 2025-07-22 13:43 | 0.011806 | T | Zone-1 operated, Fault Distance location 23km. | 132 | 37.4 | No interruption
Bheramara 230/132kV | GK 2 | 2025-07-27 11:22 | 2025-07-27 13:21 | 0.082639 | E/O | DS Loop maintenance work at GK end | 0 | 0 | No interruption
Bheramara 230/132kV | GK 2 | 2025-07-27 11:22 | 2025-07-27 13:21 | 0.082639 | E/O | DS Loop maintenance work at GK end | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-2 | 2025-07-27 11:20 | 2025-07-27 13:22 | 0.084722 | E/O | Loop maintenance | 0 | 0 | No interruption
|  |  | Total : | 0.62986 |  | Unserved Energy: |  | 73.6667
Bogura Grid Circle:
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-07-21 19:05 | 2025-07-21 20:47 | 0.070833 | T | Directional over current | 30 | 51 | Power interruption
Barapukuria 230/132/33kV | PS 230 KV Ckt2 | 2025-07-21 19:05 | 2025-07-21 20:08 | 0.04375 | T | Tripped | 30 | 31.5 | Power interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-07-21 20:48 | 2025-07-21 21:38 | 0.034722 | T | Tripped | 32 | 26.6667 | Power interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2025-07-21 20:48 | 2025-07-21 21:49 | 0.042361 | T | Tripped | 32 | 32.5333 | Power interruption
Bogura 230/132kV | Confidance UN-2 | 2025-07-21 19:06 | 2025-07-21 19:18 | 0.0083333 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2025-07-21 20:33 | 2025-07-22 12:04 | 0.64653 | T | 1.Lockout Relay Operated 2.START BFP 3 Phase 3.Lockout Relay (KT86.1) Operated. 4.Lockout Relay (KT86.2) Operated. 5.Lockout-1(K86.1) Operated. 6.Lockout-2(K86.2) Operated. 7.3P INITIATION 8.Lockout Optd. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-21 19:07 | 2025-07-21 19:15 | 0.0055556 | T | Over Current | 204 | 27.2 | Power interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-21 20:50 | 2025-07-21 20:59 | 0.00625 | T | Distance Trip | 54 | 8.1 | Power interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-23 13:11 | 2025-07-23 14:25 | 0.051389 | T | Distance Trip Ia - 4.28 ka In - 3.70 ka | 98 | 120.8667 | Power interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2025-07-25 03:56 | 2025-07-25 09:15 | 0.22153 | T | R phase trip CB ( Y,B Phase not tripped) | 0 | 0 | No interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2025-07-25 03:56 | 2025-07-25 09:15 | 0.22153 | T | R phase trip CB ( Y,B Phase not tripped) | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-21 19:06 | 2025-07-21 19:20 | 0.0097222 | T | SPS Relay pick up | 85 | 19.8333 | Power interruption
Palashbari 132/33kV | Mithapukur-01 | 2025-07-21 19:06 | 2025-07-21 19:22 | 0.011111 | T | SPS Relay operate | 42 | 11.2 | Power interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-07-21 19:06 | 2025-07-21 19:31 | 0.017361 | T | SPS Relay operate | 42 | 17.5 | Power interruption
Palashbari 132/33kV | Mahasthangarh-02 | 2025-07-21 20:45 | 2025-07-21 20:54 | 0.00625 | T | Distance relay, Backup over current protection | 100 | 15 | Power interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2025-07-07 05:46 | 2025-07-07 08:22 | 0.10833 | T | Connected with Busbar-2 | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-02 | 2025-07-07 05:46 | 2025-07-21 14:48 | 1900-01-13 09:02 | T | Connected with Busbar-2 | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-01 | 2025-07-25 03:56 | 2025-07-25 09:13 | 0.22014 | T | R phase trip,Zone-02 trip,Relay General trip | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-07-31 11:05 | 2025-07-31 11:35 | 0.020833 | T | Bad weather. | 59 | 29.5 | Power interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-07-21 21:38 | 2025-07-21 21:38 | 0 | E/O | 230 KV circuit breaker Pole discrepancy problem at BPDB power station end. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | PS 230 KV Ckt1 | 2025-07-21 21:38 | 2025-07-22 11:28 | 0.57639 | E/O | 230KV circuit breaker Pole discrepancy problem at BPDB power station end. | 32 | 107.7333 | Power interruption 21:38 to 1:00
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-07-21 22:51 | 2025-07-22 02:27 | 0.15 | E/O | 132 KV circuit breaker R phase pole don't operate nat saidpur Sub station .so need shut down for bypass with bus coupler breaker at saidpur Sub station. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-07-16 17:49 | 2025-08-04 12:14 | 1900-01-17 18:25 | E/O | Line VT( Y-Phase) Unwanted noise rechecking work finish.Line VT Problem. | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-2 | 2025-07-19 10:01 | 2025-07-19 14:03 | 0.16806 | E/O | According to order of ALDC Bogura. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-07-21 22:35 | 2025-07-22 02:24 | 0.15903 | E/O | Baropukuria ckt-02 Breaker (R- phase) pole not opened. | 0 | 0 | No interruption
|  |  | Total : | 1900-02-03 22:39 |  | Unserved Energy: |  | 498.6333
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-15 10:21 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: July 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Tr-1(404T) | 2025-07-03 14:29 | 2025-07-03 15:59 | 1:30 | S/O | Feeder Bus DS supporting insulator change | 28 | 42 | Power interruption
Bajitpur 132/33kV | Tr-2(414T) | 2025-07-03 16:15 | 2025-07-03 18:11 | 1:56 | S/O |  | 11 | 21.2667 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-07-21 13:18 | 2025-07-21 14:19 | 1:01 | S/O | Oil level LO/HI signal not reset. | 40 | 40.6667 | Power interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-07-31 05:34 | 2025-07-31 07:21 | 1:47 | S/O | Due to temperature raise | 20 | 35.6667 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-07-31 07:25 | 2025-07-31 07:25 | 0:00 | S/O | Due to temperature raise | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2025-07-02 07:43 | 2025-07-02 10:29 | 2:46 | S/O | PBs maintenance work | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2025-07-17 06:26 | 2025-07-17 08:23 | 1:57 | S/O | Work by PBS. | 60 | 117 | Power interruption
Jamalpur 132/33kV | T-1 | 2025-07-01 14:26 | 2025-07-01 15:36 | 1:10 | S/O | 33kv sarishabari feeder breaker D.S connector RedHot maintenance work by S.PDB | 10 | 11.6667 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-07-02 19:40 | 2025-07-02 22:34 | 2:54 | S/O | Shutdown taken by DPBS-1 due to 33 KV Section bus DS high temperature maintenance work | 104 | 301.6 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-07-04 07:17 | 2025-07-04 15:23 | 8:06 | S/O | 33 BUS DS Change work | 30 | 243 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-07-12 11:33 | 2025-07-12 14:28 | 2:55 | S/O | 33 kV Bus section D/S change work | 60 | 175 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-07-12 11:33 | 2025-07-12 17:55 | 6:22 | S/O | 33kV Bus section D/S change work | 90 | 573 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-07-21 06:22 | 2025-07-21 08:34 | 2:12 | S/O | 33 kv bus section ds maintenance. | 82 | 180.4 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-07-21 06:27 | 2025-07-21 09:18 | 2:51 | S/O | 33 kv bus section ds maintenance. | 64 | 182.4 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-07-21 16:40 | 2025-07-21 18:20 | 1:40 | S/O | DS maintanence work of Auxiliary Transformer-1 | 75 | 125 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-07-25 06:31 | 2025-07-25 10:16 | 3:45 | S/O | Loop connection of Auxiliary Transformer-1 | 60 | 225 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-07-02 08:37 | 2025-07-02 08:37 | 0:00 | S/O | Project Works | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-07-08 08:30 | 2025-07-08 18:01 | 9:31 | S/O | Due to 33kv side loop connection for Aux Transformer -03 | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-07-16 06:31 | 2025-07-16 09:56 | 3:25 | S/O | 33 kv Bus Shutdown, pakundia feeder hotspot maintenance work. | 30 | 102.5 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-07-16 06:55 | 2025-07-16 09:07 | 2:12 | S/O | 33 kv bus Shutdown,due to PBD feeder hotspot maintenance work | 10 | 22 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-07-27 05:57 | 2025-07-27 10:18 | 4:21 | S/O | 33/0.4kv Aux Tr-2 DS Installation work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-07-27 05:57 | 2025-07-27 10:16 | 4:19 | S/O | 33/0.4kv Aux Tr-2 DS Installation work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-07-06 09:51 | 2025-07-06 12:34 | 2:43 | S/O | Redhot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-07-26 08:19 | 2025-07-26 22:02 | 13:43 | S/O |  | 0 | 0 | No interruption
Kodda 132/33kV | Tr-4 (436T) | 2025-07-26 08:21 | 2025-07-26 19:08 | 10:47 | S/O |  | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-07-29 06:17 | 2025-07-29 08:40 | 2:23 | S/O | 33kV LDS maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-07-05 07:53 | 2025-07-05 18:50 | 10:57 | S/O |  | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-07-19 06:13 | 2025-07-19 12:40 | 6:27 | S/O |  | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-07-04 07:55 | 2025-07-04 17:14 | 9:19 | S/O | 132kV T3 Main Bus DS Installation in by G2G | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-07-05 08:01 | 2025-07-05 17:58 | 9:57 | S/O |  | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-07-06 10:25 | 2025-07-06 12:40 | 2:15 | S/O | 132 KV Reserve bus DS of T-3 XFr installation and alligenment adjustment. | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2025-07-02 17:57 | 2025-07-09 17:19 | 167:22 | S/O | OIL centrifuging | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-07-12 07:11 | 2025-07-12 08:25 | 1:14 | S/O | To perform red hot maintenance works of 33kV BPDB Gafargaon feeder. | 95 | 117.1667 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-07-26 06:29 | 2025-07-26 10:22 | 3:53 | S/O | To perform high temperature mitigate works of 132kV B-Bus B-Phase clamp. | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2025-07-26 06:50 | 2025-07-26 10:30 | 3:40 | S/O | To perform high temperature mitigate works of 132kV B-Bus B-Phase clamp. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-07-19 09:22 | 2025-07-19 13:02 | 3:40 | S/O | Red Hot 33 KV Bus Side | 15 | 55 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-07-05 08:33 | 2025-07-05 20:41 | 12:08 | S/O | Changing Jack bus conductor | 20 | 242.6667 | Power interruption
|  |  | Total : | 1900-01-12 15:08 |  | Unserved Energy: |  | 2813
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2025-07-12 08:30 | 2025-07-12 12:06 | 3:36 | S/O | Shutdown Requisition from project-1 (Energy Pack) for repair oil leakage X-former & 33kV LA,PT, Bus Cupler and replacing damage nut-bolt in switching. | 70 | 252 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-07-12 16:30 | 2025-07-12 18:21 | 1:51 | S/O | Shutdown Requisition from project-1 (Energy Pack) for repair oil leakage X-former & 33kV LA,PT, Bus Cupler and replacing damage nut-bolt in switching. | 70 | 129.5 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-07-29 11:35 | 2025-07-29 13:12 | 1:37 | S/O | Transformer Bushing clamp tightening. | 53 | 85.6833 | Power interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-07-01 09:32 | 2025-07-01 09:32 | 0:00 | S/O | GND Project Work | 0 | 0 | No interruption
Haripur 230/132kV | Bus-1 | 2025-07-05 09:01 | 2025-07-06 17:00 | 31:59 | S/O | Meghnaghat 2 DS replacement | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-07-03 16:58 | 2025-07-03 19:02 | 2:04 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-07-17 17:11 | 2025-07-17 19:04 | 1:53 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2025-07-17 17:42 | 2025-07-17 19:18 | 1:36 | S/O | Maint.work | 6 | 9.6 | Power interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-07-29 11:42 | 2025-07-29 13:21 | 1:39 | S/O | 132 kV Isolator maintenance work (DS-121) | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -02 | 2025-07-18 10:12 | 2025-07-18 11:54 | 1:42 | S/O | Maintenence purpose | 0 | 0 | No interruption
Narshingdi 132/33kV | Bhu | 2025-07-18 07:30 | 2025-07-18 10:45 | 3:15 | S/O | 95 no tower jumper reconnection | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2025-07-25 06:58 | 2025-07-25 08:07 | 1:09 | S/O | T-point maintenance | 45 | 51.75 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-07-25 08:22 | 2025-07-25 13:11 | 4:49 | S/O | Emergency Maintenance | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2025-07-24 21:50 | 2025-07-24 22:06 | 0:16 | S/O | Red Hot problem in Feeder-4 of 33 KV bus section. | 0 | 0 | No interruption
Srinagar 132/33kV | 33 kV bus | 2025-07-24 21:50 | 2025-07-24 22:06 | 0:16 | S/O | Red Hot problem in Feeder-4 of 33 KV bus section. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2025-07-25 11:12 | 2025-07-25 12:26 | 1:14 | S/O | 33 KV Bus Shutdown for Red Hot Maintenance | 20 | 24.6667 | Power interruption
Srinagar 132/33kV | 33 kV bus | 2025-07-25 11:12 | 2025-07-25 12:26 | 1:14 | S/O | 33 KV Bus Shutdown for Red Hot Maintenance | 0 | 0 | Power interruption
|  |  | Total : | 1900-01-01 12:10 |  | Unserved Energy: |  | 553.2
Chattogram Grid Circle :
Baroaulia 132/33kV | T-1(405T) | 2025-07-03 15:51 | 2025-07-03 16:17 | 0:26 | S/O | T-1 circuit breaker change work | 0 | 0 | No interruption
Baroaulia 132/33kV | T2(415T) | 2025-07-13 14:31 | 2025-07-13 15:01 | 0:30 | S/O | TR-2 (412B) CB Change. | 0 | 0 | No interruption
Baroaulia 132/33kV | T-1(405T) | 2025-07-23 07:00 | 2025-07-23 09:12 | 2:12 | S/O | Mainbus DS B phase redhot maintanance | 10 | 22 | Power interruption
Coxsbazar 132/33kV | T3 | 2025-07-23 09:24 | 2025-07-23 09:57 | 0:33 | S/O | T-3 Tripped due 33 kV over current Auxiliary Station Transformar Dropout fuse flashing. | 60 | 33 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-07-23 14:48 | 2025-07-23 15:57 | 1:09 | S/O | Due to Dohazari 33 kv feeder redhot maintenance | 71 | 81.65 | Power interruption
Hathazari 230/132/33kV | MT-02 | 2025-07-02 09:28 | 2025-07-12 12:20 | 242:52 | S/O | Oil centrifusing | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-07-30 06:06 | 2025-07-30 11:00 | 4:54 | S/O | 33 kv Bus maintenance | 40 | 196 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-07-16 10:31 | 2025-07-16 20:59 | 10:28 | S/O | Upgrading by BPDB | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-07-18 11:21 | 2025-07-18 22:50 | 11:29 | S/O | Upgrading work for BPDB | 0 | 0 | No interruption
Khulshi 132/33kV | 415T (T2) | 2025-07-09 11:57 | 2025-07-09 13:43 | 1:46 | S/O | 33 kv loop maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-07-26 09:00 | 2025-07-26 16:00 | 7:00 | S/O | 33 KV side Isolator Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-3(725T) | 2025-07-12 11:22 | 2025-07-17 15:24 | 124:02 | S/O | Fire protection maintenance by project | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-1(705T) | 2025-07-31 12:07 | 2025-07-31 18:31 | 6:24 | S/O | SCADA operation by the CNTIC Project Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-16 05:45 |  |  |  | 332.65
Cumilla Grid Circle :
Ashuganj 230/132/33kV | TR-OAT-12 | 2025-07-29 05:38 | 2025-07-29 18:05 | 12:27 | S/O | due to 132KV busbar-1 temperature issue | 0 | 0 | No interruption
Ashuganj 230/132/33kV | T-4 Kalabagan | 2025-07-29 07:44 | 2025-07-29 16:44 | 9:00 | S/O | Due to 132KV Busbar-1 tempereture issue | 50 | 450 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 | 2025-07-02 08:36 | 2025-07-02 11:32 | 2:56 | S/O | 33kV Bus-1 Maintenance for PBS | 27 | 79.2 | Power interruption
Chhatak 132/33kV | T-1 | 2025-07-25 10:10 | 2025-07-25 13:05 | 2:55 | S/O | Shutdown needed for 33KV T-1 and T-3 Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for separate the 110v DC from 33kv Companiganj PBS Panel. | 10 | 29.1667 | Power interruption
Chhatak 132/33kV | T-3 | 2025-07-25 10:10 | 2025-07-25 13:05 | 2:55 | S/O | Shutdown needed for 33KV T-1 and T-3 Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for separate the 110v DC from 33kv Companiganj PBS Panel. | 10 | 29.1667 | Power interruption
Chowmuhani 132/33kV |  | 2025-07-06 22:30 | 2025-07-07 00:27 | 1:57 | S/O | TR2 33 KV Side incoming L- Bus incoming Loop Red Hot. | 40 | 78 | Power interruption
Chowmuhani 132/33kV |  | 2025-07-09 21:37 | 2025-07-09 23:30 | 1:53 | S/O | Red Hot Maintenance | 30 | 56.5 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-07-13 14:58 | 2025-07-13 20:04 | 5:06 | S/O | U/G Cable Maintenance Purposed. | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2025-07-31 07:03 | 2025-07-31 12:04 | 5:01 | S/O | Red hot maintenance by PBS-3 | 30 | 150.5 | Power interruption
Feni 132/33kV | Bus-1 | 2025-07-20 07:05 | 2025-07-20 08:26 | 1:21 | S/O | Chaumuhani 33kv feeder loop repair | 27 | 36.45 | Power interruption
Feni 132/33kV | T-2(415T) | 2025-07-24 07:23 | 2025-07-24 09:57 | 2:34 | S/O | 33KV CT clamp red hot work | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-07-31 12:45 | 2025-07-31 20:05 | 7:20 | S/O | Project Work | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2025-07-24 12:39 | 2025-07-24 16:02 | 3:23 | S/O | 33kv REB shubornachor CT connector and breaker maintanance | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2025-07-24 12:39 | 2025-07-24 16:02 | 3:23 | S/O | 33kv REB shudharam feeder CT connector and breaker maintanance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-07-11 07:40 | 2025-07-11 10:52 | 3:12 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-07-11 07:42 | 2025-07-11 10:50 | 3:08 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-11 07:49 | 2025-07-11 09:56 | 2:07 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-14 12:40 | 2025-07-14 20:16 | 7:36 | S/O | Tr-02 Tripping fault maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-19 09:51 | 2025-07-19 16:10 | 6:19 | S/O | Shutdown taken by PDB for changing Isolator. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-07-27 22:33 | 2025-07-27 23:23 | 0:50 | S/O | Red Hot Maintenance | 10 | 8.3333 | Power interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-07-21 09:55 | 2025-07-21 10:25 | 0:30 | S/O | For 33kV GCB gas refiling work. | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2025-07-12 08:10 | 2025-07-12 17:56 | 9:46 | S/O | 33KV Sunamganj and Derai PDB Bay Extension. | 15 | 146.5 | Power interruption
Sylhet (South) | Trafo-2 | 2025-07-05 07:15 | 2025-07-05 17:32 | 10:17 | S/O | PDB Bay extension work. | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-07-04 07:17 | 2025-07-04 11:20 | 4:03 | S/O | T-1 33 KV bus "Y" phase conductor change. | 24 | 97.2 | Power interruption
|  |  | Total : | 1900-01-03 13:59 |  |  |  | 1161.0167
Khulna Grid Circle :
Barguna 132/33kV | Transformer-2 | 2025-07-20 17:23 | 2025-07-20 18:03 | 0:40 | S/O | WZPDCL-1 , B-Phase Hi Temperature Maintenance. | 8 | 5.3333 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-07-14 04:22 | 2025-07-14 06:14 | 1:52 | S/O | WZPDCL 33kV Jhalokathi feeder loop disconnect from 33kV Bus. S/D taken by WZDPCL | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2025-07-20 06:30 | 2025-07-20 09:27 | 2:57 | S/O | Red hot maintenance and loop changing work at 33kV incoming ( 33kV CB to DS ) | 42 | 123.9 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-07-21 06:06 | 2025-07-21 07:45 | 1:39 | S/O | T-2 HT bushing high temperature Remedy work | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2025-07-26 06:08 | 2025-07-26 08:25 | 2:17 | S/O | High temperature remedy work | 25 | 57.0833 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-07-26 08:41 | 2025-07-26 10:25 | 1:44 | S/O | High temperature remedy work | 0 | 0 | No interruption | 14:29
Barishal 230/132kV | T-5 | 2025-07-04 09:11 | 2025-07-04 11:02 | 1:51 | S/O | Maint.work | 30 | 55.5 | Power interruption
Barishal 230/132kV | T-5 | 2025-07-05 13:20 | 2025-07-05 13:51 | 0:31 | S/O | Bus balance checking by Energy Audit Barishal. | 50 | 25.8333 | Power interruption
Barishal 230/132kV | ATR-1 | 2025-07-08 12:07 | 2025-07-08 17:37 | 5:30 | S/O | Oil leakage repair and oil refill of auxiliary transformer of ATR-1 | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2025-07-17 11:27 | 2025-07-17 13:14 | 1:47 | S/O | Maint.work | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2025-07-20 17:15 | 2025-07-20 18:37 | 1:22 | S/O | Nobogram 33 kV feeder Bus DS maintenance (Y-phase) | 38 | 51.9333 | Power interruption
Barishal 230/132kV | T-5 | 2025-07-24 14:35 | 2025-07-24 18:17 | 3:42 | S/O | 33kv busbar section DS maintenance by Pirojpur PBS | 16 | 59.2 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2025-07-17 06:45 | 2025-07-17 09:30 | 2:45 | S/O | Red hot maintenance at 33 KV busbar and DS. | 75 | 206.25 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2025-07-20 06:29 | 2025-07-20 08:31 | 2:02 | S/O | Red Hot Maintenance. | 45 | 91.5 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-07-04 07:39 | 2025-07-04 09:27 | 1:48 | S/O | Red hot Maintenance. | 45 | 81 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-07-06 07:37 | 2025-07-06 10:30 | 2:53 | S/O | 33 Kv Bus-section-3 Hotspot Maintenance. | 50 | 144.1667 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-07-26 07:23 | 2025-07-26 12:09 | 4:46 | S/O | Maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2025-07-15 16:49 | 2025-07-15 18:01 | 1:12 | S/O | Khulna PBS taken Shutdown due to remove red hot on Therokhada feeder | 8 | 9.6 | Power interruption
Goalpara 132/33kV | T-5 | 2025-07-15 16:51 | 2025-07-15 17:59 | 1:08 | S/O | Khulna PBS taken Shutdown due to remove red hot on Therokhada feeder | 8 | 9.0667 | Power interruption
Goalpara 132/33kV | T-6 | 2025-07-15 16:54 | 2025-07-15 17:57 | 1:03 | S/O | Khulna PBS taken Shutdown due to remove red hot on Therokhada feeder | 8 | 8.4 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-07-13 12:08 | 2025-07-13 12:50 | 0:42 | S/O | Winding Thermometer -2 maintenance of T-2 Transformer. | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2025-07-18 08:05 | 2025-07-18 10:14 | 2:09 | S/O | PBS Maintenance Work | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2025-07-29 15:47 | 2025-07-29 19:05 | 3:18 | S/O | 33 kv bus Section-3 DS maintenance. | 55 | 181.5 | Power interruption
Gopalganj 400/132kV | ATR-04 | 2025-07-04 21:45 | 2025-07-04 22:56 | 1:11 | S/O | Project Work | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-07-12 13:06 | 2025-07-12 14:04 | 0:58 | S/O | T-1 Transformer leak repair work | 0 | 0 | No interruption
Rampal 400/230kV | Generator Transformer-1 (GT-1) | 2025-07-14 15:20 | 2025-07-14 15:20 | 0:00 | S/O | Permit taken Against PTW 19555 | 0 | 0 | No interruption
Rampal 400/230kV | Generator Transformer-2 (GT-2) | 2025-07-19 10:40 | 2025-07-19 10:40 | 0:00 | S/O | Electrical Protection Checking | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 03:47 |  | Unserved Energy : |  | 1110.2667
HVDC Grid Circle
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-07-05 07:04 | 2025-07-05 14:24 | 7:20 | S/O | Red Hot Maintenance | 35 | 256.6667 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2025-07-05 07:10 | 2025-07-05 14:27 | 7:17 | S/O | Red Hot Maintenance | 35 | 254.9167 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-2 | 2025-07-20 18:11 | 2025-07-20 18:30 | 0:19 | S/O | station auxiliary fuse changing work. | 30 | 9.5 | Power interruption
Ishurdi 132/33kV | 132 kV Bus-2 | 2025-07-21 10:15 | 2025-07-21 13:55 | 3:40 | S/O | Bus DS-649S redhot maintenance work. | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 | 2025-07-11 07:20 | 2025-07-11 09:23 | 2:03 | S/O | Project Work | 42 | 86.1 | Power interruption
Ullahpara 132/33kV | Power Transformer -1 | 2025-07-27 09:37 | 2025-07-27 13:20 | 3:43 | S/O | Project Work | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer -1 | 2025-07-27 09:38 | 2025-07-27 13:18 | 3:40 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 04:02 |  | Unserved Energy : |  | 607.1833
Bogura Grid Circle:
Amnura 132/33kV | T-2 (416T) | 2025-07-01 22:21 | 2025-07-01 23:26 | 1:05 | S/O | Emergency maintenance work (Red Hot) for GOMOSTAPUR 33KV feeder under Transformer-02 & 33kV bus Section-3 | 19 | 20.5833 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2025-07-12 09:25 | 2025-07-12 13:32 | 4:07 | S/O | NESCO work | 22 | 90.5667 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-07-16 16:06 | 2025-07-16 18:34 | 2:28 | S/O | Red hot maintenance at NESCO switching, moddhopara feeder | 30 | 74 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-07-19 06:08 | 2025-07-19 08:29 | 2:21 | S/O | Red hot Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2025-07-19 08:40 | 2025-07-19 09:42 | 1:02 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-07-05 10:25 | 2025-07-05 11:46 | 1:21 | S/O | For installation of Transformer-3 | 8 | 10.8 | Power interruption
Bog-Sherpur 132/33kV | Main Bus-1 | 2025-07-19 09:32 | 2025-07-19 10:52 | 1:20 | S/O | For installation work of transformer 3 | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Main Bus-2 | 2025-07-19 11:09 | 2025-07-19 13:10 | 2:01 | S/O | For installation work of transformer 3 | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Main Bus-1 | 2025-07-23 16:43 | 2025-07-27 15:45 | 95:02 | S/O | Maint.work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-07-23 17:05 | 2025-07-23 19:12 | 2:07 | S/O | Maint.work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-07-24 08:55 | 2025-07-24 10:15 | 1:20 | S/O | Maint.work | 10 | 13.3333 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-07-14 08:19 | 2025-07-14 13:59 | 5:40 | S/O | Junction point temperature high (red hot) | 15 | 85 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-07-19 07:57 | 2025-07-19 20:14 | 12:17 | S/O | Red hot. | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2025-07-09 09:14 | 2025-07-09 13:34 | 4:20 | S/O | City test | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-07-11 09:29 | 2025-07-11 11:04 | 1:35 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-07-14 10:38 | 2025-07-14 18:27 | 7:49 | S/O | Painting work by STGEP project | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-07-16 08:40 | 2025-07-16 19:26 | 10:46 | S/O | ATR-01 Painting. | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-07-17 09:17 | 2025-07-17 18:02 | 8:45 | S/O | ATR-02 PAINTING | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-07-18 08:17 | 2025-07-18 18:30 | 10:13 | S/O | Painting | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-07-19 08:35 | 2025-07-19 15:35 | 7:00 | S/O | ATR-02 Painting. | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-07-20 09:00 | 2025-07-20 18:28 | 9:28 | S/O | Painting work | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-07-21 08:47 | 2025-07-21 18:10 | 9:23 | S/O | Painting work of ATR-03 | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-07-24 13:15 | 2025-07-24 16:05 | 2:50 | S/O | Painting work | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2025-07-04 08:30 | 2025-07-04 13:03 | 4:33 | S/O | 33 kv barendra feeder bus loop change maintenance work | 25 | 113.75 | Power interruption
Chapai 132/33kV | T-3 (425T) | 2025-07-04 09:30 | 2025-07-04 11:42 | 2:12 | S/O | T-2 & T-03 broken bus section DS insulator change. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-07-03 14:43 | 2025-07-03 16:57 | 2:14 | S/O | 33 kv Bpbs-2 Sukanpukur Feeder Bus ds Damage | 30 | 67 | Power interruption
Mahasthangarh 132/33kV | 132KVMain bus 2 | 2025-07-16 10:01 | 2025-07-16 12:51 | 2:50 | S/O | Maint.work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 132KVMain bus 2 | 2025-07-17 14:52 | 2025-07-17 18:04 | 3:12 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-07-19 08:22 | 2025-07-19 11:12 | 2:50 | S/O | Project work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-07-19 11:21 | 2025-07-19 17:35 | 6:14 | S/O | Project work | 15 | 93.5 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-07-26 08:28 | 2025-07-26 12:53 | 4:25 | S/O | Nesco mahasthangarh 33 kv feeder sky wire maintenance. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 33KV Main bus T-1 | 2025-07-26 08:35 | 2025-07-26 12:54 | 4:19 | S/O | Nesco mahasthangarh 33 kv feeder sky wire maintenance. | 14 | 60.4333 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-07-29 15:30 | 2025-07-29 17:01 | 1:31 | S/O | Kalai 33 kV Feeder Source side DS Maintemance Work. | 30 | 45.5 | Power interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-07-14 08:45 | 2025-07-14 09:39 | 0:54 | S/O | Red hot LT side B ph | 20 | 18 | Power interruption
Purbasadipur 132/33kV | T-4 Transformer | 2025-07-21 09:15 | 2025-07-21 14:30 | 5:15 | S/O | Re-routing work of 33kV Sadar feeder | 5 | 26.25 | Power interruption
Rahanpur 400/132kV | AT-02 | 2025-07-08 08:26 | 2025-07-08 18:45 | 10:19 | S/O | Maint.work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-07-09 08:32 | 2025-07-09 17:00 | 8:28 | S/O | Due to project painting work. | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-07-11 09:02 | 2025-07-11 21:06 | 12:04 | S/O | Painting work at ATR-02 | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-07-12 09:21 | 2025-07-12 19:56 | 10:35 | S/O | Painting work at ATR-01 | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-07-13 08:38 | 2025-07-13 18:36 | 9:58 | S/O | Due to ATR-01 Painting work. | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-07-25 09:06 | 2025-07-25 10:30 | 1:24 | S/O | For painting work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-07-25 10:42 | 2025-07-25 18:20 | 7:38 | S/O | For painting work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-07-26 08:39 | 2025-07-26 18:28 | 9:49 | S/O | Due to project painting work. | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-07-27 08:32 | 2025-07-27 18:32 | 10:00 | S/O | Maint.work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-07-31 07:41 | 2025-07-31 09:38 | 1:57 | S/O | To remove red hotspot at Taherpur feeder at 33 Kv BUS side. | 20 | 39 | Power interruption
Rangpur 132/33kV | 33KV Bus | 2025-07-09 15:30 | 2025-07-09 17:40 | 2:10 | S/O | temparature high | 85 | 184.1667 | Power interruption
Rangpur 132/33kV | 33KV Bus | 2025-07-14 06:25 | 2025-07-14 07:45 | 1:20 | S/O | temperature high | 60 | 80 | Power interruption
Rangpur 132/33kV | T-2 (404T) | 2025-07-14 06:25 | 2025-07-14 07:45 | 1:20 | S/O | Maint.work | 0 | 0 | Power interruption
Saidpur 132/33kV | TR-2 (404T) | 2025-07-13 10:38 | 2025-07-13 17:15 | 6:37 | S/O | Bus Isolator to 33kV busbar damage loop conductor of EPZ feeder replacement. As the instruction of NLDC, Dhaka | 0 | 0 | No interruption
|  |  | Total : | 1900-01-13 02:28 |  | Unserved Energy : |  | 1021.8833
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1329:19 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-07-22 14:27 | 2025-07-22 18:01 | 3:34 | S/O | Aminbazar-Kaliakoir 400kv conductor repair work. | 60 | 214 | Power interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2025-07-22 14:27 | 2025-07-22 18:37 | 4:10 | S/O | Aminbazar-Kaliakoir 400kv conductor repair work. | 60 | 250 | Power interruption
Kabirpur 132/33kV | Manikganj-1 | 2025-07-01 06:26 | 2025-07-01 09:05 | 2:39 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-18 06:56 | 2025-07-18 10:28 | 3:32 | S/O | Red hot maintenance work Line DS | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-25 10:08 | 2025-07-25 10:08 | 0:00 | S/O | Line checking | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-25 10:09 | 2025-07-25 11:47 | 1:38 | S/O | Right of way checking | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-07-25 12:49 | 2025-07-25 15:25 | 2:36 | S/O | Emergency Right of Way checking | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-07-25 12:49 | 2025-07-26 11:04 | 22:15 | S/O | Emergency Right of Way checking | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-07-12 10:45 | 2025-07-12 18:45 | 8:00 | S/O | P.W | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-07-18 06:50 | 2025-07-18 08:54 | 2:04 | S/O | Remove Redhot | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-07-01 21:18 | 2025-07-02 00:47 | 3:29 | S/O | Bus CT hotspot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 05:57 |  | Unserved Energy: |  | 464
Dhaka (South) Grid Circle :
Bhulta 132/33kV | Narsingdi | 2025-07-06 07:42 | 2025-07-06 07:42 | 0:00 | S/O | PG clamp connection | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Madanganj | 2025-07-11 10:25 | 2025-07-11 21:28 | 11:03 | S/O | OPGW cable reconnecting/maintenance work | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Hasnabad | 2025-07-28 17:23 | 2025-07-28 20:29 | 3:06 | S/O | The Line isolator at the Hasnabad substation is overheating | 0 | 0 | No interruption
Gulshan 132/33kV | Rampura-1 | 2025-07-25 07:25 | 2025-07-25 07:25 | 0:00 | S/O | IVT replacement work at Rampura Ckt-1 | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2025-07-04 06:28 | 2025-07-06 17:34 | 59:06 | S/O | Three Set Isolator (3000amp) Replaced. | 0 | 0 | No interruption
Haripur 230/132kV | Sonargaon 2 | 2025-07-19 09:43 | 2025-07-19 12:46 | 3:03 | S/O | ordered by NLDC | 0 | 0 | No interruption
Haripur 230/132kV | EGCB 412MW | 2025-07-23 13:05 | 2025-07-28 17:56 | 124:51 | S/O | 412 MW Power Plant Work by EGCB. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-07-11 10:13 | 2025-07-11 21:58 | 11:45 | S/O | OPGW maintenance through shampur 230 S/S | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-07-28 17:32 | 2025-07-28 20:28 | 2:56 | S/O | Red hot at line Yellow phase line D/S | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Kamrangirchar Ckt, | 2025-07-18 05:29 | 2025-07-18 13:03 | 7:34 | S/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-07-11 10:24 | 2025-07-11 21:30 | 11:06 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Start Up(MPL) | 2025-07-01 10:51 | 2025-07-01 18:10 | 7:19 | S/O | Maintenance Work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-ST (MPL) | 2025-07-18 06:42 | 2025-07-18 09:29 | 2:47 | S/O | DS heating problem | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-ST (MPL) | 2025-07-19 08:27 | 2025-07-19 09:40 | 1:13 | S/O | DS heating problem | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-07-16 09:08 | 2025-07-16 10:35 | 1:27 | S/O | Aminbazar ckt -1 shutdown for changing nut-bolts of 410-CT junction point | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-07-18 07:39 | 2025-07-18 09:21 | 1:42 | S/O | For Maintenence work | 0 | 0 | No interruption
Narshingdi 132/33kV | Haripur | 2025-07-18 07:30 | 2025-07-18 10:45 | 3:15 | S/O | 95 no tower jumper reconnection | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2025-07-24 11:15 | 2025-07-24 13:55 | 2:40 | S/O | Line DS and Earth Switch alignment maintenance work. | 0 | 0 | No interruption
Rampura 230/132kV | Gulshan Ckt-01 | 2025-07-25 07:36 | 2025-07-27 18:15 | 58:39 | S/O | S/D taken by NLDC and Gulshan S/S for IVT change | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-2 | 2025-07-19 09:42 | 2025-07-19 12:46 | 3:04 | S/O | Conductor Repairing work at Sonargaon - Haripur ckt 2 ( B phase). | 0 | 0 | No interruption
Sonargaon 132/33kV | OPML(IEL-1) | 2025-07-20 10:27 | 2025-07-20 16:32 | 6:05 | S/O | Line Distance Relay change purpose | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 10:41 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV | Bar Aulia | 2025-07-02 05:22 | 2025-07-02 06:39 | 1:17 | S/O | Baraulia sub station maintenance due to red hot. | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-07-25 06:37 | 2025-07-25 13:37 | 7:00 | S/O | Maintenance Works. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2025-07-18 06:19 | 2025-07-18 12:25 | 6:06 | S/O | Due to rectification work of 132 kV Khulsi ckt-03 Bus DS-01, Bus DS-02 and replacement of faulty LA. | 0 | 0 | No interruption
Hathazari 230/132/33kV | GPH-01 | 2025-07-25 06:40 | 2025-07-25 13:38 | 6:58 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-07-18 06:20 | 2025-07-18 10:56 | 4:36 | S/O | Halishahar Grid s/s project work. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-07-04 09:40 | 2025-07-04 12:28 | 2:48 | S/O | For Army project work. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-07-04 09:46 | 2025-07-04 12:29 | 2:43 | S/O | For Army project work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-07-05 09:41 | 2025-07-05 14:39 | 4:58 | S/O | Maintenance Works. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-07-05 10:09 | 2025-07-05 14:32 | 4:23 | S/O | Maintenance Works. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-07-06 09:29 | 2025-07-06 14:33 | 5:04 | S/O | Maintenance Works. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-07-06 09:35 | 2025-07-06 14:25 | 4:50 | S/O | Maintenance Works. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-07-25 06:19 | 2025-07-25 11:23 | 5:04 | S/O | For army project work. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-07-25 06:19 | 2025-07-25 11:27 | 5:08 | S/O | for army project work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-07-26 06:18 | 2025-07-26 09:18 | 3:00 | S/O | for army project work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-07-26 06:18 | 2025-07-26 09:18 | 3:00 | S/O | for army project work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 18:55 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-07-15 09:34 | 2025-07-15 15:17 | 5:43 | S/O | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV | B.Baria 132 kV Ckt-2 | 2025-07-19 09:16 | 2025-07-19 17:43 | 8:27 | S/O | 132KV GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-1 | 2025-07-19 09:46 | 2025-07-19 17:58 | 8:12 | S/O | 132KV GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV | B.Baria 132 kV Ckt-1 | 2025-07-20 14:36 | 2025-07-20 18:29 | 3:53 | S/O | 132KV GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Kishoreganj 132 kV Ckt-2 | 2025-07-29 07:25 | 2025-07-29 10:10 | 2:45 | S/O | due to 132KV busbar-1 temperature issue | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-07-29 10:25 | 2025-07-29 14:56 | 4:31 | S/O | due to 132KV busbar-1 temperature issue | 0 | 0 | No interruption
Bibiana 400/230kV | Summit STG | 2025-07-14 10:12 | 2025-07-22 11:25 | 193:13 | S/O | Maint.work | 0 | 0 | No interruption
Bibiana 400/230kV | Summit GTG | 2025-07-22 14:39 | 2025-07-29 11:43 | 165:04 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-07-16 09:15 | 2025-07-16 16:03 | 6:48 | S/O | relocation of 6nos. tower | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-07-16 09:15 | 2025-07-16 16:03 | 6:48 | S/O | relocation of 6 nos. tower | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-07-19 09:15 | 2025-07-19 17:45 | 8:30 | S/O | Project work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-07-20 14:35 | 2025-07-20 18:29 | 3:54 | S/O | Project work | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-07-25 06:49 | 2025-07-25 20:12 | 13:23 | S/O | Project work. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1 | 2025-07-29 19:25 | 2025-07-29 21:25 | 2:00 | S/O | Emergency shutdown of TR-01 for red hot occurs at R phase 33 KV side | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-07-04 09:54 | 2025-07-04 16:54 | 7:00 | S/O | Work for Tripura end | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-07-04 07:52 | 2025-07-04 10:23 | 2:31 | S/O | ফেনী সার্কিট -1 ৪২ - ৪৩ নং টাওয়ারের মাঝে R ফেজ এর কাজের জন্য TB EA প্রজেক্ট শাটডাউন নেয় | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-07-27 05:40 | 2025-07-27 07:10 | 1:30 | S/O | emergency maintenance | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2025-07-16 08:43 | 2025-07-16 17:55 | 9:12 | S/O | For Sub-station Maintenance at PHP End | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-2 | 2025-07-25 18:52 | 2025-07-25 20:13 | 1:21 | S/O | For LILO work by EEGBPS project. | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-07-26 06:40 | 2025-07-26 18:45 | 12:05 | S/O | For LILO work by EEGBPS project | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 1 | 2025-07-19 09:00 | 2025-07-20 20:03 | 35:03 | S/O | Maint.work | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -01 | 2025-07-19 08:37 | 2025-07-20 20:02 | 35:25 | S/O | Chowmuhani 230/132 KV GIS S/S interlocking test,testing activities related to Tr-1 and Maijdee line bay-2. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-07-08 05:47 | 2025-07-08 17:35 | 11:48 | S/O | Highway maintenance work | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-07-09 05:36 | 2025-07-09 17:51 | 12:15 | S/O | 0 | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-07-11 05:41 | 2025-07-11 16:05 | 10:24 | S/O | N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-02 | 2025-07-14 05:47 | 2025-07-14 17:56 | 12:09 | S/O | N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-07-26 09:15 | 2025-07-26 15:31 | 6:16 | S/O | S/D Taken By Ashuganj End | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-07-08 05:40 | 2025-07-08 17:34 | 11:54 | S/O | Roads and highways project works. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-07-09 05:36 | 2025-07-09 17:51 | 12:15 | S/O | For highway project work at Shistaganj. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-07-11 05:32 | 2025-07-11 16:01 | 10:29 | S/O | Due to the Roads and Highway project works in Shaistaganj. | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2025-07-14 05:43 | 2025-07-14 17:54 | 12:11 | S/O | For highway project work at Shistaganj. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-07-27 05:20 | 2025-07-27 07:10 | 1:50 | S/O | REDHOT | 15 | 27.5 | Power interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-07-27 05:20 | 2025-07-27 07:10 | 1:50 | S/O | REDHOT | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-07-24 05:35 | 2025-07-24 07:08 | 1:33 | S/O | High temp maintenance of CB terminal(Red phase) | 32 | 49.6 | Power interruption
|  |  | Total : | 1900-01-25 18:12 |  | Unserved Energy: |  | 77.1
Khulna Grid Circle :
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-07-21 08:24 | 2025-07-21 10:52 | 2:28 | S/O | CT High temperature removal works. | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2025-07-22 15:41 | 2025-07-22 17:24 | 1:43 | S/O | CT Oil Leakage Maintenance (R-Phase) | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2025-07-26 09:53 | 2025-07-26 16:01 | 6:08 | S/O | B phase armoring of North ckt-1 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-2 | 2025-07-26 09:53 | 2025-07-26 16:02 | 6:09 | S/O | B phase armoring of the north ckt-1 | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-07-03 12:25 | 2025-07-24 17:43 | 509:18 | S/O | Equipment Testing at Rooppur Power Station | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-07-30 11:32 | 2025-07-30 20:34 | 9:02 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-07-31 09:32 | 2025-07-31 21:12 | 11:40 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | PDB 330MW CCPP | 2025-07-03 16:38 | 2025-07-03 18:18 | 1:40 | S/O | DFDR Integration work | 0 | 0 | No interruption
Khulna(S) 230/132kV | PDB 330MW CCPP | 2025-07-05 09:44 | 2025-07-05 23:30 | 13:46 | S/O | DFDR Integration Work | 0 | 0 | No interruption
Khulna(S) 230/132kV | PDB 330MW CCPP | 2025-07-09 10:47 | 2025-07-09 21:03 | 10:16 | S/O | DFDR Intregration work | 0 | 0 | No interruption
Rajbari 132/33kV | Bheramara-1 | 2025-07-26 08:48 | 2025-07-26 14:35 | 5:47 | S/O | CB SF6 pressure manometer replacement | 0 | 0 | No interruption
|  |  | Total : | 1900-01-23 01:57 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | 20DF21 | 2025-07-24 11:11 | 2025-07-24 13:16 | 2:05 | S/O | Corrective Maintenance of AC Filter 20DF21 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-07-12 08:29 | 2025-07-12 21:14 | 12:45 | S/O | Shathia 132 s/s LILO between the middle of Ishwardi & baghabari 132 Kv line. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-07-19 14:19 | 2025-07-19 16:04 | 1:45 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2025-07-04 09:38 | 2025-07-04 15:21 | 5:43 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2025-07-04 09:39 | 2025-07-04 15:25 | 5:46 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-07-19 06:17 | 2025-07-19 14:32 | 8:15 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-07-22 08:21 | 2025-07-23 11:23 | 27:02 | S/O | shutdown | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-07-25 08:19 | 2025-07-29 11:06 | 98:47 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2025-07-01 13:12 | 2025-07-01 16:34 | 3:22 | S/O | Relay Testing work for Magura CKT- 1 at Magura Grid End. | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-07-19 06:17 | 2025-07-19 14:31 | 8:14 | S/O | Project works | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-07-22 08:22 | 2025-07-23 11:22 | 27:00 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2025-07-25 08:20 | 2025-07-29 11:05 | 98:45 | S/O | None | 0 | 0 | No interruption
Magura 132/33kV | Jhenaidah Ckt. -1 | 2025-07-01 13:10 | 2025-07-01 16:35 | 3:25 | S/O | Relay Testing. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-11 14:54 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-07-10 13:09 | 2025-07-10 15:33 | 2:24 | S/O | Maint.work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-07-13 11:35 | 2025-07-13 20:08 | 8:33 | S/O | Project work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-07-26 08:35 | 2025-07-26 14:17 | 5:42 | S/O | 132KV Circuit breaker replacement work ( saidpur -02)at saidpur Sub station. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-07-29 09:21 | 2025-07-29 17:18 | 7:57 | S/O | Maintenance work at Saidpur Substation end. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-2 | 2025-07-20 10:23 | 2025-07-20 12:40 | 2:17 | S/O | Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 1 | 2025-07-02 09:24 | 2025-07-02 10:44 | 1:20 | S/O | red Hot Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2025-07-20 10:24 | 2025-07-20 12:40 | 2:16 | S/O | Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2025-07-10 13:10 | 2025-07-10 15:31 | 2:21 | S/O | Maintenance work at Barapukuria 230kV Substation. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2025-07-13 11:15 | 2025-07-13 20:05 | 8:50 | S/O | Project work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-06 06:55 | 2025-07-06 19:18 | 12:23 | S/O | Line Project Work. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-12 07:24 | 2025-07-12 20:08 | 12:44 | S/O | Tower maintenance. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-14 07:50 | 2025-07-14 17:35 | 9:45 | S/O | Maintenance work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-14 19:03 | 2025-07-14 22:59 | 3:56 | S/O | Line Load test of project work . | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-16 09:44 | 2025-07-16 13:25 | 3:41 | S/O | Maintenance work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-16 13:32 | 2025-07-17 12:36 | 23:04 | S/O | Mahasthangarh-Palashbari Ckt-2 Reconducting work by STGE project. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-17 13:27 | 2025-07-17 18:17 | 4:50 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-18 10:15 | 2025-07-21 19:41 | 81:26 | S/O | Project Work S/D | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-23 06:54 | 2025-07-23 16:14 | 9:20 | S/O | Maint.work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-23 16:28 | 2025-07-23 17:28 | 1:00 | S/O | project work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-07-24 06:57 | 2025-07-24 17:11 | 10:14 | S/O | project work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-07-25 07:37 | 2025-07-25 07:37 | 0:00 | S/O | STGE Project Work | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-1 | 2025-07-03 14:25 | 2025-07-03 16:46 | 2:21 | S/O | CB DC Cable change work for earth fault | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2025-07-19 14:18 | 2025-07-19 16:05 | 1:47 | S/O | Maint.work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-06 06:55 | 2025-07-06 19:19 | 12:24 | S/O | Project Work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-12 07:29 | 2025-07-12 20:09 | 12:40 | S/O | project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-01 | 2025-07-14 07:48 | 2025-07-14 17:50 | 10:02 | S/O | Re-conduct project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-07-14 07:48 | 2025-07-14 17:50 | 10:02 | S/O | Re-conduct project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-14 07:50 | 2025-07-14 17:50 | 10:00 | S/O | Re-conducting | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-16 09:42 | 2025-07-16 13:24 | 3:42 | S/O | Project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-02 | 2025-07-16 13:41 | 2025-07-17 12:35 | 22:54 | S/O | Reconducting work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-17 13:30 | 2025-07-17 18:20 | 4:50 | S/O | Project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-17 13:30 | 2025-07-17 18:20 | 4:50 | S/O | Project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-02 | 2025-07-18 10:15 | 2025-07-21 19:40 | 81:25 | S/O | Tower rectification | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-07-19 10:03 | 2025-07-19 14:02 | 3:59 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-23 06:52 | 2025-07-23 16:14 | 9:22 | S/O | project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-07-24 07:08 | 2025-07-24 17:10 | 10:02 | S/O | Maint.work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-02 | 2025-07-25 07:36 | 2025-07-25 07:36 | 0:00 | S/O | Re-conducting work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-02 | 2025-07-04 06:32 | 2025-07-06 21:38 | 63:06 | S/O | Maintenance work at Ahdani power plant side. | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-1 | 2025-07-03 14:27 | 2025-07-03 16:45 | 2:18 | S/O | shut down taken by Natore end | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2025-07-08 14:01 | 2025-07-11 13:24 | 71:23 | S/O | Reconducting | 0 | 0 | No interruption
Saidpur 132/33kV | 150 MW Cable Line | 2025-07-12 14:03 | 2025-07-12 17:51 | 3:48 | S/O | For testing | 0 | 0 | No interruption
Saidpur 132/33kV | 150 MW Cable Line | 2025-07-13 10:24 | 2025-07-13 19:58 | 9:34 | S/O | Interlock testing | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-07-26 08:36 | 2025-07-26 14:17 | 5:41 | S/O | BP Ckt-2 Breaker Replacement work. | 10 | 56.8333 | Power interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-07-29 09:10 | 2025-07-29 17:14 | 8:04 | S/O | QF-GMD-39 and as the instruction by ALDC, Bogura | 0 | 0 | No interruption
Sirajgonj 230 | NWPGCL (Unit-1) | 2025-07-13 11:55 | 2025-07-14 16:12 | 28:17 | S/O | Annual maintenance unit-1 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-24 06:34 |  | Unserved Energy: |  | 56.8333
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-16 05:10 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2025
| Area | Previous Month (June' 2025) |  |  |  | Current Month (July '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 14 | 9 | 56 | 79 | 28 | 9 | 48 | 85
2 | Dhaka (South) Grid Circle. | 25 | 14 | 22 | 61 | 26 | 9 | 38 | 73
3 | Chattogram Grid Circle. | 23 | 13 | 24 | 60 | 9 | 8 | 28 | 45
4 | Cumilla Grid Circle. | 18 | 22 | 45 | 85 | 39 | 22 | 58 | 119
5 | Khulna Grid Circle. | 22 | 8 | 70 | 100 | 36 | 16 | 38 | 90
6 | HVDC Grid Circle | 12 | 15 | 19 | 46 | 20 | 11 | 20 | 51
7 | Bogura Grid Circle. | 20 | 25 | 24 | 69 | 26 | 26 | 94 | 146
8 | Others
9 | Total | 134 | 106 | 260 | 500 | 184 | 101 | 324 | 609
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July 2025
| Area | Previous Month (June' 2025) |  |  |  | Current Month (July '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 71.77 | 177.8 | 834.61 | 1084.18 | 624.97 | 255.2 | 3277 | 4157.17
2 | Dhaka (South) Grid Circle. | 2365.57 | 277.5 | - | 2643.07 | 385.9 | 187.33 | 553.2 | 1126.43
3 | Chattogram Grid Circle. | 225.2 | 158.98 | 33.83 | 418.01 | 205.8 | 44.8 | 332.65 | 583.25
4 | Cumilla Grid Circle. | 121.66 | 485.2 | 1492.38 | 2099.24 | 349.43 | 675.41 | 1238.12 | 2262.96
5 | Khulna Grid Circle. | 241.11 | 42.1 | 732.15 | 1015.36 | 299.38 | 70.79 | 1110.27 | 1480.44
6 | HVDC Grid Circle | 77.95 | 236.12 | 162.27 | 476.34 | 170.99 | 47.33 | 607.18 | 825.5
7 | Bogura Grid Circle. | 205.58 | 443.78 | 335.93 | 985.29 | 402.8 | 464.65 | 1078.71 | 1946.16
8 | Others
9 | Total | 3308.84 | 1821.48 | 3591.17 | 8721.49 | 2439.27 | 1745.51 | 8197.13 | 12381.91
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 11 | 19 | 30 | 2 | 2 | 26 | 3549.8
2 | Dhaka (South) | 5031.6 | 9 | 6 | 15 | 3 | 2 | 10 | 902.53
3 | Chattogram | 2042 | 7 | 4 | 11 | 2 | 2 | 7 | 583.25
4 | Khulna | 2434 | 23 | 15 | 38 | 15 | 6 | 17 | 1480.45
5 | HVDC | 5954.3 | 10 | 4 | 14 | 7 |  | 7 | 751.83
6 | Bogura | 3145.6 | 12 | 16 | 28 | 2 | 4 | 22 | 1390.7
7 | Cumilla | 2981 | 32 | 11 | 43 | 16 | 7 | 20 | 1975.29
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 10633.85
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.98%
4 | Khulna | 99.8%
5 | HVDC | 99.97%
6 | Bogura | 99.95%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 2 | 6 | 1 | 2 | 3 | 607.37
2 | Dhaka (South) | 990.29 | - | 7 | - | 7 | 1 | 2 | 4 | 223.9
3 | Chattogram | 917 | - | 1 | - | 1 | - | 1 | - | 0
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | 2 | - | 2 | 2 | - | - | 73.6667
6 | Bogura | 1803.3 | - | 13 | 1 | 14 | 7 | 1 | 6 | 555.46
7 | Cumilla | 1648.16 | - | 5 | 2 | 7 | 2 | 2 | 3 | 287.68
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1748.0767
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.98%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks | 0:59
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm | [6 empty] | 1:36
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. |  | 2:00
2025-07-01 | 14 | - | 12 | 171hr 13 min | 1 | 2hr 29 min | - | - | - | - | - | - |  | 0:36
1:21
2:05
1:21
1:05
1:15
2:08
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption. | [13 empty] | 1:56
0:51
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Agargaon 230/132kV | 1 | 2:38 | 105.3333
Bajitpur 132/33kV | 2 | 7:35 | 284
Jamalpur 132/33kV | 1 | 0:54 | 21.6
Kabirpur 132/33kV | 1 | 0:49 | 57.1667
Sreepur 230/132/33kV | 1 | 0:11 | 7.7
Tangail 132/33kV | 1 | 0:29 | 5.8
Bajitpur 132/33kV | 3 | 1:13 | 48.6667
Kaliakoir 400/230/132kV | 3 | 2:11 | 0
Mirzapur 132/33kV | 3 | 1:42 | 44.2
Tangail 132/33kV | 2 | 4:06 | 162.33
Kabirpur 132/33kV | 2 | 1:10 | 60.83
Kodda 132/33kV | 1 | 0:46 | 9.2
Mirpur 132/33kV | 1 | 1:28 | 73.3333
Bajitpur 132/33kV | 2 | 3:26 | 63.27
Bhaluka 132/33kV | 2 | 2:48 | 76.33
Dhamrai 132/33kV | 1 | 1:57 | 117
Jamalpur 132/33kV | 1 | 1:10 | 11.6667
Kabirpur 132/33kV | 8 | 30:45 | 2005.4
Kishoreganj 132/33kV | 2 | 5:37 | 124.5
Mymensingh 132/33kV | 1 | 1:14 | 117.1667
Sherpur 132/33kV | 1 | 3:40 | 55
Sreepur 230/132/33kV | 2 | 12:08 | 242.6667
Aminbazar 400/230/132kV | 2 | 7:44 | 464
Madanganj 132/33kV | 2 | 4:55 | 103.5
Munshiganj 132/33kV | 1 | 0:20 | 13.6667
Narshingdi 132/33kV | 2 | 0:42 | 14.5
Sonargaon 132/33kV | 1 | 0:28 | 30.3333
Ghorashal 230kV | 1 | 0:59 | 51.1333
Siddhirganj 132/33kV | 1 | 1:36 | 11.2
Sonargaon 132/33kV | 1 | 2:30 | 125
Haripur 230/132kV | 1 | 0:40 | 8.6667
Madanganj 132/33kV | 5 | 8:47 | 181.98
Narshingdi 132/33kV | 1 | 0:19 | 33.25
Ghorashal 230kV | 3 | 7:04 | 467.18
Hasnabad 132/33kV | 1 | 1:36 | 9.6
Sonargaon 132/33kV | 1 | 1:09 | 51.75
Srinagar 132/33kV | 1 | 1:14 | 24.6667
Coxsbazar 132/33kV | 1 | 0.10486 | 145.9667
Dohazari 132/33kV | 2 | 0.026389 | 36.33
Khulshi 132/33kV | 1 | 0.032639 | 23.5
Baroaulia 132/33kV | 1 | 0.066667 | 38.4
Madunaghat 132/33kV | 2 | 0.088889 | 6.4
Baroaulia 132/33kV | 1 | 2:12 | 22
Coxsbazar 132/33kV | 1 | 0:33 | 33
Dohazari 132/33kV | 1 | 1:09 | 81.65
Hathazari 230/132/33kV | 1 | 4:54 | 196
Brahmanbaria 132/33kV | 3 | 0.030556 | 28.67
Chandpur 132/33kV | 1 | 0.034722 | 33.3333
Cumilla(N) 230/132/33kV | 2 | 0.13819 | 132.67
Cumilla(S) 132/33kV | 8 | 0.0875 | 60.88
Daudkandi 132/33kV | 3 | 0.052778 | 29.5
Feni 132/33kV | 1 | 0.01875 | 15.3
Sylhet 132/33kV | 1 | 0.025694 | 12.3333
Beanibazar 132/33kV | 3 | 0.15764 | 84.67
Brahmanbaria 132/33kV | 3 | 0.10556 | 109.72
Chowmuhani 132/33kV | 4 | 0.22431 | 220.17
Kulaura 132/33kV | 2 | 0.077083 | 47.45
Sylhet 132/33kV | 1 | 0.086806 | 39.5833
Daudkandi 132/33kV | 4 | 0.095833 | 36.75
Beanibazar 132/33kV | 1 | 0.10347 | 173.8333
Ashuganj 230/132/33kV | 1 | 0.375 | 450
Chauddagram 132/33kV | 1 | 0.12222 | 79.2
Chhatak 132/33kV | 2 | 0.24306 | 58.33
Chowmuhani 132/33kV | 2 | 0.15972 | 134.5
Daudkandi 132/33kV | 1 | 0.20903 | 150.5
Feni 132/33kV | 1 | 0.05625 | 36.45
Shahjibazar 132/33kV | 1 | 0.034722 | 8.3333
Sunamganj 132/33kV | 1 | 0.40694 | 146.5
Sylhet 132/33kV | 1 | 0.16875 | 97.2
Sylhet (South) | 1 | 1:50 | 27.5
Sylhet 132/33kV | 1 | 1:33 | 49.6
Barishal 132/33kV | 4 | 0:47 | 36.87
Barishal 230/132kV | 4 | 1:46 | 62.45
Bhandaria 132/33kV | 1 | 1:21 | 45.9
Faridpur 132/33kV | 2 | 0:48 | 52.8
Gollamari 132/33kV | 2 | 1:23 | 44.27
Gopalganj 132/33kV | 1 | 0:30 | 17.5
Khulna (C) | 2 | 0:46 | 18.4
Madaripur 132/33kV | 1 | 0:19 | 15.2
Noapara 132/33kV | 2 | 0:16 | 6
Barishal 230/132kV | 1 | 0:06 | 2.8
Mongla 132/33kV | 2 | 2:34 | 13.82
Satkhira 132/33kV | 1 | 1:05 | 54.1667
Barguna 132/33kV | 1 | 0:40 | 5.3333
Barishal 132/33kV | 2 | 5:14 | 180.98
Barishal 230/132kV | 4 | 7:26 | 192.47
Borhanuddin 230/33kV | 2 | 4:47 | 297.75
Faridpur 132/33kV | 2 | 4:41 | 225.17
Goalpara 132/33kV | 3 | 3:23 | 27.07
Gopalganj 132/33kV | 1 | 3:18 | 181.5
Bheramara(GK) 132/33kV | 6 | 3:26 | 74.82
Magura 132/33kV | 2 | 0:44 | 22.5
Chuadanga 132/33kV | 1 | 1:15 | 15
Kushtia 132/33kV | 1 | 3:14 | 32.3333
Jashore 132/33kV | 1 | 0:17 | 36.2667
Jhenaidah 230/132kV | 1 | 0:17 | 37.4
Chuadanga 132/33kV | 2 | 14:37 | 511.58
Ishurdi 132/33kV | 1 | 0:19 | 9.5
Kushtia 132/33kV | 1 | 2:03 | 86.1
Niamatpur 132/33kV | 1 | 0:49 | 4.9
Palashbari 132/33kV | 1 | 0:06 | 4.6
Purbasadipur 132/33kV | 1 | 0:24 | 2.4
Chapai 132/33kV | 1 | 2:08 | 32
Jaldhaka 132/33kV | 3 | 5:16 | 173.75
Mahasthangarh 132/33kV | 1 | 0:41 | 27.3333
Mithapukur 132/33kV | 2 | 3:12 | 61
Rangpur 132/33kV | 1 | 1:50 | 45.8333
Saidpur 132/33kV | 1 | 0:51 | 17
Barapukuria 230/132/33kV | 4 | 0.19167 | 141.7
Mahasthangarh 132/33kV | 3 | 0.063194 | 156.17
Palashbari 132/33kV | 4 | 0.044444 | 63.53
Saidpur 132/33kV | 1 | 0.020833 | 29.5
Barapukuria 230/132/33kV | 1 | 0.57639 | 107.7333
Amnura 132/33kV | 1 | 1:05 | 20.5833
Barapukuria 230/132/33kV | 2 | 6:35 | 164.57
Bog-Sherpur 132/33kV | 2 | 2:41 | 24
Bogura 132/33kV | 1 | 5:40 | 85
Chapai 132/33kV | 1 | 4:33 | 113.75
Mahasthangarh 132/33kV | 4 | 14:18 | 266.43
Purbasadipur 132/33kV | 2 | 6:09 | 44.25
Rajshahi 132/33kV | 1 | 1:57 | 39
Rangpur 132/33kV | 2 | 3:30 | 264.17
Saidpur 132/33kV | 1 | 0.23681 | 56.8333
| 223 | 376:31 | 12381.7967
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 10 | 2025-07-28 23:00
2 | AKSML | 171.9 | 2025-07-17 12:00
3 | Aftabnagar | 58 | 2025-07-27 13:00
4 | Agargaon | 153 | 2025-07-23 15:00
5 | Agrabad | 136 | 2025-07-28 11:00
6 | Amnura | 46 | 2025-07-12 23:00
7 | Ashuganj | 109 | 2025-07-20 02:00
8 | BSRM | 209 | 2025-07-29 20:00
9 | Bagerhat | 89 | 2025-07-22 23:00
10 | Bajitpur | 91 | 2025-07-27 00:00
11 | Bakulia | 104 | 2025-07-21 17:00
12 | Banani | 98 | 2025-07-27 14:00
13 | Bangabhaban | 19 | 2025-07-13 10:00
14 | Barapukuria | 78 | 2025-07-12 22:00
15 | Barguna | 26 | 2025-07-23 22:00
16 | Barishal | 128 | 2025-07-20 11:00
17 | Barishal-230 | 124 | 2025-07-23 19:30
18 | Baroaulia | 74 | 2025-07-23 15:00
19 | Baroirhat | 73 | 2025-07-26 19:30
20 | Bashundhara | 217 | 2025-07-23 15:00
21 | BashundharaCement | 17 | 2025-07-21 10:00
22 | Beanibazar | 92 | 2025-07-13 23:00
23 | Benapole | 85 | 2025-07-23 22:00
24 | Bhaluka | 174 | 2025-07-12 19:30
25 | Bhandaria | 70 | 2025-07-05 05:00
26 | Bhangura | 44 | 2025-07-23 20:00
27 | Bheramara(GK) | 78 | 2025-07-23 18:30
28 | Bhulta | 259 | 2025-07-21 20:00
29 | Bog-Sherpur | 78 | 2025-07-23 21:00
30 | Bogura | 206 | 2025-07-23 23:00
31 | Borhanuddin | 98 | 2025-07-15 22:00
32 | Brahmanbaria | 153 | 2025-07-24 01:00
33 | Cantonment | 174 | 2025-07-23 12:00
34 | Chandina | 42.8 | 2025-07-24 19:30
35 | Chandpur | 88 | 2025-07-24 20:00
36 | Chandraghona | 43 | 2025-07-16 10:00
37 | Chapai | 79 | 2025-07-23 23:00
38 | Charsaidpur | 45 | 2025-07-21 02:00
39 | Chauddagram | 79 | 2025-07-21 23:00
40 | Chhatak | 47 | 2025-07-13 23:00
41 | Chowmuhani | 215 | 2025-07-20 19:00
42 | Chuadanga | 134 | 2025-07-23 19:00
43 | Coxsbazar | 145 | 2025-07-10 20:00
44 | Cumilla(N) | 160 | 2025-07-02 21:00
45 | Cumilla(S) | 196 | 2025-07-13 19:00
46 | Daganbhuiyan | 0 | 2025-07-03 14:00
47 | Daudkandi | 161 | 2025-07-21 20:00
48 | Dhaka | 86 | 2025-07-27 13:00
49 | Dhamrai | 132 | 2025-07-03 19:30
50 | Dhanmondi | 162.5 | 2025-07-23 14:00
51 | Dohazari | 115 | 2025-07-24 19:30
52 | Faridpur | 194 | 2025-07-23 22:00
53 | Fatullah | 110 | 2025-07-23 16:00
54 | Fenchuganj | 51 | 2025-07-01 21:00
55 | Feni | 129 | 2025-07-19 20:00
56 | GPH | 97 | 2025-07-24 15:00
57 | Ghatail | 90 | 2025-07-19 23:00
58 | Ghorashal | 16 | 2025-07-06 14:00
59 | Ghorashal-230 | 96 | 2025-07-06 22:00
60 | Goalpara | 42 | 2025-07-12 20:00
61 | Gollamari | 156 | 2025-07-27 05:00
62 | Gopalganj | 123.7 | 2025-07-23 20:00
63 | Gulshan | 150 | 2025-07-23 14:00
64 | Halishahar | 86 | 2025-07-24 16:00
65 | HaripurSBU | 182 | 2025-07-05 12:00
66 | Hasnabad | 100 | 2025-07-23 23:00
67 | Hathazari | 95 | 2025-07-29 18:30
68 | Ishurdi | 95 | 2025-07-23 19:30
69 | Jaldhaka | 98 | 2025-07-01 01:00
70 | Jamalpur | 150 | 2025-07-12 23:00
71 | Jashore | 154 | 2025-07-21 19:30
72 | Jhenaidah | 147 | 2025-07-23 19:00
73 | Joydebpur | 162 | 2025-07-20 16:00
74 | Joypurhat | 80 | 2025-07-23 21:00
75 | Juldah | 20 | 2025-07-24 01:00
76 | KSRM | 47 | 2025-07-31 14:00
77 | Kabirpur | 264 | 2025-07-21 11:00
78 | Kachua | 102 | 2025-07-20 23:00
79 | Kallyanpur | 138 | 2025-07-13 13:00
80 | Kalurghat | 42 | 2025-07-13 16:00
81 | Kamrangirchar | 83.5 | 2025-07-20 13:00
82 | Kaptai | N/A | N/A
83 | Kasba | 39 | 2025-07-12 22:00
84 | Kazla | 104 | 2025-07-24 00:00
85 | Keranigonj | 104 | 2025-07-03 19:30
86 | Khagrachori | 38 | 2025-07-20 19:30
87 | Khulna | 89 | 2025-07-13 13:00
88 | Khulshi | 189 | 2025-07-22 19:30
89 | Kishoreganj | 157 | 2025-07-21 22:00
90 | Kodda | 328 | 2025-07-07 16:00
91 | Kulaura | 61 | 2025-07-01 19:30
92 | Kurigram | 74 | 2025-07-03 23:00
93 | Kushtia | 174 | 2025-07-22 20:00
94 | Laksam | 38 | 2025-07-21 06:00
95 | Lakshmipur | 43 | 2025-07-12 19:00
96 | Lalbag | 60 | 2025-07-10 13:00
97 | Lalmonirhat | 74 | 2025-07-02 19:30
98 | MI_Cement | 17 | 2025-07-01 00:00
99 | Madanganj | 52 | 2025-07-03 10:00
100 | Madaripur | 132 | 2025-07-23 23:00
101 | Madartek | 114 | 2025-07-24 00:00
102 | Madunaghat | 61 | 2025-07-23 19:00
103 | Magura | 81 | 2025-07-23 19:30
104 | Mahasthangarh | 106 | 2025-07-24 00:00
105 | Maijdee | 24 | 2025-07-27 04:00
106 | Manikganj | 143 | 2025-07-22 20:00
107 | Maniknagar | 94 | 2025-07-23 13:00
108 | Matarbari | 55 | 2025-07-21 23:00
109 | Matuail | 68 | 2025-07-12 12:00
110 | Millgate | 138 | 2025-07-23 16:00
111 | Mirpur | 141 | 2025-07-23 15:00
112 | Mirsorai | 12 | 2025-07-24 15:00
113 | Mirzapur | 50 | 2025-07-05 21:00
114 | Mithapukur | 78 | 2025-07-20 03:00
115 | Modern | N/A | N/A
116 | Mogbazar | 173.3 | 2025-07-23 16:00
117 | Mongla | 44 | 2025-07-04 00:00
118 | Motijheel | 51 | 2025-07-23 13:00
119 | Muktagacha | 43 | 2025-07-23 19:30
120 | Munshiganj | 127 | 2025-07-29 01:00
121 | Muradnagar | 48 | 2025-07-19 22:00
122 | Mymensingh | 237 | 2025-07-23 21:00
123 | Naogaon | 160 | 2025-07-23 22:00
124 | Narail | 67 | 2025-07-22 19:30
125 | Narinda | 88 | 2025-07-27 13:00
126 | Narshingdi | 195 | 2025-07-01 21:00
127 | Natore | 181 | 2025-07-14 00:00
128 | Nawabganj | 73.8 | 2025-07-23 22:00
129 | Netrakona | 149 | 2025-07-13 20:00
130 | New | 92.8 | 2025-07-15 12:00
131 | Niamatpur | 95 | 2025-07-12 22:00
132 | Noapara | 66 | 2025-07-23 00:00
133 | PHP | 10 | 2025-07-13 13:00
134 | Pabna | 145 | 2025-07-23 19:30
135 | Palashbari | 128 | 2025-07-14 00:00
136 | Panchagarh | 73 | 2025-07-12 19:30
137 | Patiya | N/A | N/A
138 | Patuakhali | 82.5 | 2025-07-01 23:00
139 | Payra | 38 | 2025-07-16 22:00
140 | Postogola | 67 | 2025-07-23 19:30
141 | Purbachal | 32 | 2025-07-11 13:00
142 | Purbasadipur | 151 | 2025-07-03 23:00
143 | Rahanpur | 41 | 2025-07-31 23:00
144 | Rahim | 38 | 2025-07-10 18:00
145 | Rajbari | 98 | 2025-07-23 19:30
146 | Rajendrapur | 144 | 2025-07-23 20:00
147 | Rajshahi | 151 | 2025-07-23 21:00
148 | Rajshahi-230 | 104 | 2025-07-26 13:00
149 | Ramganj | 124 | 2025-07-30 19:30
150 | Rampur | 47 | 2025-07-09 12:00
151 | Rangamati | 18 | 2025-07-01 19:30
152 | Rangpur | 157 | 2025-07-04 01:00
153 | Ruppur | 14 | 2025-07-19 01:00
154 | SSM | 16 | 2025-07-03 07:00
155 | Saidpur | 122 | 2025-07-23 10:00
156 | Satkhira | 145 | 2025-07-22 22:00
157 | Satmasjid | 120 | 2025-07-19 15:00
158 | Savar | 247 | 2025-07-13 15:00
159 | SevenRings | 22.14 | 2025-07-22 15:00
160 | ShahCement | 36 | 2025-07-22 22:00
161 | Shahjadpur | 103 | 2025-07-23 21:00
162 | Shahjibazar | 141 | 2025-07-12 22:00
163 | Shahmirpur | 67 | 2025-07-01 00:00
164 | Shariatpur | 104 | 2025-07-23 22:00
165 | Sherpur | 174 | 2025-07-14 00:00
166 | Shikalbaha | 24 | 2025-07-24 11:00
167 | Shitalakhya | 93 | 2025-07-02 12:00
168 | Sholosohor | 50 | 2025-07-23 18:30
169 | Shyampur | 180 | 2025-07-24 16:00
170 | Siddhirganj | 129 | 2025-07-23 12:00
171 | Sirajganj | 136 | 2025-07-23 20:00
172 | Sonargaon | 125 | 2025-07-21 23:00
173 | Sreemongol | 95 | 2025-07-12 19:30
174 | Sreepur | 112 | 2025-07-13 11:00
175 | Srinagar | 59.85 | 2025-07-23 22:00
176 | Sunamganj | 66 | 2025-07-13 21:00
177 | Sylhet | 77 | 2025-07-18 19:00
178 | Sylhet-132 | 153 | 2025-07-13 19:00
179 | TK | 45 | 2025-07-16 23:00
180 | Tangail | 196 | 2025-07-13 21:00
181 | Taraganj | 27 | 2025-07-23 19:30
182 | Thakurgaon | 123 | 2025-07-18 21:00
183 | Tongi | 155 | 2025-07-12 15:00
184 | Ullahpara | 46 | 2025-07-23 19:30
185 | Ullon | 50 | 2025-07-23 23:00
186 | Uttara | 98 | 2025-07-23 15:00
187 | UttaraNew | 78 | 2025-07-01 15:00
188 | Zigatola | 80 | 2025-07-12 23:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: July 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5817.32 | 2025-07-23 | 12:00
Chattogram | 1639 | 2025-07-25 | 0:00
Cumilla | 1512.38 | 2025-07-23 | 22:00
Mymensingh | 1328 | 2025-07-12 | 21:00
Sylhet | 725 | 2025-07-12 | 22:00
Khulna | 2026 | 2025-07-23 | 22:00
Barishal | 520.5 | 2025-07-23 | 22:00
Rajshahi | 1814 | 2025-07-23 | 22:00
Rangpur | 1052 | 2025-07-12 | 22:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 392 | 2025-07-09 05:00 | 365 | 2025-07-12 15:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 412 | 2025-07-24 04:00 | 360 | 2025-07-19 12:00
4 | Bibiana | 400 | 392 | 2025-07-24 05:00 | 372 | 2025-07-21 09:00
5 | BIPTC | 400 | 409 | 2025-07-31 06:00 | 391 | 2025-07-02 23:00
6 | Bogura | 400 | 393 | 2025-07-24 09:00 | 354 | 2025-07-12 21:00
7 | Gopalganj | 400 | 406 | 2025-07-25 15:00 | 373 | 2025-07-19 19:30
8 | Kaliakoir | 400 | 388 | 2025-07-24 05:00 | 349 | 2025-07-21 09:00
9 | Madunaghat | 400 | 400 | 2025-07-09 06:00 | 383 | 2025-07-12 15:00
10 | Meghnaghat | 400 | 395 | 2025-07-09 05:00 | 369 | 2025-07-13 11:00
11 | Payra | 400 | 419 | 2025-07-25 15:00 | 405 | 2025-07-12 16:00
12 | Rahanpur | 400 | 409 | 2025-07-24 09:00 | 364 | 2025-07-12 21:00
13 | Rampal | 400 | 411 | 2025-07-24 05:00 | 371 | 2025-07-19 19:30
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 230 | 2025-07-24 06:00 | 210 | 2025-07-13 12:00
2 | AKSML | 230 | 237 | 2025-07-07 19:30 | 220 | 2025-07-25 23:00
3 | Aminbazar | 230 | 255 | 2025-07-03 04:00 | 211 | 2025-07-13 07:00
4 | Ashuganj | 230 | 237 | 2025-07-24 04:00 | 212 | 2025-07-16 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2025-07-25 08:00 | 222 | 2025-07-21 09:00
7 | Barapukuria | 230 | 227 | 2025-07-09 17:00 | 196 | 2025-07-29 23:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 235 | 2025-07-09 06:00 | 215 | 2025-07-23 23:00
10 | Bheramara | 230 | 234 | 2025-07-03 08:00 | 221 | 2025-07-01 20:00
11 | Bhulta | 230 | 238 | 2025-07-24 04:00 | 208 | 2025-07-05 15:00
12 | Bibiana | 230 | 233 | 2025-07-24 06:00 | 217 | 2025-07-21 15:00
13 | BIPTC | 230 | 263 | 2025-07-18 06:00 | 220 | 2025-07-18 21:00
14 | Bogura | 230 | 238 | 2025-07-24 09:00 | 217 | 2025-07-12 21:00
15 | Bogura-400 | 230 | 238 | 2025-07-24 09:00 | 216 | 2025-07-12 21:00
16 | Borhanuddin | 230 | 241 | 2025-07-09 16:00 | 222 | 2025-07-16 00:00
17 | BSRM | 230 | 231 | 2025-07-05 18:00 | 216 | 2025-07-25 23:00
18 | Cumilla(N) | 230 | 226 | 2025-07-25 07:00 | 211 | 2025-07-25 23:00
19 | Faridpur | 230 | 233 | 2025-07-25 14:00 | 210 | 2025-07-12 19:00
20 | Fenchuganj | 230 | 233 | 2025-07-24 06:00 | 216 | 2025-07-21 15:00
21 | Ghorashal | 230 | 240 | 2025-07-09 04:00 | 220 | 2025-07-01 09:00
22 | Ghorashal-230 | 230 | 233 | 2025-07-24 04:00 | 208 | 2025-07-21 09:00
23 | Gopalganj | 230 | 233 | 2025-07-25 15:00 | 213 | 2025-07-20 01:00
24 | GPH | 230 | 235 | 2025-07-05 19:30 | 220 | 2025-07-17 23:00
25 | Haripur | 230 | 228 | 2025-07-24 05:00 | 209 | 2025-07-24 15:00
26 | Hasnabad | 230 | 227 | 2025-07-09 07:00 | 208 | 2025-07-13 12:00
27 | Hathazari | 230 | 235 | 2025-07-02 21:00 | 211 | 2025-07-28 00:00
28 | Ishurdi | 230 | 237 | 2025-07-03 08:00 | 223 | 2025-07-01 20:00
29 | Jhenaidah | 230 | 234 | 2025-07-05 08:00 | 212 | 2025-07-12 19:30
30 | Kaliakoir | 230 | 241 | 2025-07-24 05:00 | 216 | 2025-07-19 14:00
31 | Keranigonj | 230 | 228 | 2025-07-24 05:00 | 208 | 2025-07-13 12:00
32 | Khulna(S) | 230 | 236 | 2025-07-15 07:00 | 211 | 2025-07-19 19:30
33 | Madunaghat | 230 | 237 | 2025-07-05 19:00 | 224 | 2025-07-25 22:00
34 | Madunaghat-400 | 230 | 238 | 2025-07-05 20:00 | 225 | 2025-07-25 00:00
35 | Maniknagar | 230 | 226 | 2025-07-24 04:00 | 206 | 2025-07-29 10:00
36 | Meghnaghat | 230 | 233 | 2025-07-24 05:00 | 216 | 2025-07-13 12:00
37 | Meghnaghat-400 | 230 | 233 | 2025-07-06 16:00 | 213 | 2025-07-13 12:00
38 | Mirsorai | 230 | 232 | 2025-07-05 17:00 | 217 | 2025-07-17 01:00
39 | Rajshahi | 230 | 235 | 2025-07-03 08:00 | 218 | 2025-07-18 21:00
40 | Rampal | 230 | 236 | 2025-07-25 17:00 | 208 | 2025-07-19 19:30
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 260 | 2025-07-30 16:00 | 205 | 2025-07-19 15:00
43 | Shikalbaha | 230 | 236 | 2025-07-05 18:30 | 222 | 2025-07-12 12:00
44 | Shyampur | 230 | 230 | 2025-07-05 18:00 | 209 | 2025-07-13 12:00
45 | Siddhirganj | 230 | 243 | 2025-07-17 16:00 | 210 | 2025-07-12 09:00
46 | Sirajgonj | 230 | 268 | 2025-07-03 18:30 | 228 | 2025-07-21 09:00
47 | Sreepur | 230 | 234 | 2025-07-24 05:00 | 214 | 2025-07-21 09:00
48 | Tongi | 230 | 236 | 2025-07-24 04:00 | 208 | 2025-07-21 09:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2025-07-03 06:00 | 120 | 2025-07-23 15:00
2 | Agargaon | 132 | 158 | 2025-07-18 19:30 | 120 | 2025-07-16 18:30
3 | Agrabad | 132 | 136 | 2025-07-07 20:00 | 124 | 2025-07-21 11:00
4 | AKS | 132 | 134 | 2025-07-05 18:00 | 123 | 2025-07-25 23:00
5 | Aminbazar | 132 | 135 | 2025-07-03 06:00 | 122 | 2025-07-13 12:00
6 | Amnura | 132 | 139 | 2025-07-24 10:00 | 115 | 2025-07-12 19:30
7 | Ashuganj | 132 | 144 | 2025-07-24 05:00 | 130 | 2025-07-06 21:00
8 | Bagerhat | 132 | 140 | 2025-07-25 16:00 | 115 | 2025-07-19 19:30
9 | Bajitpur | 132 | 135 | 2025-07-24 05:00 | 121 | 2025-07-11 22:00
10 | Bakulia | 132 | 164 | 2025-07-06 03:00 | 126 | 2025-07-14 13:00
11 | Banani | 132 | 142 | 2025-07-24 04:00 | 120 | 2025-07-23 15:00
12 | Bangabhaban | 132 | 135 | 2025-07-24 05:00 | 121 | 2025-07-24 12:00
13 | Barapukuria | 132 | 139 | 2025-07-09 17:00 | 118 | 2025-07-29 23:00
14 | Barguna | 132 | 138 | 2025-07-25 14:00 | 128 | 2025-07-01 22:00
0 | Barishal | 132 | 140 | 2025-07-25 15:00 | 123 | 2025-07-23 23:00
16 | Barishal-230 | 132 | 139 | 2025-07-11 09:00 | 125 | 2025-07-12 19:30
17 | Baroaulia | 132 | 135 | 2025-07-05 18:00 | 126 | 2025-07-14 14:00
18 | Baroirhat | 132 | 130 | 2025-07-25 10:00 | 113 | 2025-07-25 22:00
19 | Bashundhara | 132 | 142 | 2025-07-03 05:00 | 118 | 2025-07-01 11:00
20 | BashundharaCement | 132 | 136 | 2025-07-27 18:00 | 114 | 2025-07-24 01:00
21 | Beanibazar | 132 | 130 | 2025-07-05 18:00 | 113 | 2025-07-21 19:00
22 | Benapole | 132 | 141 | 2025-07-13 15:00 | 114 | 2025-07-23 23:00
23 | Bhaluka | 132 | 134 | 2025-07-24 05:00 | 126 | 2025-07-14 13:00
24 | Bhandaria | 132 | 138 | 2025-07-25 15:00 | 115 | 2025-07-12 23:00
25 | Bhangura | 132 | 157 | 2025-07-18 20:00 | 125 | 2025-07-12 21:00
26 | Bheramara | 132 | 139 | 2025-07-14 18:00 | 129 | 2025-07-21 09:00
27 | Bheramara(GK) | 132 | 138 | 2025-07-06 07:00 | 128 | 2025-07-21 10:00
28 | Bhulta | 132 | 129 | 2025-07-07 19:00 | 111 | 2025-07-05 15:00
29 | Bog-Sherpur | 132 | 138 | 2025-07-24 09:00 | 124 | 2025-07-26 23:00
30 | Bogura | 132 | 141 | 2025-07-24 09:00 | 126 | 2025-07-26 23:00
31 | Bogura-230 | 132 | 141 | 2025-07-24 09:00 | 127 | 2025-07-12 00:00
32 | Brahmanbaria | 132 | 137 | 2025-07-21 09:00 | 122 | 2025-07-05 23:00
33 | Cantonment | 132 | 136 | 2025-07-09 05:00 | 121 | 2025-07-13 12:00
34 | Chandina | 132 | 134 | 2025-07-25 15:00 | 119 | 2025-07-21 22:00
35 | Chandpur | 132 | 135 | 2025-07-25 07:00 | 111 | 2025-07-03 01:00
36 | Chandraghona | 132 | 138 | 2025-07-06 21:00 | 127 | 2025-07-25 22:00
37 | Chapai | 132 | 139 | 2025-07-24 10:00 | 116 | 2025-07-12 19:30
39 | Charsaidpur | 132 | 134 | 2025-07-24 05:00 | 121 | 2025-07-12 16:00
40 | Chauddagram | 132 | 130 | 2025-07-25 09:00 | 112 | 2025-07-25 22:00
41 | Chhatak | 132 | 130 | 2025-07-04 10:00 | 111 | 2025-07-21 14:00
42 | Chowmuhani | 132 | 129 | 2025-07-25 09:00 | 105 | 2025-07-22 04:00
43 | Chuadanga | 132 | 138 | 2025-07-14 17:00 | 114 | 2025-07-23 19:00
44 | Coxsbazar | 132 | 132 | 2025-07-25 08:00 | 107 | 2025-07-16 18:30
45 | Cumilla(N) | 132 | 131 | 2025-07-25 07:00 | 118 | 2025-07-25 23:00
46 | Cumilla(S) | 132 | 135 | 2025-07-18 05:00 | 116 | 2025-07-25 23:00
47 | Daganbhuiyan | 132 | 129 | 2025-07-25 10:00 | 108 | 2025-07-20 19:00
48 | Daudkandi | 132 | 129 | 2025-07-05 10:00 | 111 | 2025-07-27 22:00
49 | Dhaka | 132 | 141 | 2025-07-03 05:00 | 122 | 2025-07-19 15:00
50 | Dhamrai | 132 | 140 | 2025-07-24 05:00 | 119 | 2025-07-21 09:00
51 | Dhanmondi | 132 | 141.6 | 2025-07-24 04:00 | 121 | 2025-07-23 15:00
52 | Dohazari | 132 | 135 | 2025-07-05 21:00 | 120 | 2025-07-12 12:00
53 | Faridpur | 132 | 138 | 2025-07-25 14:00 | 125 | 2025-07-12 19:00
54 | Fatullah | 132 | 136 | 2025-07-24 05:00 | 117 | 2025-07-31 01:00
55 | Fenchuganj | 132 | 138 | 2025-07-24 06:00 | 126 | 2025-07-20 19:00
56 | Feni | 132 | 129 | 2025-07-25 10:00 | 112 | 2025-07-31 22:00
57 | Ghatail | 132 | 135 | 2025-07-24 07:00 | 117 | 2025-07-22 19:30
58 | Ghorashal | 132 | 140 | 2025-07-01 07:00 | 126 | 2025-07-21 09:00
59 | Goalpara | 132 | 142 | 2025-07-25 16:00 | 124 | 2025-07-12 19:00
60 | Gollamari | 132 | 142 | 2025-07-25 16:00 | 125 | 2025-07-12 19:30
61 | Gopalganj | 132 | 141 | 2025-07-25 16:00 | 124 | 2025-07-23 23:00
62 | Gopalganj-400 | 132 | 140 | 2025-07-25 15:00 | 128 | 2025-07-12 19:30
63 | Gulshan | 132 | 140 | 2025-07-03 06:00 | 121 | 2025-07-23 15:00
64 | Halishahar | 132 | 138 | 2025-07-05 19:30 | 125 | 2025-07-01 11:00
65 | Haripur | 132 | 134 | 2025-07-24 04:00 | 121 | 2025-07-13 12:00
66 | HaripurSBU | 132 | 134 | 2025-07-24 04:00 | 121 | 2025-07-13 12:00
67 | Hasnabad | 132 | 137 | 2025-07-24 04:00 | 123 | 2025-07-12 16:00
68 | Hathazari | 132 | 136 | 2025-07-05 20:00 | 125 | 2025-07-12 14:00
69 | Ishurdi | 132 | 139 | 2025-07-03 08:00 | 130 | 2025-07-11 19:30
70 | Jaldhaka | 132 | 133 | 2025-07-14 18:30 | 109 | 2025-07-29 23:00
71 | Jamalpur | 132 | 140 | 2025-07-20 11:00 | 123 | 2025-07-11 11:00
72 | Jashore | 132 | 142 | 2025-07-14 05:00 | 115 | 2025-07-12 19:30
73 | Jhenaidah | 132 | 140 | 2025-07-25 15:00 | 117 | 2025-07-23 19:00
74 | Jhenaidah-230 | 132 | 139 | 2025-07-05 08:00 | 122 | 2025-07-12 19:30
75 | Joydebpur | 132 | 141 | 2025-07-24 04:00 | 117 | 2025-07-21 09:00
76 | Joypurhat | 132 | 139 | 2025-07-24 09:00 | 116 | 2025-07-12 00:00
77 | Juldah | 132 | 138 | 2025-07-07 19:00 | 126 | 2025-07-25 22:00
78 | Kabirpur | 132 | 138 | 2025-07-13 06:00 | 116 | 2025-07-12 19:30
79 | Kachua | 132 | 131 | 2025-07-24 21:00 | 112 | 2025-07-21 01:00
80 | Kaliakoir | 132 | 139 | 2025-07-15 23:00 | 123 | 2025-07-21 09:00
81 | Kallyanpur | 132 | 136 | 2025-07-24 04:00 | 122 | 2025-07-12 13:00
82 | Kalurghat | 132 | 135 | 2025-07-05 20:00 | 126 | 2025-07-25 22:00
83 | Kamrangirchar | 132 | 138 | 2025-07-24 05:00 | 122 | 2025-07-13 12:00
84 | Kaptai | 132 | N/A | N/A | N/A | N/A
85 | Kasba | 132 | 128 | 2025-07-05 18:00 | 114 | 2025-07-25 23:00
86 | Kazla | 132 | 139 | 2025-07-18 20:00 | 121 | 2025-07-13 13:00
87 | Keranigonj | 132 | 139 | 2025-07-04 18:30 | 120 | 2025-07-02 16:00
88 | Khagrachori | 132 | 134 | 2025-07-07 19:00 | 125 | 2025-07-25 22:00
89 | Khulna | 132 | 140 | 2025-07-25 16:00 | 120 | 2025-07-19 19:30
90 | Khulna(S) | 132 | 142 | 2025-07-25 16:00 | 124 | 2025-07-19 15:00
91 | Khulshi | 132 | 135 | 2025-07-07 19:00 | 124 | 2025-07-16 15:00
92 | Kishoreganj | 132 | 131 | 2025-07-08 06:00 | 115 | 2025-07-19 23:00
93 | Kodda | 132 | 139 | 2025-07-29 17:00 | 117 | 2025-07-14 11:00
94 | KSRM | 132 | 136 | 2025-07-05 19:30 | 125 | 2025-07-25 22:00
95 | Kulaura | 132 | 137 | 2025-07-24 06:00 | 123 | 2025-07-21 19:00
96 | Kurigram | 132 | 139 | 2025-07-21 19:30 | 112 | 2025-07-11 19:30
97 | Kushtia | 132 | 138 | 2025-07-14 18:00 | 123 | 2025-07-21 13:00
98 | Laksam | 132 | 131 | 2025-07-24 21:00 | 111 | 2025-07-21 02:00
99 | Lakshmipur | 132 | 130 | 2025-07-25 09:00 | 106 | 2025-07-27 23:00
100 | Lalbag | 132 | 138 | 2025-07-24 05:00 | 123 | 2025-07-12 16:00
101 | Lalmonirhat | 132 | 134 | 2025-07-14 18:00 | 113 | 2025-07-24 05:00
102 | Madanganj | 132 | 132 | 2025-07-04 18:00 | 121 | 2025-07-01 11:00
103 | Madaripur | 132 | 140 | 2025-07-25 16:00 | 127 | 2025-07-12 19:00
104 | Madartek | 132 | 140 | 2025-07-03 06:00 | 120 | 2025-07-21 09:00
105 | Madunaghat | 132 | 135 | 2025-07-05 18:30 | 126 | 2025-07-01 10:00
106 | Magura | 132 | 138 | 2025-07-05 07:00 | 118 | 2025-07-12 19:30
107 | Mahasthangarh | 132 | 140 | 2025-07-24 09:00 | 122 | 2025-07-26 23:00
108 | Maijdee | 132 | 131 | 2025-07-25 09:00 | 104 | 2025-07-21 03:00
109 | Manikganj | 132 | 133 | 2025-07-24 06:00 | 114 | 2025-07-27 12:00
110 | Maniknagar | 132 | 136 | 2025-07-24 05:00 | 122 | 2025-07-13 12:00
111 | Matarbari | 132 | 133 | 2025-07-25 08:00 | 107 | 2025-07-16 19:00
112 | Matuail | 132 | 134.5 | 2025-07-24 05:00 | 121 | 2025-07-24 12:00
113 | Millgate | 132 | 137 | 2025-07-24 04:00 | 118 | 2025-07-19 14:00
114 | Mirpur | 132 | 134 | 2025-07-10 04:00 | 120 | 2025-07-13 12:00
115 | Mirzapur | 132 | 136 | 2025-07-24 05:00 | 119 | 2025-07-23 19:00
116 | Mithapukur | 132 | 138 | 2025-07-21 19:30 | 109 | 2025-07-26 23:00
117 | MI_Cement | 132 | 137.5 | 2025-07-24 05:00 | 121 | 2025-07-01 11:00
118 | Modern | 132 | N/A | N/A | N/A | N/A
119 | Mogbazar | 132 | 143 | 2025-07-24 05:00 | 122 | 2025-07-21 08:00
120 | Mongla | 132 | 140 | 2025-07-14 05:00 | 116 | 2025-07-19 19:30
121 | Motijheel | 132 | 135 | 2025-07-24 05:00 | 121 | 2025-07-24 12:00
122 | Muktagacha | 132 | 154 | 2025-07-07 08:00 | 121 | 2025-07-22 21:00
123 | Munshiganj | 132 | 132 | 2025-07-04 18:00 | 120 | 2025-07-24 12:00
124 | Muradnagar | 132 | 129 | 2025-07-25 12:00 | 115 | 2025-07-27 22:00
125 | Mymensingh | 132 | 138 | 2025-07-25 00:00 | 110 | 2025-07-11 22:00
126 | Naogaon | 132 | 139 | 2025-07-24 09:00 | 119 | 2025-07-12 22:00
127 | Narail | 132 | 139 | 2025-07-25 15:00 | 118 | 2025-07-13 23:00
128 | Narinda | 132 | 0 | 2025-07-01 00:00 | N/A | N/A
129 | Narshingdi | 132 | 143 | 2025-07-24 04:00 | 116 | 2025-07-05 22:00
130 | Natore | 132 | 136 | 2025-07-04 17:00 | 125 | 2025-07-18 23:00
131 | Nawabganj | 132 | 138 | 2025-07-24 05:00 | 122 | 2025-07-13 12:00
132 | Netrakona | 132 | 129 | 2025-07-05 07:00 | 106 | 2025-07-23 19:00
133 | New | 132 | 137 | 2025-07-24 05:00 | 120 | 2025-07-19 14:00
134 | Niamatpur | 132 | 160 | 2025-07-24 21:00 | 121 | 2025-07-12 21:00
135 | Noapara | 132 | 140 | 2025-07-13 15:00 | 119 | 2025-07-19 19:30
136 | Pabna | 132 | 137 | 2025-07-25 18:00 | 126 | 2025-07-21 13:00
137 | Palashbari | 132 | 139 | 2025-07-24 09:00 | 107 | 2025-07-27 01:00
139 | Panchagarh | 132 | 140 | 2025-07-14 18:30 | 114 | 2025-07-07 13:00
140 | Patiya | 132 | N/A | N/A | N/A | N/A
141 | Patuakhali | 132 | 137 | 2025-07-19 22:00 | 129 | 2025-07-15 22:00
142 | Payra | 132 | 166 | 2025-07-02 21:00 | 132 | 2025-07-12 16:00
143 | PHP | 132 | 130 | 2025-07-25 10:00 | 112 | 2025-07-25 23:00
144 | Postogola | 132 | 135 | 2025-07-24 04:00 | 123 | 2025-07-13 12:00
145 | Purbachal | 132 | 141 | 2025-07-03 06:00 | 120 | 2025-07-12 16:00
146 | Purbasadipur | 132 | 134 | 2025-07-14 18:30 | 114 | 2025-07-07 13:00
147 | Rahanpur | 132 | 141 | 2025-07-24 10:00 | 123 | 2025-07-12 19:30
148 | Rahanpur-400 | 132 | 141 | 2025-07-24 10:00 | 123 | 2025-07-12 19:30
149 | Rahim | 132 | 135 | 2025-07-24 05:00 | 121 | 2025-07-13 12:00
150 | Rajbari | 132 | 139 | 2025-07-25 16:00 | 122 | 2025-07-12 19:30
151 | Rajendrapur | 132 | 140 | 2025-07-02 08:00 | 119 | 2025-07-12 14:00
152 | Rajshahi | 132 | 136 | 2025-07-04 09:00 | 125 | 2025-07-18 21:00
153 | Rajshahi-230 | 132 | 136 | 2025-07-03 08:00 | 135 | 2025-07-14 18:30
154 | Ramganj | 132 | 131 | 2025-07-25 11:00 | 105 | 2025-07-21 02:00
155 | Rampur | 132 | 135 | 2025-07-05 19:30 | 124 | 2025-07-25 23:00
156 | Rampura | 132 | 144 | 2025-07-24 05:00 | 121 | 2025-07-21 09:00
157 | Rangamati | 132 | 134 | 2025-07-05 18:30 | 126 | 2025-07-25 23:00
158 | Rangpur | 132 | 135 | 2025-07-09 17:00 | 115 | 2025-07-11 19:30
159 | Ruppur | 132 | 164 | 2025-07-17 14:00 | 129 | 2025-07-21 09:00
160 | Saidpur | 132 | 134 | 2025-07-10 18:30 | 113 | 2025-07-29 23:00
161 | Satkhira | 132 | 140 | 2025-07-14 08:00 | 117 | 2025-07-23 23:00
162 | Satmasjid | 132 | 135 | 2025-07-09 04:00 | 120 | 2025-07-09 12:00
163 | Savar | 132 | 137 | 2025-07-13 01:00 | 122 | 2025-07-12 13:00
164 | SevenRings | 132 | 141 | 2025-07-24 05:00 | 124 | 2025-07-21 09:00
165 | ShahCement | 132 | 134 | 2025-07-24 05:00 | 121 | 2025-07-12 16:00
166 | Shahjadpur | 132 | 140 | 2025-07-25 16:00 | 130 | 2025-07-01 23:00
167 | Shahjibazar | 132 | 137 | 2025-07-09 07:00 | 123 | 2025-07-05 23:00
168 | Shahmirpur | 132 | 138 | 2025-07-07 20:00 | 126 | 2025-07-25 22:00
169 | Shariatpur | 132 | 140 | 2025-07-25 16:00 | 123 | 2025-07-23 23:00
170 | Sherpur | 132 | 138 | 2025-07-15 14:00 | 117 | 2025-07-11 12:00
171 | Shikalbaha | 132 | 126 | 2025-07-05 18:30 | 115 | 2025-07-25 22:00
172 | Shikalbaha-230 | 132 | 138 | 2025-07-01 12:00 | 126 | 2025-07-18 00:00
173 | Shitalakhya | 132 | 138 | 2025-07-07 02:00 | 121 | 2025-07-01 11:00
174 | Sholosohor | 132 | 135 | 2025-07-07 19:00 | 126 | 2025-07-24 11:00
175 | Shyampur | 132 | 135 | 2025-07-07 07:00 | 121 | 2025-07-01 11:00
176 | Shyampur-230 | 132 | 135 | 2025-07-24 05:00 | 120 | 2025-07-29 19:30
177 | Siddhirganj | 132 | 135 | 2025-07-24 05:00 | 122 | 2025-07-12 16:00
178 | Sirajganj | 132 | 137 | 2025-07-25 18:00 | 123 | 2025-07-12 22:00
179 | Sonargaon | 132 | 134 | 2025-07-08 05:00 | 118 | 2025-07-24 12:00
180 | Sreemongol | 132 | 135 | 2025-07-09 08:00 | 122 | 2025-07-31 19:00
181 | Sreepur | 132 | 138 | 2025-07-24 05:00 | 120 | 2025-07-21 12:00
182 | Srinagar | 132 | 139 | 2025-07-24 05:00 | 123 | 2025-07-13 12:00
183 | SSM | 132 | 139 | 2025-07-01 07:00 | 125 | 2025-07-09 19:00
184 | Sunamganj | 132 | 128 | 2025-07-04 10:00 | 109 | 2025-07-21 19:00
185 | Sylhet | 132 | 132 | 2025-07-09 08:00 | 114 | 2025-07-21 19:00
186 | Sylhet-132 | 132 | 130 | 2025-07-04 08:00 | 116 | 2025-07-21 15:00
187 | Tangail | 132 | 134 | 2025-07-24 06:00 | 115 | 2025-07-23 19:00
188 | Taraganj | 132 | 156 | 2025-07-22 04:00 | 111 | 2025-07-26 19:00
189 | Thakurgaon | 132 | 138 | 2025-07-05 19:00 | 111 | 2025-07-07 13:00
190 | TK | 132 | 136 | 2025-07-08 01:00 | 125 | 2025-07-25 23:00
191 | Tongi | 132 | 140 | 2025-07-24 04:00 | 123 | 2025-07-12 18:30
192 | Ullahpara | 132 | 137 | 2025-07-25 17:00 | 125 | 2025-07-12 21:00
193 | Ullon | 132 | 140 | 2025-07-01 06:00 | 122 | 2025-07-12 15:00
194 | Uttara | 132 | 136 | 2025-07-24 05:00 | 120 | 2025-07-13 12:00
195 | UttaraNew | 132 | 133 | 2025-07-09 05:00 | 120 | 2025-07-13 12:00
196 | Zigatola | 132 | 138 | 2025-07-24 05:00 | 123 | 2025-07-13 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: July 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 23-07-2025 | 19:00 | 446 | 202 | 94.1562
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 23-07-2025 | 19:00 | 446 | 202 | 94.1562
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 23-07-2025 | 19:00 | 446 | 202 | 94.1562
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-07-2025 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 23-07-2025 | 16:00 | 216 | 95 | 45.3785
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 23-07-2025 | 16:00 | 216 | 95 | 45.3785
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 12-07-2025 | 20:00 | 238 | 73 | 47.8738
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 12-07-2025 | 20:00 | 229 | 64 | 45.726
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 21-07-2025 | 17:00 | 589 | 109 | 79.8668
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 21-07-2025 | 17:00 | 589 | 109 | 79.8668
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 19-07-2025 | 15:00 | 481 | 81 | 65.0363
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 04-07-2025 | 22:00 | 192 | 38 | 60.2229
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 01-07-2025 | 22:00 | 196 | 55 | 62.6371
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 01-07-2025 | 22:00 | 196 | 55 | 62.6371
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 16-07-2025 | 22:00 | 245 | 3 | 32.6691
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 07-07-2025 | 23:00 | 312 | 113 | 63.814
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 07-07-2025 | 23:00 | 312 | 113 | 63.814
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 11-07-2025 | 19:30 | 301 | 51 | 93.9354
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 11-07-2025 | 19:30 | 301 | 51 | 93.9354
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 21-07-2025 | 12:00 | 407 | 163 | 58.4569
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 21-07-2025 | 12:00 | 407 | 163 | 58.4569
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 21-07-2025 | 12:00 | 407 | 163 | 58.4569
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 23-07-2025 | 19:00 | 505 | 123 | 69.3018
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 23-07-2025 | 19:00 | 505 | 122 | 69.2704
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 |  |  |  |  | 0
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 23-07-2025 | 23:00 | 389 | 97 | 77.0984
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 23-07-2025 | 23:00 | 385 | 95 | 76.2592
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 23-07-2025 | 22:00 | 70 | 26 | 22.9762
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 23-07-2025 | 22:00 | 70 | 26 | 22.9762
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 07-07-2025 | 21:00 | 299 | 97 | 60.4501
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 13-07-2025 | 13:00 | 327 | 99 | 65.7034
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 23-07-2025 | 13:00 | 218 | 98 | 79.6715
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 23-07-2025 | 13:00 | 218 | 98 | 79.6715
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 05-07-2025 | 12:00 | 183 | 52 | 84.5531
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 05-07-2025 | 12:00 | 183 | 52 | 84.5531
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 05-07-2025 | 12:00 | 183 | 52 | 84.5531
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 29-07-2025 | 13:00 | 240 | 120 | 89.4427
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 03-07-2025 | 00:00 | 260 | 36 | 87.4935
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 12-07-2025 | 05:00 | 232 | 30 | 77.9772
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 19-07-2025 | 04:00 | 195 | 25 | 87.376
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 02-07-2025 | 19:30 | 220 | 22 | 98.2655
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 01-07-2025 | 01:00 | 203 | 64 | 94.5999
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 17-07-2025 | 19:00 | 295 | 44 | 99.4211
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 26-07-2025 | 00:00 | 178 | 56 | 62.2004
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 08-07-2025 | 13:00 | 180 | 41 | 61.5368
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 23-07-2025 | 19:30 | 112 | 10 | 49.9758
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 23-07-2025 | 19:30 | 112 | 10 | 49.9758
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 21-07-2025 | 22:00 | 184 | 43 | 83.9812
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 21-07-2025 | 22:00 | 184 | 43 | 83.9812
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 21-07-2025 | 22:00 | 248 | 61 | 85.1306
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 21-07-2025 | 22:00 | 248 | 61 | 85.1306
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 01-07-2025 | 15:00 | 160 | 71 | 77.7981
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 27-07-2025 | 22:00 | 158 | 73 | 77.355
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 01-07-2025 | 15:00 | 172 | 73 | 83.0445
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 01-07-2025 | 19:30 | 201 | 76 | 71.6294
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 01-07-2025 | 19:30 | 252 | 97 | 90.008
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 25-07-2025 | 01:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 25-07-2025 | 01:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 25-07-2025 | 00:00 | 106 | 70 | 56.4567
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 22-07-2025 | 08:00 | 116 | 68 | 59.7608
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 25-07-2025 | 00:00 | 110 | 74 | 58.922
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 25-07-2025 | 00:00 | 83 | 58 | 45.0032
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 25-07-2025 | 00:00 | 83 | 58 | 45.0032
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 25-07-2025 | 00:00 | 83 | 58 | 45.0032
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 02-07-2025 | 11:00 | 112 | 49 | 81.4998
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-07-2025 | 10:00 | 100 | 47 | 73.6629
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 02-07-2025 | 11:00 | 112 | 49 | 81.4998
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 02-07-2025 | 11:00 | 112 | 49 | 81.4998
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 24-07-2025 | 05:00 | 107 | 53 | 53.0697
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 24-07-2025 | 05:00 | 107 | 53 | 53.0697
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 24-07-2025 | 05:00 | 107 | 53 | 53.0697
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 23-07-2025 | 19:30 | 217 | 59 | 74.9592
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 23-07-2025 | 19:30 | 217 | 59 | 74.9592
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 03-07-2025 | 02:00 | 276 | 41 | 93.0096
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 23-07-2025 | 22:00 | 210 | 65 | 73.2765
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 23-07-2025 | 22:00 | 210 | 65 | 73.2765
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-07-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 26-07-2025 | 13:00 | 174 | 64 | 82.3986
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 26-07-2025 | 13:00 | 174 | 64 | 82.3986
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 26-07-2025 | 12:00 | 246 | 72 | 85.44
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 16-07-2025 | 19:00 | 139 | 23 | 46.9633
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 16-07-2025 | 19:00 | 139 | 23 | 46.9633
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 11-07-2025 | 21:00 | 127 | 26 | 43.2114
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 29-07-2025 | 09:00 | 223 | 44 | 75.7665
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 29-07-2025 | 09:00 | 223 | 44 | 75.7665
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 24-07-2025 | 05:00 | 114 | 18 | 38.4708
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 24-07-2025 | 05:00 | 114 | 18 | 38.4708
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-07-2025 | 00:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 04-07-2025 | 10:00 | 1 | 0 | 0.33333
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 23-07-2025 | 16:00 | 301 | 59 | 68.1618
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 23-07-2025 | 16:00 | 301 | 59 | 68.1618
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 23-07-2025 | 16:00 | 301 | 59 | 68.1618
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 16-07-2025 | 15:00 | 220 | 127 | 84.6752
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 16-07-2025 | 15:00 | 220 | 127 | 84.6752
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 25-07-2025 | 00:00 | 145 | 48 | 50.9128
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 25-07-2025 | 00:00 | 145 | 48 | 50.9128
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 24-07-2025 | 23:00 | 117 | 6 | 39.0512
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 24-07-2025 | 23:00 | 117 | 6 | 39.0512
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 26-07-2025 | 19:00 | 254 | 116 | 93.0782
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 26-07-2025 | 19:00 | 254 | 116 | 93.0782
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 23-07-2025 | 15:00 | 205 | 37 | 92.5832
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 20-07-2025 | 11:00 | 188 | 42 | 85.6153
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 20-07-2025 | 11:00 | 188 | 42 | 85.6153
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: July 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: July 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-07-01 | 15920.39 | 15920.39 | 152 | 21:00 Hr. | 0 | 0 | 15 | 90 | 0 | 0 | 0 | 0 | 47 | - | 2025-07-01 | 14266.07 | 14266.07 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-02 | 15485.2 | 15540.2 | 53 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | - | 2025-07-02 | 14160.34 | 14160.34 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-03 | 15394 | 15465 | 68 | 21:00 Hr. | 5 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 43 | - | 2025-07-03 | 13888.66 | 13888.66 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-04 | 13879 | 13879 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-04 | 12021 | 12021 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-05 | 14938.72 | 14965.72 | 26 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | - | 2025-07-05 | 12655.78 | 12655.78 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-06 | 14723.24 | 14810.24 | 83 | 21:00 Hr. | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 33 | - | 2025-07-06 | 12630.72 | 12640.72 | 10 | 12:00 Hr. | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
2025-07-07 | 14319 | 14339.9 | 20 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | - | 2025-07-07 | 13142.28 | 13142.28 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-08 | 13391.34 | 13391.34 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-08 | 12340.47 | 12340.47 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-09 | 13092 | 13092 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-09 | 11975.95 | 11975.95 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-10 | 13843 | 13875.4 | 31 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | - | 2025-07-10 | 12221.24 | 12221.24 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-07-11 | 14340.57 | 14340.57 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-11 | 11861.13 | 11861.13 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-12 | 16270.11 | 14771.11 | 97 | 21:00 Hr. | 5 | 0 | 0 | 20 | 0 | 0 | 5 | 0 | 67 | - | 2025-07-12 | 13362.32 | 13362.32 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-13 | 15602.51 | 15679.51 | 74 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | - | 2025-07-13 | 14716.75 | 14716.75 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-14 | 13945.22 | 13945.22 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-14 | 12647.51 | 12647.51 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-15 | 14369.2 | 14369.2 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-15 | 12859.96 | 12859.96 | 0 | 11:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-16 | 14916.01 | 14916.01 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-07-16 | 13591 | 13591 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-17 | 14992.2 | 15030.2 | 36 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | - | 2025-07-17 | 13712.55 | 13712.55 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-18 | 14693.2 | 14749.2 | 54 | 21:00 Hr. | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 49 | - | 2025-07-18 | 12649.92 | 12649.92 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-19 | 16006.2 | 16129.51 | 118 | 21:00 Hr. | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 78 | - | 2025-07-19 | 13644.45 | 13644.45 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-20 | 15702.7 | 15860.16 | 103 | 21:00 Hr. | 47 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 18 | - | 2025-07-20 | 13944.46 | 13944.46 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-21 | 15152.08 | 16001.08 | 812 | 21:00 Hr. | 0 | 0 | 40 | 30 | 55 | 0 | 0 | 0 | 687 | - | 2025-07-21 | 14535.9 | 14583.97 | 46 | 12:00 Hr. | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-22 | 16372.21 | 14739.48 | 279 | 21:00 Hr. | 65 | 0 | 45 | 40 | 30 | 0 | 0 | 0 | 99 | - | 2025-07-22 | 14739.48 | 14883.48 | 138 | 12:00 Hr. | 100 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-23 | 16794 | 17099.14 | 292 | 21:00 Hr. | 28 | 0 | 60 | 64 | 45 | 0 | 0 | 0 | 95 | - | 2025-07-23 | 14859 | 15057.55 | 190 | 12:00 Hr. | 85 | 0 | 25 | 70 | 0 | 0 | 0 | 0 | 10 | -
2025-07-24 | 15732.19 | 15900.19 | 161 | 20:00 Hr | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 101 | - | 2025-07-24 | 14124 | 14124 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-25 | 13553 | 13600 | 45 | 21:00 Hr. | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | - | 2025-07-25 | 10710.13 | 10710.13 | 0 | 09:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-26 | 15395.2 | 15549.86 | 148 | 21:00 Hr. | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 113 | - | 2025-07-26 | 13217.98 | 13217.98 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-27 | 15221.5 | 15320.5 | 95 | 21:00 Hr. | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 70 | - | 2025-07-27 | 14359.3 | 14359.3 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-28 | 14883.5 | 14935.5 | 50 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | - | 2025-07-28 | 13646.48 | 13646.48 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-29 | 14891.98 | 15000.98 | 104 | 21:00 Hr. | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 74 |  | 2025-07-29 | 13670.88 | 13670.88 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-30 | 15216.96 | 15359.96 | 128 | 20:00 Hr | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 88 |  | 2025-07-30 | 13613.91 | 13613.91 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-07-31 | 14524.46 | 14580.27 | 45 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 |  | 2025-07-31 | 13228.14 | 13228.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: July 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16794 | 2025-07-23 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 14859 | 2025-07-23 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 17099.14 | 2025-07-23 | 21:00 Hr.
4 | Minimum Generation | MW | 9799.07 | 2025-07-25 | 17:00 Hr
5 | Average of the daily evening peak Genaration | MW | 14953.5771 | - | -
6 | Average of the daily day peak Genaration | MW | 13322.5084 | - | -
7 | Maximum load shed (Evening Peak) | MW | 812 | 2025-07-21 | 21:00 Hr.
8 | Minimum load shed | MW | 0 | 2024-07-04 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 14 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 100.9667 | - | -
11 | Total Generation | MkWh | 10116.2745 | - | -
12 | Total Generation by BPDB | MkWh | 1285.2058 | % of total Gen. | 12.7%
13 | Total Generation by IPP | MkWh | 3008.2106 | '' | 29.74%
14 | A) Total Generation by Generation Companies | MkWh | 4093.7217 | '' | 40.47%
| B) Total Generation by REB | MkWh | 48.2102 | " | 0.4766%
| C) Total Generation by RENTAL | MkWh | 135.6626 | " | 1.341%
| D) Total Imported from India (BIPTC) | MkWh | 648.1179 | " | 6.407%
| E) Total Imported from Tripura, India (A.C) | MkWh | 25.5274 | " | 0.2523%
| F) Total Imported from Nepal | MkWh | 27.5228 | " | 0.2721%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 844.0956 | " | 8.344%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4241.0786 | % of total Gen. | 41.92%
| B) Oil | MkWh | 1124.304 | '' | 11.11%
| C) Hydro | MkWh | 148.0037 | '' | 1.463%
| D) Solar | MkWh | 99.5917 | '' | 0.9845%
| E) Coal | MkWh | 2943.4421 | '' | 29.1%
| F) BIPTC (Import from India) | MkWh | 648.1179 | '' | 6.384%
| G) A.C (Import from Tripura, India) | MkWh | 25.5274 | '' | 0.2523%
| H) Total Imported from Nepal | MkWh | 27.5228 | '' | 0.2721%
| I) Adani (Import from India) | MkWh | 844.0956 | '' | 8.367%
| J) Wind | MkWh | 14.5906 | '' | 0.1446%
16 | Maximun of the daily total Generation . | MkWh | 363.9719 | 2025-07-23
17 | Monthly Load factor | % | 80.9643 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 62764.8628 | - | -
| A) Gas | M.Taka | 14584.2813 | - | -
| B) Coal | M.Taka | 17917.1177 | - | -
| C) HFO | M.Taka | 20924.4454 | - | -
| D) HSD | M.Taka | 0.95508 | - | -
| E) Hydro | M.Taka | 14.8004 | - | -
| F) Solar | M.Taka | 1640.6376 | - | -
| G) Total Import | M.Taka | 7682.6254 | - | -
| H) Wind |  | 213.6058
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2641.1205 | 2025-07-23
| A) Gas | M.Taka | 519.2248 | 2025-07-08
| B) Coal | M.Taka | 657.2563 | 2025-07-31
| C) HFO | M.Taka | 1217.7564 | 2025-07-23
| D) HSD | M.Taka | 0.95508 | 2025-07-22 | -
| E) Hydro | M.Taka | 0.53266 | 2025-07-26 | -
| F) Solar | M.Taka | 82.1046 | 2025-07-12 | -
| G) Total Import |  | 291.8573 | 2025-07-23
| H) Wind | M.Taka | 18.2286 | 2025-07-25
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.2255
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.3911
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/2025 | 06:00
b) | Actual | FT (MSL) | 105.74 | 31/07/2025 | 06:00
22 | Peak Genaration of July 2024 | MW | 15223 | 2024-07-28 | 21:00
23 | Peak Demand of July 2024 | MW | 16000 | 2024-07-30 | 21:00
24 | Maximum peak Generation recorded upto 31/07/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/07/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/07/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [22 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | 305 | Capable | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [30 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | 412 | Capable | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | [5 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable | [23 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [20 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | 194 | Capable |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable | [8 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
26 | b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
27 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
28 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
29 | Bibiyana South 400 MW CCPP | BPDB | 400 | Capable | [28 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
| Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244 | Capable | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150 | Capable | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105 | Capable
40 | Gazipur 100 MW PP | IPP | 105 | Capable
41 | United Payra Power Ltd. | IPP | 150 | Capable
42 | Madhumati 100 MW PP | IPP | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149 | Capable
48 | Feni Lanka Power | IPP | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55 | Capable
52 | Zodiac 54 MW | IPP | 54 | Capable
53 | Anlima Energy Ltd | IPP | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 | Capable | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | 1234 | Capable | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | 307 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Payra 1320 MW Unit-2 | BCPCL | 622 | Capable | [12 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
| Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
Total Installed capacity |  |  |  |  | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: July 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | √ | √ | [10 empty] | √ | [13 empty] | √
5 | Meghnaghat CCPP(Summit) | IPP | 305 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360
7 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | 410
9 | Haripur 412 MW CCPP | EGCB | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | 97
11 | Chandpur 150 MW CCPP | BPDB | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210
13 | Shikalbaha 225 MW CCPP | BPDB | 225
14 | Shikalbaha Peaking GT | BPDB | 150
15 | Shahjibazar 330 MW CCPP | BPDB | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | 104
18 | Bhola 225 MW CCPP | BPDB | 194 | √
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | √ | √ | [24 empty] | √
21 | Siddhirganj 335 MW CCPP | EGCB | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | 231
24 | RPCL 210 MW CCPP | IPP | 210
25 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
27 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | 220
33 | Haripur 360MW CCPP(HPL) | IPP | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150 | [10 empty] | √ | √ | √ | √ | √ | √ | √ | √ |  | √
36 | Anwara 300 MW PP (United) | IPP | 300
37 | Chandpur 200MW (Desh energy) | IPP | 200 | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105
40 | Gazipur 100 MW PP | IPP | 105
41 | United Payra Power Ltd. | IPP | 150
42 | Madhumati 100 MW PP | IPP | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105
44 | Karnaphuli Power Ltd. | IPP | 110
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300
46 | Madanganj-55 MW PP(Summit) | IPP | 55
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149
48 | Feni Lanka Power | IPP | 114 | [11 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | 110
50 | Manikganj 162 MW (MPGL) | IPP | 162 | [13 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55
52 | Zodiac 54 MW | IPP | 54
53 | Anlima Energy Ltd | IPP | 116
54 | Thakurgaon 115 MW (EPV) | IPP | 115
55 | Confidence Unit-2 Bogura | IPP | 113
56 | Confidence Unit-1 Bogura | IPP | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | 54 | [24 empty] | √ | √ | √ | √ | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55
59 | Kodda 150 MW (BR Power) | IPP | 149
60 | Chandpur 115 MW (Doreen) | IPP | 115 | [15 empty] | √ | √ | √ | √ | √ | √ | √
61 | Kanchan Purbachal Power Ltd | IPP | 55
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 | √ | √ | √ | √ | √ | [14 empty] | √ |  |  |  |  | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 |  |  |  |  | √ | [9 empty] | √ |  |  |  |  | √ |  |  |  |  | √
64 | Rampal 1320 MW (BIFPCL) | BIFPCL | 1234 | √ | [23 empty] | √
65 | Barishal 307 MW PP (BEPCL) | Private | 307 |  |  |  |  | √ | [6 empty] | √ | √ | √ | √ |  |  |  |  | √ |  |  |  |  | √
| Unique Meghnaghat Power Limited (UMPL) | IPP |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | [7 empty] | √
| Bibiyana South 400 MW | BPDB | 383
| Ashuganj 420 MW CCPP(East) | APSCL | 400
| Ashuganj 55 MW PP (Precision) | QRPP | 55
| Bagura 113 MW PP (Confidence)-2 | IPP | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP | 115
| Chandpur 150 MW CCPP | BPDB | 163
| Khulna 225 MW CCPP | NWPGCL | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
| Shajibazar 100 MW PP | BPDB | 100
| Payra 1320 MW Unit-1 | BCPCL | 622