## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-09-2025 | during | 02-09-2025 | during | 02-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 365 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 380 | 319 | 400.75 | 400.75 | 368 | 368 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 400 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 302 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 5 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 60 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 36.3 | 44 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 58 | 104 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 50 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.2 | 24 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 185 | 297 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 108 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 154 | 141 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 300 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2539.5 | 2847 | 5900.34 | 5911.34 | 3835.67 | 3846.67
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 170 | 212 | 150 | 150 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 50 | 90 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 68 | 70 | 70 | 48 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 49 | 57 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 7 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 41 | 82 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.14 | 0 | 2.13 | 0 | 2.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 100 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 30 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 110 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 980 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 60 | 40 | 40 | 40 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 631 | 630 | 635 | 635 | 635 | 635 | machine problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2155.14 | 2733 | 3640.85 | 3643.72 | 3506.85 | 3544.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 192 | 191 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 331 | 337 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 36 | 46.7 | 46.7 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 38 | 40 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 137 | 137 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 36 | 88 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 27 | 34 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 137 | 160 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 54 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 41 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 48 | 100 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 8 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 87 | 92 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 45 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1537 | 1661 | 2435.86 | 2370.86 | 2120.66 | 2055.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-09-2025 | during | 02-09-2025 | during | 02-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 70 | 157.5 | 157.5 | 104 | 104 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 38 | 40 | 40 | 55 | 75 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 88 | 104 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.66 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 261.66 | 259 | 430.2 | 383 | 338.2 | 329
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 68 | 70 | 70 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 135 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 82 | 82 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 0 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 365 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1179 | 1008 | 1276 | 1276 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 917 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 12 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 184 | 192 | 410 | 410 | 308 | 308 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1160 | 1222 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2401 | 2402 | 3646.2 | 3554.2 | 3364.2 | 3272.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 299 | 300 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1081 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 136 | 150 | 150 | 150 | 150 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 273 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1993.58 | 2292 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 62.12 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 202 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 184 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 185 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 380 | 345 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.73 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1036 | 1149.82 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.07 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2081.92 | 2533.02 | 3183.47 | 3016.87 | 3109.68 | 2943.08
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 145 | 153 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 29 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 211 | 0 | 189.87 | 0 | 189.87 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 464 | 544 | 638.47 | 412 | 638.47 | 412
System Total |  |  |  |  | 28823.2 | 27829.875 | 14612.8 | 16279.02 | 23313.39 | 22728.99 | 20233.73 | 19722.33
Forecast Scenario (02-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15870 |  | 0 |  | 15870
|  |  |  | 1:00 | 15530 |  | 0 |  | 15530
|  |  |  | 2:00 | 14940 |  | 0 |  | 14940
|  |  |  | 3:00 | 14560 |  | 0 |  | 14560
|  |  |  | 4:00 | 14200 |  | 0 |  | 14200
|  |  |  | 5:00 | 14030 |  | 0 |  | 14030
|  |  |  | 6:00 | 13610 |  | 0 |  | 13610
|  |  |  | 7:00 | 13620 |  | 0 |  | 13620
|  |  |  | 8:00 | 13670 |  | 0 |  | 13670
|  |  |  | 9:00 | 13900 |  | 0 |  | 13900
|  |  |  | 10:00 | 14100 |  | 0 |  | 14100
|  |  |  | 11:00 | 14450 |  | 0 |  | 14450
|  |  |  | 12:00 | 14800 |  | 0 |  | 14800
|  |  |  | 13:00 | 14830 |  | 0 |  | 14830
|  |  |  | 14:00 | 14880 |  | 0 |  | 14880
|  |  |  | 15:00 | 15140 |  | 0 |  | 15140
|  |  |  | 16:00 | 14830 |  | 0 |  | 14830
|  |  |  | 17:00 | 14540 |  | 0 |  | 14540
|  |  |  | 18:00 | 14040 |  | 0 |  | 14040
|  |  |  | 18:30 | 15000 |  | 0 |  | 15000
|  |  |  | 19:00 | 15780 |  | 0 |  | 15780
|  |  |  | 19:30 | 16400 |  | 0 |  | 16400
|  |  |  | 20:00 | 16240 |  | 0 |  | 16240
|  |  |  | 21:00 | 16100 |  | 0 |  | 16100
|  |  |  | 22:00 | 15900 |  | 0 |  | 15900
|  |  |  | 23:00 | 15800 |  | 0 |  | 15800
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 14800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 355.36 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:51 hrs on 02-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-09-2025 | [28 empty] | Date: | 01-09-2025 | [28 empty] | Date: | 01-09-2025 | [28 empty] | Date: | 01-09-2025 | [28 empty] | Date: | 01-09-2025 | [14 empty] | Date: | 01-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 103 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 50 | 17 | 149 | 121 | 297 | 15 | 55 | 158 | 0 | 360 | 292 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 23.5 | 22 | 0 | 300 | 0 | 0 | 69 | 0 | 0 | 66 | 60 | 0 | 12 | 12 | 0 | 219 | 51 | 32 | 630 | 16 | 0 | 26 | 17 | 102 | 218 | 0 | 0 | 0 | 858 | 0 | 51 | 117 | 8 | 0 | 344 | 330 | 44 | 201 | 38 | 93 | 70 | 181 | 0 | 19 | 114 | 48 | 43 | 0 | 37 | 320 | 0 | 388 | 0 | 60 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 141 | 17 | 110 | 76 | 80 | 0 | 0 | 0 | 8382.5 | 915 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 17 | 1129.56 | 0 | 40 | 0 | 0 | 70 | 0 | 96 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 199 | 0 | 181 | 0 | 186 | 0 | 414 | 0 | 0 | 154 | 0 | 114 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 300 | 1042 | 138 | 7309.56 | 15692.06 | 107.91
01:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 42.5 | 0 | 149 | 122 | 297 | 0 | 55 | 147 | 0 | 360 | 282 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 290 | 0 | 0 | 68 | 0 | 0 | 66 | 60 | 0 | 12 | 12 | 0 | 219 | 48 | 32 | 632 | 0 | 0 | 26 | 8 | 94 | 219 | 0 | 0 | 0 | 852 | 0 | 51 | 115 | 8 | 0 | 351 | 330 | 44 | 188 | 38 | 93 | 70 | 180 | 0 | 19 | 114 | 48 | 43 | 0 | 37 | 310 | 0 | 368 | 0 | 60 | 152 | 0 | 0 | 84 | 30 | 0 | 18 | 141 | 17 | 110 | 57 | 80 | 0 | 0 | 0 | 8119.5 | 910 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1173 | 17 | 1143.13 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 180 | 0 | 186 | 0 | 396 | 0 | 0 | 152 | 0 | 114 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 300 | 1040 | 127 | 7075.13 | 15194.63 | 107.91
02:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 44.5 | 0 | 149 | 76 | 195 | 0 | 53 | 140 | 0 | 330 | 284 | 0 | 0 | 17 | 290 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 295 | 0 | 0 | 50 | 0 | 0 | 66 | 52 | 0 | 12 | 12 | 0 | 220 | 47 | 32 | 630 | 0 | 0 | 26 | 8 | 95 | 219 | 0 | 0 | 0 | 847 | 0 | 51 | 80 | 8 | 0 | 348 | 330 | 44 | 193 | 38 | 92 | 70 | 180 | 0 | 19 | 114 | 46 | 43 | 0 | 37 | 305 | 0 | 382 | 0 | 60 | 146 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 110 | 57 | 80 | 0 | 0 | 0 | 7799.5 | 910 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 17 | 1149.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 185 | 0 | 342 | 0 | 0 | 154 | 0 | 114 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 300 | 1040 | 139 | 6934.59 | 14734.09 | 107.91
03:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 46 | 0 | 104 | 75 | 0 | 0 | 17 | 120 | 0 | 330 | 291 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 296 | 0 | 0 | 47 | 0 | 0 | 66 | 38 | 0 | 12 | 12 | 0 | 220 | 48 | 33 | 635 | 0 | 0 | 26 | 0 | 94 | 219 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 8 | 0 | 347 | 330 | 44 | 199 | 38 | 93 | 70 | 180 | 0 | 19 | 114 | 46 | 43 | 0 | 37 | 310 | 0 | 386 | 0 | 60 | 142 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 110 | 57 | 83 | 0 | 0 | 0 | 7473 | 911 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 0 | 1143.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 180 | 0 | 183 | 0 | 358 | 0 | 0 | 150 | 0 | 114 | 0 | 105 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 300 | 1042 | 95 | 6893.94 | 14366.94 | 107.91
04:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 29.2 | 0 | 72 | 60 | 0 | 0 | 17 | 68 | 0 | 330 | 291 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0 | 220 | 28 | 33 | 635 | 0 | 0 | 26 | 0 | 93 | 219 | 0 | 0 | 0 | 825 | 0 | 51 | 0 | 8 | 0 | 349 | 330 | 44 | 194 | 38 | 93 | 70 | 180 | 0 | 19 | 114 | 44 | 43 | 0 | 37 | 315 | 0 | 371 | 0 | 60 | 143 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 109 | 57 | 85 | 0 | 0 | 0 | 7229.2 | 911 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 1089.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 180 | 0 | 183 | 0 | 345 | 0 | 0 | 149 | 0 | 70 | 0 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 300 | 1042 | 0 | 6653.81 | 13883.01 | 107.92
05:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15.8 | 0 | 51 | 45 | 0 | 0 | 17 | 16 | 0 | 330 | 292 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 635 | 0 | 0 | 26 | 0 | 51 | 219 | 0 | 0 | 0 | 849 | 0 | 51 | 0 | 8 | 0 | 348 | 330 | 44 | 199 | 38 | 93 | 70 | 180 | 0 | 19 | 114 | 44 | 43 | 0 | 37 | 310 | 0 | 390 | 0 | 60 | 144 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 109 | 57 | 85 | 0 | 0 | 0 | 7109.8 | 910 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1149.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 180 | 0 | 184 | 0 | 357 | 0 | 0 | 149 | 0 | 35 | 0 | 49 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 300 | 1041 | 0 | 6673.18 | 13782.98 | 107.92
06:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 15.4 | 0 | 51 | 45 | 0 | 0 | 17 | 0 | 0 | 330 | 288 | 0 | 0 | 0 | 327 | 0 | 0 | 1 | 108 | 0 | 22 | 0 | 290 | 0 | 0 | 0 | 0 | 1 | 66 | 0 | 0 | 12 | 12 | 0.03 | 220 | 0 | 33 | 631 | 0 | 0 | 26 | 0 | 50 | 219 | 0 | 0 | 0 | 792 | 0 | 51 | 0 | 8 | 0 | 300 | 330 | 45 | 197 | 38 | 91 | 50 | 180 | 0 | 19 | 114 | 42 | 43 | 2 | 36 | 310 | 0 | 390 | 0 | 60 | 142 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 101 | 57 | 85 | 0 | 1.14 | 0 | 6909.57 | 911 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.68 | 1120 | 0 | 1140.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0 | 0 | 0 | 1 | 199 | 0 | 180 | 0 | 186 | 0 | 351 | 0 | 0.08 | 150 | 0 | 0 | 0 | 34 | 0 | 100 | 0 | 0 | 2 | 0.02 | 0 | 200 | 115 | 220 | 0 | 300 | 1041 | 0 | 6476.98 | 13386.55 | 107.92
07:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 15.8 | 0 | 51 | 45 | 0 | 0 | 17 | 0 | 0 | 330 | 295 | 0 | 0 | 0 | 328 | 0 | 0 | 7 | 108 | 20 | 22 | 0 | 296 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 0 | 12 | 12 | 0 | 221 | 0 | 20 | 634 | 0 | 0 | 25 | 0 | 49 | 219 | 0 | 0 | 0 | 830 | 0 | 51 | 0 | 8 | 0 | 300 | 330 | 44 | 198 | 35 | 81 | 50 | 179 | 0 | 14 | 114 | 40 | 43 | 16 | 36 | 315 | 0 | 382 | 0 | 60 | 146 | 0 | 0 | 84 | 30 | 0 | 18 | 149 | 0 | 100 | 57 | 81 | 0 | 10.8 | 0 | 7004.6 | 911 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.35 | 1043 | 0 | 1155.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.51 | 16 | 0 | 0 | 11.56 | 198 | 0 | 180 | 0 | 189 | 0 | 358 | 0 | 0.85 | 153 | 0 | 0 | 6 | 34 | 0 | 100 | 0 | 0.6 | 41 | 0.14 | 0 | 169 | 115 | 220 | 0 | 303 | 1042 | 0 | 6498.12 | 13502.72 | 107.92
08:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 14.7 | 0 | 51 | 60 | 0 | 0 | 17 | 0 | 0 | 330 | 288 | 0 | 0 | 0 | 290 | 0 | 0 | 16 | 108 | 24.5 | 22 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 12 | 0.92 | 222 | 0 | 10 | 632 | 0 | 0 | 25 | 0 | 45 | 219 | 0 | 0 | 0 | 840 | 1 | 51 | 0 | 8 | 0 | 300 | 295 | 43 | 195 | 31 | 72 | 70 | 180 | 0 | 16 | 114 | 38 | 43 | 37 | 36 | 310 | 0 | 344 | 0 | 60 | 138 | 0 | 0 | 81 | 30 | 0 | 18 | 149 | 0 | 100 | 57 | 71 | 1 | 24.87 | 0 | 6854.99 | 918 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33.06 | 985 | 0 | 1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.38 | 42 | 0 | 0 | 28 | 199 | 0 | 185 | 0 | 188 | 0 | 347 | 0 | 1.67 | 152 | 0 | 0 | 16 | 34 | 0 | 100 | 0 | 2.3 | 103 | 0.31 | 0 | 168 | 100 | 180 | 0 | 300 | 1030 | 0 | 6514.72 | 13369.71 | 107.92
09:00 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15.4 | 0 | 51 | 59 | 0 | 0 | 29 | 16 | 0 | 330 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 23 | 90 | 22.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 12 | 3.05 | 222 | 0 | 2 | 630 | 0 | 0 | 26 | 0 | 47 | 217 | 0 | 0 | 0 | 840 | 1 | 51 | 0 | 8 | 0 | 300 | 280 | 42 | 199 | 34 | 73 | 70 | 179 | 0 | 19 | 114 | 34 | 43 | 55 | 27 | 310 | 0 | 335 | 0 | 60 | 141 | 0 | 0 | 81 | 30 | 0 | 18 | 149 | 0 | 90 | 56 | 70 | 2 | 38.23 | 0 | 6878.18 | 918 | 179 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 1003 | 0 | 1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.51 | 73 | 0 | 0 | 45.63 | 150 | 0 | 150 | 0 | 140 | 0 | 358 | 0 | 4.14 | 151 | 0 | 0 | 25 | 34 | 0 | 100 | 0 | 5.5 | 153 | 0.44 | 0 | 170 | 100 | 180 | 0 | 299 | 1020 | 0 | 6556.22 | 13434.4 | 107.92
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 16.1 | 0 | 69 | 58 | 0 | 0 | 55 | 16 | 0 | 330 | 295 | 0 | 0 | 0 | 320 | 0 | 0 | 27 | 90 | 22 | 22 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 12 | 1.72 | 222 | 0 | 2 | 630 | 0 | 0 | 26 | 0 | 49 | 214 | 0 | 0 | 0 | 840 | 2 | 51 | 0 | 8 | 0 | 319 | 330 | 40 | 201 | 34 | 73 | 50 | 174 | 0 | 19 | 114 | 36 | 43 | 64 | 27 | 315 | 0 | 387 | 0 | 60 | 147 | 0 | 0 | 77 | 30 | 0 | 16 | 150 | 0 | 90 | 56 | 69 | 2 | 46.7 | 0 | 7107.52 | 917 | 183 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63 | 1012 | 0 | 1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.34 | 98 | 0 | 0 | 57.95 | 140 | 0 | 140 | 0 | 140 | 0 | 372 | 0 | 5.07 | 148 | 0 | 0 | 32 | 34 | 0 | 100 | 0 | 7.5 | 188 | 0.53 | 0 | 188 | 115 | 220 | 0 | 299 | 1068 | 0 | 6660.39 | 13767.91 | 107.92
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 15.8 | 14 | 69 | 59 | 0 | 0 | 55 | 70 | 0 | 330 | 299 | 0 | 0 | 20 | 323 | 0 | 0 | 26 | 90 | 21.8 | 22 | 0 | 320 | 0 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 12 | 12 | 2.16 | 222 | 0 | 2 | 633 | 0 | 0 | 39 | 0 | 49 | 213 | 0 | 0 | 0 | 844 | 8 | 51 | 1 | 8 | 0 | 331 | 330 | 38 | 192 | 35 | 75 | 50 | 138 | 4 | 8 | 47 | 36 | 43 | 47 | 27 | 315 | 0 | 379 | 0 | 60 | 153 | 0 | 0 | 75 | 30 | 0 | 16 | 149 | 0 | 90 | 56 | 69 | 2 | 50.33 | 0 | 7151.09 | 918 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 1143 | 0 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.96 | 114 | 0 | 0 | 64.77 | 140 | 0 | 140 | 0 | 140 | 0 | 387 | 0 | 5.62 | 147 | 0 | 0 | 36 | 34 | 0 | 100 | 0 | 8 | 208 | 0.49 | 0 | 219 | 115 | 220 | 0 | 300 | 1078 | 0 | 6880.84 | 14031.93 | 107.93
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 36.3 | 17 | 108 | 58 | 185 | 5 | 55 | 154 | 0 | 300 | 297 | 0 | 0 | 50 | 320 | 0 | 0 | 27 | 90 | 21.2 | 21 | 0 | 320 | 0 | 0 | 41 | 0 | 0 | 49 | 4 | 0 | 12 | 12 | 3.14 | 222 | 0 | 2 | 631 | 0 | 0 | 50 | 0 | 50 | 170 | 0 | 0 | 0 | 900 | 9 | 51 | 36 | 8 | 0 | 331 | 330 | 38 | 192 | 36 | 87 | 70 | 137 | 8 | 8 | 48 | 44 | 41 | 45 | 27 | 320 | 0 | 374 | 0 | 60 | 152 | 0 | 0 | 77 | 30 | 0 | 16 | 150 | 0 | 88 | 55 | 66 | 2 | 50.66 | 0 | 7672.3 | 918 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 101 | 1160 | 0 | 1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.12 | 112 | 0 | 0 | 66.07 | 140 | 0 | 140 | 0 | 140 | 0 | 380 | 0 | 5.73 | 145 | 0 | 29 | 37 | 34 | 0 | 0 | 0 | 8 | 211 | 0.58 | 0 | 278 | 115 | 220 | 0 | 299 | 1081 | 0 | 6940.5 | 14612.8 | 107.93
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 47.1 | 17 | 146 | 57 | 277 | 50 | 55 | 147 | 0 | 300 | 288 | 0 | 0 | 55 | 317 | 0 | 0 | 32 | 108 | 21 | 21 | 0 | 300 | 0 | 0 | 67 | 0 | 2 | 48 | 37 | 0 | 12 | 12 | 2.52 | 222 | 0 | 6 | 630 | 0 | 0 | 50 | 0 | 49 | 170 | 0 | 0 | 0 | 900 | 18 | 51 | 78 | 8 | 0 | 336 | 330 | 39 | 192 | 38 | 91 | 70 | 144 | 8 | 19 | 92 | 44 | 41 | 49 | 26 | 310 | 0 | 374 | 0 | 50 | 152 | 0 | 0 | 76 | 30 | 0 | 15 | 165 | 0 | 88 | 55 | 66 | 2 | 49.58 | 0 | 7985.2 | 917 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 1140 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.86 | 111 | 0 | 0 | 62.63 | 140 | 0 | 140 | 0 | 140 | 0 | 345 | 0 | 5.55 | 147 | 0 | 50 | 36 | 34 | 0 | 0 | 0 | 8 | 204 | 0.45 | 0 | 272 | 115 | 220 | 0 | 299 | 1080 | 0 | 6983.49 | 14968.69 | 107.93
14:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 48.5 | 17 | 142 | 27 | 277 | 55 | 55 | 154 | 0 | 300 | 292 | 0 | 0 | 20 | 317 | 0 | 0 | 28 | 108 | 22 | 21 | 0 | 300 | 0 | 0 | 88 | 0 | 1 | 48 | 59 | 0 | 12 | 12 | 3.05 | 222 | 0 | 2 | 630 | 60 | 0 | 50 | 1 | 17 | 170 | 0 | 0 | 0 | 900 | 3 | 51 | 90 | 8 | 0 | 332 | 330 | 40 | 192 | 38 | 89 | 70 | 146 | 8 | 19 | 100 | 48 | 41 | 57 | 26 | 315 | 0 | 368 | 0 | 50 | 148 | 0 | 0 | 76 | 30 | 0 | 15 | 159 | 0 | 96 | 55 | 66 | 2 | 45.84 | 0 | 8013.39 | 918 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 1154 | 0 | 1156.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.87 | 106 | 0 | 0 | 56.85 | 140 | 0 | 140 | 0 | 140 | 0 | 364 | 0 | 5.11 | 146 | 0 | 50 | 32 | 34 | 0 | 100 | 0 | 6.8 | 188 | 0.44 | 0 | 276 | 115 | 220 | 0 | 301 | 1082 | 0 | 7063.28 | 15076.67 | 107.93
15:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 40.7 | 17 | 142 | 27 | 297 | 55 | 55 | 155 | 0 | 300 | 298 | 0 | 0 | 0 | 316 | 0 | 0 | 22 | 108 | 21 | 21 | 0 | 300 | 0 | 0 | 86 | 0 | 0 | 59 | 59 | 0 | 12 | 12 | 1.71 | 222 | 0 | 2 | 633 | 127 | 0 | 50 | 17 | 31 | 169 | 0 | 0 | 0 | 887 | 2 | 51 | 90 | 8 | 0 | 332 | 330 | 40 | 192 | 34 | 86 | 50 | 140 | 8 | 19 | 105 | 48 | 41 | 36 | 26 | 315 | 0 | 369 | 0 | 68 | 149 | 0 | 0 | 75 | 30 | 0 | 15 | 125 | 0 | 88 | 55 | 66 | 2 | 37.97 | 0 | 8040.38 | 917 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1216 | 0 | 1136.7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 36.68 | 61 | 0 | 0 | 45.54 | 140 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 4.2 | 151 | 0 | 74 | 26 | 34 | 0 | 100 | 0 | 5.6 | 167 | 0.23 | 0 | 276 | 115 | 220 | 0 | 298 | 1080 | 13 | 7062.95 | 15103.33 | 107.93
16:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 33.2 | 17 | 141 | 27 | 297 | 55 | 55 | 156 | 0 | 300 | 299 | 0 | 0 | 17 | 320 | 0 | 0 | 11 | 108 | 21 | 21 | 0 | 300 | 0 | 0 | 87 | 0 | 0 | 56 | 59 | 0 | 12 | 12 | 0.77 | 222 | 9 | 2 | 633 | 123 | 0 | 50 | 17 | 67 | 207 | 0 | 0 | 0 | 901 | 2 | 51 | 97 | 8 | 0 | 337 | 330 | 40 | 210 | 34 | 90 | 50 | 170 | 8 | 19 | 100 | 46 | 40 | 16 | 27 | 310 | 0 | 357 | 0 | 68 | 150 | 0 | 0 | 74 | 30 | 0 | 12 | 30 | 0.7 | 88 | 37 | 69 | 1 | 24.75 | 0 | 8015.42 | 918 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1242 | 0 | 1149.78 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 19.47 | 53 | 0 | 0 | 29.63 | 140 | 0 | 140 | 0 | 140 | 0 | 401 | 0 | 2.84 | 155 | 0 | 114 | 18 | 34 | 0 | 100 | 0 | 0 | 94 | 0.31 | 0 | 267 | 115 | 220 | 0 | 300 | 1100 | 72 | 7110.03 | 15125.45 | 107.93
17:00 | 7 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 33.7 | 17 | 145 | 27 | 297 | 55 | 55 | 147 | 0 | 300 | 296 | 0 | 0 | 17 | 280 | 0 | 0 | 4 | 108 | 23 | 21 | 0 | 300 | 0 | 0 | 92 | 0 | 31 | 65 | 62 | 0 | 25 | 12 | 0.56 | 222 | 49 | 5 | 630 | 106 | 0 | 50 | 17 | 64 | 213 | 0 | 0 | 0 | 882 | 0 | 51 | 93 | 8 | 0 | 300 | 280 | 40 | 188 | 35 | 87 | 50 | 158 | 8 | 19 | 100 | 44 | 36 | 5 | 34 | 310 | 0 | 314 | 0 | 68 | 143 | 0 | 0 | 75 | 30 | 0 | 12 | 0 | 17 | 104 | 46 | 68 | 0 | 11.21 | 0 | 7799.47 | 917 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1233 | 17 | 1147.31 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8.82 | 22 | 0 | 0 | 11.57 | 140 | 0 | 140 | 0 | 140 | 0 | 340 | 0 | 1.2 | 158 | 0 | 114 | 9 | 34 | 0 | 100 | 0 | 3.8 | 51 | 0.08 | 32 | 193 | 115 | 180 | 0 | 301 | 1100 | 72 | 6850.78 | 14650.25 | 107.93
18:00 | 7 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 41.1 | 17 | 149 | 27 | 297 | 55 | 55 | 142 | 0 | 300 | 300 | 0 | 0 | 17 | 250 | 0 | 0 | 1 | 108 | 23 | 21 | 0 | 300 | 0 | 0 | 88 | 0 | 34 | 65 | 68 | 0 | 25 | 12 | 0 | 182 | 48 | 6 | 632 | 51 | 0 | 50 | 17 | 61 | 213 | 0 | 0 | 0 | 940 | 0 | 51 | 86 | 8 | 0 | 300 | 280 | 22 | 154 | 36 | 90 | 70 | 152 | 8 | 19 | 95 | 40 | 32 | 0 | 34 | 300 | 0 | 338 | 0 | 68 | 139 | 0 | 0 | 76 | 30 | 0 | 12 | 0 | 18 | 104 | 38 | 70 | 0 | 1.33 | 2 | 7690.43 | 918 | 188 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1144 | 17 | 1028.28 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 1.23 | 3 | 0 | 0 | 1.28 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0.13 | 155 | 0 | 114 | 1 | 62 | 0 | 100 | 0 | 0.2 | 8 | 0 | 32 | 170 | 100 | 180 | 0 | 301 | 1050 | 72 | 6446.12 | 14136.55 | 107.93
19:00 | 7 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 50.5 | 17 | 149 | 104 | 297 | 55 | 55 | 156 | 0 | 350 | 301 | 0 | 0 | 17 | 322 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 300 | 28 | 0 | 88 | 0 | 63 | 66 | 68 | 0 | 25 | 12 | 0 | 181 | 60 | 4 | 630 | 110 | 0 | 13 | 17 | 78 | 212 | 0 | 0 | 0 | 962 | 0 | 51 | 85 | 8 | 0 | 338 | 330 | 16 | 185 | 36 | 90 | 70 | 158 | 8 | 19 | 105 | 28 | 43 | 0 | 34 | 320 | 0 | 353 | 0 | 68 | 149 | 0 | 0 | 77 | 30 | 0 | 15 | 0 | 35 | 104 | 38 | 70 | 0 | 0 | 12 | 8251.5 | 918 | 192 | 0 | 0 | 8 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 17 | 1152.28 | 0 | 42 | 0 | 90 | 66 | 0 | 85 | 12 | 52.2 | 0 | 0 | 27 | 0 | 0 | 173 | 0 | 180 | 0 | 180 | 0 | 340 | 0 | 0 | 153 | 0 | 114 | 0 | 113 | 0 | 163 | 0 | 0 | 0 | 0 | 35 | 260 | 115 | 220 | 0 | 300 | 1120 | 136 | 7496.48 | 15747.98 | 107.93
19:30 | 60 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 44 | 17 | 149 | 104 | 297 | 55 | 55 | 141 | 0 | 400 | 302 | 0 | 0 | 17 | 322 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 300 | 30 | 0 | 82 | 0 | 60 | 57 | 68 | 0 | 25 | 12 | 0 | 221 | 100 | 7 | 630 | 110 | 0 | 32 | 17 | 90 | 212 | 0 | 0 | 0 | 980 | 0 | 51 | 88 | 8 | 0 | 337 | 330 | 40 | 191 | 36 | 92 | 70 | 160 | 8 | 19 | 100 | 54 | 43 | 0 | 34 | 320 | 0 | 365 | 0 | 68 | 135 | 0 | 0 | 77 | 28 | 0 | 15 | 0 | 35 | 104 | 38 | 70 | 0 | 0 | 12 | 8508 | 917 | 192 | 0 | 4 | 12 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 17 | 1149.82 | 0 | 47 | 0 | 108 | 113 | 0 | 95 | 25 | 52.2 | 0 | 0 | 27 | 0 | 0 | 202 | 0 | 184 | 0 | 185 | 0 | 345 | 0 | 0 | 153 | 0 | 114 | 0 | 113 | 0 | 164 | 0 | 0 | 0 | 0 | 48 | 273 | 115 | 220 | 0 | 300 | 1200 | 136 | 7771.02 | 16279.02
20:00 | 64 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 43.4 | 17 | 149 | 104 | 297 | 55 | 55 | 139 | 0 | 400 | 302 | 0 | 0 | 35 | 322 | 0 | 0 | 0 | 108 | 11 | 20 | 0 | 300 | 17 | 0 | 82 | 0 | 63 | 66 | 68 | 0 | 25 | 12 | 0 | 221 | 108 | 10 | 630 | 116 | 0 | 29 | 17 | 91 | 213 | 0 | 0 | 0 | 1000 | 0 | 51 | 86 | 8 | 0 | 336 | 330 | 38 | 191 | 36 | 92 | 70 | 160 | 9 | 19 | 104 | 54 | 43 | 0 | 35 | 305 | 0 | 317 | 0 | 67 | 135 | 10 | 0 | 78 | 30 | 0 | 15 | 0 | 35 | 105 | 38 | 70 | 0 | 0 | 12 | 8493.4 | 918 | 187 | 0 | 12 | 18 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 17 | 1142.11 | 0 | 47 | 0 | 113 | 113 | 0 | 94 | 38 | 52.2 | 0 | 0 | 27 | 0 | 0 | 202 | 0 | 184 | 0 | 185 | 0 | 347 | 0 | 0 | 154 | 0 | 114 | 0 | 113 | 0 | 164 | 0 | 0 | 0 | 0 | 21 | 274 | 115 | 220 | 0 | 300 | 1110 | 100 | 7644.31 | 16137.71 | 107.93
21:00 | 7 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 47 | 17 | 149 | 120 | 297 | 55 | 55 | 151 | 0 | 400 | 283 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 108 | 25 | 20 | 0 | 300 | 15 | 0 | 89 | 0 | 27 | 66 | 68 | 0 | 25 | 12 | 0 | 220 | 110 | 15 | 632 | 116 | 0 | 33 | 17 | 95 | 218 | 0 | 0 | 0 | 970 | 0 | 51 | 102 | 8 | 0 | 340 | 330 | 41 | 187 | 37 | 92 | 50 | 163 | 8 | 19 | 96 | 54 | 43 | 0 | 34 | 310 | 0 | 309 | 0 | 67 | 145 | 10 | 0 | 80 | 28 | 0 | 16 | 0 | 35 | 106 | 37 | 70 | 0 | 0 | 0 | 8459 | 918 | 187 | 0 | 28 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 17 | 1141.6 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 52.2 | 0 | 0 | 25 | 0 | 0 | 201 | 0 | 184 | 0 | 185 | 0 | 340 | 0 | 0 | 157 | 0 | 114 | 0 | 113 | 0 | 164 | 0 | 0 | 0 | 0 | 16 | 271 | 115 | 220 | 0 | 300 | 1095 | 100 | 7647.8 | 16106.8 | 107.93
22:00 | 7 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 44.2 | 17 | 149 | 120 | 297 | 55 | 55 | 143 | 0 | 350 | 280 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 300 | 13 | 0 | 91 | 0 | 18 | 66 | 68 | 0 | 25 | 12 | 0 | 220 | 34 | 12 | 632 | 45 | 0 | 33 | 17 | 51 | 218 | 0 | 0 | 0 | 860 | 0 | 51 | 112 | 8 | 0 | 346 | 330 | 42 | 182 | 37 | 85 | 50 | 198 | 9 | 19 | 92 | 54 | 43 | 0 | 34 | 300 | 0 | 303 | 0 | 67 | 137 | 10 | 0 | 80 | 30 | 0 | 16 | 0 | 20 | 107 | 37 | 70 | 0 | 0 | 0 | 8026.2 | 918 | 187 | 0 | 25 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1136.98 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 202 | 0 | 180 | 0 | 180 | 0 | 332 | 0 | 0 | 156 | 0 | 114 | 0 | 113 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 300 | 1085 | 73 | 7530.18 | 15556.38 | 107.93
23:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 43 | 17 | 124 | 45 | 95 | 55 | 47 | 94 | 0 | 320 | 285 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 92 | 23 | 15 | 0 | 300 | 13 | 0 | 57 | 0 | 18 | 66 | 52 | 0 | 25 | 12 | 0 | 220 | 34 | 14 | 635 | 45 | 0 | 33 | 17 | 50 | 220 | 0 | 0 | 0 | 895 | 0 | 51 | 50 | 8 | 0 | 320 | 280 | 43 | 187 | 37 | 86 | 70 | 198 | 8 | 19 | 95 | 50 | 43 | 0 | 35 | 295 | 0 | 315 | 0 | 70 | 136 | 8 | 0 | 80 | 30 | 0 | 16 | 0 | 0 | 106 | 37 | 70 | 0 | 0 | 0 | 7380 | 918 | 183 | 0 | 25 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 0 | 1146.19 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 160 | 0 | 160 | 0 | 340 | 0 | 0 | 156 | 0 | 114 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 223 | 100 | 180 | 0 | 300 | 1070 | 54 | 7167.19 | 14547.19 | 107.93
Total KWH | 129622 | 1546416 | 352027 | 0 | 0 | 0 | 0 | 0 | 8161200 | 0 | 0 | 843372 | 249480 | 2657376 | 1543680 | 3930742 | 676230 | 1053381 | 2448000 | 0 | 8108000 | 7045527 | 0 | 0 | 509735 | 7427331 | 0 | 0 | 216319 | 2473200 | 416400 | 477000 | 0 | 7653636.36 | 111655 | 0 | 1157760 | 0 | 291360 | 1287823 | 929444 | 0 | 372480 | 296640 | 22918 | 5260607 | 780300 | 356640 | 15301818.18 | 948436 | 0 | 863040 | 196491.6 | 1573199 | 4898559 | 0 | 0 | 0 | 21207270 | 48870 | 1191984 | 1408436 | 217454.54 | 0 | 8267900 | 7720000 | 954240 | 4694000 | 875520 | 2084160 | 1497650 | 4064640 | 110040 | 419010 | 2490900 | 1078080 | 996950 | 443273 | 786624 | 7545500 | 0 | 8937000 | 0 | 1435080 | 3481363.64 | 101424 | 0 | 1908480 | 713664 | 0 | 398000 | 2432430 | 203040 | 2373600 | 1207200 | 1696320 | 15700 | 398000 | 30720 | 186002368.32 | 22178181 | 4581792 | 0 | 88320 | 109696 | 912000 | 0 | 0 | 0 | 0 | 0 | 543600 | 27658180 | 1388160 | 26099273 | 0 | 253681 | 0 | 611136 | 825984 | 0 | 619696 | 186390 | 214493 | 417639 | 842254 | 160410 | 0 | 482248 | 4290545 | 0 | 4119118 | 0 | 4208444 | 0 | 8704873 | 0 | 42480 | 3759000 | 0 | 1692845 | 276413 | 1620432 | 0 | 2394630 | 0 | 55923.84 | 1646000 | 3948 | 163200 | 5869000 | 2683000 | 5225650 | 0 | 7221096 | 26218181.82 | 1114800 | 169482712.66 | 355485080.98

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14612.8 | MW | 12:00 Hr. | Energy Generated |  |  | 355.4851 |  | MKWHr.
| Day Peak Demand |  |  | 14612.8 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.187 |  | MKWHr.
| Evening Peak Generation |  |  | 16279.02 | MW | 19:30 Hr. | Energy Demand |  |  | 356.6721 |  | MKWHr.
| Evening Peak Demand |  |  | 16450.02 | MW | 19:30 Hr. | Maximum Temperature |  |  | 37 |  | °C
| Minimum Generation of the Day |  |  | 13369.71 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 977.62 |  | MMCFD
| Maximum Generation of the Day |  |  | 16279.02 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.8827 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.2891 | 0 | 18.4133 | 0 | 0 | 0.21632 | 0 | 0 | 57.9187 | Gas | 132.8447 | Gas | 476802395.1954
| Chattogram Zone |  |  | 5.2552 | 36.5091 | 8.5173 | 0 | 5.2606 | 0.071788 | 0 | 0.29136 | 55.9053 | Coal | 107.2345 | Coal | 634795916.091
| Cumilla Zone |  |  | 25.8378 | 0 | 11.9418 | 0 | 0 | 0.44327 | 1.0781 | 0 | 39.3009 | HFO | 51.7361 | HFO | 954974370.698
| Mymensingh Zone |  |  | 1.6963 | 0 | 3.8146 | 0 | 0 | 0.4137 | 0 | 0 | 5.9246 | HSD | 2.3946 | HSD | 0
| Sylhet Zone |  |  | 26.9529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9529 | Hydro | 5.2606 | Hydro | 526060.7
| Khulna Zone |  |  | 4.5818 | 27.6582 | 1.5862 | 0 | 0 | 0.5436 | 23.0902 | 0 | 57.4599 | Solar | 5.4556 | Solar | 83275757.8964
| Barishal Zone |  |  | 7.9086 | 39.3083 | 1.278 | 0 | 0 | 0.003948 | 0 | 0 | 48.4989 | Import | 50.2675 | Import | 292017264.4
| Rajshahi Zone |  |  | 21.323 | 0 | 2.8718 | 0 | 0 | 1.7846 | 26.0993 | 0 | 52.0787 | Wind | 0.29136 | Wind | 4294646.4
| Rangpur Zone |  |  | 0 | 3.759 | 3.3133 | 2.3946 | 0 | 1.9783 | 0 | 0 | 11.4452
| Total |  |  | 132.8447 | 107.2345 | 51.7361 | 2.3946 | 5.2606 | 5.4556 | 50.2675 | 0.29136 | 355.4851
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 476802395.1954 |  | Hydro | 526060.7
|  |  |  | Coal | 634795916.091 |  | Solar | 83275757.8964
|  |  |  | HFO | 954974370.698 |  | Import | 292017264.4
|  |  |  | HSD | 0 |  | Wind | 4294646.4
[5 empty] | Total: | 244,66,86,411 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1782 | Peak Hr Flow | 917.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48858400.08 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.0993 | Peak Hr Flow | 1149.82 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2214 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0781 | Peak Hr Flow | 54.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2860 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.3555 | Peak Hr Flow | 2120.82 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5652
|  |  |  | Chattogram |  | 10 |  | 1475
|  |  |  | Cumilla |  | 10 |  | 1440
|  |  |  | Mymensingh |  | 100 |  | 1229
|  |  |  | Sylhet |  | 34 |  | 631
|  |  |  | Khulna |  | 0 |  | 1971
|  |  |  | Barishal |  | 0 |  | 422
|  |  |  | Rajshahi |  | 0 |  | 1719
|  |  |  | Rangpur |  | 0 |  | 1144
|  |  |  | Total |  | 164 |  | 15683
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:00 | Siddhirganj 132/33kV S/S T-2 HT is restored.
|  | 08:01 | Siddhirganj 132/33kV S/S T-2 LT is restored.
| 08:55 | 09:39 | Mymensingh-Netrokona 132kV Ckt-2 Tripped from Netrakona 132/33kV end showing Unknown
relays Due to None
| 09:51 | 20:40 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Shutdown is taken from Baharampur end
| 10:20 |  | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Red Hot | [7 empty] | 15.0MW load
|  |  | Maintenance And Conductor Change of CT to GCB Y Phase | [7 empty] | interrup.
Chowmuhani 132/33kV
end
| 10:33 | 13:00 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Scheduled S/D Due to Shutdown Taken by EGCB For
Relay testing.
| 10:41 | 11:49 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to Oil sample collection.
| 10:42 | 11:45 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Oil sample collection.
| 11:10 | 17:16 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to 33kv source DS & 33kv
load DS hot spot maintenance
| 11:12 | 17:15 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to 33kv source DS & load DS
hot spot maintenance
| 11:42 |  | S/D-Saidpur 150 MW power station.
| 11:52 | 12:51 | Amnura 132/33kV S/S T-2 (416T) LT Scheduled S/D Due to Oil sample collection.
| 11:54 | 12:47 | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Oil sample collection.
| 12:00 |  | Day Peak Generation 14610 MW
| 12:04 | 14:15 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to High Temperature in DS joint
all phase and CB joint.
| 12:38 | 14:07 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Tripped showing Same relays Due to Same | [7 empty] | 15.0MW load
|  |  | as HT | [7 empty] | interrup.
| 12:46 | 18:46 | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Shutdown
has been taken to restore Fatullah & Shitalakkya ckt to it's previous condition. and from
Shitalakhya 132/33kV end Due to Feeder transfer to hasnabad now new fattullah
| 12:46 | 19:24 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Shutdown has been
taken to restore Fatullah & Shitalakkya ckt to it's previous condition.
| 13:38 | 14:06 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Tripped showing Lockut Relay relays Due | [7 empty] | 15.0MW load
|  |  | to WTI fluse Trip | [7 empty] | interrup.
| 13:40 |  | Syn-Saidpur 150 MW power station.
| 14:36 | 14:55 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to CB joint point High Temperature
|  | 15:50 | BIPTC S/S 20DF12 is restored.
| 22:52 | 23:15 | Bajitpur 132/33kV S/S Tr-1(404T) LT Tripped showing RET650 relays Due to 33kv bangalgao | [7 empty] | 50.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 23:05 | 23:52 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red Hot Remove | [7 empty] | 16.0MW load
interrup.
| 23:07 | 23:52 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to red hot remove | [7 empty] | 16.0MW load
interrup.
| 01:36 | 02:42 | Sirajganj 132/33kV S/S T3-(435) LT Tripped showing 51/50 over current. relays Due to PBS | [7 empty] | 5.0MW load
|  |  | 33 kv feeder (Pipulbaria) loop disconnect from bus. | [7 empty] | interrup.
| 01:36 | 02:42 | Sirajganj 132/33kV S/S T4-(445) LT Tripped showing 67 o/c trip relays Due to PBS 33 kv | [7 empty] | 5.0MW load
|  |  | feeder (Pipulbaria) loop disconnect from bus. | [7 empty] | interrup.
| 01:36 | 02:35 | Sirajganj 132/33kV S/S T4-(445) HT Tripped showing no relays Due to PBS 33 kv feeder | [7 empty] | 5.0MW load
|  |  | (Pipulbaria) loop disconnect from bus. | [7 empty] | interrup.
| 02:15 | 04:01 | Chapai 132/33kV S/S T-4 (435T) LT Tripped showing 50/51. 50/51N relays. | [7 empty] | 8.0MW load
interrup.
| 02:15 | 06:28 | Chapai 132/33kV S/S T-2 (415T) HT Tripped showing Differential trip, Distance Trip R
Phase relays.
| 02:15 | 06:29 | Chapai 132/33kV S/S T-2 (415T) LT Tripped showing Doc/DEF R- Phase relays.
| 03:25 | 03:33 | Saidpur 132/33kV S/S TR-5 (434T) LT Tripped showing Protection relay + Backup Protection | [7 empty] | 36.0MW load
|  |  | relay relays Due to 33 kv Niamotpur-02 feeder fault (O/C + E/F). | [7 empty] | interrup.
| 06:10 |  | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to Maintenance Work | [7 empty] | 45.0MW load
interrup.
| 06:11 |  | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to Maintenance work | [7 empty] | 45.0MW load
interrup.
| 06:40 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to 33kv busbar-1 maintenance work | [7 empty] | 25.0MW load
interrup.
| 06:40 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to 33kv busbar-1 maintenance work | [7 empty] | 25.0MW load
interrup.
| 06:40 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to 33kv D/S Maintenance. Shutdown
Taken By Pdb
| 06:40 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to 33kv D/S Maintenance
| 06:41 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to 33kv D/S Maintenance
| 06:41 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D Due to 33kv busbar-1 maintenance work | [7 empty] | 25.0MW load
interrup.
| 06:42 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Shutdown Taken By Pdb
| 07:00 |  | Minimum Generation: 12046 MW.
| 07:00 |  | Minimum Generation is 12046 MW
| 07:06 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kV T-1 Transformer R phase
DS Red Hot Maintenance.
| 07:06 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to Red hot maintenance | [7 empty] | 50.0MW load
interrup.
| 07:19 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to To Remove red hot problem. | [7 empty] | 30.0MW load
interrup.
| 07:20 |  | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to To Remove red hot. | [7 empty] | 30.0MW load
interrup.
| 07:40 |  | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to Emergency 33 kv loop conductor | [7 empty] | 10.0MW load
|  |  | Maintenance at pipulbaria 33kV Feeder DS Raiser cable. | [7 empty] | interrup.
| 07:40 |  | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to Emergency 33 kv loop conductor | [7 empty] | 10.0MW load
|  |  | Maintenance at pipulbaria 33kV Feeder DS Raiser cable. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 319 | 8161200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8108000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 302 | 7045527 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 676230 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7427331 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 60 | 129622 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 843372 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 104 | 1543680 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1053381 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 509735 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 416400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 477000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 352027 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 297 | 3930742 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2657376 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1546416 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 141 | 2448000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 216319 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 249480 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7653636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2473200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2847 | 57918674.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 196491.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 48870 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 863040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5260607 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 212 | 4898559 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 1573199 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 929444 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 57 | 1287823 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 372480 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 356640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 1157760 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22918 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 100 | 780300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 296640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 111655 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 110 | 948436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 980 | 21207270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 60 | 291360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 630 | 15301818.18 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2733 | 55905310.78
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 191 | 4694000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 337 | 8267900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7720000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 875520 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 954240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217454.54 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1191984 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 88 | 1408436 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 786624 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1497650 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 4064640 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1078080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 996950 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 419010 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2490900 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 110040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 2084160 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 443273 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1661 | 39300861.54
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 70 | 1696320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 38 | 1207200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 2373600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 398000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 30720 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 203040 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 259 | 5924580
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1435080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 135 | 3481363.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 713664 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1908480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 2432430 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 398000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 101424 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7545500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8937000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1008 | 26952941.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 917 | 22178181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 88320 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 12 | 109696 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 192 | 4581792 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 1388160 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 543600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1222 | 27658180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2402 | 57459929
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 300 | 7221096 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 163200 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2683000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 26218181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5225650 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 136 | 1114800 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 5869000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3948 | -
Barishal Area Total |  |  |  |  | 2236 | 2292 | 48498875.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 417639 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 253681 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 186390 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 202 | 4290545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4119118 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 185 | 4208444 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8704873 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 160410 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 214493 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 619696 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 825984 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 108 | 611136 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 42480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1149.82 | 26099273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 482248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 842254 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2533.02 | 52078664
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 164 | 2394630 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3759000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1620432 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55923.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1692845 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 276413 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1646000 | -
Rangpur Area Total |  |  |  |  | 950 | 544 | 11445243.84
Eastern Grid Total |  |  |  |  | 17385.715 | 8508 | 186002368.32
Western Grid Total |  |  |  |  | 10444.16 | 7771.02 | 169482712.66
National Grid Total |  |  |  |  | 27829.875 | 16279.02 | 355485080.98
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-09-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10263.76 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5256.7 | MW
i) Dhaka area |  |  | 5642.2 |  | MW | i) Khulna area |  |  |  | 1971.4 | MW
ii) Chattogram area |  |  | 1465.2 |  | MW | ii) Barishal area |  |  |  | 421.9 | MW
iii) Cumilla area |  |  | 1430.36 |  | MW | iii) Rajshahi area |  |  |  | 1719.4 | MW
iv) Mymensingh area |  |  | 1129 |  | MW | iv) Rangpur area |  |  |  | 1144 | MW
v) Sylhet area |  |  | 597 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15520.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 86 | 13:00 | 133 | PHP | 9 | 13:00
2 | AKSML | 126 | 02:00 | 68 | Ishurdi | 91 | 19:00 | 134 | Pabna | 142 | 19:30
3 | Aftabnagar | 46 | 18:30 | 69 | Jaldhaka | 98 | 19:30 | 135 | Palashbari | 138 | 19:30
4 | Agargaon | 150 | 16:00 | 70 | Jamalpur | 128 | 07:00 | 136 | Panchagarh | 70 | 22:00
5 | Agrabad | 106 | 18:00 | 71 | Jashore | 160 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 31 | 22:00 | 72 | Jhenaidah | 145 | 19:00 | 138 | Patuakhali | 72.5 | 19:00
7 | Ashuganj | 85 | 01:00 | 73 | Joydebpur | 163 | 15:00 | 139 | Payra | 34 | 00:00
8 | BSRM | 195 | 05:00 | 74 | Joypurhat | 73 | 23:00 | 140 | Postogola | 62 | 23:00
9 | Bagerhat | 86 | 19:00 | 75 | Juldah | 16.5 | 00:00 | 141 | Purbachal | 26 | 22:00
10 | Bajitpur | 100 | 21:00 | 76 | KSRM | 25 | 07:00 | 142 | Purbasadipur | 139 | 19:30
11 | Bakulia | 106 | 18:30 | 77 | Kabirpur | 226 | 21:00 | 143 | Rahanpur | 45 | 22:00
12 | Banani | 56.8 | 13:00 | 78 | Kachua | 102 | 21:00 | 144 | Rahim | 46 | 15:00
13 | Bangabhaban | 26 | 11:00 | 79 | Kallyanpur | 114 | 21:00 | 145 | Rajbari | 94 | 22:00
14 | Barapukuria | 78 | 22:00 | 80 | Kalurghat | 42 | 15:00 | 146 | Rajendrapur | 139 | 19:00
15 | Barguna | 24 | 20:00 | 81 | Kamrangirchar | 77 | 18:30 | 147 | Rajshahi | 124 | 22:00
16 | Barishal | 119 | 19:30 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 114 | 21:00
17 | Barishal-230 | 96 | 00:00 | 83 | Kasba | 42 | 20:00 | 149 | Ramganj | 112 | 01:00
18 | Baroaulia | 69 | 16:00 | 84 | Kazla | 108 | 16:00 | 150 | Rampur | 45 | 18:30
19 | Baroirhat | 69 | 18:30 | 85 | Keranigonj | 89 | 19:00 | 151 | Rangamati | 19 | 19:00
20 | Bashundhara | 229 | 15:00 | 86 | Khagrachori | 38 | 18:30 | 152 | Rangpur | 160 | 21:00
21 | BashundharaCement | 2 | 12:00 | 87 | Khulna | 76 | 20:00 | 153 | Ruppur | 8.4 | 11:00
22 | Beanibazar | 80 | 00:00 | 88 | Khulshi | 173 | 00:00 | 154 | SSM | 6 | 23:00
23 | Benapole | 71 | 21:00 | 89 | Kishoreganj | 136 | 00:00 | 155 | Saidpur | 117 | 19:00
24 | Bhaluka | 150 | 18:00 | 90 | Kodda | 297 | 21:00 | 156 | Satkhira | 140 | 19:00
25 | Bhandaria | 54 | 20:00 | 91 | Kulaura | 53 | 00:00 | 157 | Satmasjid | 109 | 16:00
26 | Bhangura | 44 | 21:00 | 92 | Kurigram | 74 | 19:30 | 158 | Savar | 245 | 15:00
27 | Bheramara(GK) | 78 | 22:00 | 93 | Kushtia | 173 | 19:30 | 159 | SevenRings | 5.4 | 04:00
28 | Bhulta | 209 | 21:00 | 94 | Laksam | 40 | 19:00 | 160 | ShahCement | 31 | 12:00
29 | Bog-Sherpur | 86 | 23:00 | 95 | Lakshmipur | 33 | 04:00 | 161 | Shahjadpur | 99 | 19:30
30 | Bogura | 187 | 21:00 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 144 | 19:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 74 | 19:00 | 163 | Shahmirpur | 64 | 18:00
32 | Brahmanbaria | 152 | 20:00 | 98 | MI_Cement | 10.8 | 00:00 | 164 | Shariatpur | 98 | 22:00
33 | Cantonment | 162 | 15:00 | 99 | Madanganj | 32 | 00:00 | 165 | Sherpur | 154 | 00:00
34 | Chandina | 19.4 | 22:00 | 100 | Madaripur | 133 | 21:00 | 166 | Shikalbaha | 25 | 15:00
35 | Chandpur | 88 | 00:00 | 101 | Madartek | 110 | 22:00 | 167 | Shitalakhya | 78.1 | 16:00
36 | Chandraghona | 38 | 19:00 | 102 | Madunaghat | 63 | 18:30 | 168 | Sholosohor | 52 | 15:00
37 | Chapai | 78 | 23:00 | 103 | Magura | 76 | 19:30 | 169 | Shyampur | 160 | 03:00
38 | Charsaidpur | 42 | 00:00 | 104 | Mahasthangarh | 90 | 23:00 | 170 | Siddhirganj | 125 | 18:30
39 | Chauddagram | 82 | 22:00 | 105 | Maijdee | 15 | 01:00 | 171 | Sirajganj | 134 | 20:00
40 | Chhatak | 41 | 00:00 | 106 | Manikganj | 139 | 19:30 | 172 | Sonargaon | 132 | 18:30
41 | Chowmuhani | 180 | 01:00 | 107 | Maniknagar | 59 | 13:00 | 173 | Sreemongol | 88 | 00:00
42 | Chuadanga | 136 | 22:00 | 108 | Matarbari | 52 | 00:00 | 174 | Sreepur | 109 | 19:30
43 | Coxsbazar | 131 | 06:00 | 109 | Matuail | 75 | 16:00 | 175 | Srinagar | 53.57 | 21:00
44 | Cumilla(N) | 155 | 21:00 | 110 | Millgate | 140 | 15:00 | 176 | Sunamganj | 64 | 00:00
45 | Cumilla(S) | 167 | 20:00 | 111 | Mirpur | 137 | 18:30 | 177 | Sylhet | 61 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 15:00 | 178 | Sylhet-132 | 126 | 13:00
47 | Daudkandi | 156 | 21:00 | 113 | Mirzapur | 50 | 17:00 | 179 | TK | 45 | 18:30
48 | Dhaka | 104 | 13:00 | 114 | Mithapukur | 84 | 19:00 | 180 | Tangail | 184 | 20:00
49 | Dhamrai | 136 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 26 | 19:30
50 | Dhanmondi | 152 | 13:00 | 116 | Mogbazar | 125.8 | 17:00 | 182 | Thakurgaon | 122 | 21:00
51 | Dohazari | 115 | 19:00 | 117 | Mongla | 44 | 12:00 | 183 | Tongi | 117 | 15:00
52 | Faridpur | 198 | 22:00 | 118 | Motijheel | 51 | 18:30 | 184 | Ullahpara | 46 | 19:00
53 | Fatullah | 110 | 16:00 | 119 | Muktagacha | 38 | 00:00 | 185 | Ullon | 69 | 22:00
54 | Fenchuganj | 49 | 00:00 | 120 | Munshiganj | 122 | 00:00 | 186 | Uttara | 96 | 16:00
55 | Feni | 122 | 00:00 | 121 | Muradnagar | 46 | 22:00 | 187 | UttaraNew | 72 | 21:00
56 | GPH | 83 | 23:00 | 122 | Mymensingh | 226 | 23:00 | 188 | Zigatola | 80 | 18:30
57 | Ghatail | 88 | 00:00 | 123 | Naogaon | 157 | 22:00
58 | Ghorashal | 14 | 16:00 | 124 | Narail | 66 | 19:00
59 | Ghorashal-230 | 97 | 19:00 | 125 | Narinda | 80 | 13:00
60 | Goalpara | 42 | 19:30 | 126 | Narshingdi | 196 | 21:00
61 | Gollamari | 104 | 19:30 | 127 | Natore | 169 | 22:00
62 | Gopalganj | 119.7 | 19:00 | 128 | Nawabganj | 65.2 | 21:00
63 | Gulshan | 144 | 15:00 | 129 | Netrakona | 142 | 00:00
64 | Halishahar | 79.5 | 15:00 | 130 | New | 78.2 | 16:00
65 | HaripurSBU | 159 | 17:00 | 131 | Niamatpur | 86 | 22:00
66 | Hasnabad | 97 | 22:00 | 132 | Noapara | 50 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15692.06 | 42 |  | 15735.95
1:00 | 15194.63 | 25 |  | 15220.63
2:00 | 14734.09 | 21 |  | 14756.09
3:00 | 14366.94 | 0 |  | 14366.94
4:00 | 13883.01 | 0 |  | 13883.01
5:00 | 13782.98 | 0 |  | 13782.98
6:00 | 13386.55 | 0 |  | 13386.55
7:00 | 13502.72 | 0 |  | 13502.72
8:00 | 13369.71 | 0 |  | 13369.71
9:00 | 13434.4 | 0 |  | 13434.4
10:00 | 13767.91 | 0 |  | 13767.91
11:00 | 14031.93 | 0 |  | 14031.93
12:00 | 14612.8 | 0 |  | 14612.8
13:00 | 14968.69 | 0 |  | 14968.69
14:00 | 15076.67 | 0 |  | 15076.67
15:00 | 15103.33 | 50 |  | 15155.33
16:00 | 15125.45 | 67 |  | 15195.45
17:00 | 14650.25 | 71 |  | 14724.25
18:00 | 14136.55 | 33 |  | 14170.55
19:00 | 15747.98 | 194 |  | 15950.98
19:30 | 16279.02 | 164 |  | 16450.02
20:00 | 16137.71 | 156 |  | 16300.71
21:00 | 16106.8 | 176 |  | 16290.8
22:00 | 15556.38 | 196 |  | 15761.38
23:00 | 14547.19 | 156 |  | 14710.19
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8382.5 | 7309.56 | 15692.06 | DAILY GENERATION CURVE
00:30 | 8251 | 7192.345 | 15443.345
01:00 | 8119.5 | 7075.13 | 15194.63 | 01-09-2025
01:30 | 7959.5 | 7004.86 | 14964.36
02:00 | 7799.5 | 6934.59 | 14734.09
02:30 | 7636.25 | 6914.265 | 14550.515
03:00 | 7473 | 6893.94 | 14366.94
03:30 | 7351.1 | 6773.875 | 14124.975
04:00 | 7229.2 | 6653.81 | 13883.01
04:30 | 7169.5 | 6663.495 | 13832.995
05:00 | 7109.8 | 6673.18 | 13782.98
05:30 | 7009.685 | 6575.08 | 13584.765
06:00 | 6909.57 | 6476.98 | 13386.55
06:30 | 6957.085 | 6487.55 | 13444.635
07:00 | 7004.6 | 6498.12 | 13502.72
07:30 | 6929.795 | 6506.42 | 13436.215
08:00 | 6854.99 | 6514.72 | 13369.71
08:30 | 6866.585 | 6535.47 | 13402.055
09:00 | 6878.18 | 6556.22 | 13434.4
09:30 | 6992.85 | 6608.305 | 13601.155
10:00 | 7107.52 | 6660.39 | 13767.91
10:30 | 7129.305 | 6770.615 | 13899.92
11:00 | 7151.09 | 6880.84 | 14031.93
11:30 | 7411.695 | 6910.67 | 14322.365
12:00 | 7672.3 | 6940.5 | 14612.8
12:30 | 7828.75 | 6961.995 | 14790.745
13:00 | 7985.2 | 6983.49 | 14968.69
13:30 | 7999.295 | 7023.385 | 15022.68
14:00 | 8013.39 | 7063.28 | 15076.67
14:30 | 8026.885 | 7063.115 | 15090
15:00 | 8040.38 | 7062.95 | 15103.33
15:30 | 8027.9 | 7086.49 | 15114.39
16:00 | 8015.42 | 7110.03 | 15125.45
16:30 | 7907.445 | 6980.405 | 14887.85
17:00 | 7799.47 | 6850.78 | 14650.25
17:30 | 7744.95 | 6648.45 | 14393.4
18:00 | 7690.43 | 6446.12 | 14136.55
18:30 | 7970.965 | 6971.3 | 14942.265
19:00 | 8251.5 | 7496.48 | 15747.98
19:30 | 8508 | 7771.02 | 16279.02
20:00 | 8493.4 | 7644.31 | 16137.71
20:30 | 8476.2 | 7646.055 | 16122.255 |  | Executive Engineer
21:00 | 8459 | 7647.8 | 16106.8 |  | Network Operation Division
21:30 | 8242.6 | 7588.99 | 15831.59
22:00 | 8026.2 | 7530.18 | 15556.38
22:30 | 7703.1 | 7348.685 | 15051.785
23:00 | 7380 | 7167.19 | 14547.19

## En-Curve
QF-LDC-12
Date | 01-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3830 | 1932.5 | 915 | 38 | 48 | 1129.56 | 219 | 4456 | 0 | 720 | 2304 | 100 | 0 | 0 | 42 | DAILY ENERGY CURVE
00:30 | 3794.5 | 1915.25 | 912.5 | 38 | 48 | 1136.345 | 219 | 4437.5 | 0 | 633.5 | 2208.75 | 100 | 0 | 0 | 33.5 | 01-09-2025
01:00 | 3759 | 1898 | 910 | 38 | 48 | 1143.13 | 219 | 4419 | 0 | 547 | 2113.5 | 100 | 0 | 0 | 25
01:30 | 3741 | 1869 | 910 | 38 | 47 | 1146.36 | 219.5 | 4415 | 0 | 468 | 2010.5 | 100 | 0 | 0 | 23 | Energy Generated | 355.4851 |  | MKWHr
02:00 | 3723 | 1840 | 910 | 38 | 46 | 1149.59 | 220 | 4411 | 0 | 389 | 1907.5 | 100 | 0 | 0 | 21 | Energy not Served | 1.187 |  | MKWHr
02:30 | 3764 | 1845 | 910.5 | 38 | 46 | 1146.765 | 220 | 4426.5 | 0 | 381.5 | 1672.25 | 100 | 0 | 0 | 10.5 | Total Energy Requirement | 356.6721 |  | MKWHr
03:00 | 3805 | 1850 | 911 | 38 | 46 | 1143.94 | 220 | 4442 | 0 | 374 | 1437 | 100 | 0 | 0 | 0
03:30 | 3793.5 | 1849 | 911 | 38 | 45 | 1116.875 | 220 | 4427.5 | 0 | 359 | 1265.1 | 100 | 0 | 0 | 0
04:00 | 3782 | 1848 | 911 | 38 | 44 | 1089.81 | 220 | 4413 | 0 | 344 | 1093.2 | 100 | 0 | 0 | 0
04:30 | 3802.5 | 1850 | 910.5 | 38 | 44 | 1119.495 | 220 | 4425 | 0 | 336.5 | 987 | 100 | 0 | 0 | 0
05:00 | 3823 | 1852 | 910 | 38 | 44 | 1149.18 | 220 | 4437 | 0 | 329 | 880.8 | 100 | 0 | 0 | 0
05:30 | 3781.5 | 1847 | 910.5 | 38 | 43 | 1144.715 | 220 | 4335.5 | 4.95 | 317 | 842.1 | 100 | 0 | 0.5 | 0
06:00 | 3740 | 1842 | 911 | 38 | 42 | 1140.25 | 220 | 4234 | 9.9 | 305 | 803.4 | 100 | 0 | 1 | 0
06:30 | 3742 | 1853.5 | 911 | 38 | 41 | 1147.68 | 220.5 | 4204 | 73.855 | 315 | 796.6 | 100 | 0 | 1.5 | 0
07:00 | 3744 | 1865 | 911 | 38 | 40 | 1155.11 | 221 | 4174 | 137.81 | 325 | 789.8 | 100 | 0 | 2 | 0
07:30 | 3673.5 | 1828.75 | 914.5 | 38 | 39 | 1153.055 | 221.5 | 4140.5 | 235.66 | 307.5 | 783.25 | 100 | 0 | 1 | 0
08:00 | 3603 | 1792.5 | 918 | 38 | 38 | 1151 | 222 | 4107 | 333.51 | 290 | 776.7 | 100 | 0 | 0 | 0
08:30 | 3528.5 | 1797 | 918 | 38 | 36 | 1153 | 222 | 4110 | 433.505 | 279 | 787.05 | 100 | 0 | 0 | 0
09:00 | 3454 | 1801.5 | 918 | 38 | 34 | 1155 | 222 | 4113 | 533.5 | 268 | 797.4 | 100 | 0 | 0 | 0
09:30 | 3533 | 1822.25 | 917.5 | 38 | 35 | 1101.5 | 222 | 4149 | 587.655 | 277 | 818.25 | 100 | 0 | 0 | 0
10:00 | 3612 | 1843 | 917 | 38 | 36 | 1048 | 222 | 4185 | 641.81 | 286 | 839.1 | 100 | 0 | 0 | 0
10:30 | 3622 | 1852.9 | 917.5 | 38 | 36 | 1033 | 222 | 4274.5 | 668.57 | 286.5 | 848.95 | 100 | 0 | 0 | 0
11:00 | 3632 | 1862.8 | 918 | 38 | 36 | 1018 | 222 | 4364 | 695.33 | 287 | 858.8 | 100 | 0 | 0 | 0
11:30 | 3628 | 1849 | 918 | 38 | 40 | 1027 | 222 | 4429 | 717.815 | 305 | 1098.55 | 50 | 0 | 0 | 0
12:00 | 3624 | 1835.2 | 918 | 38 | 44 | 1036 | 222 | 4494 | 740.3 | 323 | 1338.3 | 0 | 0 | 0 | 0
12:30 | 3589.5 | 1823.1 | 917.5 | 38 | 44 | 1097.5 | 222 | 4481 | 728.445 | 347 | 1501.7 | 0 | 0 | 1 | 0
13:00 | 3555 | 1811 | 917 | 38 | 44 | 1159 | 222 | 4468 | 716.59 | 371 | 1665.1 | 0 | 0 | 2 | 0
13:30 | 3561 | 1812.5 | 917.5 | 38 | 46 | 1157.605 | 222 | 4478.5 | 679.775 | 367 | 1691.3 | 50 | 0 | 1.5 | 0
14:00 | 3567 | 1814 | 918 | 38 | 48 | 1156.21 | 222 | 4489 | 642.96 | 363 | 1717.5 | 100 | 0 | 1 | 0
14:30 | 3580.5 | 1816.5 | 917.5 | 38 | 48 | 1146.455 | 222 | 4515 | 556.445 | 368.5 | 1780.6 | 100 | 0 | 0.5 | 25
15:00 | 3594 | 1819 | 917 | 38 | 48 | 1136.7 | 222 | 4541 | 469.93 | 374 | 1843.7 | 100 | 0 | 0 | 50
15:30 | 3561 | 1817 | 917.5 | 38 | 47 | 1143.24 | 222 | 4569.5 | 383.85 | 373 | 1942.3 | 100 | 0 | 0 | 58.5
16:00 | 3528 | 1815 | 918 | 38 | 46 | 1149.78 | 222 | 4598 | 297.77 | 372 | 2040.9 | 100 | 0 | 0 | 67
16:30 | 3380.5 | 1793 | 917.5 | 38 | 45 | 1148.545 | 222 | 4547.5 | 217.505 | 371.5 | 2091.3 | 100 | 0 | 15.5 | 69
17:00 | 3233 | 1771 | 917 | 38 | 44 | 1147.31 | 222 | 4497 | 137.24 | 371 | 2141.7 | 100 | 0 | 31 | 71
17:30 | 3201 | 1758 | 917.5 | 38 | 42 | 1087.795 | 202 | 4444.5 | 78.705 | 374.5 | 2116.9 | 100 | 0 | 32.5 | 52
18:00 | 3169 | 1745 | 918 | 38 | 40 | 1028.28 | 182 | 4392 | 20.17 | 378 | 2092.1 | 100 | 0 | 34 | 33
18:30 | 3346 | 1802.5 | 918 | 38 | 34 | 1090.28 | 181.5 | 4506 | 10.085 | 522 | 2313.9 | 131.5 | 0 | 48.5 | 113.5
19:00 | 3523 | 1860 | 918 | 38 | 28 | 1152.28 | 181 | 4620 | 0 | 666 | 2535.7 | 163 | 0 | 63 | 194
19:30 | 3586 | 1924 | 917 | 38 | 54 | 1149.82 | 221 | 4758 | 0 | 693 | 2714.2 | 164 | 0 | 60 | 164
20:00 | 3530 | 1907 | 918 | 38 | 54 | 1142.11 | 221 | 4693 | 0 | 729 | 2678.6 | 164 | 0 | 63 | 156
20:30 | 3528 | 1917 | 918 | 38 | 54 | 1141.855 | 220.5 | 4678.5 | 0 | 745.5 | 2671.9 | 164 | 0 | 45 | 166
21:00 | 3526 | 1927 | 918 | 38 | 54 | 1141.6 | 220 | 4664 | 0 | 762 | 2665.2 | 164 | 0 | 27 | 176
21:30 | 3507.5 | 1880 | 918 | 38 | 54 | 1139.29 | 220 | 4599.6 | 0 | 749 | 2539.7 | 164 | 0 | 22.5 | 186
22:00 | 3489 | 1833 | 918 | 38 | 54 | 1136.98 | 220 | 4535.2 | 0 | 736 | 2414.2 | 164 | 0 | 18 | 196
22:30 | 3398 | 1805 | 918 | 38 | 52 | 1141.585 | 220 | 4497.1 | 0 | 671 | 2161.1 | 132 | 0 | 18 | 176
23:00 | 3307 | 1777 | 918 | 38 | 50 | 1146.19 | 220 | 4459 | 0 | 606 | 1908 | 100 | 0 | 18 | 156
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 366 | 11:00 | Payra | 413 | 23:00 | 407 | 11:00
Ashuganj | 401 | 06:00 | 385 | 15:00 | Rahanpur | 398 | 18:00 | 390 | 13:00
Bhulta | 396 | 01:00 | 340 | 13:00 | Rampal | 402 | 08:00 | 388 | 19:00
Bibiana | 386 | 23:00 | 375 | 15:00
BIPTC | 401 | 06:00 | 385 | 15:00
Bogura | 379 | 18:00 | 370 | 13:00
Gopalganj | 394 | 23:00 | 381 | 18:30
Kaliakoir | 380 | 07:00 | 355 | 11:00
Madunaghat | 392 | 18:00 | 386 | 11:00
Meghnaghat | 380 | 06:00 | 368 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 02:00 | 212 | 11:00 | Keranigonj | 221 | 06:00 | 210 | 11:00
AKSML | 231 | 19:00 | 221 | 11:00 | Khulna(S) | 228 | 06:00 | 216 | 19:00
Aminbazar | 223 | 01:00 | 213 | 11:00 | Madunaghat | 233 | 22:00 | 226 | 11:00
Ashuganj | 230 | 02:00 | 215 | 12:00 | Madunaghat-400 | 233 | 18:00 | 227 | 12:00
Ashuganj-400 | 230 | 02:00 | 215 | 12:00 | Maniknagar | 217 | 04:00 | 209 | 15:00
Baghabari | 232 | 05:00 | 226 | 12:00 | Meghnaghat | 228 | 06:00 | 218 | 12:00
Barapukuria | 226 | 18:00 | 217 | 13:00 | Meghnaghat-400 | 222 | 06:00 | 213 | 16:00
Barapukuria-230 | 226 | 18:00 | 217 | 13:00 | Mirsorai | 229 | 22:00 | 218 | 11:00
Barishal | 227 | 08:00 | 221 | 00:00 | Rajshahi | 229 | 06:00 | 220 | 12:00
Bheramara | 231 | 06:00 | 223 | 12:00 | Rampal | 230 | 22:00 | 217 | 19:00
Bhulta | 228 | 00:00 | 206 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 06:00 | 218 | 18:30 | Rampura | 228 | 02:00 | 202 | 11:00
BIPTC | 233 | 06:00 | 223 | 19:00 | Shikalbaha | 231 | 19:00 | 225 | 10:00
Bogura | 237 | 18:00 | 230 | 13:00 | Shyampur | 220 | 02:00 | 211 | 11:00
Bogura-400 | 236 | 09:00 | 231 | 13:00 | Siddhirganj | 220 | 22:00 | 212 | 15:00
Borhanuddin | 230 | 08:00 | 226 | 00:00 | Sirajgonj | 266 | 13:00 | 235 | 15:00
BSRM | 228 | 23:00 | 217 | 11:00 | Sreepur | 226 | 06:00 | 216 | 18:30
Cumilla(N) | 220 | 04:00 | 212 | 18:30 | Tongi | 229 | 23:00 | 213 | 15:00
Faridpur | 223 | 08:00 | 215 | 18:30
Fenchuganj | 225 | 09:00 | 220 | 18:30
Ghorashal | 230 | 10:00 | 220 | 13:00
Ghorashal-230 | 227 | 02:00 | 209 | 11:00
Gopalganj | 224 | 08:00 | 217 | 18:30
GPH | 229 | 18:00 | 222 | 11:00
Haripur | 219 | 06:00 | 211 | 11:00
Hasnabad | 221 | 02:00 | 211 | 18:30
Hathazari | 229 | 18:00 | 220 | 11:00
Ishurdi | 233 | 06:00 | 226 | 12:00
Jhenaidah | 230 | 22:00 | 215 | 19:00
Kaliakoir | 230 | 02:00 | 218 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 00:00 | 120 | 11:00 | Lalmonirhat | 129 | 18:30 | 118 | 19:00
Agargaon | 132 | 23:00 | 122 | 11:00 | Madanganj | 127 | 22:00 | 122 | 10:00
Agrabad | 131 | 22:00 | 126 | 10:00 | Madaripur | 132 | 07:00 | 128 | 00:00
AKS | 129 | 17:00 | 124 | 11:00 | Madartek | 134.5 | 02:00 | 117 | 11:00
Aminbazar | 133 | 01:00 | 125 | 11:00 | Madunaghat | 132 | 21:00 | 128 | 10:00
Amnura | 135 | 18:00 | 126 | 13:00 | Magura | 135 | 22:00 | 120 | 19:00
Ashuganj | 140 | 23:00 | 132 | 18:30 | Mahasthangarh | 130 | 09:00 | 125 | 00:00
Bagerhat | 135 | 22:00 | 118 | 00:00 | Maijdee | 119 | 18:00 | 109 | 03:00
Bajitpur | 127 | 05:00 | 116 | 18:30 | Manikganj | 131 | 23:00 | 115 | 20:00
Bakulia | 133 | 22:00 | 127 | 12:00 | Maniknagar | 132 | 05:00 | 125 | 12:00
Banani | 136 | 23:00 | 118 | 11:00 | Matarbari | 119 | 17:00 | 111 | 01:00
Bangabhaban | 132 | 02:00 | 125 | 11:00 | Matuail | 127 | 02:00 | 122 | 11:00
Barapukuria | 138 | 18:00 | 127 | 13:00 | Millgate | 133 | 01:00 | 120 | 11:00
Barguna | 137 | 00:00 | 131 | 13:00 | Mirpur | 132 | 02:00 | 123 | 10:00
Barishal | 132 | 07:00 | 128 | 00:00 | Mirzapur | 131 | 23:00 | 122 | 12:00
Barishal-230 | 133 | 08:00 | 128 | 00:00 | Mithapukur | 131 | 18:00 | 123 | 12:00
Baroaulia | 131 | 00:00 | 120 | 10:00 | MI_Cement | 129 | 22:00 | 121 | 11:00
Baroirhat | 124 | 09:00 | 118 | 01:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 135 | 01:00 | 118 | 11:00 | Mogbazar | 137 | 02:00 | 121 | 11:00
BashundharaCement | 128 | 23:00 | 121 | 11:00 | Mongla | 135 | 22:00 | 119 | 19:00
Beanibazar | 125 | 07:00 | 117 | 18:30 | Motijheel | 132 | 02:00 | 125 | 11:00
Benapole | 136 | 22:00 | 118 | 19:00 | Muktagacha | 130 | 18:00 | 124 | 06:00
Bhaluka | 128 | 05:00 | 118 | 18:30 | Munshiganj | 128 | 23:00 | 121 | 11:00
Bhandaria | 127 | 09:00 | 120 | 00:00 | Muradnagar | 123 | 06:00 | 116 | 18:30
Bhangura | 133 | 06:00 | 128 | 13:00 | Mymensingh | 131 | 17:00 | 109 | 20:00
Bheramara | 136 | 06:00 | 131 | 19:00 | Naogaon | 128 | 18:00 | 121 | 01:00
Bheramara(GK) | 136 | 06:00 | 131 | 15:00 | Narail | 136 | 22:00 | 120 | 19:00
Bhulta | 121 | 07:00 | 118 | 16:00 | Narinda | 132 | 05:00 | 125 | 12:00
Bog-Sherpur | 131 | 08:00 | 127 | 13:00 | Narshingdi | 137 | 23:00 | 117 | 11:00
Bogura | 134 | 18:30 | 128 | 13:00 | Natore | 131 | 05:00 | 127 | 00:00
Bogura-230 | 134 | 18:30 | 128 | 01:00 | Nawabganj | 132 | 04:00 | 123 | 15:00
Brahmanbaria | 132 | 07:00 | 122 | 18:30 | Netrakona | 119 | 06:00 | 108 | 18:30
Cantonment | 130 | 01:00 | 121 | 11:00 | New | 134 | 01:00 | 119 | 19:00
Chandina | 126 | 06:00 | 121 | 12:00 | Niamatpur | 135 | 10:00 | 132 | 00:00
Chandpur | 129 | 09:00 | 121 | 15:00 | Noapara | 137 | 22:00 | 122 | 19:00
Chandraghona | 132 | 21:00 | 128 | 11:00 | Pabna | 132 | 05:00 | 127 | 18:30
Chapai | 134 | 03:00 | 131 | 13:00 | Palashbari | 129 | 18:00 | 121 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 22:00 | 122 | 11:00 | Panchagarh | 139 | 16:00 | 121 | 12:00
Chauddagram | 123 | 08:00 | 117 | 12:00 | Patiya | 133 | 17:00 | 124 | 09:00
Chhatak | 125 | 06:00 | 111 | 18:30 | Patuakhali | 138 | 00:00 | 131 | 11:00
Chowmuhani | 119 | 07:00 | 107 | 15:00 | Payra | 137 | 02:00 | 133 | 11:00
Chuadanga | 131 | 09:00 | 116 | 19:00 | PHP | 123 | 09:00 | 116 | 12:00
Coxsbazar | 118 | 16:00 | 112 | 01:00 | Postogola | 133 | 02:00 | 126 | 11:00
Cumilla(N) | 126 | 05:00 | 120 | 18:30 | Purbachal | 135 | 02:00 | 117 | 11:00
Cumilla(S) | 132 | 05:00 | 119 | 15:00 | Purbasadipur | 135 | 18:00 | 120 | 12:00
Daganbhuiyan | 121 | 09:00 | 113 | 01:00 | Rahanpur | 137 | 18:00 | 133 | 01:00
Daudkandi | 121 | 05:00 | 114 | 18:30 | Rahanpur-400 | 137 | 18:00 | 134 | 00:00
Dhaka | 135 | 00:00 | 118 | 11:00 | Rahim | 128 | 23:00 | 122 | 11:00
Dhamrai | 136 | 23:00 | 120 | 11:00 | Rajbari | 130 | 06:00 | 125 | 00:00
Dhanmondi | 136 | 02:00 | 118.7 | 11:00 | Rajendrapur | 138 | 23:00 | 118 | 18:30
Dohazari | 129 | 17:00 | 123 | 12:00 | Rajshahi | 130 | 07:00 | 126 | 12:00
Faridpur | 132 | 08:00 | 127 | 00:00 | Rajshahi-230 | 131 | 07:00 | 126 | 12:00
Fatullah | 129 | 23:00 | 122 | 11:00 | Ramganj | 122 | 23:00 | 113 | 01:00
Fenchuganj | 133 | 00:00 | 127 | 18:30 | Rampur | 130 | 00:00 | 125 | 11:00
Feni | 122 | 07:00 | 116 | 14:00 | Rampura | 135 | 02:00 | 118 | 11:00
Ghatail | 128 | 23:00 | 120 | 14:00 | Rangamati | 131 | 18:00 | 128 | 11:00
Ghorashal | 136 | 04:00 | 127 | 15:00 | Rangpur | 132 | 18:00 | 124 | 13:00
Goalpara | 137 | 22:00 | 125 | 19:00 | Ruppur | 135 | 06:00 | 131 | 15:00
Gollamari | 138 | 22:00 | 126 | 19:00 | Saidpur | 136 | 18:30 | 123 | 12:00
Gopalganj | 134 | 22:00 | 125 | 19:00 | Satkhira | 134 | 22:00 | 117 | 19:00
Gopalganj-400 | 134 | 06:00 | 129 | 18:30 | Satmasjid | 133 | 23:00 | 122 | 11:00
Gulshan | 136 | 22:00 | 118 | 11:00 | Savar | 131 | 00:00 | 124 | 10:00
Halishahar | 133 | 22:00 | 126 | 10:00 | SevenRings | 138 | 23:00 | 126 | 11:00
Haripur | 128 | 22:00 | 123 | 11:00 | ShahCement | 129 | 22:00 | 122 | 11:00
HaripurSBU | 128 | 22:00 | 123 | 11:00 | Shahjadpur | 136 | 04:00 | 132 | 19:00
Hasnabad | 132 | 00:00 | 126 | 11:00 | Shahjibazar | 132 | 08:00 | 123 | 18:30
Hathazari | 132 | 16:00 | 128 | 13:00 | Shahmirpur | 133 | 22:00 | 127 | 12:00
Ishurdi | 136 | 06:00 | 131 | 19:00 | Shariatpur | 131 | 07:00 | 125 | 00:00
Jaldhaka | 134 | 18:30 | 122 | 13:00 | Sherpur | 131 | 18:00 | 118 | 01:00
Jamalpur | 134 | 17:00 | 123 | 02:00 | Shikalbaha | 122 | 18:00 | 117 | 10:00
Jashore | 138 | 22:00 | 120 | 19:00 | Shikalbaha-230 | 134 | 21:00 | 129 | 10:00
Jhenaidah | 136 | 09:00 | 117 | 19:00 | Shitalakhya | 129 | 22:00 | 121 | 11:00
Jhenaidah-230 | 136 | 22:00 | 125 | 19:30 | Sholosohor | 131 | 18:00 | 127 | 11:00
Joydebpur | 144 | 23:00 | 118 | 11:00 | Shyampur | 130 | 23:00 | 123 | 11:00
Joypurhat | 126 | 18:00 | 119 | 01:00 | Shyampur-230 | 129 | 23:00 | 122 | 11:00
Juldah | 133 | 21:00 | 127 | 12:00 | Siddhirganj | 128 | 03:00 | 123 | 11:00
Kabirpur | 139 | 23:00 | 119 | 11:00 | Sirajganj | 130 | 09:00 | 124 | 19:00
Kachua | 127 | 08:00 | 119 | 14:00 | Sonargaon | 126 | 22:00 | 120 | 11:00
Kaliakoir | 133 | 02:00 | 125 | 11:00 | Sreemongol | 130 | 07:00 | 123 | 18:30
Kallyanpur | 132 | 01:00 | 125 | 11:00 | Sreepur | 130 | 06:00 | 122 | 18:30
Kalurghat | 132 | 22:00 | 127 | 11:00 | Srinagar | 133 | 07:00 | 124 | 15:00
Kamrangirchar | 133 | 06:00 | 123 | 15:00 | SSM | 134 | 00:00 | 130 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 121 | 08:00 | 111 | 18:30
Kasba | 122 | 07:00 | 115 | 18:30 | Sylhet | 126 | 00:00 | 119 | 18:00
Kazla | 131 | 01:00 | 124 | 16:00 | Sylhet-132 | 127 | 06:00 | 118 | 16:00
Keranigonj | 133 | 06:00 | 124 | 11:00 | Tangail | 127 | 23:00 | 119 | 13:00
Khagrachori | 130 | 21:00 | 126 | 11:00 | Taraganj | 133 | 18:30 | 124 | 12:00
Khulna | 137 | 22:00 | 125 | 19:00 | Thakurgaon | 138 | 18:30 | 119 | 12:00
Khulna(S) | 137 | 22:00 | 126 | 19:00 | TK | 132 | 17:00 | 128 | 11:00
Khulshi | 130 | 18:00 | 125 | 10:00 | Tongi | 135 | 23:00 | 124 | 15:00
Kishoreganj | 126 | 07:00 | 114 | 18:30 | Ullahpara | 132 | 04:00 | 127 | 19:00
Kodda | 137 | 23:00 | 121 | 11:00 | Ullon | 136 | 00:00 | 118 | 11:00
KSRM | 132 | 18:00 | 127 | 11:00 | Uttara | 132 | 02:00 | 122 | 16:00
Kulaura | 132 | 06:00 | 126 | 18:30 | UttaraNew | 132 | 01:00 | 122 | 11:00
Kurigram | 128 | 18:00 | 118 | 19:00 | Zigatola | 132 | 07:00 | 124 | 12:00
Kushtia | 132 | 04:00 | 124 | 19:00
Laksam | 126 | 08:00 | 118 | 15:00
Lakshmipur | 120 | 18:00 | 110 | 03:00
Lalbag | 131 | 02:00 | 123 | 18:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division