## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-09-2025 | during | 05-09-2025 | during | 05-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 344 | 329 | 0 | 0 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 293 | 272 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 332 | 335 | 335 | 333 | 333 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 64 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 44.5 | 44 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 47 | 123 | 133 | 133 | 117 | 117 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 22 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 23 | 23 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 296 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 146 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 85 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 153 | 140 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 36 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 27 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 320 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 52 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2479.5 | 2867 | 5408.79 | 5377.79 | 3285.7 | 3327.7
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 44 | 50 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 77 | 48 | 78 | 40 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 46 | 66 | 0 | 0 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 27 | 35 | 42 | 35 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.37 | 0 | 1.42 | 0 | 1.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 15 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 15 | 75 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1132 | 987 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 15 | 0 | 13 | 3 | 13 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 484 | 480 | 255 | 255 | 635 | 635 | machine problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2306.37 | 2305 | 3140.14 | 3151.72 | 3355.28 | 3379.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 180 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 349 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 35 | 46.7 | 46.7 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 38 | 40 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 63 | 195 | 195 | 200 | 200 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 80 | 126 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 34 | 34 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 105 | 198 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 50 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 34 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 55 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 75 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1551 | 1697 | 2440.86 | 2370.86 | 2143.66 | 2073.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-09-2025 | during | 05-09-2025 | during | 05-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 50 | 50 | 157.5 | 157.5 | 72 | 72 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 37 | 47 | 40 | 40 | 40 | 40 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 102 | 108 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.84 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 219.84 | 222 | 435 | 383 | 302 | 250
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 70 | 70 | 70 | 70 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 137 | 150 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 84 | 84 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 0 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 350 | 350 | 350 | 357 | 357 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1079 | 1082 | 1133 | 1133 | 1119 | 1119
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 926 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 226 | 186 | 410 | 410 | 226 | 226 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1073 | 1110 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2336 | 2290 | 3266.2 | 3216.2 | 2887.2 | 2837.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 302 | 301 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1200 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 190 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 138 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 198 | 261 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.83 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1800.83 | 2235 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 58.35 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 180 | 197 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 187 | 189 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 325 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 26 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 0 | 0 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.82 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1364.59 | 1446.38 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.98 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 63 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2115.74 | 2736.38 | 3078.52 | 2921.87 | 3100.14 | 2943.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 100 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 182 | 170 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 102 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 175.55 | 0 | 175.55 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 520 | 552 | 624.15 | 412 | 624.15 | 412
System Total |  |  |  |  | 28823.2 | 27829.875 | 14408.28 | 15986.38 | 21688.66 | 21127.44 | 18899.13 | 18423.91
Forecast Scenario (05-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15750 |  | 0 |  | 15750
|  |  |  | 1:00 | 15390 |  | 0 |  | 15390
|  |  |  | 2:00 | 14930 |  | 0 |  | 14930
|  |  |  | 3:00 | 14460 |  | 0 |  | 14460
|  |  |  | 4:00 | 14180 |  | 0 |  | 14180
|  |  |  | 5:00 | 13960 |  | 0 |  | 13960
|  |  |  | 6:00 | 13150 |  | 0 |  | 13150
|  |  |  | 7:00 | 12700 |  | 0 |  | 12700
|  |  |  | 8:00 | 12430 |  | 0 |  | 12430
|  |  |  | 9:00 | 12150 |  | 0 |  | 12150
|  |  |  | 10:00 | 12060 |  | 0 |  | 12060
|  |  |  | 11:00 | 12220 |  | 0 |  | 12220
|  |  |  | 12:00 | 12820 |  | 0 |  | 12820
|  |  |  | 13:00 | 13450 |  | 0 |  | 13450
|  |  |  | 14:00 | 12880 |  | 0 |  | 12880
|  |  |  | 15:00 | 12870 |  | 0 |  | 12870
|  |  |  | 16:00 | 12110 |  | 0 |  | 12110
|  |  |  | 17:00 | 11760 |  | 0 |  | 11760
|  |  |  | 18:00 | 11770 |  | 0 |  | 11770
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14120 |  | 0 |  | 14120
|  |  |  | 19:30 | 14570 |  | 0 |  | 14570
|  |  |  | 20:00 | 14630 |  | 0 |  | 14630
|  |  |  | 21:00 | 14740 |  | 0 |  | 14740
|  |  |  | 22:00 | 14830 |  | 0 |  | 14830
|  |  |  | 23:00 | 14990 |  | 0 |  | 14990
Probable Maximum Temperature: |  |  | 33.20°C
Probable Maximum Demand at Day Peak: |  |  | 12820.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14740.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14740.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.35 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 07:47 hrs on 05-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-09-2025 | [28 empty] | Date: | 04-09-2025 | [28 empty] | Date: | 04-09-2025 | [28 empty] | Date: | 04-09-2025 | [28 empty] | Date: | 04-09-2025 | [14 empty] | Date: | 04-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 48.5 | 17 | 149 | 60 | 294 | 55 | 55 | 154 | 0 | 300 | 297 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 52 | 21.2 | 21 | 0 | 347 | 0 | 0 | 0 | 0 | 25 | 66 | 68 | 0 | 12 | 12 | 0 | 219 | 33 | 37 | 485 | 138 | 0 | 33 | 17 | 49 | 221 | 0 | 0 | 0 | 1092 | 0 | 51 | 120 | 8 | 0 | 351 | 330 | 20 | 195 | 34 | 72 | 90 | 181 | 0 | 19 | 34 | 54 | 43 | 0 | 35 | 315 | 0 | 316 | 0 | 60 | 156 | 8 | 0 | 82 | 30 | 0 | 0 | 101 | 17 | 101 | 48 | 50 | 0 | 0 | 0 | 8142.7 | 914 | 144 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1236 | 0 | 1286 | 0 | 39 | 0 | 113 | 113 | 0 | 97 | 37 | 52 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0 | 145 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 305 | 115 | 220 | 0 | 301 | 1212 | 154 | 7603 | 15745.7 | 107.88
01:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 45.6 | 0 | 149 | 47 | 195 | 30 | 55 | 143 | 0 | 300 | 298 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 52 | 21.2 | 21 | 0 | 348 | 0 | 0 | 0 | 0 | 16 | 66 | 52 | 0 | 12 | 12 | 0 | 218 | 25 | 37 | 485 | 46 | 0 | 19 | 17 | 17 | 221 | 0 | 0 | 0 | 1100 | 0 | 51 | 122 | 8 | 0 | 352 | 330 | 20 | 198 | 34 | 73 | 90 | 178 | 0 | 19 | 34 | 52 | 43 | 0 | 35 | 310 | 0 | 331 | 0 | 60 | 154 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 17 | 102 | 38 | 50 | 0 | 0 | 0 | 7756.8 | 916 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 1458 | 0 | 39 | 0 | 50 | 70 | 0 | 97 | 37 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0 | 148 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 266 | 115 | 220 | 0 | 301 | 1120 | 155 | 7385 | 15141.8 | 107.87
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 47 | 0 | 149 | 47 | 95 | 30 | 55 | 150 | 0 | 300 | 299 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 52 | 22 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 15 | 66 | 52 | 0 | 12 | 12 | 0 | 218 | 30 | 37 | 485 | 15 | 0 | 19 | 8 | 15 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 80 | 8 | 0 | 352 | 330 | 20 | 197 | 34 | 73 | 90 | 163 | 0 | 19 | 34 | 50 | 43 | 0 | 35 | 315 | 0 | 331 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 17 | 102 | 38 | 50 | 0 | 0 | 0 | 7552 | 916 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1154 | 0 | 1454 | 0 | 39 | 0 | 35 | 35 | 0 | 97 | 37 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 133 | 0 | 0 | 149 | 0 | 115 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 266 | 115 | 220 | 0 | 301 | 1096 | 100 | 7060 | 14612 | 107.87
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 47.8 | 0 | 130 | 47 | 15 | 0 | 42 | 108 | 0 | 300 | 303 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 52 | 18.5 | 21 | 0 | 365 | 0 | 0 | 0 | 0 | 17 | 66 | 30 | 0 | 12 | 12 | 0 | 219 | 0 | 37 | 485 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 80 | 8 | 0 | 351 | 330 | 20 | 200 | 34 | 72 | 90 | 162 | 0 | 19 | 34 | 48 | 43 | 0 | 36 | 315 | 0 | 336 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 102 | 38 | 50 | 0 | 0 | 0 | 7145.3 | 917 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1161 | 0 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 146 | 0 | 192 | 0 | 188 | 0 | 0 | 0 | 0 | 149 | 0 | 115 | 0 | 85 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 301 | 1090 | 17 | 6750 | 13895.3 | 107.87
04:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 33 | 0 | 95 | 47 | 0 | 0 | 17 | 72 | 0 | 300 | 299 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 52 | 18.5 | 21 | 0 | 366 | 0 | 0 | 0 | 0 | 17 | 66 | 7 | 0 | 12 | 12 | 0 | 219 | 0 | 37 | 485 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 355 | 330 | 30 | 198 | 34 | 73 | 91 | 162 | 0 | 19 | 34 | 48 | 43 | 0 | 36 | 315 | 0 | 334 | 0 | 60 | 160 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 102 | 38 | 50 | 0 | 0 | 0 | 6909.5 | 917 | 175 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 0 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 193 | 0 | 192 | 0 | 0 | 0 | 0 | 150 | 0 | 50 | 0 | 49 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 301 | 1092 | 0 | 6672 | 13581.5 | 107.87
05:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 16.2 | 0 | 95 | 47 | 0 | 0 | 17 | 68 | 0 | 300 | 298 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 18.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 24 | 66 | 7 | 0 | 12 | 12 | 0 | 220 | 0 | 38 | 485 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 985 | 0 | 51 | 0 | 8 | 0 | 354 | 330 | 44 | 194 | 34 | 72 | 91 | 162 | 0 | 19 | 34 | 46 | 43 | 0 | 36 | 320 | 0 | 323 | 0 | 60 | 158 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 102 | 38 | 50 | 0 | 0 | 0 | 6840.7 | 917 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1143 | 0 | 1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 193 | 0 | 196 | 0 | 0 | 0 | 0 | 150 | 0 | 50 | 0 | 49 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 266 | 115 | 220 | 0 | 301 | 1094 | 0 | 6680 | 13520.7 | 107.87
06:00 | 0 | 34 | 2 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 83 | 47 | 0 | 0 | 17 | 17 | 0 | 300 | 295 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 18.7 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 66 | 7 | 0 | 12 | 12 | 0.06 | 220 | 0 | 39 | 485 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 990 | 1 | 51 | 0 | 8 | 0 | 356 | 330 | 45 | 195 | 34 | 73 | 91 | 162 | 0 | 19 | 34 | 44 | 0 | 3 | 37 | 300 | 0 | 329 | 0 | 60 | 151 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 102 | 38 | 50 | 0 | 0.65 | 0 | 6638.41 | 916 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.28 | 1088 | 0 | 1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 1 | 0 | 0 | 0.75 | 205 | 0 | 195 | 0 | 198 | 0 | 0 | 0 | 0.06 | 148 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0.02 | 0 | 222 | 115 | 220 | 0 | 301 | 1000 | 0 | 6405.59 | 13044 | 107.87
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 60 | 47 | 0 | 0 | 17 | 0 | 0 | 300 | 302 | 0 | 0 | 0 | 300 | 0 | 0 | 9 | 0 | 18.7 | 21 | 0 | 335 | 0 | 0 | 0 | 0 | 8 | 33 | 7 | 0 | 12 | 12 | 0.27 | 220 | 0 | 39 | 485 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 6 | 51 | 0 | 8 | 0 | 351 | 330 | 45 | 201 | 34 | 72 | 90 | 161 | 0 | 19 | 34 | 42 | 0 | 18 | 36 | 310 | 0 | 333 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 102 | 38 | 50 | 0 | 9.52 | 0 | 6640.49 | 916 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.1 | 1018 | 0 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.35 | 13 | 0 | 0 | 17.26 | 205 | 0 | 198 | 0 | 201 | 0 | 0 | 0 | 0.99 | 150 | 0 | 0 | 3 | 0 | 0 | 100 | 0 | 1.5 | 20 | 0.11 | 0 | 170 | 115 | 220 | 0 | 301 | 1000 | 0 | 6380.31 | 13020.8 | 107.87
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 60 | 47 | 0 | 0 | 17 | 0 | 0 | 300 | 301 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 52 | 22 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 3 | 33 | 7 | 0 | 12 | 12 | 0.96 | 221 | 0 | 10 | 482 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1003 | 11 | 51 | 0 | 8 | 0 | 300 | 290 | 45 | 196 | 34 | 73 | 90 | 162 | 0 | 19 | 34 | 38 | 0 | 39 | 36 | 305 | 0 | 357 | 0 | 60 | 150 | 8 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 103 | 38 | 50 | 0 | 25.93 | 0 | 6579.89 | 916 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54.13 | 988 | 0 | 1455.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.97 | 30 | 0 | 0 | 11.84 | 205 | 0 | 203 | 0 | 202 | 0 | 0 | 0 | 1.51 | 147 | 0 | 0 | 8 | 0 | 0 | 100 | 0 | 3.5 | 44 | 0.15 | 0 | 171 | 115 | 180 | 0 | 302 | 997 | 0 | 6397.98 | 12977.87 | 107.87
09:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 64 | 47 | 0 | 0 | 26 | 15 | 0 | 300 | 299 | 0 | 0 | 0 | 300 | 0 | 0 | 23 | 52 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 9 | 33 | 8 | 0 | 12 | 12 | 2.81 | 221 | 0 | 3 | 488 | 0 | 0 | 2 | 0 | 0 | 218 | 0 | 0 | 0 | 1040 | 7 | 51 | 0 | 8 | 0 | 345 | 280 | 43 | 198 | 32 | 72 | 90 | 160 | 0 | 19 | 34 | 38 | 0 | 56 | 36 | 315 | 0 | 356 | 0 | 60 | 144 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 112 | 38 | 50 | 1 | 41.29 | 0 | 6740.1 | 917 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65.57 | 997 | 0 | 1379.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.64 | 86 | 0 | 0 | 45.05 | 170 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 4.51 | 150 | 0 | 0 | 17 | 0 | 0 | 100 | 0 | 4.2 | 110 | 0.71 | 0 | 170 | 115 | 180 | 0 | 302 | 1010 | 0 | 6459.49 | 13199.59 | 107.87
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 83 | 47 | 0 | 0 | 35 | 46 | 0 | 300 | 298 | 0 | 0 | 5 | 300 | 0 | 0 | 30 | 52 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 33 | 7 | 0 | 12 | 12 | 4.4 | 220 | 0 | 2 | 488 | 0 | 0 | 18 | 0 | 0 | 215 | 0 | 0 | 0 | 1100 | 11 | 43 | 1 | 8 | 0 | 343 | 330 | 43 | 198 | 32 | 73 | 90 | 150 | 0 | 12 | 34 | 38 | 0 | 68 | 36 | 315 | 0 | 360 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 112 | 38 | 50 | 2 | 43.08 | 1 | 6966.48 | 916 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1027 | 0 | 1324.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.17 | 88 | 0 | 0 | 53.96 | 170 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 5.68 | 149 | 0 | 0 | 35 | 0 | 0 | 100 | 0 | 6.8 | 170 | 0.23 | 0 | 172 | 115 | 220 | 0 | 302 | 1000 | 0 | 6526.23 | 13492.71 | 107.86
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35.8 | 15 | 91 | 47 | 145 | 20 | 48 | 140 | 0 | 300 | 289 | 0 | 0 | 50 | 270 | 0 | 0 | 32 | 52 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 33 | 10 | 0 | 12 | 12 | 3.37 | 220 | 4 | 2 | 484 | 14 | 0 | 27 | 0 | 19 | 216 | 0 | 0 | 0 | 1120 | 16 | 43 | 35 | 8 | 0 | 322 | 330 | 40 | 209 | 33 | 73 | 90 | 111 | 0 | 12 | 34 | 42 | 0 | 74 | 34 | 310 | 0 | 333 | 0 | 60 | 153 | 0 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 102 | 37 | 50 | 2 | 42.37 | 12 | 7328.54 | 916 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1059 | 0 | 1364.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.76 | 58 | 0 | 0 | 46.28 | 180 | 0 | 190 | 0 | 198 | 0 | 0 | 0 | 1.23 | 183 | 0 | 0 | 36 | 0 | 0 | 100 | 0 | 7.5 | 131 | 0.82 | 0 | 190 | 100 | 190 | 0 | 302 | 990 | 0 | 6614.97 | 13943.51 | 107.86
12:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 44.5 | 27 | 146 | 47 | 145 | 55 | 55 | 153 | 0 | 320 | 293 | 0 | 0 | 55 | 300 | 0 | 0 | 36 | 52 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 46 | 38 | 0 | 12 | 12 | 4.37 | 219 | 14 | 2 | 484 | 15 | 0 | 34 | 1 | 44 | 215 | 0 | 0 | 0 | 1132 | 19 | 43 | 80 | 8 | 0 | 340 | 330 | 38 | 208 | 33 | 72 | 90 | 105 | 0 | 17 | 34 | 44 | 0 | 75 | 34 | 305 | 0 | 357 | 0 | 60 | 137 | 10 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 102 | 37 | 50 | 2 | 16.84 | 12 | 7635.71 | 917 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 1073 | 0 | 1364.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.35 | 63 | 0 | 0 | 59.98 | 180 | 0 | 187 | 0 | 197 | 0 | 0 | 0 | 5.82 | 182 | 0 | 0 | 30 | 0 | 0 | 100 | 0 | 8 | 200 | 0.83 | 0 | 198 | 100 | 190 | 0 | 302 | 1010 | 0 | 6772.57 | 14408.28 | 107.86
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 46.7 | 0 | 148 | 46 | 195 | 55 | 55 | 149 | 0 | 320 | 295 | 0 | 0 | 55 | 300 | 0 | 0 | 34 | 52 | 20 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 26 | 64 | 45 | 0 | 12 | 12 | 4.17 | 218 | 14 | 12 | 484 | 15 | 0 | 50 | 10 | 46 | 213 | 0 | 0 | 0 | 1129 | 16 | 43 | 80 | 8 | 0 | 336 | 330 | 40 | 207 | 33 | 71 | 90 | 104 | 0 | 17 | 34 | 46 | 0 | 73 | 34 | 310 | 0 | 359 | 0 | 60 | 144 | 10 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 102 | 37 | 44 | 1 | 52.55 | 12 | 7804.42 | 919 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1094 | 0 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.41 | 101 | 0 | 0 | 31.7 | 180 | 0 | 187 | 0 | 160 | 0 | 96 | 0 | 4.24 | 182 | 0 | 0 | 16 | 0 | 0 | 100 | 0 | 7.4 | 163 | 0.95 | 0 | 199 | 115 | 190 | 0 | 302 | 1080 | 0 | 6866.7 | 14671.12 | 107.86
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 46 | 18 | 149 | 46 | 230 | 55 | 55 | 146 | 0 | 320 | 286 | 0 | 0 | 55 | 270 | 0 | 0 | 4 | 52 | 21 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 35 | 64 | 50 | 0 | 12 | 12 | 4.67 | 218 | 15 | 6 | 487 | 16 | 0 | 50 | 17 | 45 | 216 | 0 | 0 | 0 | 1070 | 14 | 43 | 80 | 41 | 0 | 310 | 295 | 41 | 200 | 33 | 72 | 90 | 103 | 0 | 19 | 34 | 48 | 0 | 43 | 34 | 310 | 0 | 360 | 0 | 60 | 146 | 10 | 0 | 79 | 30 | 0 | 0 | 100 | 10 | 100 | 37 | 44 | 1 | 28.46 | 12 | 7668.13 | 918 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1042 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.58 | 112 | 0 | 0 | 51.9 | 170 | 0 | 172 | 0 | 160 | 0 | 270 | 0 | 5.55 | 184 | 0 | 0 | 33 | 0 | 0 | 100 | 0 | 7 | 135 | 0.73 | 0 | 200 | 100 | 220 | 0 | 300 | 1050 | 0 | 6936.76 | 14604.89 | 107.86
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 48.8 | 35 | 149 | 46 | 230 | 55 | 55 | 156 | 0 | 320 | 295 | 0 | 0 | 35 | 322 | 0 | 0 | 7 | 52 | 21 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 39 | 64 | 50 | 0 | 12 | 12 | 1.56 | 218 | 15 | 2 | 482 | 65 | 0 | 50 | 17 | 51 | 214 | 0 | 0 | 0 | 1050 | 7 | 43 | 92 | 76 | 0 | 339 | 330 | 41 | 197 | 28 | 75 | 90 | 104 | 0 | 19 | 34 | 50 | 0 | 53 | 34 | 315 | 0 | 330 | 0 | 60 | 153 | 14 | 0 | 79 | 30 | 0 | 0 | 100 | 17 | 100 | 37 | 48 | 1 | 38.46 | 12 | 7937.82 | 930 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65 | 1052 | 0 | 1117.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.44 | 39 | 0 | 0 | 24.12 | 151 | 0 | 155 | 0 | 150 | 0 | 414 | 0 | 4.87 | 147 | 0 | 0 | 31 | 0 | 0 | 100 | 0 | 5.5 | 133 | 0.7 | 0 | 247 | 100 | 220 | 0 | 301 | 1070 | 0 | 6723.26 | 14661.08 | 107.85
16:00 | 7 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 46.4 | 35 | 149 | 46 | 296 | 55 | 55 | 148 | 0 | 320 | 292 | 0 | 0 | 35 | 328 | 0 | 0 | 6 | 52 | 20.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 52 | 65 | 50 | 0 | 12 | 12 | 0.43 | 219 | 15 | 2 | 475 | 62 | 0 | 50 | 17 | 63 | 217 | 0 | 0 | 0 | 1035 | 10 | 51 | 100 | 83 | 0 | 337 | 330 | 38 | 195 | 33 | 79 | 90 | 104 | 0 | 19 | 34 | 48 | 0 | 35 | 34 | 310 | 0 | 320 | 0 | 60 | 148 | 14 | 0 | 79 | 30 | 0 | 0 | 100 | 17 | 101 | 47 | 49 | 1 | 23.71 | 0 | 7965.04 | 926 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 1120 | 0 | 1117.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.87 | 6 | 0 | 0 | 25.22 | 202 | 0 | 170 | 0 | 170 | 0 | 350 | 0 | 3.31 | 149 | 0 | 0 | 21 | 0 | 0 | 100 | 0 | 2.2 | 30 | 0.36 | 0 | 245 | 100 | 220 | 0 | 301 | 1120 | 0 | 6688.79 | 14653.83 | 107.85
17:00 | 7 | 66 | 25 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 45.6 | 35 | 149 | 46 | 296 | 55 | 55 | 146 | 0 | 300 | 298 | 0 | 0 | 35 | 325 | 0 | 0 | 6 | 52 | 20.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 31 | 65 | 58 | 0 | 25 | 12 | 0 | 220 | 15 | 16 | 480 | 30 | 0 | 50 | 17 | 62 | 216 | 0 | 0 | 0 | 1050 | 5 | 51 | 108 | 81 | 0 | 336 | 320 | 27 | 199 | 33 | 81 | 90 | 105 | 0 | 13 | 34 | 46 | 0 | 15 | 34 | 310 | 0 | 325 | 0 | 60 | 139 | 14 | 0 | 22 | 30 | 0 | 0 | 100 | 17 | 100 | 47 | 48 | 0 | 9.4 | 8 | 7846.5 | 926 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1051 | 0 | 1007.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.51 | 6 | 0 | 0 | 0 | 205 | 0 | 150 | 0 | 150 | 0 | 367 | 0 | 0 | 175 | 0 | 0 | 6 | 0 | 0 | 100 | 0 | 2 | 37 | 0.89 | 0 | 199 | 100 | 220 | 0 | 301 | 1060 | 0 | 6337.27 | 14183.77 | 107.85
18:00 | 7 | 66 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 44.2 | 17 | 149 | 46 | 296 | 55 | 55 | 142 | 0 | 300 | 305 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 142 | 20.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 65 | 77 | 0 | 25 | 12 | 0.1 | 221 | 14 | 10 | 478 | 30 | 0 | 50 | 17 | 59 | 188 | 0 | 0 | 0 | 1020 | 0 | 51 | 113 | 81 | 0 | 300 | 300 | 10 | 180 | 35 | 85 | 90 | 147 | 0 | 19 | 34 | 44 | 0 | 1 | 34 | 310 | 0 | 335 | 0 | 60 | 131 | 14 | 0 | 23 | 30 | 0 | 0 | 100 | 17 | 100 | 47 | 48 | 0 | 0.37 | 12 | 7657.17 | 927 | 197 | 0 | 12 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1017 | 0 | 1012.78 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0.35 | 0 | 12 | 0 | 0 | 170 | 0 | 150 | 0 | 150 | 0 | 310 | 0 | 0.01 | 175 | 0 | 35 | 0 | 32 | 0 | 100 | 0 | 0.2 | 6 | 0 | 0 | 185 | 100 | 180 | 0 | 301 | 1030 | 0 | 6161.34 | 13818.51 | 107.84
19:00 | 7 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 46.4 | 17 | 149 | 123 | 296 | 55 | 55 | 148 | 0 | 350 | 284 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 5 | 66 | 77 | 0 | 25 | 12 | 0 | 222 | 15 | 25 | 480 | 93 | 0 | 33 | 17 | 63 | 216 | 0 | 0 | 0 | 1030 | 0 | 51 | 122 | 76 | 0 | 344 | 330 | 19 | 189 | 35 | 77 | 90 | 198 | 0 | 19 | 34 | 52 | 21 | 0 | 34 | 305 | 0 | 350 | 0 | 60 | 146 | 0 | 0 | 78 | 30 | 0 | 0 | 100 | 17 | 101 | 47 | 50 | 0 | 0 | 12 | 8264.4 | 926 | 190 | 0 | 34 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 1345.28 | 0 | 48 | 0 | 100 | 55 | 0 | 93 | 20 | 9 | 0 | 0 | 28 | 0 | 0 | 186 | 0 | 188 | 0 | 166 | 0 | 396 | 0 | 0 | 168 | 0 | 95 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 12 | 270 | 115 | 220 | 0 | 301 | 1105 | 123 | 7611.28 | 15875.68 | 107.84
19:30 | 64 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 44 | 17 | 149 | 123 | 296 | 55 | 55 | 140 | 0 | 320 | 272 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 77 | 0 | 25 | 12 | 0 | 222 | 15 | 27 | 480 | 75 | 0 | 33 | 17 | 50 | 219 | 0 | 0 | 0 | 987 | 0 | 51 | 126 | 63 | 0 | 349 | 330 | 40 | 180 | 35 | 55 | 90 | 198 | 0 | 19 | 34 | 50 | 43 | 0 | 34 | 295 | 0 | 350 | 0 | 60 | 150 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 108 | 47 | 50 | 0 | 0 | 0 | 8173 | 926 | 186 | 0 | 30 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1446.38 | 0 | 47 | 0 | 108 | 100 | 0 | 50 | 30 | 26 | 0 | 0 | 28 | 0 | 0 | 197 | 0 | 189 | 0 | 190 | 0 | 325 | 0 | 0 | 170 | 0 | 115 | 0 | 102 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 261 | 115 | 220 | 0 | 301 | 1200 | 138 | 7813.38 | 15986.38
20:00 | 64 | 84 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 43.1 | 17 | 149 | 122 | 245 | 15 | 55 | 140 | 0 | 320 | 287 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 22.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 2 | 66 | 77 | 0 | 25 | 12 | 0 | 222 | 14 | 29 | 480 | 0 | 0 | 33 | 17 | 49 | 220 | 0 | 0 | 0 | 1040 | 0 | 51 | 127 | 16 | 0 | 345 | 330 | 42 | 193 | 35 | 57 | 90 | 198 | 0 | 19 | 34 | 52 | 43 | 0 | 34 | 300 | 0 | 370 | 0 | 58 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 111 | 47 | 50 | 0 | 0 | 0 | 8015.6 | 927 | 184 | 0 | 31 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 1461.51 | 0 | 47 | 0 | 35 | 35 | 0 | 50 | 31 | 8 | 0 | 0 | 28 | 0 | 0 | 197 | 0 | 189 | 0 | 190 | 0 | 342 | 0 | 0 | 167 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 274 | 115 | 220 | 0 | 301 | 1205 | 138 | 7754.51 | 15770.11 | 107.83
21:00 | 7 | 84 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 44.9 | 17 | 149 | 122 | 245 | 0 | 55 | 142 | 0 | 320 | 285 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 7 | 66 | 77 | 0 | 25 | 12 | 0 | 222 | 15 | 26 | 485 | 0 | 0 | 33 | 0 | 46 | 220 | 0 | 0 | 0 | 1022 | 0 | 51 | 128 | 16 | 0 | 348 | 330 | 43 | 190 | 37 | 74 | 90 | 198 | 0 | 19 | 34 | 50 | 43 | 0 | 34 | 305 | 0 | 365 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 7 | 102 | 47 | 50 | 0 | 0 | 0 | 8015.9 | 926 | 177 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 1446.35 | 0 | 47 | 0 | 35 | 35 | 0 | 50 | 32 | 0 | 0 | 0 | 28 | 0 | 0 | 193 | 0 | 189 | 0 | 190 | 0 | 396 | 0 | 0 | 167 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 5 | 271 | 115 | 220 | 0 | 300 | 1212 | 155 | 7807.35 | 15823.25 | 107.83
22:00 | 7 | 84 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 44.2 | 17 | 149 | 122 | 245 | 0 | 55 | 139 | 0 | 320 | 287 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 66 | 70 | 0 | 25 | 12 | 0 | 222 | 17 | 32 | 455 | 0 | 0 | 33 | 14 | 44 | 219 | 0 | 0 | 0 | 1040 | 0 | 51 | 132 | 0 | 0 | 348 | 330 | 43 | 191 | 37 | 74 | 90 | 198 | 0 | 19 | 34 | 54 | 8 | 0 | 34 | 305 | 0 | 375 | 0 | 58 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 101 | 47 | 50 | 0 | 0 | 0 | 7954.2 | 925 | 167 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 1450.71 | 0 | 47 | 0 | 35 | 35 | 0 | 50 | 32 | 0 | 0 | 0 | 28 | 0 | 0 | 191 | 0 | 185 | 0 | 189 | 0 | 401 | 0 | 0 | 170 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 300 | 1225 | 155 | 7794.71 | 15748.91 | 107.82
23:00 | 7 | 84 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 45.2 | 17 | 149 | 45 | 245 | 0 | 55 | 145 | 0 | 320 | 296 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 14 | 66 | 70 | 0 | 25 | 12 | 0 | 220 | 16 | 35 | 455 | 0 | 0 | 33 | 17 | 46 | 219 | 0 | 0 | 0 | 1044 | 0 | 51 | 133 | 0 | 0 | 346 | 330 | 44 | 200 | 37 | 76 | 90 | 199 | 0 | 19 | 34 | 56 | 8 | 0 | 35 | 310 | 0 | 365 | 0 | 60 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 102 | 47 | 50 | 0 | 0 | 0 | 7873.2 | 926 | 157 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 0 | 1449.01 | 0 | 47 | 0 | 35 | 35 | 0 | 50 | 32 | 0 | 0 | 0 | 28 | 0 | 0 | 188 | 0 | 184 | 0 | 186 | 0 | 414 | 0 | 0 | 170 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 280 | 115 | 220 | 0 | 300 | 1226 | 150 | 7743.01 | 15616.21 | 107.82
Total KWH | 138672 | 1306560 | 492000 | 0 | 0 | 0 | 0 | 0 | 8726400 | 0 | 0 | 849240 | 301320 | 3025296 | 1448640 | 3722487 | 604507 | 1081967 | 2730240 | 0 | 7701000 | 7141876 | 0 | 0 | 813499 | 7294558 | 0 | 0 | 213201 | 1590000 | 476400 | 512280 | 0 | 8147272.73 | 0 | 0 | 0 | 0 | 434880 | 1368027 | 1007206 | 0 | 375360 | 290880 | 24238 | 5305136 | 318650 | 512160 | 11600000 | 486764 | 0 | 654240 | 231174 | 787018 | 5163007 | 0 | 0 | 0 | 25210906 | 121500 | 1180816 | 1861745 | 602182 | 0 | 8498400 | 7834000 | 867840 | 4829000 | 825984 | 1801920 | 2103470 | 3703680 | 0 | 427450 | 839040 | 1116480 | 354931 | 562245 | 835872 | 7528500 | 0 | 8675000 | 0 | 1391400 | 3609327 | 210072 | 0 | 1841280 | 716736 | 0 | 80000 | 2403080 | 210240 | 2421600 | 998400 | 1129920 | 12500 | 307310 | 100320 | 182089301.73 | 22261090 | 4668768 | 0 | 173280 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 528480 | 26232730 | 0 | 32640000 | 0 | 377131 | 0 | 422400 | 499200 | 0 | 504800 | 223520 | 42840 | 345044 | 591080 | 242080 | 0 | 335248 | 4531000 | 0 | 4493327 | 0 | 4493682 | 0 | 4553163 | 0 | 30660 | 3950000 | 0 | 1180155 | 235530 | 1085952 | 0 | 2637810 | 0 | 51716.16 | 1240560 | 4204.5 | 51552 | 5586000 | 2663000 | 5281810 | 0 | 7229090.91 | 26669090.91 | 1112400 | 168080394.48 | 350169696.21

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14408.28 | MW | 12:00 Hr. | Energy Generated |  |  | 350.1697 |  | MKWHr.
| Day Peak Demand |  |  | 14444.86 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3 |  | MKWHr.
| Evening Peak Generation |  |  | 15986.38 | MW | 19:30 Hr. | Energy Demand |  |  | 353.1697 |  | MKWHr.
| Evening Peak Demand |  |  | 16140.38 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.9 |  | °C
| Minimum Generation of the Day |  |  | 12977.87 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 976.55 |  | MMCFD
| Maximum Generation of the Day |  |  | 15986.38 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.5516 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.9998 | 0 | 18.1044 | 0 | 0 | 0.2132 | 0 | 0 | 58.3174 | Gas | 131.1142 | Gas | 469583049.0341
| Chattogram Zone |  |  | 5.6752 | 36.8109 | 5.5193 | 0 | 5.3051 | 0.14574 | 0 | 0.43488 | 53.8911 | Coal | 106.4778 | Coal | 632809282.0087
| Cumilla Zone |  |  | 27.1691 | 0 | 9.3972 | 0 | 0 | 0.56224 | 1.1165 | 0 | 38.2451 | HFO | 42.6668 | HFO | 779889488.34
| Mymensingh Zone |  |  | 1.1299 | 0 | 3.7306 | 0 | 0 | 0.31981 | 0 | 0 | 5.1803 | HSD | 2.6378 | HSD | 0
| Sylhet Zone |  |  | 26.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.4554 | Hydro | 5.3051 | Hydro | 530513.6
| Khulna Zone |  |  | 4.6688 | 26.2327 | 0.17328 | 0 | 0 | 0.52848 | 23.1731 | 0 | 54.7763 | Solar | 4.6035 | Solar | 69466222.6986
| Barishal Zone |  |  | 7.9448 | 39.4842 | 1.164 | 0 | 0 | 0.0042045 | 0 | 0 | 48.5971 | Import | 56.9296 | Import | 335473529.1
| Rajshahi Zone |  |  | 18.0712 | 0 | 2.312 | 0 | 0 | 1.302 | 32.64 | 0 | 54.3252 | Wind | 0.43488 | Wind | 6410131.2
| Rangpur Zone |  |  | 0 | 3.95 | 2.2661 | 2.6378 | 0 | 1.5278 | 0 | 0 | 10.3817
| Total |  |  | 131.1142 | 106.4778 | 42.6668 | 2.6378 | 5.3051 | 4.6035 | 56.9296 | 0.43488 | 350.1697
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 469583049.0341 |  | Hydro | 530513.6
|  |  |  | Coal | 632809282.0087 |  | Solar | 69466222.6986
|  |  |  | HFO | 779889488.34 |  | Import | 335473529.1
|  |  |  | HSD | 0 |  | Wind | 6410131.2
[5 empty] | Total: | 229,41,62,215 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2611 | Peak Hr Flow | 926.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51850000.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.64 | Peak Hr Flow | 1446.38 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2604 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1165 | Peak Hr Flow | 50.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2798 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.0176 | Peak Hr Flow | 2422.38 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 25 |  | 5642
|  |  |  | Chattogram |  | 0 |  | 1452
|  |  |  | Cumilla |  | 0 |  | 1382
|  |  |  | Mymensingh |  | 122 |  | 1253
|  |  |  | Sylhet |  | 0 |  | 695
|  |  |  | Khulna |  | 0 |  | 1815
|  |  |  | Barishal |  | 0 |  | 463
|  |  |  | Rajshahi |  | 0 |  | 1526
|  |  |  | Rangpur |  | 0 |  | 1112
|  |  |  | Total |  | 147 |  | 15340
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:29 | Mirpur 132/33kV S/S T2 HT is restored.
| 08:59 | 20:06 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown has been taken from Baharampur end.
|  | 09:01 | Feni 132/33kV S/S Bus-2 is restored.
|  | 09:16 | Goalpara 132/33kV S/S T1 HT is restored.
|  | 09:16 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 09:16 | Goalpara 132/33kV S/S T-5 HT is restored.
|  | 09:18 | Goalpara 132/33kV S/S T1 LT is restored.
|  | 09:18 | Goalpara 132/33kV S/S T-5 LT is restored.
|  | 09:18 | Goalpara 132/33kV S/S T-6 LT is restored.
|  | 09:21 | Sirajgonj 230 S/S SNWPCL (Unit-04) is restored.
| 09:24 | 10:58 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Satkhira 132/33kV end. and from
Khulna(S) 230/132kVend.
| 09:33 | 17:40 | Patiya 132/33kV S/S TRAFO-02 LT Project Work S/D Due to Blast wall painting work.
| 09:33 | 17:38 | Patiya 132/33kV S/S TRAFO-02 HT Project Work S/D Due to Blast wall painting work.
| 11:15 | 13:24 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end. and from
Khulna(S) 230/132kVend.
| 12:00 |  | Day peak Generation is 14403 MW
| 12:01 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 12:15 | 19:24 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to Project Work
| 12:15 | 13:02 | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to WZPDCL-1 ,B-Phase Bus Loop Red | [7 empty] | 8.0MW load
|  |  | Hot Maintenance. | [7 empty] | interrup.
| 12:16 | 13:01 | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to WZPDCL-1 ,B-Phase Bus Loop Red | [7 empty] | 8.0MW load
|  |  | Hot Maintenance. | [7 empty] | interrup.
| 13:19 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 14:53 | 18:30 | Bogura 230/132kV S/S Bogura (W) CKT-1 Project Work S/D Due to Dfdr Integration
| 15:01 | 15:48 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Scheduled S/D Due to Partial Discharge
monitor checking
| 15:23 | 17:53 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Forced S/D
| 15:23 | 17:54 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Forced S/D | [7 empty] | 32.0MW load
interrup.
| 15:23 | 17:56 | Satkhira 132/33kV S/S TR-03 HT Forced S/D
| 15:23 | 17:56 | Satkhira 132/33kV S/S TR-03 HT Forced S/D
| 15:23 | 17:56 | Satkhira 132/33kV S/S TR-03 LT Forced S/D Due to ashasuni 33kv feeder bus side Y phase | [7 empty] | 13.0MW load
|  |  | red hot maintenance work. | [7 empty] | interrup.
| 19:30 |  | Evening Peak Generation: 15986 MW.
|  | 21:48 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 is restored.
| 22:28 | 23:33 | Chauddagram 132/33kV S/S 132 kv T-2 LT Forced S/D Due to Red hot at Lalbag feeder of PBS | [7 empty] | 38.0MW load
|  |  | end under bus-02. | [7 empty] | interrup.
| 23:46 |  | Shahjibazar-Sreemangal 132kV Ckt-2 Project Work S/D from Sreemongol 132/33kV end Due to
RHD Project Works.
| 23:46 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end Due to
RHD Project Works
| 01:29 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
| 01:55 |  | Ashuganj North CCPP was shutdown at due to compressor offline washing
| 01:55 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 04:20 |  | Matarbari 2*600 MW (CPGCBL) Unit-2 was forced shutdown due to boiler slagging problem.
| 06:20 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to RED HOT MAINTENANCE WORK
| 06:20 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to RED HOT MAINTENANCE WORK
| 06:23 | 07:41 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to project work
| 06:23 | 07:41 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Project work
| 06:47 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Scheduled S/D Due to 33kV bus loop change. | [7 empty] | 15.0MW load
interrup.
| 06:48 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Scheduled S/D Due to 33kV bus loop change. | [7 empty] | 15.0MW load
interrup.
| 07:00 |  | Minimum Generation: 12547 MW.
| 07:26 |  | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to High Temperature Maintenance.
| 07:26 |  | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to High Temperature Maintenance.
| 07:45 |  | Meghnaghat 230/132kV S/S Bus1 Project Work S/D Due to Aminbazar line Dismantling and
re-installation work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 329 | 8726400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7701000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 272 | 7141876 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 604507 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7294558 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 138672 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 849240 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 1448640 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1081967 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 813499 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 476400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 512280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 492000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 296 | 3722487 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3025296 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 85 | 1306560 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 2730240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 213201 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 301320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 8147272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1590000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2867 | 58317415.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 231174 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121500 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 654240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5305136 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5163007 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 50 | 787018 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 77 | 1007206 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1368027 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 375360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 512160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 318650 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 290880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 75 | 486764 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 987 | 25210906 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 434880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 480 | 11600000 | machine problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2305 | 53891146
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 180 | 4829000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 349 | 8498400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7834000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 825984 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 867840 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 602182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1180816 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 126 | 1861745 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 835872 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2103470 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 198 | 3703680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 50 | 1116480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 354931 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 427450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 839040 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 55 | 1801920 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 562245 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1697 | 38245055
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 50 | 1129920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 998400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2421600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 307310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 100320 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 210240 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 222 | 5180290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1391400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3609327 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716736 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1841280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403080 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 80000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 210072 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7528500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8675000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1082 | 26455395
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 926 | 22261090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 173280 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 186 | 4668768 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 528480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1110 | 26232730 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2290 | 54776348
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7229090.91 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 51552 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2663000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 26669090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5281810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 138 | 1112400 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 261 | 5586000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4204.5 | -
Barishal Area Total |  |  |  |  | 2236 | 2235 | 48597148.32
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 345044 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 377131 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 223520 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 197 | 4531000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4493327 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4493682 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 325 | 4553163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 242080 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 26 | 42840 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 504800 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 499200 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 108 | 422400 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446.38 | 32640000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 335248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 591080 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2736.38 | 54325175
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 165 | 2637810 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3950000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 1085952 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51716.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1180155 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 235530 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1240560 | -
Rangpur Area Total |  |  |  |  | 950 | 552 | 10381723.16
Eastern Grid Total |  |  |  |  | 17385.715 | 8173 | 182089301.73
Western Grid Total |  |  |  |  | 10444.16 | 7813.38 | 168080394.48
National Grid Total |  |  |  |  | 27829.875 | 15986.38 | 350169696.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-09-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10276.45 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4916.4 | MW
i) Dhaka area |  |  | 5616.57 |  | MW | i) Khulna area |  |  |  | 1815 | MW
ii) Chattogram area |  |  | 1452 |  | MW | ii) Barishal area |  |  |  | 463 | MW
iii) Cumilla area |  |  | 1381.88 |  | MW | iii) Rajshahi area |  |  |  | 1526.4 | MW
iv) Mymensingh area |  |  | 1131 |  | MW | iv) Rangpur area |  |  |  | 1112 | MW
v) Sylhet area |  |  | 695 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15192.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 18:30 | 133 | PHP | 9 | 08:00
2 | AKSML | 145 | 03:00 | 68 | Ishurdi | 81 | 19:00 | 134 | Pabna | 130 | 19:00
3 | Aftabnagar | 42 | 00:00 | 69 | Jaldhaka | 94 | 22:00 | 135 | Palashbari | 134 | 19:30
4 | Agargaon | 143 | 13:00 | 70 | Jamalpur | 120 | 22:00 | 136 | Panchagarh | 66 | 19:30
5 | Agrabad | 104 | 13:00 | 71 | Jashore | 143 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 22:00 | 72 | Jhenaidah | 138 | 19:00 | 138 | Patuakhali | 71.5 | 21:00
7 | Ashuganj | 90 | 00:00 | 73 | Joydebpur | 155 | 19:30 | 139 | Payra | 36 | 22:00
8 | BSRM | 141 | 20:00 | 74 | Joypurhat | 67 | 00:00 | 140 | Postogola | 59 | 00:00
9 | Bagerhat | 83 | 20:00 | 75 | Juldah | 17 | 00:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 99 | 21:00 | 76 | KSRM | 38 | 18:00 | 142 | Purbasadipur | 132 | 19:00
11 | Bakulia | 99 | 16:00 | 77 | Kabirpur | 256 | 16:00 | 143 | Rahanpur | 40 | 00:00
12 | Banani | 54 | 13:00 | 78 | Kachua | 104 | 21:00 | 144 | Rahim | 41 | 14:00
13 | Bangabhaban | 25 | 11:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 86 | 19:00
14 | Barapukuria | 74 | 19:30 | 80 | Kalurghat | 40 | 10:00 | 146 | Rajendrapur | 139 | 23:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 82 | 13:00 | 147 | Rajshahi | 110 | 00:00
16 | Barishal | 116 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 102 | 13:00
17 | Barishal-230 | 94 | 22:00 | 83 | Kasba | 38 | 20:00 | 149 | Ramganj | 100 | 00:00
18 | Baroaulia | 62 | 00:00 | 84 | Kazla | 121 | 17:00 | 150 | Rampur | 44 | 23:00
19 | Baroirhat | 67 | 23:00 | 85 | Keranigonj | 87 | 19:00 | 151 | Rangamati | 18 | 18:30
20 | Bashundhara | 218 | 13:00 | 86 | Khagrachori | 34 | 18:30 | 152 | Rangpur | 159 | 19:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulna | 71 | 09:00 | 153 | Ruppur | 8.8 | 16:00
22 | Beanibazar | 86 | 21:00 | 88 | Khulshi | 191 | 15:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 62 | 19:00 | 89 | Kishoreganj | 130 | 20:00 | 155 | Saidpur | 111 | 19:00
24 | Bhaluka | 155 | 18:30 | 90 | Kodda | 304 | 18:30 | 156 | Satkhira | 128 | 19:00
25 | Bhandaria | 55 | 23:00 | 91 | Kulaura | 60 | 19:30 | 157 | Satmasjid | 109 | 19:00
26 | Bhangura | 38 | 19:00 | 92 | Kurigram | 76 | 19:00 | 158 | Savar | 255 | 16:00
27 | Bheramara(GK) | 69 | 22:00 | 93 | Kushtia | 158 | 19:00 | 159 | SevenRings | 15.85 | 19:00
28 | Bhulta | 220 | 00:00 | 94 | Laksam | 37 | 23:00 | 160 | ShahCement | 39 | 19:00
29 | Bog-Sherpur | 78 | 00:00 | 95 | Lakshmipur | 33 | 19:30 | 161 | Shahjadpur | 88 | 22:00
30 | Bogura | 171 | 23:00 | 96 | Lalbag | 63 | 14:00 | 162 | Shahjibazar | 145 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 70 | 19:00 | 163 | Shahmirpur | 66 | 00:00
32 | Brahmanbaria | 144 | 21:00 | 98 | MI_Cement | 16 | 23:00 | 164 | Shariatpur | 93 | 22:00
33 | Cantonment | 156 | 13:00 | 99 | Madanganj | 33 | 13:00 | 165 | Sherpur | 146 | 19:00
34 | Chandina | 18.52 | 21:00 | 100 | Madaripur | 120 | 22:00 | 166 | Shikalbaha | 14 | 01:00
35 | Chandpur | 84 | 23:00 | 101 | Madartek | 90 | 00:00 | 167 | Shitalakhya | 82.4 | 16:00
36 | Chandraghona | 36 | 18:30 | 102 | Madunaghat | 56 | 00:00 | 168 | Sholosohor | 50 | 15:00
37 | Chapai | 70 | 00:00 | 103 | Magura | 69 | 19:00 | 169 | Shyampur | 168 | 12:00
38 | Charsaidpur | 40 | 20:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 124 | 15:00
39 | Chauddagram | 75 | 00:00 | 105 | Maijdee | 16 | 13:00 | 171 | Sirajganj | 111 | 21:00
40 | Chhatak | 43 | 00:00 | 106 | Manikganj | 131 | 23:00 | 172 | Sonargaon | 136 | 23:00
41 | Chowmuhani | 197 | 22:00 | 107 | Maniknagar | 66 | 12:00 | 173 | Sreemongol | 93 | 00:00
42 | Chuadanga | 117 | 22:00 | 108 | Matarbari | 52 | 19:30 | 174 | Sreepur | 108 | 16:00
43 | Coxsbazar | 133 | 13:00 | 109 | Matuail | 74 | 00:00 | 175 | Srinagar | 50.7 | 22:00
44 | Cumilla(N) | 151 | 00:00 | 110 | Millgate | 139 | 12:00 | 176 | Sunamganj | 62 | 18:30
45 | Cumilla(S) | 154 | 15:00 | 111 | Mirpur | 134 | 15:00 | 177 | Sylhet | 55 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 151 | 18:30
47 | Daudkandi | 155 | 18:30 | 113 | Mirzapur | 40 | 15:00 | 179 | TK | 37 | 21:00
48 | Dhaka | 100 | 13:00 | 114 | Mithapukur | 79 | 19:00 | 180 | Tangail | 164 | 19:00
49 | Dhamrai | 134 | 23:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 00:00
50 | Dhanmondi | 150 | 13:00 | 116 | Mogbazar | 120.1 | 15:00 | 182 | Thakurgaon | 116 | 19:30
51 | Dohazari | 112 | 19:00 | 117 | Mongla | 35 | 19:00 | 183 | Tongi | 112 | 18:30
52 | Faridpur | 174 | 23:00 | 118 | Motijheel | 47 | 13:00 | 184 | Ullahpara | 41 | 19:00
53 | Fatullah | 105 | 15:00 | 119 | Muktagacha | 42 | 19:00 | 185 | Ullon | 61 | 00:00
54 | Fenchuganj | 49 | 18:30 | 120 | Munshiganj | 119 | 00:00 | 186 | Uttara | 103 | 13:00
55 | Feni | 126 | 18:30 | 121 | Muradnagar | 45 | 21:00 | 187 | UttaraNew | 67 | 00:00
56 | GPH | 98 | 01:00 | 122 | Mymensingh | 214 | 22:00 | 188 | Zigatola | 76 | 19:00
57 | Ghatail | 94 | 19:00 | 123 | Naogaon | 144 | 22:00
58 | Ghorashal | 15 | 15:00 | 124 | Narail | 61 | 19:30
59 | Ghorashal-230 | 97 | 00:00 | 125 | Narinda | 83 | 13:00
60 | Goalpara | 36 | 18:30 | 126 | Narshingdi | 191 | 23:00
61 | Gollamari | 92 | 19:00 | 127 | Natore | 154 | 00:00
62 | Gopalganj | 107 | 20:00 | 128 | Nawabganj | 63.2 | 22:00
63 | Gulshan | 138 | 13:00 | 129 | Netrakona | 142 | 19:30
64 | Halishahar | 68 | 15:00 | 130 | New | 81.4 | 15:00
65 | HaripurSBU | 171 | 16:00 | 131 | Niamatpur | 80 | 00:00
66 | Hasnabad | 92 | 00:00 | 132 | Noapara | 46 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15745.7 | 215 |  | 15970.38
1:00 | 15141.8 | 228 |  | 15379.8
2:00 | 14612 | 227 |  | 14849
3:00 | 13895.3 | 225 |  | 14130.3
4:00 | 13581.5 | 219 |  | 13810.5
5:00 | 13520.7 | 210 |  | 13739.7
6:00 | 13044 | 161 |  | 13212
7:00 | 13020.8 | 175 |  | 13203.8
8:00 | 12977.87 | 170 |  | 13155.52
9:00 | 13199.59 | 110 |  | 13314.54
10:00 | 13492.71 | 19 |  | 13512.57
11:00 | 13943.51 | 20 |  | 13964.41
12:00 | 14408.28 | 35 |  | 14444.86
13:00 | 14671.12 | 79 |  | 14753.68
14:00 | 14604.89 | 104 |  | 14713.57
15:00 | 14661.08 | 157 |  | 14825.15
16:00 | 14653.83 | 125 |  | 14784.46
17:00 | 14183.77 | 0 |  | 14183.77
18:00 | 13818.51 | 0 |  | 13818.51
19:00 | 15875.68 | 0 |  | 15875.68
19:30 | 15986.38 | 147 |  | 16140.38
20:00 | 15770.11 | 116 |  | 15891.11
21:00 | 15823.25 | 103 |  | 15930.89
22:00 | 15748.91 | 117 |  | 15871.18
23:00 | 15616.21 | 185 |  | 15809.54
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8142.7 | 7603 | 15745.7 | DAILY GENERATION CURVE
00:30 | 7949.75 | 7494 | 15443.75
01:00 | 7756.8 | 7385 | 15141.8 | 04-09-2025
01:30 | 7654.4 | 7222.5 | 14876.9
02:00 | 7552 | 7060 | 14612
02:30 | 7348.65 | 6905 | 14253.65
03:00 | 7145.3 | 6750 | 13895.3
03:30 | 7027.4 | 6711 | 13738.4
04:00 | 6909.5 | 6672 | 13581.5
04:30 | 6875.1 | 6676 | 13551.1
05:00 | 6840.7 | 6680 | 13520.7
05:30 | 6739.555 | 6542.795 | 13282.35
06:00 | 6638.41 | 6405.59 | 13044
06:30 | 6639.45 | 6392.95 | 13032.4
07:00 | 6640.49 | 6380.31 | 13020.8
07:30 | 6610.19 | 6389.145 | 12999.335
08:00 | 6579.89 | 6397.98 | 12977.87
08:30 | 6659.995 | 6428.735 | 13088.73
09:00 | 6740.1 | 6459.49 | 13199.59
09:30 | 6853.29 | 6492.86 | 13346.15
10:00 | 6966.48 | 6526.23 | 13492.71
10:30 | 7147.51 | 6570.6 | 13718.11
11:00 | 7328.54 | 6614.97 | 13943.51
11:30 | 7482.125 | 6693.77 | 14175.895
12:00 | 7635.71 | 6772.57 | 14408.28
12:30 | 7720.065 | 6819.635 | 14539.7
13:00 | 7804.42 | 6866.7 | 14671.12
13:30 | 7736.275 | 6901.73 | 14638.005
14:00 | 7668.13 | 6936.76 | 14604.89
14:30 | 7802.975 | 6830.01 | 14632.985
15:00 | 7937.82 | 6723.26 | 14661.08
15:30 | 7951.43 | 6706.025 | 14657.455
16:00 | 7965.04 | 6688.79 | 14653.83
16:30 | 7905.77 | 6513.03 | 14418.8
17:00 | 7846.5 | 6337.27 | 14183.77
17:30 | 7751.835 | 6249.305 | 14001.14
18:00 | 7657.17 | 6161.34 | 13818.51
18:30 | 7960.785 | 6886.31 | 14847.095
19:00 | 8264.4 | 7611.28 | 15875.68
19:30 | 8173 | 7813.38 | 15986.38
20:00 | 8015.6 | 7754.51 | 15770.11
20:30 | 8015.75 | 7780.93 | 15796.68 |  | Executive Engineer
21:00 | 8015.9 | 7807.35 | 15823.25 |  | Network Operation Division
21:30 | 7985.05 | 7801.03 | 15786.08
22:00 | 7954.2 | 7794.71 | 15748.91
22:30 | 7913.7 | 7768.86 | 15682.56
23:00 | 7873.2 | 7743.01 | 15616.21

## En-Curve
QF-LDC-12
Date | 04-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3399 | 1902.2 | 914 | 38 | 54 | 1286 | 219 | 4776 | 0 | 612 | 2420.5 | 100 | 0 | 25 | 215 | DAILY ENERGY CURVE
00:30 | 3402.5 | 1899.7 | 915 | 38 | 53 | 1372 | 218.5 | 4679 | 0 | 570 | 2175.55 | 100 | 0 | 20.5 | 221.5 | 04-09-2025
01:00 | 3406 | 1897.2 | 916 | 38 | 52 | 1458 | 218 | 4582 | 0 | 528 | 1930.6 | 100 | 0 | 16 | 228
01:30 | 3327.5 | 1903.1 | 916 | 38 | 51 | 1456 | 218 | 4566.5 | 0 | 511.5 | 1773.8 | 100 | 0 | 15.5 | 227.5 | Energy Generated | 350.1697 |  | MKWHr
02:00 | 3249 | 1909 | 916 | 38 | 50 | 1454 | 218 | 4551 | 0 | 495 | 1617 | 100 | 0 | 15 | 227 | Energy not Served | 3 |  | MKWHr
02:30 | 3258 | 1916.75 | 916.5 | 38 | 49 | 1457 | 218.5 | 4502.5 | 0 | 398 | 1383.4 | 100 | 0 | 16 | 226 | Total Energy Requirement | 353.1697 |  | MKWHr
03:00 | 3267 | 1924.5 | 917 | 38 | 48 | 1460 | 219 | 4454 | 0 | 301 | 1149.8 | 100 | 0 | 17 | 225
03:30 | 3304.5 | 1929.5 | 917 | 38 | 48 | 1458 | 219 | 4456.5 | 0 | 271.5 | 979.4 | 100 | 0 | 17 | 222
04:00 | 3342 | 1934.5 | 917 | 38 | 48 | 1456 | 219 | 4459 | 0 | 242 | 809 | 100 | 0 | 17 | 219
04:30 | 3343.5 | 1935 | 917 | 38 | 47 | 1457.5 | 219.5 | 4441.5 | 0 | 242 | 789.6 | 100 | 0 | 20.5 | 214.5
05:00 | 3345 | 1935.5 | 917 | 38 | 46 | 1459 | 220 | 4424 | 0 | 242 | 770.2 | 100 | 0 | 24 | 210
05:30 | 3347.5 | 1896.6 | 916.5 | 38 | 45 | 1459 | 220 | 4329 | 4.65 | 243.5 | 660.1 | 100 | 0 | 22.5 | 185.5
06:00 | 3350 | 1857.7 | 916 | 38 | 44 | 1459 | 220 | 4234 | 9.3 | 245 | 550 | 100 | 0 | 21 | 161
06:30 | 3372.5 | 1886.7 | 916 | 38 | 43 | 1457.5 | 220 | 4179 | 67.2 | 209 | 529 | 100 | 0 | 14.5 | 168
07:00 | 3395 | 1915.7 | 916 | 38 | 42 | 1456 | 220 | 4124 | 125.1 | 173 | 508 | 100 | 0 | 8 | 175
07:30 | 3355 | 1858.85 | 916 | 38 | 40 | 1455.94 | 220.5 | 4107 | 194.045 | 199 | 509.5 | 100 | 0 | 5.5 | 172.5
08:00 | 3315 | 1802 | 916 | 38 | 38 | 1455.88 | 221 | 4090 | 262.99 | 225 | 511 | 100 | 0 | 3 | 170
08:30 | 3286 | 1797 | 916.5 | 38 | 38 | 1417.845 | 221 | 4123.5 | 385.885 | 230 | 529 | 100 | 0 | 6 | 140
09:00 | 3257 | 1792 | 917 | 38 | 38 | 1379.81 | 221 | 4157 | 508.78 | 235 | 547 | 100 | 0 | 9 | 110
09:30 | 3287 | 1807.5 | 916.5 | 38 | 38 | 1352.1 | 220.5 | 4197.5 | 551.55 | 242.5 | 583.5 | 100 | 0 | 11.5 | 64.5
10:00 | 3317 | 1823 | 916 | 38 | 38 | 1324.39 | 220 | 4238 | 594.32 | 250 | 620 | 100 | 0 | 14 | 19
10:30 | 3307.5 | 1796 | 916 | 38 | 40 | 1344.385 | 220 | 4283 | 576.325 | 250.5 | 828.4 | 100 | 0 | 18 | 19.5
11:00 | 3298 | 1769 | 916 | 38 | 42 | 1364.38 | 220 | 4328 | 558.33 | 251 | 1036.8 | 100 | 0 | 22 | 20
11:30 | 3322.5 | 1776.5 | 916.5 | 38 | 43 | 1364.485 | 219.5 | 4354.5 | 609.76 | 267 | 1145.65 | 100 | 0 | 18.5 | 27.5
12:00 | 3347 | 1784 | 917 | 38 | 44 | 1364.59 | 219 | 4381 | 661.19 | 283 | 1254.5 | 100 | 0 | 15 | 35
12:30 | 3388 | 1807 | 918 | 38 | 45 | 1363.795 | 218.5 | 4425.5 | 637.305 | 299.5 | 1278.6 | 100 | 0 | 20.5 | 57
13:00 | 3429 | 1830 | 919 | 38 | 46 | 1363 | 218 | 4470 | 613.42 | 316 | 1302.7 | 100 | 0 | 26 | 79
13:30 | 3444 | 1856.5 | 918.5 | 38 | 47 | 1368.5 | 218 | 4401.5 | 561.155 | 318.5 | 1335.85 | 100 | 0 | 30.5 | 91.5
14:00 | 3459 | 1883 | 918 | 38 | 48 | 1374 | 218 | 4333 | 508.89 | 321 | 1369 | 100 | 0 | 35 | 104
14:30 | 3558 | 1926 | 924 | 38 | 49 | 1245.815 | 218 | 4341 | 462.27 | 321 | 1412.9 | 100 | 0 | 37 | 130.5
15:00 | 3657 | 1969 | 930 | 38 | 50 | 1117.63 | 218 | 4349 | 415.65 | 321 | 1456.8 | 100 | 0 | 39 | 157
15:30 | 3654.5 | 1968.25 | 928 | 38 | 49 | 1117.73 | 218.5 | 4397 | 321.375 | 321.5 | 1498.1 | 100 | 0 | 45.5 | 141
16:00 | 3652 | 1967.5 | 926 | 38 | 48 | 1117.83 | 219 | 4445 | 227.1 | 322 | 1539.4 | 100 | 0 | 52 | 125
16:30 | 3634.5 | 1925 | 926 | 38 | 47 | 1062.85 | 219.5 | 4380.5 | 172.95 | 334 | 1537 | 100 | 0 | 41.5 | 62.5
17:00 | 3617 | 1882.5 | 926 | 38 | 46 | 1007.87 | 220 | 4316 | 118.8 | 346 | 1534.6 | 100 | 0 | 31 | 0
17:30 | 3470 | 1829 | 926.5 | 38 | 45 | 1010.325 | 220.5 | 4261 | 63.915 | 422.5 | 1591.9 | 100 | 0 | 22.5 | 0
18:00 | 3323 | 1775.5 | 927 | 38 | 44 | 1012.78 | 221 | 4206 | 9.03 | 499 | 1649.2 | 100 | 0 | 14 | 0
18:30 | 3513 | 1870.75 | 926.5 | 38 | 48 | 1179.03 | 221.5 | 4338.5 | 4.515 | 637 | 1928.3 | 132.5 | 0 | 9.5 | 0
19:00 | 3703 | 1966 | 926 | 38 | 52 | 1345.28 | 222 | 4471 | 0 | 775 | 2207.4 | 165 | 0 | 5 | 0
19:30 | 3672 | 1902 | 926 | 38 | 50 | 1446.38 | 222 | 4509 | 0 | 737 | 2319 | 165 | 0 | 0 | 147
20:00 | 3670 | 1886.5 | 927 | 38 | 52 | 1461.51 | 222 | 4599 | 0 | 737 | 2010.1 | 165 | 0 | 2 | 116
20:30 | 3725 | 1903.75 | 926.5 | 38 | 51 | 1453.93 | 222 | 4604 | 0 | 739.5 | 1963.5 | 165 | 0 | 4.5 | 109.5
21:00 | 3780 | 1921 | 926 | 38 | 50 | 1446.35 | 222 | 4609 | 0 | 742 | 1916.9 | 165 | 0 | 7 | 103
21:30 | 3773.5 | 1916 | 925.5 | 38 | 52 | 1448.53 | 222 | 4607 | 0 | 726.5 | 1908.55 | 165 | 0 | 3.5 | 110
22:00 | 3767 | 1911 | 925 | 38 | 54 | 1450.71 | 222 | 4605 | 0 | 711 | 1900.2 | 165 | 0 | 0 | 117
22:30 | 3771 | 1922 | 925.5 | 38 | 55 | 1449.86 | 221 | 4618.5 | 0 | 636.5 | 1905.7 | 132.5 | 0 | 7 | 151
23:00 | 3775 | 1933 | 926 | 38 | 56 | 1449.01 | 220 | 4632 | 0 | 562 | 1911.2 | 100 | 0 | 14 | 185
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 18:00 | 347 | 14:00 | Payra | 412 | 05:00 | 409 | 13:00
Ashuganj | 309 | 2:00 | 368 | 9:00 | Rahanpur | 400 | 18:00 | 383 | 23:00
Bhulta | 389 | 18:00 | 362 | 12:00 | Rampal | 402 | 08:00 | 389 | 23:00
Bibiana | 382 | 02:00 | 376 | 10:00
BIPTC | 402 | 04:00 | 388 | 13:00
Bogura | 381 | 18:00 | 361 | 23:00
Gopalganj | 393 | 07:00 | 382 | 23:00
Kaliakoir | 368 | 06:00 | 357 | 10:00
Madunaghat | 390 | 18:00 | 385 | 11:00
Meghnaghat | 376 | 07:00 | 367 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 18:00 | 210 | 10:00 | Keranigonj | 219 | 18:00 | 208 | 10:00
AKSML | 228 | 18:00 | 221 | 10:00 | Khulna(S) | 231 | 18:00 | 219 | 19:00
Aminbazar | 221 | 17:00 | 211 | 09:00 | Madunaghat | 231 | 18:00 | 225 | 10:00
Ashuganj | 229 | 18:00 | 216 | 08:00 | Madunaghat-400 | 231 | 18:00 | 226 | 13:00
Ashuganj-400 | 229 | 18:00 | 216 | 08:00 | Maniknagar | 215 | 18:00 | 206 | 12:00
Baghabari | 231 | 17:00 | 224 | 10:00 | Meghnaghat | 223 | 18:00 | 216 | 11:00
Barapukuria | 224 | 18:00 | 216 | 07:00 | Meghnaghat-400 | 220 | 18:00 | 212 | 10:00
Barapukuria-230 | 224 | 18:00 | 216 | 07:00 | Mirsorai | 227 | 00:00 | 219 | 11:00
Barishal | 228 | 18:00 | 219 | 23:00 | Rajshahi | 232 | 18:00 | 221 | 01:00
Bheramara | 233 | 18:00 | 222 | 12:00 | Rampal | 230 | 17:00 | 219 | 23:00
Bhulta | 223 | 02:00 | 206 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 06:00 | 219 | 13:00 | Rampura | 221 | 02:00 | 204 | 10:00
BIPTC | 236 | 18:00 | 223 | 03:00 | Shikalbaha | 229 | 17:00 | 223 | 10:00
Bogura | 237 | 18:00 | 226 | 04:00 | Shyampur | 218 | 18:00 | 208 | 10:00
Bogura-400 | 238 | 18:30 | 227 | 23:00 | Siddhirganj | 217 | 18:00 | 209 | 10:00
Borhanuddin | 232 | 18:00 | 226 | 21:00 | Sirajgonj | 239 | 18:00 | 231 | 12:00
BSRM | 228 | 18:00 | 219 | 10:00 | Sreepur | 227 | 18:00 | 215 | 09:00
Cumilla(N) | 220 | 18:00 | 211 | 10:00 | Tongi | 222 | 19:30 | 208 | 09:00
Faridpur | 224 | 18:00 | 215 | 23:00
Fenchuganj | 225 | 14:00 | 219 | 15:00
Ghorashal | 232 | 11:00 | 220 | 15:00
Ghorashal-230 | 224 | 18:00 | 207 | 10:00
Gopalganj | 225 | 18:00 | 217 | 23:00
GPH | 229 | 18:00 | 221 | 13:00
Haripur | 217 | 18:00 | 209 | 10:00
Hasnabad | 218 | 18:00 | 211 | 09:00
Hathazari | 228 | 18:00 | 219 | 10:00
Ishurdi | 234 | 18:00 | 223 | 12:00
Jhenaidah | 232 | 18:00 | 218 | 22:00
Kaliakoir | 229 | 18:00 | 213 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 123 | 12:00 | Lalmonirhat | 127 | 01:00 | 122 | 14:00
Agargaon | 132 | 06:00 | 124 | 10:00 | Madanganj | 128 | 18:00 | 120 | 10:00
Agrabad | 129 | 18:00 | 124 | 10:00 | Madaripur | 135 | 18:00 | 128 | 23:00
AKS | 128 | 18:00 | 124 | 10:00 | Madartek | 136 | 02:00 | 123 | 12:00
Aminbazar | 130 | 04:00 | 122 | 09:00 | Madunaghat | 131 | 18:00 | 127 | 10:00
Amnura | 135 | 18:00 | 125 | 12:00 | Magura | 135 | 18:00 | 125 | 21:00
Ashuganj | 136 | 18:00 | 133 | 08:00 | Mahasthangarh | 131 | 18:00 | 123 | 23:00
Bagerhat | 132 | 08:00 | 120 | 22:00 | Maijdee | 118 | 18:00 | 108 | 01:00
Bajitpur | 128 | 17:00 | 122 | 20:00 | Manikganj | 123 | 18:00 | 114 | 10:00
Bakulia | 131 | 18:00 | 127 | 10:00 | Maniknagar | 129 | 02:00 | 123 | 10:00
Banani | 136 | 01:00 | 123 | 12:00 | Matarbari | 118 | 16:00 | 108 | 20:00
Bangabhaban | 130 | 06:00 | 122 | 13:00 | Matuail | 127 | 18:00 | 121 | 10:00
Barapukuria | 137 | 18:00 | 127 | 07:00 | Millgate | 129 | 18:00 | 118 | 10:00
Barguna | 139 | 20:00 | 132 | 05:00 | Mirpur | 128 | 02:00 | 120 | 10:00
Barishal | 133 | 18:00 | 127 | 22:00 | Mirzapur | 128 | 18:30 | 121 | 12:00
Barishal-230 | 133 | 07:00 | 127 | 23:00 | Mithapukur | 129 | 18:00 | 123 | 14:00
Baroaulia | 129 | 02:00 | 126 | 11:00 | MI_Cement | 128 | 18:00 | 120 | 10:00
Baroirhat | 122 | 07:00 | 115 | 22:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 01:00 | 119 | 10:00 | Mogbazar | 138 | 02:00 | 124 | 12:00
BashundharaCement | 128 | 18:00 | 120 | 10:00 | Mongla | 132 | 07:00 | 121 | 23:00
Beanibazar | 125 | 07:00 | 118 | 00:00 | Motijheel | 130 | 06:00 | 122 | 12:00
Benapole | 133 | 18:00 | 121 | 22:00 | Muktagacha | 131 | 19:30 | 119 | 22:00
Bhaluka | 129 | 18:00 | 120 | 09:00 | Munshiganj | 127 | 18:00 | 120 | 10:00
Bhandaria | 129 | 09:00 | 119 | 23:00 | Muradnagar | 123 | 18:00 | 116 | 13:00
Bhangura | 132 | 17:00 | 127 | 10:00 | Mymensingh | 130 | 19:30 | 112 | 20:00
Bheramara | 136 | 18:00 | 131 | 04:00 | Naogaon | 130 | 18:00 | 120 | 12:00
Bheramara(GK) | 136 | 18:00 | 130 | 23:00 | Narail | 136 | 18:00 | 125 | 19:00
Bhulta | 120 | 03:00 | 115 | 09:00 | Narinda | 129 | 02:00 | 123 | 10:00
Bog-Sherpur | 132 | 18:00 | 125 | 23:00 | Narshingdi | 136 | 18:00 | 117 | 10:00
Bogura | 134 | 18:30 | 127 | 00:00 | Natore | 133 | 18:00 | 126 | 12:00
Bogura-230 | 134 | 18:00 | 127 | 04:00 | Nawabganj | 133 | 05:00 | 126 | 12:00
Brahmanbaria | 129 | 04:00 | 126 | 00:00 | Netrakona | 122 | 16:00 | 109 | 21:00
Cantonment | 131 | 02:00 | 123 | 10:00 | New | 128 | 07:00 | 119 | 12:00
Chandina | 126 | 18:00 | 120 | 10:00 | Niamatpur | 137 | 18:00 | 130 | 22:00
Chandpur | 130 | 18:00 | 119 | 13:00 | Noapara | 135 | 18:00 | 124 | 23:00
Chandraghona | 131 | 18:00 | 128 | 12:00 | Pabna | 133 | 04:00 | 127 | 12:00
Chapai | 134 | 17:00 | 129 | 04:00 | Palashbari | 127 | 18:00 | 119 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:00 | 120 | 10:00 | Panchagarh | 133 | 02:00 | 121 | 14:00
Chauddagram | 120 | 08:00 | 115 | 13:00 | Patiya | 130 | 18:00 | 126 | 10:00
Chhatak | 124 | 05:00 | 115 | 18:30 | Patuakhali | 140 | 00:00 | 132 | 04:00
Chowmuhani | 119 | 18:00 | 108 | 13:00 | Payra | 136 | 00:00 | 134 | 04:00
Chuadanga | 134 | 18:00 | 122 | 00:00 | PHP | 121 | 08:00 | 114 | 02:00
Coxsbazar | 118 | 16:00 | 108 | 20:00 | Postogola | 130 | 18:00 | 123 | 10:00
Cumilla(N) | 126 | 18:00 | 120 | 10:00 | Purbachal | 135 | 00:00 | 118 | 10:00
Cumilla(S) | 132 | 04:00 | 118 | 12:00 | Purbasadipur | 131 | 18:00 | 122 | 13:00
Daganbhuiyan | 118 | 08:00 | 111 | 01:00 | Rahanpur | 138 | 18:00 | 131 | 09:00
Daudkandi | 121 | 18:00 | 113 | 22:00 | Rahanpur-400 | 138 | 18:00 | 131 | 23:00
Dhaka | 137 | 02:00 | 124 | 12:00 | Rahim | 127 | 18:00 | 121 | 10:00
Dhamrai | 128 | 18:00 | 120 | 09:00 | Rajbari | 132 | 16:00 | 125 | 22:00
Dhanmondi | 137 | 02:00 | 125 | 09:00 | Rajendrapur | 136 | 18:00 | 119 | 10:00
Dohazari | 127 | 18:00 | 121 | 19:00 | Rajshahi | 133 | 18:00 | 125 | 12:00
Faridpur | 133 | 07:00 | 128 | 00:00 | Rajshahi-230 | 133 | 18:00 | 125 | 12:00
Fatullah | 130 | 18:00 | 120 | 10:00 | Ramganj | 123 | 18:00 | 114 | 00:00
Fenchuganj | 132 | 04:00 | 128 | 00:00 | Rampur | 129 | 18:00 | 125 | 13:00
Feni | 122 | 18:00 | 113 | 01:00 | Rampura | 137 | 02:00 | 124 | 11:00
Ghatail | 128 | 18:30 | 116 | 23:00 | Rangamati | 130 | 18:00 | 127 | 10:00
Ghorashal | 135 | 17:00 | 126 | 10:00 | Rangpur | 131 | 18:30 | 124 | 07:00
Goalpara | 136 | 06:00 | 127 | 23:00 | Ruppur | 136 | 18:00 | 130 | 12:00
Gollamari | 137 | 18:00 | 128 | 22:00 | Saidpur | 133 | 18:30 | 124 | 23:00
Gopalganj | 135 | 18:00 | 127 | 23:00 | Satkhira | 136 | 17:00 | 122 | 19:00
Gopalganj-400 | 135 | 07:00 | 130 | 23:00 | Satmasjid | 132 | 18:00 | 124 | 10:00
Gulshan | 135 | 00:00 | 124 | 12:00 | Savar | 130 | 18:00 | 120 | 10:00
Halishahar | 131 | 18:00 | 125 | 10:00 | SevenRings | 136 | 18:00 | 126 | 10:00
Haripur | 127 | 18:00 | 121 | 10:00 | ShahCement | 128 | 18:00 | 120 | 10:00
HaripurSBU | 127 | 18:00 | 121 | 10:00 | Shahjadpur | 135 | 18:00 | 130 | 12:00
Hasnabad | 128 | 01:00 | 123 | 12:00 | Shahjibazar | 130 | 07:00 | 124 | 00:00
Hathazari | 131 | 17:00 | 127 | 11:00 | Shahmirpur | 131 | 18:00 | 127 | 10:00
Ishurdi | 138 | 18:00 | 131 | 03:00 | Shariatpur | 133 | 07:00 | 125 | 23:00
Jaldhaka | 130 | 18:00 | 121 | 23:00 | Sherpur | 132 | 18:30 | 117 | 11:00
Jamalpur | 134 | 19:30 | 118 | 19:00 | Shikalbaha | 120 | 01:00 | 117 | 11:00
Jashore | 136 | 18:00 | 124 | 22:00 | Shikalbaha-230 | 132 | 17:00 | 128 | 10:00
Jhenaidah | 136 | 17:00 | 120 | 23:00 | Shitalakhya | 128 | 18:00 | 120 | 10:00
Jhenaidah-230 | 138 | 18:00 | 128 | 22:00 | Sholosohor | 130 | 18:00 | 127 | 10:00
Joydebpur | 140 | 18:00 | 126 | 08:00 | Shyampur | 130 | 18:00 | 122 | 10:00
Joypurhat | 128 | 18:00 | 117 | 23:00 | Shyampur-230 | 130 | 18:00 | 120 | 10:00
Juldah | 130 | 17:00 | 126 | 10:00 | Siddhirganj | 127 | 18:00 | 121 | 10:00
Kabirpur | 133 | 19:30 | 114 | 12:00 | Sirajganj | 130 | 18:00 | 124 | 23:00
Kachua | 128 | 18:00 | 119 | 13:00 | Sonargaon | 124 | 02:00 | 120 | 11:00
Kaliakoir | 133 | 18:30 | 126 | 12:00 | Sreemongol | 129 | 06:00 | 124 | 00:00
Kallyanpur | 130 | 17:00 | 122 | 10:00 | Sreepur | 132 | 18:00 | 124 | 09:00
Kalurghat | 130 | 18:00 | 127 | 10:00 | Srinagar | 133 | 04:00 | 126 | 12:00
Kamrangirchar | 134 | 07:00 | 126 | 10:00 | SSM | 132 | 01:00 | 130 | 08:00
Kaptai | 133 | 1:00 | 131 | 11:00 | Sunamganj | 123 | 06:00 | 114 | 0:00
Kasba | 123 | 18:00 | 116 | 12:00 | Sylhet | 126 | 07:00 | 120 | 00:00
Kazla | 130 | 04:00 | 122 | 13:00 | Sylhet-132 | 126 | 08:00 | 121 | 18:30
Keranigonj | 134 | 18:00 | 127 | 10:00 | Tangail | 127 | 18:30 | 116 | 12:00
Khagrachori | 129 | 06:00 | 126 | 11:00 | Taraganj | 130 | 03:00 | 122 | 23:00
Khulna | 136 | 18:00 | 127 | 22:00 | Thakurgaon | 133 | 03:00 | 119 | 14:00
Khulna(S) | 138 | 18:00 | 129 | 22:00 | TK | 131 | 18:00 | 127 | 10:00
Khulshi | 129 | 18:00 | 124 | 10:00 | Tongi | 130 | 9:00 | 122 | 09:00
Kishoreganj | 128 | 05:00 | 120 | 14:00 | Ullahpara | 133 | 18:00 | 127 | 11:00
Kodda | 136 | 18:00 | 120 | 11:00 | Ullon | 136 | 01:00 | 124 | 11:00
KSRM | 131 | 01:00 | 126 | 12:00 | Uttara | 128 | 01:00 | 120 | 10:00
Kulaura | 131 | 05:00 | 126 | 19:30 | UttaraNew | 130 | 18:00 | 120 | 10:00
Kurigram | 127 | 18:00 | 118 | 23:00 | Zigatola | 133 | 04:00 | 127 | 13:00
Kushtia | 132 | 18:00 | 126 | 02:00
Laksam | 127 | 18:00 | 118 | 01:00
Lakshmipur | 119 | 18:00 | 109 | 02:00
Lalbag | 133 | 04:00 | 126 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division