## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-09-2025 | during | 07-09-2025 | during | 07-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 372 | 331 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 297 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 14 | 44.9 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 121 | 133 | 133 | 117 | 117 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.2 | 26 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 23 | 23 | 23 | 23 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 80 | 138 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 50 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 70 | 144 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 320 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 52 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 1954.2 | 2746.9 | 5813.54 | 5821.54 | 3636.45 | 3717.45
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 218 | 214 | 214 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 47 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 60 | 0 | 0 | 40 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 22 | 28 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.26 | 0 | 2.49 | 0 | 2.49 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 46 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 62 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1145 | 1151 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 260 | 260 | 260 | 260 | 260 | 260 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1972.26 | 2225 | 3122.21 | 3114.72 | 2939.35 | 2974.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 137 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 148 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 26 | 27 | 46.7 | 46.7 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 38 | 44 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 173 | 127 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 80 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 172 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 54 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 70 | 90 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 77 | 0 | 75 | 0 | 75 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1228 | 1753 | 2445.86 | 2370.86 | 2143.66 | 2068.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-09-2025 | during | 07-09-2025 | during | 07-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 122 | 124 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 39 | 39 | 40 | 40 | 40 | 40 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 103 | 103 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.05 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 300.05 | 283 | 435 | 383 | 387.5 | 335.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 70 | 69 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 138 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 12 | 25 | 25 | 15 | 15 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 386 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1219 | 1194 | 1278 | 1278 | 1170 | 1170
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 840 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 392 | 369 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1024 | 1230 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2471 | 2477 | 3592.2 | 3552.2 | 3397 | 3357
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 302 | 303 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 945 | 1216 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-11 Shutdown under Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 277 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.78 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1641.78 | 2075 | 2052 | 2051 | 2022 | 2021
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 58.46 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 189 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 167 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 165 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 349 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 97 | 97 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.85 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1023.73 | 1446.75 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 67.21 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 117 | 0 | 50 | 0 | 50 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2106.25 | 2677.75 | 3142.52 | 3025.87 | 3016.14 | 2899.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 100 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 151 | 151 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.3 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 136 | 0 | 172.68 | 0 | 172.68 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 417.3 | 543 | 607.28 | 398 | 607.28 | 398
System Total |  |  |  |  | 28823.2 | 27829.875 | 13309.84 | 15974.65 | 22488.61 | 21995.19 | 19319.38 | 18941.96
Forecast Scenario (07-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15970 |  | 0 |  | 15970
|  |  |  | 1:00 | 15380 |  | 0 |  | 15380
|  |  |  | 2:00 | 14850 |  | 0 |  | 14850
|  |  |  | 3:00 | 14130 |  | 0 |  | 14130
|  |  |  | 4:00 | 13810 |  | 0 |  | 13810
|  |  |  | 5:00 | 13740 |  | 0 |  | 13740
|  |  |  | 6:00 | 13210 |  | 0 |  | 13210
|  |  |  | 7:00 | 13200 |  | 0 |  | 13200
|  |  |  | 8:00 | 13150 |  | 0 |  | 13150
|  |  |  | 9:00 | 13310 |  | 0 |  | 13310
|  |  |  | 10:00 | 13510 |  | 0 |  | 13510
|  |  |  | 11:00 | 13960 |  | 0 |  | 13960
|  |  |  | 12:00 | 14440 |  | 0 |  | 14440
|  |  |  | 13:00 | 14750 |  | 0 |  | 14750
|  |  |  | 14:00 | 14710 |  | 0 |  | 14710
|  |  |  | 15:00 | 14820 |  | 0 |  | 14820
|  |  |  | 16:00 | 14780 |  | 0 |  | 14780
|  |  |  | 17:00 | 14180 |  | 0 |  | 14180
|  |  |  | 18:00 | 13810 |  | 0 |  | 13810
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15870 |  | 0 |  | 15870
|  |  |  | 19:30 | 16140 |  | 0 |  | 16140
|  |  |  | 20:00 | 15890 |  | 0 |  | 15890
|  |  |  | 21:00 | 15930 |  | 0 |  | 15930
|  |  |  | 22:00 | 15870 |  | 0 |  | 15870
|  |  |  | 23:00 | 15810 |  | 0 |  | 15810
Probable Maximum Temperature: |  |  | 33.40°C
Probable Maximum Demand at Day Peak: |  |  | 14440.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16140.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16140.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 349.08 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:05 hrs on 07-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-09-2025 | [28 empty] | Date: | 06-09-2025 | [28 empty] | Date: | 06-09-2025 | [28 empty] | Date: | 06-09-2025 | [28 empty] | Date: | 06-09-2025 | [14 empty] | Date: | 06-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 50.3 | 54 | 53 | 122 | 145 | 15 | 55 | 158 | 0 | 300 | 284 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 52 | 14.5 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 12 | 0 | 220 | 24 | 33 | 257 | 0 | 0 | 19 | 8 | 28 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 173 | 0 | 0 | 330 | 44 | 195 | 31 | 91 | 90 | 198 | 0 | 19 | 114 | 56 | 43 | 0 | 29 | 315 | 0 | 380 | 0 | 70 | 158 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 48 | 143 | 0 | 0 | 12 | 7764.8 | 926 | 298 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1447.7 | 0 | 47 | 0 | 35 | 113 | 0 | 94 | 30 | 0 | 0 | 0 | 28 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 347 | 0 | 0 | 166 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 303 | 1216 | 0 | 7579.9 | 15344.7 | 107.79
01:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 46 | 0 | 72 | 90 | 145 | 0 | 55 | 149 | 0 | 300 | 286 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 52 | 14.5 | 15 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 12 | 0 | 219 | 31 | 40 | 258 | 0 | 0 | 19 | 8 | 31 | 218 | 0 | 0 | 0 | 1224 | 0 | 43 | 133 | 173 | 0 | 0 | 330 | 44 | 195 | 31 | 90 | 90 | 164 | 0 | 19 | 114 | 52 | 43 | 0 | 29 | 310 | 0 | 384 | 0 | 70 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 164 | 0 | 103 | 39 | 142 | 0 | 0 | 12 | 7586.5 | 927 | 306 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 1444.34 | 0 | 47 | 0 | 0 | 35 | 0 | 41 | 30 | 0 | 0 | 0 | 28 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 347 | 0 | 0 | 158 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 110 | 0 | 303 | 1214 | 0 | 7392.34 | 14978.84 | 107.79
02:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 44.2 | 0 | 143 | 75 | 45 | 0 | 55 | 143 | 0 | 300 | 279 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 52 | 14.5 | 15 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 12 | 0 | 219 | 30 | 40 | 257 | 0 | 0 | 19 | 8 | 30 | 217 | 0 | 0 | 0 | 1224 | 0 | 43 | 133 | 173 | 0 | 0 | 330 | 44 | 193 | 31 | 91 | 90 | 103 | 0 | 19 | 114 | 52 | 25 | 0 | 29 | 300 | 0 | 359 | 0 | 70 | 150 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 7 | 103 | 39 | 143 | 0 | 0 | 12 | 7399.7 | 926 | 319 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 1449.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 336 | 0 | 0 | 156 | 0 | 115 | 0 | 88 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 110 | 0 | 303 | 1214 | 0 | 7177.46 | 14577.16 | 107.79
03:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 44.3 | 0 | 149 | 60 | 0 | 0 | 55 | 72 | 0 | 300 | 272 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 52 | 14.5 | 22 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 12 | 0 | 219 | 0 | 42 | 255 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 173 | 0 | 0 | 330 | 44 | 181 | 31 | 91 | 90 | 103 | 0 | 19 | 114 | 50 | 8 | 0 | 30 | 305 | 0 | 350 | 0 | 70 | 150 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 39 | 142 | 0 | 0 | 12 | 7085.8 | 926 | 332 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 1449.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 325 | 0 | 0 | 156 | 0 | 70 | 0 | 68 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 265 | 115 | 110 | 0 | 303 | 1214 | 0 | 7107.78 | 14193.58 | 107.78
04:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 95 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 52 | 14.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 12 | 0 | 219 | 0 | 42 | 258 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 173 | 0 | 100 | 330 | 44 | 198 | 31 | 91 | 90 | 103 | 0 | 19 | 114 | 50 | 8 | 0 | 30 | 315 | 0 | 366 | 0 | 70 | 145 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 0 | 104 | 39 | 155 | 0 | 0 | 12 | 6941.5 | 927 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 1446.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 141 | 0 | 360 | 0 | 0 | 156 | 0 | 70 | 0 | 49 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 179 | 115 | 110 | 0 | 303 | 1224 | 0 | 6966.62 | 13908.12 | 107.78
05:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 52 | 14.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 65 | 0 | 12 | 12 | 0 | 220 | 0 | 42 | 259 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 173 | 0 | 138 | 330 | 44 | 201 | 31 | 91 | 90 | 104 | 0 | 19 | 114 | 48 | 8 | 0 | 30 | 310 | 0 | 386 | 0 | 70 | 136 | 0 | 0 | 84 | 30 | 0 | 0 | 165 | 0 | 104 | 39 | 156 | 0 | 0 | 12 | 6922.5 | 926 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 0 | 1448.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 360 | 0 | 0 | 155 | 0 | 35 | 0 | 49 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 180 | 115 | 110 | 0 | 303 | 1120 | 0 | 6769.37 | 13691.87 | 107.78
06:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 282 | 0 | 0 | 0 | 315 | 0 | 0 | 1 | 52 | 14.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 66 | 0 | 12 | 12 | 0.15 | 220 | 0 | 42 | 260 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 1224 | 1 | 51 | 0 | 173 | 0 | 20 | 330 | 44 | 191 | 31 | 91 | 90 | 104 | 0 | 19 | 114 | 46 | 8 | 1 | 30 | 300 | 0 | 366 | 0 | 70 | 136 | 0 | 0 | 84 | 30 | 0 | 0 | 165 | 0 | 104 | 39 | 156 | 0 | 0.57 | 8 | 6743.22 | 927 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 929 | 0 | 1275.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 338 | 0 | 0.01 | 154 | 0 | 35 | 0 | 34 | 0 | 100 | 0 | 0 | 2 | 0.08 | 0 | 174 | 115 | 110 | 0 | 303 | 1000 | 0 | 6328.38 | 13071.6 | 107.78
07:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 279 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 52 | 14.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 12 | 12 | 0.46 | 221 | 0 | 42 | 260 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 1224 | 5 | 51 | 0 | 173 | 0 | 18 | 330 | 44 | 190 | 31 | 90 | 90 | 103 | 0 | 19 | 114 | 42 | 8 | 18 | 30 | 305 | 0 | 360 | 0 | 70 | 137 | 0 | 0 | 84 | 30 | 0 | 0 | 164 | 0 | 104 | 38 | 157 | 0 | 5.03 | 12 | 6711.99 | 926 | 381 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 850 | 0 | 1266.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.29 | 11 | 0 | 0 | 2.35 | 140 | 0 | 140 | 0 | 140 | 0 | 336 | 0 | 0.73 | 149 | 0 | 35 | 6 | 34 | 0 | 100 | 0 | 0.9 | 20 | 0.08 | 0 | 176 | 115 | 110 | 0 | 303 | 985 | 0 | 6289.04 | 13001.03 | 107.78
08:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 58 | 60 | 0 | 0 | 8 | 0 | 0 | 300 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 16 | 52 | 12.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 0 | 12 | 12 | 1.05 | 222 | 0 | 17 | 260 | 0 | 0 | 19 | 0 | 0 | 187 | 0 | 0 | 0 | 1153 | 11 | 51 | 0 | 173 | 0 | 19 | 310 | 44 | 198 | 31 | 91 | 90 | 103 | 0 | 19 | 114 | 40 | 8 | 9 | 0 | 305 | 0 | 399 | 0 | 70 | 136 | 8 | 0 | 84 | 30 | 0 | 0 | 164 | 0 | 104 | 38 | 157 | 1 | 23.8 | 12 | 6536.35 | 926 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 821 | 0 | 1155.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.23 | 39 | 0 | 0 | 7.28 | 140 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 0 | 100 | 0 | 1.3 | 58 | 0.26 | 0 | 183 | 100 | 110 | 0 | 301 | 910 | 0 | 6143.84 | 12680.19 | 107.77
09:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 52 | 30 | 0 | 0 | 35 | 0 | 0 | 300 | 279 | 0 | 0 | 0 | 330 | 0 | 0 | 24 | 52 | 21.5 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 12 | 12 | 0 | 222 | 0 | 22 | 260 | 0 | 0 | 19 | 0 | 0 | 187 | 0 | 0 | 0 | 1049 | 14 | 51 | 0 | 173 | 0 | 23 | 280 | 44 | 186 | 30 | 77 | 90 | 103 | 0 | 19 | 114 | 40 | 8 | 45 | 0 | 310 | 0 | 360 | 0 | 70 | 143 | 0 | 0 | 84 | 30 | 0 | 0 | 164 | 0 | 103 | 39 | 150 | 1 | 30.9 | 12 | 6472.4 | 927 | 395 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 849 | 0 | 1109.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.7 | 79 | 0 | 0 | 16.69 | 140 | 0 | 140 | 0 | 140 | 0 | 333 | 0 | 2.59 | 150 | 0 | 0 | 24 | 0 | 0 | 100 | 0 | 2.4 | 109 | 0.23 | 0 | 173 | 115 | 110 | 0 | 304 | 895 | 0 | 6268.19 | 12740.59 | 107.77
10:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 60 | 30 | 0 | 0 | 35 | 0 | 0 | 300 | 284 | 0 | 0 | 0 | 280 | 0 | 0 | 30 | 0 | 20.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 12 | 12 | 2.81 | 222 | 0 | 20 | 260 | 0 | 0 | 19 | 0 | 0 | 188 | 0 | 0 | 0 | 906 | 17 | 51 | 0 | 173 | 0 | 99 | 280 | 24 | 190 | 0 | 72 | 90 | 104 | 0 | 19 | 52 | 40 | 8 | 23 | 0 | 300 | 0 | 304 | 0 | 68 | 135 | 0 | 0 | 84 | 30 | 0 | 0 | 164 | 0 | 103 | 39 | 136 | 2 | 43.89 | 12 | 6095.2 | 927 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 823 | 0 | 1017.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.58 | 100 | 0 | 0 | 31.84 | 140 | 0 | 140 | 0 | 140 | 0 | 280 | 0 | 4.86 | 148 | 0 | 0 | 28 | 0 | 0 | 100 | 0 | 3.3 | 134 | 0.23 | 0 | 173 | 115 | 110 | 0 | 304 | 860 | 0 | 6150.3 | 12245.5 | 107.77
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 13 | 60 | 15 | 0 | 0 | 35 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 33 | 35 | 20.5 | 22 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 12 | 12 | 4.05 | 222 | 0 | 22 | 260 | 0 | 0 | 19 | 0 | 0 | 200 | 0 | 0 | 0 | 947 | 16 | 51 | 0 | 173 | 0 | 120 | 310 | 10 | 162 | 25 | 70 | 90 | 104 | 0 | 19 | 52 | 42 | 8 | 47 | 0 | 310 | 0 | 375 | 0 | 68 | 145 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 0 | 103 | 39 | 136 | 2 | 26.07 | 12 | 6391.62 | 927 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 855 | 0 | 1022.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.56 | 99 | 0 | 0 | 63.99 | 140 | 0 | 140 | 0 | 140 | 0 | 384 | 0 | 5.72 | 149 | 0 | 0 | 17 | 0 | 0 | 100 | 0 | 7.8 | 152 | 0.24 | 0 | 171 | 115 | 110 | 0 | 304 | 850 | 0 | 6344.62 | 12736.24 | 107.77
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 14 | 17 | 80 | 15 | 0 | 0 | 35 | 70 | 0 | 300 | 290 | 0 | 0 | 0 | 280 | 0 | 0 | 34 | 35 | 20.2 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 12 | 12 | 3.26 | 221 | 0 | 22 | 260 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 1145 | 18 | 51 | 0 | 173 | 0 | 148 | 330 | 38 | 0 | 26 | 70 | 90 | 104 | 0 | 19 | 52 | 42 | 8 | 77 | 0 | 315 | 0 | 389 | 0 | 70 | 157 | 10 | 0 | 83 | 30 | 0 | 0 | 165 | 0 | 103 | 39 | 122 | 3 | 21.05 | 12 | 6673.51 | 927 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 1024 | 0 | 1023.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.46 | 117 | 0 | 0 | 67.21 | 140 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 5.85 | 151 | 0 | 0 | 27 | 0 | 0 | 100 | 0 | 3.3 | 136 | 0.78 | 0 | 171 | 113 | 110 | 0 | 302 | 945 | 0 | 6636.33 | 13309.84 | 107.77
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 22.5 | 17 | 135 | 15 | 0 | 0 | 46 | 145 | 0 | 300 | 288 | 0 | 0 | 10 | 280 | 0 | 0 | 33 | 35 | 20.2 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 10 | 0 | 44 | 0 | 12 | 12 | 4.38 | 219 | 0 | 15 | 260 | 0 | 0 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 1110 | 18 | 51 | 0 | 175 | 0 | 230 | 330 | 41 | 0 | 29 | 70 | 90 | 104 | 0 | 12 | 52 | 48 | 8 | 71 | 0 | 315 | 0 | 383 | 0 | 70 | 154 | 10 | 0 | 83 | 30 | 0 | 0 | 166 | 0 | 103 | 39 | 120 | 1 | 34.89 | 12 | 6858.97 | 926 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 1123 | 0 | 1023.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.51 | 110 | 0 | 0 | 64.88 | 178 | 0 | 170 | 0 | 170 | 0 | 414 | 0 | 5.71 | 152 | 0 | 0 | 25 | 0 | 0 | 100 | 0 | 2.6 | 150 | 0.7 | 0 | 168 | 115 | 110 | 0 | 302 | 1050 | 0 | 6904.13 | 13763.1 | 107.77
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 30.2 | 17 | 135 | 15 | 0 | 0 | 55 | 146 | 0 | 300 | 282 | 0 | 0 | 17 | 280 | 0 | 0 | 29 | 35 | 20 | 7 | 0 | 320 | 0 | 0 | 0 | 0 | 9 | 0 | 44 | 0 | 12 | 12 | 3.96 | 218 | 0 | 9 | 260 | 0 | 0 | 50 | 3 | 0 | 214 | 0 | 0 | 0 | 1130 | 17 | 51 | 0 | 172 | 0 | 335 | 330 | 41 | 0 | 29 | 70 | 90 | 103 | 0 | 12 | 52 | 48 | 8 | 60 | 0 | 305 | 0 | 370 | 0 | 70 | 151 | 10 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 104 | 39 | 120 | 1 | 22.84 | 12 | 6973 | 926 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 1131 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.72 | 100 | 0 | 0 | 56.97 | 188 | 0 | 186 | 0 | 170 | 0 | 384 | 0 | 5.17 | 151 | 0 | 0 | 22 | 0 | 0 | 100 | 0 | 0.9 | 165 | 0.44 | 0 | 164 | 115 | 110 | 0 | 304 | 1040 | 0 | 6898.2 | 13871.2 | 107.77
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 31.2 | 17 | 133 | 15 | 0 | 0 | 55 | 150 | 0 | 300 | 296 | 0 | 0 | 17 | 319 | 0 | 0 | 24 | 35 | 20 | 15 | 0 | 360 | 0 | 0 | 0 | 0 | 8 | 0 | 44 | 0 | 12 | 12 | 2.21 | 218 | 0 | 6 | 260 | 0 | 0 | 50 | 8 | 0 | 213 | 0 | 0 | 0 | 1190 | 14 | 51 | 0 | 168 | 0 | 327 | 330 | 41 | 0 | 29 | 69 | 90 | 104 | 0 | 19 | 52 | 48 | 8 | 26 | 0 | 315 | 0 | 384 | 0 | 58 | 153 | 14 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 104 | 39 | 115 | 1 | 15.57 | 12 | 7111.98 | 926 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 1162 | 0 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.78 | 80 | 0 | 0 | 46.52 | 195 | 0 | 193 | 0 | 170 | 0 | 400 | 0 | 4.3 | 150 | 0 | 0 | 18 | 0 | 0 | 100 | 0 | 0 | 55 | 0.5 | 0 | 211 | 115 | 110 | 0 | 305 | 1040 | 0 | 6736.1 | 13848.08 | 107.77
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 33.8 | 17 | 133 | 15 | 70 | 0 | 55 | 161 | 0 | 300 | 284 | 0 | 0 | 17 | 321 | 0 | 0 | 17 | 35 | 26 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 3 | 0 | 44 | 0 | 12 | 12 | 1.59 | 218 | 0 | 4 | 260 | 0 | 0 | 50 | 8 | 0 | 217 | 0 | 0 | 0 | 1144 | 10 | 51 | 33 | 173 | 0 | 333 | 330 | 40 | 0 | 29 | 68 | 90 | 102 | 0 | 19 | 52 | 48 | 8 | 21 | 0 | 320 | 0 | 383 | 0 | 58 | 153 | 14 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 102 | 39 | 117 | 0 | 4.21 | 12 | 7148.6 | 927 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1157 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6 | 53 | 0 | 0 | 33.59 | 199 | 0 | 197 | 0 | 170 | 0 | 396 | 0 | 3.33 | 158 | 0 | 0 | 8 | 0 | 0 | 100 | 0 | 0.6 | 88 | 0.31 | 0 | 247 | 115 | 110 | 0 | 305 | 1060 | 0 | 6716.43 | 13865.03 | 107.77
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 30.4 | 18 | 133 | 15 | 145 | 0 | 55 | 145 | 0 | 300 | 284 | 0 | 0 | 17 | 323 | 0 | 0 | 6 | 35 | 20 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 12 | 12 | 0.18 | 218 | 0 | 6 | 260 | 0 | 0 | 50 | 8 | 0 | 218 | 0 | 0 | 0 | 1118 | 3 | 51 | 50 | 178 | 0 | 337 | 330 | 40 | 0 | 29 | 69 | 90 | 103 | 0 | 19 | 80 | 44 | 8 | 13 | 26 | 305 | 0 | 311 | 0 | 68 | 140 | 14 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 102 | 39 | 118 | 0 | 1.16 | 12 | 7152.74 | 926 | 380 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 1141 | 0 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.62 | 10 | 0 | 0 | 9.71 | 189 | 0 | 186 | 0 | 170 | 0 | 340 | 0 | 1.01 | 152 | 0 | 0 | 3 | 0 | 0 | 100 | 0 | 0.4 | 24 | 0.13 | 0 | 240 | 115 | 110 | 0 | 305 | 1090 | 0 | 6485.87 | 13638.61 | 107.76
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 29.4 | 35 | 133 | 15 | 145 | 0 | 53 | 141 | 0 | 300 | 293 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 35 | 26 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 12 | 12 | 0.03 | 218 | 0 | 18 | 260 | 0 | 0 | 50 | 8 | 2 | 216 | 0 | 0 | 0 | 1151 | 0 | 51 | 50 | 178 | 0 | 280 | 280 | 41 | 0 | 29 | 68 | 90 | 123 | 0 | 19 | 98 | 44 | 16 | 1 | 28 | 300 | 0 | 336 | 0 | 68 | 134 | 8 | 0 | 43 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 118 | 0 | 0.19 | 12 | 7058.62 | 927 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1070 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 1.5 | 181 | 0 | 168 | 0 | 140 | 0 | 361 | 0 | 0.17 | 147 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 2 | 0.01 | 0 | 247 | 115 | 110 | 0 | 304 | 1000 | 0 | 6210.18 | 13268.8 | 107.76
19:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 44.9 | 35 | 133 | 122 | 293 | 4 | 55 | 155 | 0 | 300 | 287 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 142 | 26 | 15 | 0 | 320 | 3 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 12 | 12 | 0 | 218 | 16 | 18 | 256 | 70 | 0 | 26 | 12 | 88 | 217 | 0 | 0 | 0 | 1154 | 0 | 51 | 82 | 172 | 0 | 342 | 330 | 42 | 0 | 28 | 80 | 90 | 167 | 0 | 19 | 114 | 52 | 34 | 0 | 28 | 320 | 0 | 382 | 0 | 68 | 152 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 124 | 0 | 0 | 12 | 8049.9 | 926 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1189 | 0 | 1299 | 0 | 0 | 0 | 90 | 37 | 0 | 75 | 8 | 0 | 0 | 0 | 27 | 0 | 0 | 188 | 0 | 187 | 0 | 210 | 0 | 399 | 0 | 0 | 150 | 0 | 100 | 0 | 59 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 110 | 0 | 305 | 1075 | 37 | 7439 | 15488.9 | 107.76
19:30 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 45.5 | 17 | 133 | 121 | 293 | 55 | 55 | 143 | 0 | 300 | 293 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 142 | 26 | 15 | 0 | 320 | 13 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 12 | 12 | 0 | 218 | 51 | 26 | 260 | 60 | 0 | 26 | 17 | 82 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 172 | 0 | 345 | 330 | 42 | 0 | 28 | 90 | 90 | 164 | 0 | 19 | 114 | 52 | 43 | 0 | 28 | 305 | 0 | 360 | 0 | 69 | 147 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 124 | 0 | 0 | 12 | 8069.5 | 926 | 369 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 1448 | 0 | 26 | 0 | 108 | 108 | 0 | 92 | 25 | 8 | 0 | 0 | 27 | 0 | 0 | 176 | 0 | 170 | 0 | 160 | 0 | 335 | 0 | 0 | 150 | 0 | 109 | 0 | 101 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 110 | 0 | 305 | 1210 | 54 | 7807 | 15876.5
20:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 44.5 | 17 | 133 | 121 | 293 | 55 | 55 | 141 | 0 | 300 | 294 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 142 | 26 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 1 | 66 | 62 | 0 | 12 | 12 | 0 | 220 | 51 | 27 | 270 | 64 | 0 | 26 | 17 | 49 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 137 | 0 | 347 | 330 | 43 | 83 | 27 | 90 | 90 | 165 | 0 | 19 | 114 | 54 | 43 | 0 | 28 | 305 | 0 | 376 | 0 | 69 | 138 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 124 | 0 | 0 | 0 | 8115.5 | 841 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1209 | 0 | 1448 | 0 | 48 | 0 | 113 | 108 | 0 | 92 | 32 | 8 | 0 | 0 | 27 | 0 | 0 | 177 | 0 | 166 | 0 | 176 | 0 | 345 | 0 | 0 | 152 | 0 | 114 | 0 | 102 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 110 | 0 | 303 | 1216 | 54 | 7801 | 15916.5 | 107.76
21:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 44.9 | 17 | 138 | 121 | 293 | 55 | 55 | 144 | 0 | 300 | 297 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 142 | 26 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 60 | 0 | 12 | 12 | 0 | 220 | 46 | 28 | 260 | 62 | 0 | 26 | 17 | 47 | 218 | 0 | 0 | 0 | 1151 | 0 | 51 | 80 | 127 | 0 | 347 | 330 | 44 | 137 | 27 | 90 | 90 | 172 | 0 | 19 | 114 | 54 | 43 | 0 | 28 | 310 | 0 | 386 | 0 | 69 | 138 | 12 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 39 | 124 | 0 | 0 | 0 | 8201.9 | 840 | 369 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 1446.75 | 0 | 47 | 0 | 50 | 113 | 0 | 92 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 189 | 0 | 167 | 0 | 165 | 0 | 349 | 0 | 0 | 151 | 0 | 114 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 110 | 0 | 303 | 1216 | 54 | 7772.75 | 15974.65 | 107.76
22:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 46.7 | 17 | 149 | 120 | 293 | 55 | 54 | 147 | 0 | 300 | 304 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 35 | 26 | 22 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 66 | 59 | 0 | 12 | 12 | 0 | 220 | 47 | 24 | 260 | 40 | 0 | 26 | 17 | 49 | 218 | 0 | 0 | 0 | 1156 | 0 | 51 | 88 | 127 | 0 | 346 | 330 | 44 | 137 | 27 | 90 | 90 | 176 | 0 | 19 | 114 | 54 | 43 | 0 | 21 | 310 | 0 | 392 | 0 | 70 | 143 | 12 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 121 | 0 | 0 | 0 | 8105.7 | 811 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 1447.6 | 0 | 47 | 0 | 7 | 70 | 0 | 92 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 194 | 0 | 170 | 0 | 168 | 0 | 379 | 0 | 0 | 149 | 0 | 114 | 0 | 113 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 110 | 0 | 303 | 1216 | 54 | 7658.6 | 15764.3 | 107.76
23:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 51.4 | 17 | 149 | 120 | 293 | 55 | 55 | 158 | 0 | 300 | 305 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 35 | 24 | 22 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 66 | 62 | 0 | 12 | 12 | 0 | 222 | 50 | 25 | 260 | 50 | 0 | 26 | 17 | 48 | 217 | 0 | 0 | 0 | 1160 | 0 | 51 | 115 | 138 | 0 | 345 | 330 | 45 | 137 | 27 | 79 | 90 | 187 | 0 | 19 | 114 | 56 | 43 | 0 | 22 | 320 | 0 | 391 | 0 | 70 | 154 | 12 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 103 | 29 | 121 | 0 | 0 | 0 | 8223.4 | 911 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1445.24 | 0 | 40 | 0 | 0 | 70 | 0 | 92 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 199 | 0 | 178 | 0 | 177 | 0 | 385 | 0 | 0 | 149 | 0 | 114 | 0 | 113 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 110 | 0 | 303 | 1216 | 54 | 7771.44 | 15994.84 | 107.76
Total KWH | 0 | 1163520 | 269760 | 0 | 0 | 0 | 0 | 0 | 8323200 | 0 | 0 | 627840 | 299160 | 2629584 | 1430880 | 2245887 | 289467 | 1007924 | 2234880 | 0 | 7581500 | 6965236 | 0 | 0 | 444859 | 7475003 | 0 | 0 | 254555 | 1269600 | 480600 | 433800 | 0 | 7807272.73 | 25091 | 0 | 0 | 0 | 32640 | 1031088 | 1285680 | 0 | 301440 | 300480 | 22918 | 5301680 | 373020 | 648000 | 6283636.36 | 282691 | 0 | 638880 | 155125.8 | 444109 | 5021814 | 0 | 0 | 0 | 27523634 | 139590 | 1203414 | 1135781 | 4048000 | 0 | 4716500 | 7800000 | 973440 | 2803000 | 665928 | 1932480 | 2133270 | 3010080 | 0 | 432050 | 2236680 | 1138560 | 452530 | 449545 | 421936 | 7529000 | 0 | 9217000 | 0 | 1619640 | 3500182 | 186168 | 0 | 1967040 | 720384 | 0 | 0 | 4494740 | 225000 | 2469600 | 864000 | 3123840 | 10550 | 229060 | 240240 | 174995682.89 | 22261818 | 8885952 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 637920 | 25898180 | 0 | 29540280 | 0 | 279381 | 0 | 319776 | 632832 | 0 | 232256 | 184550 | 15547 | 418628 | 811490 | 189000 | 0 | 379504 | 4062636 | 0 | 4072073 | 0 | 3989736 | 0 | 8704872 | 0 | 38580 | 3726000 | 0 | 1194810 | 185338 | 1143475 | 0 | 2662537.5 | 0 | 28358.88 | 1159920 | 4539 | 0 | 5389000 | 2742000 | 2685980 | 0 | 7330909.09 | 26805818.18 | 309600 | 167835296.65 | 342830979.54

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13309.84 | MW | 12:00 Hr. | Energy Generated |  |  | 342.831 |  | MKWHr.
| Day Peak Demand |  |  | 13333.88 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.63 |  | MKWHr.
| Evening Peak Generation |  |  | 15974.65 | MW | 21:00 Hr. | Energy Demand |  |  | 344.461 |  | MKWHr.
| Evening Peak Demand |  |  | 16021.65 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 12245.5 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1010.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 15994.84 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.2956 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.0666 | 0 | 13.9134 | 0 | 0 | 0.25455 | 0 | 0 | 53.2345 | Gas | 137.0133 | Gas | 493193604.3841
| Chattogram Zone |  |  | 5.6698 | 33.8073 | 4.8376 | 0 | 5.3017 | 0.16251 | 0 | 0.03264 | 49.8115 | Coal | 102.9572 | Coal | 614641950.3298
| Cumilla Zone |  |  | 24.7756 | 0 | 9.1895 | 0 | 0 | 0.44954 | 1.1386 | 0 | 35.5532 | HFO | 36.2405 | HFO | 663512645.474
| Mymensingh Zone |  |  | 3.1238 | 0 | 3.7988 | 0 | 0 | 0.23961 | 0 | 0 | 7.1623 | HSD | 2.6625 | HSD | 0
| Sylhet Zone |  |  | 29.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2342 | Hydro | 5.3017 | Hydro | 530168
| Khulna Zone |  |  | 8.886 | 25.8982 | 0 | 0 | 0 | 0.63792 | 23.1738 | 0 | 58.5959 | Solar | 4.7705 | Solar | 70516443.0548
| Barishal Zone |  |  | 5.428 | 39.5257 | 0.3096 | 0 | 0 | 0.004539 | 0 | 0 | 45.2678 | Import | 53.8527 | Import | 315439805.58
| Rajshahi Zone |  |  | 20.8293 | 0 | 1.8533 | 0 | 0 | 1.6482 | 29.5403 | 0 | 53.8711 | Wind | 0.03264 | Wind | 481113.6
| Rangpur Zone |  |  | 0 | 3.726 | 2.3383 | 2.6625 | 0 | 1.3736 | 0 | 0 | 10.1004
| Total |  |  | 137.0133 | 102.9572 | 36.2405 | 2.6625 | 5.3017 | 4.7705 | 53.8527 | 0.03264 | 342.831
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 493193604.3841 |  | Hydro | 530168
|  |  |  | Coal | 614641950.3298 |  | Solar | 70516443.0548
|  |  |  | HFO | 663512645.474 |  | Import | 315439805.58
|  |  |  | HSD | 0 |  | Wind | 481113.6
[5 empty] | Total: | 215,83,15,730 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2618 | Peak Hr Flow | 840.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41845927.38 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.5403 | Peak Hr Flow | 1446.75 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2388 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1386 | Peak Hr Flow | 54.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2622 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.9407 | Peak Hr Flow | 2340.75 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5404
|  |  |  | Chattogram |  | 0 |  | 1380
|  |  |  | Cumilla |  | 0 |  | 1547
|  |  |  | Mymensingh |  | 45 |  | 1266
|  |  |  | Sylhet |  | 0 |  | 710
|  |  |  | Khulna |  | 0 |  | 1913
|  |  |  | Barishal |  | 0 |  | 490
|  |  |  | Rajshahi |  | 0 |  | 1682
|  |  |  | Rangpur |  | 0 |  | 1060
|  |  |  | Total |  | 45 |  | 15452
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:59 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- st
| 08:59 |  | Ashuganj North CCPP ST was sync.
| 09:31 |  | Full interruption (around 495MW) occurred from 09:31 to 09:47 hrs under Bhaluka,
Mymensingh, Netrokona, Kishoreganj and Bajitpur substations due to the tripping of
Ashuganj-Bajitpur ckt-1 showing distance relay from Ashuganj end (NB: Ashuganj-Bajitpur
ckt-2 was under shut down condition). Now, no interruption is occurring.
| 09:32 | 09:50 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Tripped showing Line Diff. pro. relays Due | [7 empty] | 130.0MW load
|  |  | to OC/EF | [7 empty] | interrup.
| 09:35 | 09:47 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Tripped showing 86.1,86.2 relays Due to None | [7 empty] | 124.0MW load
interrup.
| 09:35 | 09:54 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Tripped showing 86.1,86.2 operated R,Y,B phase | [7 empty] | 124.0MW load
|  |  | relays. | [7 empty] | interrup.
| 09:35 | 21:25 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken by baharampur end.
| 09:40 | 17:31 | Patiya 132/33kV S/S TRAFO-02 LT Project Work S/D Due to Project work
| 09:41 | 17:29 | Patiya 132/33kV S/S TRAFO-02 HT Project Work S/D Due to Project work
| 09:44 | 09:48 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing No signal (
Instruction from NLDC) relays.
| 09:44 | 09:58 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing No signal (
Instruction from NLDC) relays.
| 09:46 | 09:59 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing No signal ( Instruction from
NLDC) relays.
| 09:46 | 09:59 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Tripped showing No signal ( operation by NLDC)
relays Due to No signal ( Instruction from NLDC)
| 10:36 | 10:50 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing D/R O/C & E/F Relay relays Due to Due to | [7 empty] | 48.0MW load
|  |  | PBS Boorpa feeder overcurrent fault. | [7 empty] | interrup.
| 10:36 | 16:17 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Bay Extension Work
| 10:36 | 16:16 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Bay Extension Work
|  | 10:47 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
|  | 10:50 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 10:52 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 10:57 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 11:31 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 11:46 |  | Ashuganj 225MW was shut down at 11:46 hrs for offline washing.
| 11:46 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 12:00 |  | Nutan Bidyut 230 kv bus - 2 was shut down due to project work (Piling work)
| 12:00 |  | Day Peak Generation 13306 MW.
| 13:14 | 13:33 | Sylhet (South) S/S Trafo-2 LT Tripped showing 86.1/2 , 50/51N optd. relays Due to fault | [7 empty] | 35.0MW load
|  |  | to connecting local grounding at moglabazar feeder. | [7 empty] | interrup.
| 14:02 | 15:08 | Bajitpur 132/33kV S/S Tr-2(414T) LT Scheduled S/D
|  | 16:01 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT is restored.
|  | 16:01 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT is restored.
| 19:41 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 21:20 | 21:26 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Tripped showing 50N/51N relays Due to 33 KV | [7 empty] | 19.0MW load
|  |  | Bironia feeder fault. | [7 empty] | interrup.
| 03:18 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT 2
| 03:24 | 03:50 | Thakurgaon 132/33kV S/S T-3(432T) HT Tripped showing N/A relays Due to 914B, 905B, 920B & | [7 empty] | 19.0MW load
|  |  | 923B Trip করে T-3 ওপেন হয়ে যায়। | [7 empty] | interrup.
| 03:24 | 03:50 | Thakurgaon 132/33kV S/S T-2(412T) HT Tripped showing N/A relays Due to 914B, 905B, 920B & | [7 empty] | 36.0MW load
|  |  | 923B Trip করে T-2 ওপেন হয়ে যায়। | [7 empty] | interrup.
| 03:24 | 03:50 | Thakurgaon 132/33kV S/S T-1(422T) HT Tripped showing N/A relays Due to 914B, 905B, 920B & | [7 empty] | 36.0MW load
|  |  | 923B Trip করে T-1 ওপেন হয়ে যায়। | [7 empty] | interrup.
| 03:24 | 04:19 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Tripped showing SIEMENS 7SA87 relays Due to 920 B | [7 empty] | 23.0MW load
|  |  | & 923B Trip | [7 empty] | interrup.
| 03:24 | 04:19 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Thakurgaon 132/33kV end showing Micom P442 | [7 empty] | 23.0MW load
|  |  | relays Due to 905 B & 920B Trip and from Panchagarh 132/33kV end showing MiCOM P442 | [7 empty] | interrup.
|  |  | (DISTANCE PROTECTION RELAY) relays. | [7 empty] | Thakurgaon 132/33kV
end and 48.0MW load
interrup.
Panchagarh 132/33kV
end
| 06:18 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 07:00 |  | Minimum Generation is 13253 MW
| 07:00 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized
| 07:45 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to High temperature
correction.
| 07:45 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to High temperature
minimize.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 331 | 8323200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7581500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 297 | 6965236 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 289467 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7475003 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.9 | 627840 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 121 | 1430880 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1007924 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 444859 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 480600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 433800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 269760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 2245887 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 138 | 2629584 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 1163520 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2234880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 254555 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 299160 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 7807272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1269600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2746.9 | 53234527.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 155125.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 139590 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 638880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5301680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5021814 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 47 | 444109 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 1285680 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1031088 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 301440 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 648000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22918 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 46 | 373020 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 300480 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 25091 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 62 | 282691 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1151 | 27523634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 32640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 260 | 6283636.36 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2225 | 49811517.16
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 137 | 2803000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 4716500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7800000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 27 | 665928 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 973440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 127 | 4048000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1203414 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1135781 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 421936 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2133270 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3010080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1138560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 452530 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 432050 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2236680 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1932480 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 449545 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1753 | 35553194
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 124 | 3123840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 39 | 864000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 2469600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 229060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 240240 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 225000 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 283 | 7162290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 69 | 1619640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3500182 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720384 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1967040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4494740 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 12 | 186168 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7529000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 9217000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1194 | 29234154
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 840 | 22261818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 369 | 8885952 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 637920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1230 | 25898180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2477 | 58595870
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 303 | 7330909.09 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2742000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1216 | 26805818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2685980 | GT-11 Shutdown under Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 309600 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5389000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4539 | -
Barishal Area Total |  |  |  |  | 2236 | 2075 | 45267846.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 418628 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 279381 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 184550 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 4062636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 167 | 4072073 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 165 | 3989736 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 349 | 8704872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 189000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 15547 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 232256 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 632832 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 319776 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446.75 | 29540280 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 379504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 811490 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2677.75 | 53871141
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 165 | 2662537.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 151 | 3726000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1143475 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28358.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1194810 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185338 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1159920 | -
Rangpur Area Total |  |  |  |  | 950 | 543 | 10100439.38
Eastern Grid Total |  |  |  |  | 17385.715 | 8201.9 | 174995682.89
Western Grid Total |  |  |  |  | 10444.16 | 7772.75 | 167835296.65
National Grid Total |  |  |  |  | 27829.875 | 15974.65 | 342830979.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-09-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10262.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5144.6 | MW
i) Dhaka area |  |  | 5404.02 |  | MW | i) Khulna area |  |  |  | 1913 | MW
ii) Chattogram area |  |  | 1380.5 |  | MW | ii) Barishal area |  |  |  | 490 | MW
iii) Cumilla area |  |  | 1547.06 |  | MW | iii) Rajshahi area |  |  |  | 1681.6 | MW
iv) Mymensingh area |  |  | 1221 |  | MW | iv) Rangpur area |  |  |  | 1060 | MW
v) Sylhet area |  |  | 710 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15407.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 87 | 20:00 | 133 | PHP | 9 | 02:00
2 | AKSML | 109 | 10:00 | 68 | Ishurdi | 86 | 19:00 | 134 | Pabna | 138 | 19:00
3 | Aftabnagar | 46 | 23:00 | 69 | Jaldhaka | 88 | 00:00 | 135 | Palashbari | 136 | 19:00
4 | Agargaon | 144 | 23:00 | 70 | Jamalpur | 132 | 05:00 | 136 | Panchagarh | 64 | 00:00
5 | Agrabad | 90 | 20:00 | 71 | Jashore | 155 | 19:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 34 | 22:00 | 72 | Jhenaidah | 143 | 19:00 | 138 | Patuakhali | 76.2 | 23:00
7 | Ashuganj | 99 | 23:00 | 73 | Joydebpur | 160 | 22:00 | 139 | Payra | 38 | 00:00
8 | BSRM | 136 | 23:00 | 74 | Joypurhat | 77 | 20:00 | 140 | Postogola | 59 | 23:00
9 | Bagerhat | 86 | 19:30 | 75 | Juldah | 15 | 23:00 | 141 | Purbachal | 25 | 23:00
10 | Bajitpur | 98 | 21:00 | 76 | KSRM | 17 | 00:00 | 142 | Purbasadipur | 132 | 21:00
11 | Bakulia | 92 | 23:00 | 77 | Kabirpur | 241 | 20:00 | 143 | Rahanpur | 43 | 22:00
12 | Banani | 38.8 | 18:30 | 78 | Kachua | 110 | 00:00 | 144 | Rahim | 11 | 09:00
13 | Bangabhaban | 7 | 12:00 | 79 | Kallyanpur | 120 | 23:00 | 145 | Rajbari | 91 | 23:00
14 | Barapukuria | 72 | 20:00 | 80 | Kalurghat | 32 | 23:00 | 146 | Rajendrapur | 129 | 23:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 70 | 18:30 | 147 | Rajshahi | 115 | 21:00
16 | Barishal | 117 | 23:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 108 | 22:00
17 | Barishal-230 | 102 | 18:30 | 83 | Kasba | 38 | 00:00 | 149 | Ramganj | 106 | 19:00
18 | Baroaulia | 60 | 00:00 | 84 | Kazla | 117 | 19:30 | 150 | Rampur | 45 | 23:00
19 | Baroirhat | 73 | 14:00 | 85 | Keranigonj | 99 | 22:00 | 151 | Rangamati | 18 | 19:00
20 | Bashundhara | 205 | 20:00 | 86 | Khagrachori | 34 | 20:00 | 152 | Rangpur | 158 | 18:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulna | 63 | 18:30 | 153 | Ruppur | 7.4 | 11:00
22 | Beanibazar | 90 | 18:30 | 88 | Khulshi | 171 | 12:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 72 | 21:00 | 89 | Kishoreganj | 140 | 21:00 | 155 | Saidpur | 111 | 19:00
24 | Bhaluka | 148 | 19:30 | 90 | Kodda | 280 | 19:00 | 156 | Satkhira | 132 | 22:00
25 | Bhandaria | 55 | 20:00 | 91 | Kulaura | 58 | 19:00 | 157 | Satmasjid | 114 | 00:00
26 | Bhangura | 42 | 19:00 | 92 | Kurigram | 71 | 19:30 | 158 | Savar | 227 | 15:00
27 | Bheramara(GK) | 71 | 19:00 | 93 | Kushtia | 160 | 19:00 | 159 | SevenRings | 11.81 | 00:00
28 | Bhulta | 202 | 09:00 | 94 | Laksam | 45 | 00:00 | 160 | ShahCement | 31 | 01:00
29 | Bog-Sherpur | 80 | 19:00 | 95 | Lakshmipur | 41 | 23:00 | 161 | Shahjadpur | 94 | 20:00
30 | Bogura | 186 | 19:30 | 96 | Lalbag | 51 | 13:00 | 162 | Shahjibazar | 137 | 23:00
31 | Borhanuddin | 92 | 00:00 | 97 | Lalmonirhat | 65 | 01:00 | 163 | Shahmirpur | 64 | 23:00
32 | Brahmanbaria | 142 | 23:00 | 98 | MI_Cement | 16.3 | 02:00 | 164 | Shariatpur | 99 | 23:00
33 | Cantonment | 149 | 23:00 | 99 | Madanganj | 38 | 18:30 | 165 | Sherpur | 152 | 00:00
34 | Chandina | 25.19 | 01:00 | 100 | Madaripur | 123 | 00:00 | 166 | Shikalbaha | 8 | 00:00
35 | Chandpur | 92 | 10:00 | 101 | Madartek | 95 | 23:00 | 167 | Shitalakhya | 73.8 | 13:00
36 | Chandraghona | 38 | 18:30 | 102 | Madunaghat | 56 | 23:00 | 168 | Sholosohor | 43 | 18:30
37 | Chapai | 76 | 22:00 | 103 | Magura | 73 | 19:00 | 169 | Shyampur | 176 | 10:00
38 | Charsaidpur | 36 | 01:00 | 104 | Mahasthangarh | 86 | 00:00 | 170 | Siddhirganj | 105 | 21:00
39 | Chauddagram | 79 | 00:00 | 105 | Maijdee | 13 | 05:00 | 171 | Sirajganj | 122 | 22:00
40 | Chhatak | 46 | 20:00 | 106 | Manikganj | 128 | 00:00 | 172 | Sonargaon | 123 | 14:00
41 | Chowmuhani | 191 | 19:00 | 107 | Maniknagar | 62 | 23:00 | 173 | Sreemongol | 93 | 21:00
42 | Chuadanga | 121 | 19:00 | 108 | Matarbari | 53 | 22:00 | 174 | Sreepur | 107 | 16:00
43 | Coxsbazar | 140 | 21:00 | 109 | Matuail | 76 | 16:00 | 175 | Srinagar | 55.45 | 22:00
44 | Cumilla(N) | 152 | 23:00 | 110 | Millgate | 113 | 15:00 | 176 | Sunamganj | 64 | 20:00
45 | Cumilla(S) | 166 | 18:30 | 111 | Mirpur | 134 | 18:30 | 177 | Sylhet | 56 | 23:00
46 | Daganbhuiyan | N/A | N/A | 112 | Mirsorai | 8 | 00:00 | 178 | Sylhet-132 | 139 | 17:00
47 | Daudkandi | 154 | 19:00 | 113 | Mirzapur | 41 | 00:00 | 179 | TK | 36 | 00:00
48 | Dhaka | 50 | 16:00 | 114 | Mithapukur | 80 | 19:30 | 180 | Tangail | 184 | 23:00
49 | Dhamrai | 134 | 20:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 20:00
50 | Dhanmondi | 116 | 18:30 | 116 | Mogbazar | 100 | 16:00 | 182 | Thakurgaon | 113 | 01:00
51 | Dohazari | 118 | 19:00 | 117 | Mongla | 32 | 00:00 | 183 | Tongi | 104 | 23:00
52 | Faridpur | 186 | 20:00 | 118 | Motijheel | 43 | 20:00 | 184 | Ullahpara | 43 | 20:00
53 | Fatullah | 107 | 16:00 | 119 | Muktagacha | 38 | 21:00 | 185 | Ullon | 65 | 23:00
54 | Fenchuganj | 51 | 18:30 | 120 | Munshiganj | 122 | 23:00 | 186 | Uttara | 94 | 18:30
55 | Feni | 129 | 19:00 | 121 | Muradnagar | 46 | 21:00 | 187 | UttaraNew | 72 | 23:00
56 | GPH | 6 | 19:00 | 122 | Mymensingh | 204 | 21:00 | 188 | Zigatola | 82 | 23:00
57 | Ghatail | 94 | 20:00 | 123 | Naogaon | 157 | 23:00
58 | Ghorashal | 16 | 20:00 | 124 | Narail | 64 | 19:00
59 | Ghorashal-230 | 102 | 22:00 | 125 | Narinda | 58 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 196 | 22:00
61 | Gollamari | 98 | 13:00 | 127 | Natore | 164 | 23:00
62 | Gopalganj | 118 | 22:00 | 128 | Nawabganj | 68.4 | 22:00
63 | Gulshan | 102 | 13:00 | 129 | Netrakona | 152 | 19:00
64 | Halishahar | 49 | 12:00 | 130 | New | 68.4 | 12:00
65 | HaripurSBU | 146 | 19:00 | 131 | Niamatpur | 85 | 22:00
66 | Hasnabad | 76 | 23:00 | 132 | Noapara | 47 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15344.7 | 54 |  | 15401.13
1:00 | 14978.84 | 117 |  | 15101.11
2:00 | 14577.16 | 109 |  | 14691.07
3:00 | 14193.58 | 103 |  | 14301.22
4:00 | 13908.12 | 89 |  | 14001.13
5:00 | 13691.87 | 75 |  | 13770.25
6:00 | 13071.6 | 49 |  | 13122.81
7:00 | 13001.03 | 22 |  | 13024.02
8:00 | 12680.19 | 0 |  | 12680.19
9:00 | 12740.59 | 0 |  | 12740.59
10:00 | 12245.5 | 0 |  | 12245.5
11:00 | 12736.24 | 0 |  | 12736.24
12:00 | 13309.84 | 23 |  | 13333.88
13:00 | 13763.1 | 41 |  | 13806.1
14:00 | 13871.2 | 52 |  | 13925.2
15:00 | 13848.08 | 100 |  | 13952.08
16:00 | 13865.03 | 114 |  | 13984.03
17:00 | 13638.61 | 80 |  | 13722.61
18:00 | 13268.8 | 51 |  | 13321.8
19:00 | 15488.9 | 155 |  | 15650.9
19:30 | 15876.5 | 128 |  | 16010.5
20:00 | 15916.5 | 90 |  | 16010.5
21:00 | 15974.65 | 45 |  | 16021.65
22:00 | 15764.3 | 102 |  | 15871.3
23:00 | 15994.84 | 159 |  | 16160.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7764.8 | 7579.9 | 15344.7 | DAILY GENERATION CURVE
00:30 | 7675.65 | 7486.12 | 15161.77
01:00 | 7586.5 | 7392.34 | 14978.84 | 06-09-2025
01:30 | 7493.1 | 7284.9 | 14778
02:00 | 7399.7 | 7177.46 | 14577.16
02:30 | 7242.75 | 7142.62 | 14385.37
03:00 | 7085.8 | 7107.78 | 14193.58
03:30 | 7013.65 | 7037.2 | 14050.85
04:00 | 6941.5 | 6966.62 | 13908.12
04:30 | 6932 | 6867.995 | 13799.995
05:00 | 6922.5 | 6769.37 | 13691.87
05:30 | 6832.86 | 6548.875 | 13381.735
06:00 | 6743.22 | 6328.38 | 13071.6
06:30 | 6727.605 | 6308.71 | 13036.315
07:00 | 6711.99 | 6289.04 | 13001.03
07:30 | 6624.17 | 6216.44 | 12840.61
08:00 | 6536.35 | 6143.84 | 12680.19
08:30 | 6504.375 | 6206.015 | 12710.39
09:00 | 6472.4 | 6268.19 | 12740.59
09:30 | 6283.8 | 6209.245 | 12493.045
10:00 | 6095.2 | 6150.3 | 12245.5
10:30 | 6243.41 | 6247.46 | 12490.87
11:00 | 6391.62 | 6344.62 | 12736.24
11:30 | 6532.565 | 6490.475 | 13023.04
12:00 | 6673.51 | 6636.33 | 13309.84
12:30 | 6766.24 | 6770.23 | 13536.47
13:00 | 6858.97 | 6904.13 | 13763.1
13:30 | 6915.985 | 6901.165 | 13817.15
14:00 | 6973 | 6898.2 | 13871.2
14:30 | 7042.49 | 6817.15 | 13859.64
15:00 | 7111.98 | 6736.1 | 13848.08
15:30 | 7130.29 | 6726.265 | 13856.555
16:00 | 7148.6 | 6716.43 | 13865.03
16:30 | 7150.67 | 6601.15 | 13751.82
17:00 | 7152.74 | 6485.87 | 13638.61
17:30 | 7105.68 | 6348.025 | 13453.705
18:00 | 7058.62 | 6210.18 | 13268.8
18:30 | 7554.26 | 6824.59 | 14378.85
19:00 | 8049.9 | 7439 | 15488.9
19:30 | 8069.5 | 7807 | 15876.5
20:00 | 8115.5 | 7801 | 15916.5
20:30 | 8158.7 | 7786.875 | 15945.575 |  | Executive Engineer
21:00 | 8201.9 | 7772.75 | 15974.65 |  | Network Operation Division
21:30 | 8153.8 | 7715.675 | 15869.475
22:00 | 8105.7 | 7658.6 | 15764.3
22:30 | 8164.55 | 7715.02 | 15879.57
23:00 | 8223.4 | 7771.44 | 15994.84

## En-Curve
QF-LDC-12
Date | 06-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3532 | 2038.5 | 926 | 38 | 56 | 1447.7 | 220 | 4674.2 | 0 | 609 | 1803.3 | 0 | 0 | 0 | 54 | DAILY ENERGY CURVE
00:30 | 3532 | 1977.5 | 926.5 | 38 | 54 | 1446.02 | 219.5 | 4666.1 | 0 | 562.5 | 1689.65 | 50 | 0 | 0 | 85.5 | 06-09-2025
01:00 | 3532 | 1916.5 | 927 | 38 | 52 | 1444.34 | 219 | 4658 | 0 | 516 | 1576 | 100 | 0 | 0 | 117
01:30 | 3513.5 | 1905.5 | 926.5 | 38 | 52 | 1446.9 | 219 | 4650 | 0 | 435.5 | 1491.1 | 100 | 0 | 0 | 113 | Energy Generated | 342.831 |  | MKWHr
02:00 | 3495 | 1894.5 | 926 | 38 | 52 | 1449.46 | 219 | 4642 | 0 | 355 | 1406.2 | 100 | 0 | 0 | 109 | Energy not Served | 1.63 |  | MKWHr
02:30 | 3486 | 1902 | 926 | 38 | 51 | 1449.62 | 219 | 4637.5 | 0 | 344 | 1232.25 | 100 | 0 | 0 | 106 | Total Energy Requirement | 344.461 |  | MKWHr
03:00 | 3477 | 1909.5 | 926 | 38 | 50 | 1449.78 | 219 | 4633 | 0 | 333 | 1058.3 | 100 | 0 | 0 | 103
03:30 | 3570.5 | 1924 | 926.5 | 38 | 50 | 1448.2 | 219 | 4548.5 | 0 | 333 | 893.15 | 100 | 0 | 0 | 96
04:00 | 3664 | 1938.5 | 927 | 38 | 50 | 1446.62 | 219 | 4464 | 0 | 333 | 728 | 100 | 0 | 0 | 89
04:30 | 3694 | 1926 | 926.5 | 38 | 49 | 1447.495 | 219.5 | 4377 | 0 | 328.5 | 693.5 | 100.5 | 0 | 0 | 82
05:00 | 3724 | 1913.5 | 926 | 38 | 48 | 1448.37 | 220 | 4290 | 0 | 324 | 659 | 101 | 0 | 0 | 75
05:30 | 3637.5 | 1905.5 | 926.5 | 38 | 47 | 1362.02 | 220 | 4167 | 3.715 | 324.5 | 649.5 | 100.5 | 0 | 0 | 62
06:00 | 3551 | 1897.5 | 927 | 38 | 46 | 1275.67 | 220 | 4044 | 7.43 | 325 | 640 | 100 | 0 | 0 | 49
06:30 | 3534 | 1899 | 926.5 | 38 | 44 | 1271.18 | 220.5 | 3995.5 | 53.135 | 314 | 640.5 | 100 | 0 | 0 | 35.5
07:00 | 3517 | 1900.5 | 926 | 38 | 42 | 1266.69 | 221 | 3947 | 98.84 | 303 | 641 | 100 | 0 | 0 | 22
07:30 | 3499.5 | 1893.5 | 926 | 38 | 41 | 1211.23 | 221.5 | 3862.5 | 174.38 | 263 | 610 | 100 | 0 | 0 | 11
08:00 | 3482 | 1886.5 | 926 | 38 | 40 | 1155.77 | 222 | 3778 | 249.92 | 223 | 579 | 100 | 0 | 0 | 0
08:30 | 3490 | 1892.5 | 926.5 | 38 | 40 | 1132.675 | 222 | 3729 | 357.215 | 200 | 582.5 | 100 | 0 | 0 | 0
09:00 | 3498 | 1898.5 | 927 | 38 | 40 | 1109.58 | 222 | 3680 | 464.51 | 177 | 586 | 100 | 0 | 0 | 0
09:30 | 3426.5 | 1870.5 | 927 | 38 | 40 | 1063.535 | 222 | 3577 | 512.51 | 159 | 557 | 100 | 0 | 0 | 0
10:00 | 3355 | 1842.5 | 927 | 38 | 40 | 1017.49 | 222 | 3474 | 560.51 | 141 | 528 | 100 | 0 | 0 | 0
10:30 | 3486.5 | 1877.5 | 927 | 38 | 41 | 1019.9 | 222 | 3505 | 597.47 | 143 | 533.5 | 100 | 0 | 0 | 0
11:00 | 3618 | 1912.5 | 927 | 38 | 42 | 1022.31 | 222 | 3536 | 634.43 | 145 | 539 | 100 | 0 | 0 | 0
11:30 | 3597 | 1921.35 | 927 | 38 | 42 | 1023.02 | 221.5 | 3767 | 648.17 | 145 | 593 | 100 | 0 | 0 | 11.5
12:00 | 3576 | 1930.2 | 927 | 38 | 42 | 1023.73 | 221 | 3998 | 661.91 | 145 | 647 | 100 | 0 | 0 | 23
12:30 | 3663 | 1912.2 | 926.5 | 38 | 45 | 1023.73 | 220 | 4081.5 | 647.29 | 144.5 | 729.75 | 100 | 0 | 5 | 32
13:00 | 3750 | 1894.2 | 926 | 38 | 48 | 1023.73 | 219 | 4165 | 632.67 | 144 | 812.5 | 100 | 0 | 10 | 41
13:30 | 3784.5 | 1884.1 | 926 | 38 | 48 | 1023.865 | 218.5 | 4172.5 | 620.835 | 144 | 847.35 | 100 | 0 | 9.5 | 46.5
14:00 | 3819 | 1874 | 926 | 38 | 48 | 1024 | 218 | 4180 | 609 | 144 | 882.2 | 100 | 0 | 9 | 52
14:30 | 3854.5 | 1913 | 926 | 38 | 48 | 978 | 218 | 4249 | 496.44 | 144 | 886.2 | 100 | 0 | 8.5 | 76
15:00 | 3890 | 1952 | 926 | 38 | 48 | 932 | 218 | 4318 | 383.88 | 144 | 890.2 | 100 | 0 | 8 | 100
15:30 | 3903 | 1932.5 | 926.5 | 38 | 48 | 928 | 218 | 4324.5 | 334.555 | 152 | 946 | 100 | 0 | 5.5 | 107
16:00 | 3916 | 1913 | 927 | 38 | 48 | 924 | 218 | 4331 | 285.23 | 160 | 1001.8 | 100 | 0 | 3 | 114
16:30 | 3826 | 1899.5 | 926.5 | 38 | 46 | 926 | 218 | 4318.5 | 192.22 | 206 | 1053.6 | 100 | 0 | 1.5 | 97
17:00 | 3736 | 1886 | 926 | 38 | 44 | 928 | 218 | 4306 | 99.21 | 252 | 1105.4 | 100 | 0 | 0 | 80
17:30 | 3653 | 1871 | 926.5 | 38 | 44 | 925.5 | 218 | 4242.5 | 52.805 | 253 | 1129.4 | 100 | 0 | 0 | 65.5
18:00 | 3570 | 1856 | 927 | 38 | 44 | 923 | 218 | 4179 | 6.4 | 254 | 1153.4 | 100 | 0 | 0 | 51
18:30 | 3739.5 | 1890 | 926.5 | 38 | 48 | 1111 | 218 | 4292 | 3.2 | 416 | 1564.15 | 132.5 | 0 | 0 | 103
19:00 | 3909 | 1924 | 926 | 38 | 52 | 1299 | 218 | 4405 | 0 | 578 | 1974.9 | 165 | 0 | 0 | 155
19:30 | 3718 | 1918 | 926 | 38 | 52 | 1448 | 218 | 4547 | 0 | 637 | 2209.5 | 165 | 0 | 0 | 128
20:00 | 3850 | 1877 | 841 | 38 | 54 | 1448 | 220 | 4574 | 0 | 684 | 2164.5 | 165 | 0 | 1 | 90
20:30 | 3892.5 | 1879 | 840.5 | 38 | 54 | 1447.375 | 220 | 4581 | 0 | 682.5 | 2145.2 | 165 | 0 | 0.5 | 67.5
21:00 | 3935 | 1881 | 840 | 38 | 54 | 1446.75 | 220 | 4588 | 0 | 681 | 2125.9 | 165 | 0 | 0 | 45
21:30 | 3957 | 1896 | 825.5 | 38 | 54 | 1447.175 | 220 | 4589.5 | 0 | 623 | 2071.8 | 147.5 | 0 | 0 | 73.5
22:00 | 3979 | 1911 | 811 | 38 | 54 | 1447.6 | 220 | 4591 | 0 | 565 | 2017.7 | 130 | 0 | 0 | 102
22:30 | 3997.5 | 1929 | 861 | 38 | 55 | 1446.42 | 221 | 4596.1 | 0 | 563.5 | 2042.05 | 130 | 0 | 0 | 130.5
23:00 | 4016 | 1947 | 911 | 38 | 56 | 1445.24 | 222 | 4601.2 | 0 | 562 | 2066.4 | 130 | 0 | 0 | 159
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 370 | 15:00 | Payra | 414 | 06:00 | 409 | 00:00
Ashuganj | 400 | 6:00 | 372 | 14:00 | Rahanpur | 402 | 10:00 | 387 | 00:00
Bhulta | 388 | 17:00 | 369 | 12:00 | Rampal | 406 | 09:00 | 391 | 21:00
Bibiana | 385 | 08:00 | 378 | 15:00
BIPTC | 399 | 08:00 | 385 | 13:00
Bogura | 386 | 10:00 | 367 | 00:00
Gopalganj | 397 | 09:00 | 383 | 23:00
Kaliakoir | 372 | 06:00 | 361 | 12:00
Madunaghat | 391 | 10:00 | 385 | 15:00
Meghnaghat | 382 | 06:00 | 375 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 218 | 12:00 | Keranigonj | 222 | 06:00 | 216 | 12:00
AKSML | 230 | 09:00 | 223 | 00:00 | Khulna(S) | 233 | 09:00 | 217 | 23:00
Aminbazar | 226 | 05:00 | 219 | 15:00 | Madunaghat | 231 | 04:00 | 227 | 13:00
Ashuganj | 228 | 05:00 | 220 | 12:00 | Madunaghat-400 | 231 | 07:00 | 227 | 15:00
Ashuganj-400 | 230 | 6:00 | 217 | 14:00 | Maniknagar | 219 | 04:00 | 214 | 12:00
Baghabari | 234 | 06:00 | 226 | 00:00 | Meghnaghat | 227 | 05:00 | 221 | 12:00
Barapukuria | 225 | 18:30 | 213 | 00:00 | Meghnaghat-400 | 223 | 06:00 | 217 | 12:00
Barapukuria-230 | 225 | 18:00 | 214 | 0:00 | Mirsorai | 228 | 08:00 | 222 | 12:00
Barishal | 228 | 09:00 | 217 | 23:00 | Rajshahi | 233 | 09:00 | 220 | 00:00
Bheramara | 233 | 09:00 | 223 | 22:00 | Rampal | 232 | 09:00 | 218 | 21:00
Bhulta | 223 | 06:00 | 212 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 07:00 | 221 | 15:00 | Rampura | 221 | 06:00 | 208 | 12:00
BIPTC | 237 | 10:00 | 222 | 23:00 | Shikalbaha | 229 | 08:00 | 224 | 16:00
Bogura | 240 | 10:00 | 229 | 00:00 | Shyampur | 221 | 06:00 | 215 | 12:00
Bogura-400 | 240 | 10:00 | 229 | 00:00 | Siddhirganj | 220 | 03:00 | 217 | 13:00
Borhanuddin | 232 | 09:00 | 224 | 21:00 | Sirajgonj | 241 | 10:00 | 235 | 00:00
BSRM | 228 | 09:00 | 221 | 15:00 | Sreepur | 227 | 10:00 | 219 | 22:00
Cumilla(N) | 222 | 09:00 | 215 | 14:00 | Tongi | 225 | 10:00 | 217 | 13:00
Faridpur | 225 | 08:00 | 213 | 23:00
Fenchuganj | 228 | 10:00 | 221 | 02:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 224 | 06:00 | 214 | 12:00
Gopalganj | 227 | 09:00 | 217 | 22:00
GPH | 229 | 09:00 | 224 | 15:00
Haripur | 220 | 06:00 | 215 | 12:00
Hasnabad | 222 | 05:00 | 216 | 11:00
Hathazari | 229 | 07:00 | 220 | 15:00
Ishurdi | 236 | 09:00 | 225 | 22:00
Jhenaidah | 232 | 09:00 | 215 | 23:00
Kaliakoir | 230 | 06:00 | 222 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 126 | 12:00 | Lalmonirhat | 129 | 18:30 | 118 | 00:00
Agargaon | 135 | 06:00 | 130 | 12:00 | Madanganj | 128 | 00:00 | 125 | 12:00
Agrabad | 130 | 06:00 | 126 | 13:00 | Madaripur | 136 | 10:00 | 128 | 22:00
AKS | 129 | 08:00 | 125 | 14:00 | Madartek | 137 | 02:00 | 126 | 12:00
Aminbazar | 132 | 00:00 | 128 | 10:00 | Madunaghat | 131 | 05:00 | 128 | 14:00
Amnura | 136 | 10:00 | 126 | 18:00 | Magura | 136 | 10:00 | 122 | 22:00
Ashuganj | 140 | 10:00 | 134 | 12:00 | Mahasthangarh | 131 | 10:00 | 124 | 00:00
Bagerhat | 135 | 09:00 | 118 | 23:00 | Maijdee | 118 | 09:00 | 104 | 22:00
Bajitpur | 129 | 06:00 | 120 | 21:00 | Manikganj | 127 | 10:00 | 120 | 00:00
Bakulia | 132 | 08:00 | 127 | 13:00 | Maniknagar | 132 | 06:00 | 128 | 15:00
Banani | 135 | 04:00 | 126 | 12:00 | Matarbari | 117 | 09:00 | 106 | 19:00
Bangabhaban | 132 | 06:00 | 128 | 12:00 | Matuail | 129 | 07:00 | 125 | 15:00
Barapukuria | 137 | 18:30 | 125 | 00:00 | Millgate | 131 | 04:00 | 124 | 12:00
Barguna | 135 | 09:00 | 130 | 00:00 | Mirpur | 131 | 18:00 | 13 | 02:00
Barishal | 133 | 07:00 | 125 | 22:00 | Mirzapur | 131 | 06:00 | 124 | 18:30
Barishal-230 | 134 | 09:00 | 125 | 23:00 | Mithapukur | 131 | 18:30 | 122 | 00:00
Baroaulia | 130 | 00:00 | 127 | 13:00 | MI_Cement | 130 | 00:00 | 126 | 12:00
Baroirhat | 125 | 09:00 | 116 | 14:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 05:00 | 124 | 12:00 | Mogbazar | 137 | 06:00 | 128 | 12:00
BashundharaCement | 128 | 00:00 | 125 | 12:00 | Mongla | 136 | 09:00 | 122 | 00:00
Beanibazar | 127 | 08:00 | 120 | 21:00 | Motijheel | 132 | 06:00 | 128 | 12:00
Benapole | 134 | 09:00 | 117 | 23:00 | Muktagacha | 132 | 08:00 | 123 | 19:00
Bhaluka | 137 | 10:00 | 120 | 23:00 | Munshiganj | 130 | 01:00 | 125 | 12:00
Bhandaria | 129 | 09:00 | 116 | 23:00 | Muradnagar | 123 | 06:00 | 116 | 22:00
Bhangura | 134 | 06:00 | 128 | 00:00 | Mymensingh | 133 | 08:00 | 111 | 21:00
Bheramara | 137 | 09:00 | 132 | 00:00 | Naogaon | 131 | 10:00 | 120 | 22:00
Bheramara(GK) | 137 | 06:00 | 131 | 22:00 | Narail | 137 | 10:00 | 122 | 22:00
Bhulta | 123 | 02:00 | 119 | 12:00 | Narinda | 132 | 6:00 | 128 | 15:00
Bog-Sherpur | 133 | 10:00 | 126 | 22:00 | Narshingdi | 134 | 06:00 | 119 | 22:00
Bogura | 134 | 10:00 | 128 | 00:00 | Natore | 133 | 10:00 | 126 | 23:00
Bogura-230 | 135 | 10:00 | 128 | 02:00 | Nawabganj | 137 | 06:00 | 131 | 12:00
Brahmanbaria | 134 | 10:00 | 127 | 22:00 | Netrakona | 122 | 10:00 | 108 | 23:00
Cantonment | 135 | 07:00 | 130 | 12:00 | New | 132 | 17:00 | 125 | 12:00
Chandina | 127 | 09:00 | 121 | 15:00 | Niamatpur | 137 | 10:00 | 130 | 22:00
Chandpur | 126 | 09:00 | 119 | 10:00 | Noapara | 137 | 09:00 | 122 | 23:00
Chandraghona | 132 | 09:00 | 129 | 13:00 | Pabna | 138 | 00:00 | 128 | 19:00
Chapai | 137 | 17:00 | 127 | 22:00 | Palashbari | 128 | 17:00 | 124 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 06:00 | 126 | 12:00 | Panchagarh | 134 | 20:00 | 121 | 11:00
Chauddagram | 123 | 07:00 | 115 | 14:00 | Patiya | 129 | 01:00 | 126 | 13:00
Chhatak | 126 | 09:00 | 117 | 20:00 | Patuakhali | 136 | 19:30 | 132 | 00:00
Chowmuhani | 117 | 09:00 | 108 | 22:00 | Payra | 136 | 07:00 | 134 | 00:00
Chuadanga | 134 | 09:00 | 118 | 22:00 | PHP | 123 | 09:00 | 114 | 22:00
Coxsbazar | 117 | 09:00 | 106 | 21:00 | Postogola | 133 | 04:00 | 128 | 12:00
Cumilla(N) | 127 | 09:00 | 121 | 14:00 | Purbachal | 136 | 06:00 | 125 | 12:00
Cumilla(S) | 132 | 06:00 | 120 | 14:00 | Purbasadipur | 132 | 18:30 | 120 | 00:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Rahanpur | 138 | 10:00 | 132 | 00:00
Daudkandi | 123 | 18:00 | 115 | 14:00 | Rahanpur-400 | 138 | 11:00 | 133 | 00:00
Dhaka | 136 | 05:00 | 128 | 12:00 | Rahim | 129 | 05:00 | 126 | 16:00
Dhamrai | 132 | 06:00 | 124 | 15:00 | Rajbari | 132 | 08:00 | 124 | 22:00
Dhanmondi | 136 | 05:00 | 127 | 12:00 | Rajendrapur | 136 | 18:00 | 120 | 22:00
Dohazari | 126 | 18:00 | 121 | 12:00 | Rajshahi | 133 | 09:00 | 126 | 00:00
Faridpur | 133 | 06:00 | 126 | 23:00 | Rajshahi-230 | 133 | 09:00 | 126 | 22:00
Fatullah | 131 | 05:00 | 127 | 12:00 | Ramganj | 120 | 09:00 | 112 | 14:00
Fenchuganj | 134 | 08:00 | 130 | 18:00 | Rampur | 130 | 05:00 | 126 | 12:00
Feni | 123 | 08:00 | 114 | 14:00 | Rampura | 136 | 06:00 | 127 | 12:00
Ghatail | 128 | 07:00 | 120 | 22:00 | Rangamati | 131 | 18:00 | 128 | 12:00
Ghorashal | 135 | 01:00 | 130 | 00:00 | Rangpur | 130 | 17:00 | 123 | 00:00
Goalpara | 140 | 09:00 | 125 | 22:00 | Ruppur | 137 | 09:00 | 131 | 00:00
Gollamari | 139 | 09:00 | 127 | 22:00 | Saidpur | 133 | 18:30 | 120 | 00:00
Gopalganj | 136 | 09:00 | 125 | 23:00 | Satkhira | 137 | 09:00 | 120 | 22:00
Gopalganj-400 | 136 | 07:00 | 130 | 22:00 | Satmasjid | 135 | 06:00 | 130 | 00:00
Gulshan | 136 | 05:00 | 127 | 12:00 | Savar | 133 | 01:00 | 126 | 11:00
Halishahar | 131 | 06:00 | 127 | 12:00 | SevenRings | 135 | 18:30 | 129 | 11:00
Haripur | 129 | 06:00 | 126 | 12:00 | ShahCement | 129 | 00:00 | 126 | 12:00
HaripurSBU | 129 | 06:00 | 126 | 12:00 | Shahjadpur | 137 | 03:00 | 132 | 22:00
Hasnabad | 132 | 03:00 | 128 | 15:00 | Shahjibazar | 135 | 10:00 | 126 | 22:00
Hathazari | 133 | 05:00 | 128 | 21:00 | Shahmirpur | 131 | 03:00 | 127 | 12:00
Ishurdi | 138 | 09:00 | 132 | 00:00 | Shariatpur | 134 | 09:00 | 124 | 23:00
Jaldhaka | 130 | 15:00 | 116 | 00:00 | Sherpur | 129 | 07:00 | 116 | 19:00
Jamalpur | 131 | 14:00 | 118 | 19:00 | Shikalbaha | 120 | 02:00 | 117 | 22:00
Jashore | 136 | 09:00 | 120 | 19:00 | Shikalbaha-230 | 132 | 06:00 | 129 | 12:00
Jhenaidah | 138 | 10:00 | 120 | 23:00 | Shitalakhya | 138 | 01:00 | 126 | 12:00
Jhenaidah-230 | 138 | 09:00 | 126 | 22:00 | Sholosohor | 131 | 09:00 | 128 | 12:00
Joydebpur | 135 | 17:00 | 122 | 11:00 | Shyampur | 131 | 18:30 | 127 | 00:00
Joypurhat | 126 | 07:00 | 116 | 22:00 | Shyampur-230 | 132 | 06:00 | 128 | 12:00
Juldah | 131 | 05:00 | 127 | 21:00 | Siddhirganj | 129 | 05:00 | 126 | 12:00
Kabirpur | 135 | 02:00 | 123 | 12:00 | Sirajganj | 132 | 10:00 | 124 | 22:00
Kachua | 127 | 09:00 | 119 | 14:00 | Sonargaon | 127 | 04:00 | 123 | 15:00
Kaliakoir | 137 | 02:00 | 128 | 12:00 | Sreemongol | 133 | 10:00 | 123 | 00:00
Kallyanpur | 132 | 18:00 | 129 | 15:00 | Sreepur | 132 | 10:00 | 125 | 22:00
Kalurghat | 131 | 18:00 | 128 | 12:00 | Srinagar | 136 | 06:00 | 131 | 15:00
Kamrangirchar | 137 | 08:00 | 131 | 12:00 | SSM | 132 | 09:00 | 130 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 10:00 | 116 | 00:00
Kasba | 124 | 18:00 | 117 | 15:00 | Sylhet | 128 | 10:00 | 122 | 00:00
Kazla | 132 | 06:00 | 128 | 13:00 | Sylhet-132 | 128 | 09:00 | 123 | 23:00
Keranigonj | 137 | 06:00 | 131 | 12:00 | Tangail | 128 | 06:00 | 120 | 19:00
Khagrachori | 130 | 06:00 | 126 | 13:00 | Taraganj | 131 | 18:30 | 120 | 00:00
Khulna | 138 | 09:00 | 125 | 22:00 | Thakurgaon | 133 | 18:30 | 119 | 12:00
Khulna(S) | 140 | 09:00 | 127 | 22:00 | TK | 131 | 03:00 | 128 | 12:00
Khulshi | 129 | 07:00 | 125 | 12:00 | Tongi | 132 | 07:00 | 128 | 11:00
Kishoreganj | 126 | 06:00 | 117 | 12:00 | Ullahpara | 133 | 10:00 | 127 | 02:00
Kodda | 135 | 17:00 | 122 | 11:00 | Ullon | 135 | 05:00 | 127 | 12:00
KSRM | 132 | 09:00 | 127 | 14:00 | Uttara | 132 | 03:00 | 126 | 11:00
Kulaura | 133 | 08:00 | 128 | 00:00 | UttaraNew | 131 | 01:00 | 126 | 11:00
Kurigram | 129 | 18:30 | 115 | 00:00 | Zigatola | 139 | 04:00 | 132 | 12:00
Kushtia | 134 | 09:00 | 125 | 23:00
Laksam | 126 | 18:00 | 117 | 22:00
Lakshmipur | 118 | 09:00 | 102 | 22:00
Lalbag | 136 | 09:00 | 131 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division