## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-09-2025 | during | 09-09-2025 | during | 09-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 382 | 334 | 400.75 | 400.75 | 382 | 382 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 300 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 330 | 335 | 335 | 334 | 334 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 5 | 65 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 51.4 | 46.6 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 105 | 123 | 133 | 133 | 112 | 112 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.4 | 21 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 23 | 23 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 293 | 65 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 91 | 103 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 51 | 87.5 | 87.5 | 34 | 51 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 156 | 149 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 330 | 340 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 52 | 160 | 160 | 52 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2736.8 | 2551.6 | 5812.54 | 5778.54 | 3697 | 3753
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 40 | 96 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 75 | 0 | 0 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 65 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 21 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | Maintenance Shutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.56 | 0 | 4.23 | 0 | 4.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 19 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 13 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 150 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 545 | 983 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 262 | 262 | 255 | 255 | 255 | 255 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1453.56 | 2234 | 3108.95 | 3119.72 | 2917.59 | 2965.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 193 | 199 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 342 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 37 | 46.7 | 46.7 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 44 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 70 | 33 | 195 | 195 | 142 | 142 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 120 | 130 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 36 | 47 | 47 | 47 | 47 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 182 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 52 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 74 | 89 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1643 | 1797 | 2434.56 | 2379.56 | 2083.36 | 2028.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-09-2025 | during | 09-09-2025 | during | 09-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 70 | 71 | 157.5 | 157.5 | 127 | 127 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 38 | 38 | 32 | 32 | 32 | 32 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 93 | 102 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.79 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 261.79 | 240 | 421.9 | 375 | 343.9 | 297
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 69 | 68 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 12 | 12 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 390 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1193 | 1200 | 1260 | 1260 | 1183 | 1183
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 862 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 19 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 41 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 232 | 131 | 410 | 410 | 364 | 364 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1189 | 1175 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2483 | 2266 | 3644.2 | 3546.2 | 3403.2 | 3305.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 304 | 305 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 60 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1145 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 140 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.75 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2062.75 | 2296 | 2162 | 2161 | 2132 | 2131
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 61.02 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 150 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 150 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 150 | 220 | 220 | 220 | 220 | Low gas pressure
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 362 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.95 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1215 | 1366.43 | 748 | 748 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.18 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2390.15 | 2654.43 | 2500.64 | 2333.99 | 3115.14 | 2948.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 66 | 66 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 176 | 174 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 72 | 0 | 130.05 | 0 | 130.05 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 389.5 | 517 | 628.65 | 462 | 628.65 | 462
System Total |  |  |  |  | 28823.2 | 27829.875 | 14613.55 | 15756.03 | 21973.44 | 21416.01 | 19503.84 | 19073.41
Forecast Scenario (09-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16100 |  | 0 |  | 16100
|  |  |  | 1:00 | 15730 |  | 0 |  | 15730
|  |  |  | 2:00 | 15220 |  | 0 |  | 15220
|  |  |  | 3:00 | 14630 |  | 0 |  | 14630
|  |  |  | 4:00 | 14270 |  | 0 |  | 14270
|  |  |  | 5:00 | 14030 |  | 0 |  | 14030
|  |  |  | 6:00 | 13640 |  | 0 |  | 13640
|  |  |  | 7:00 | 13610 |  | 0 |  | 13610
|  |  |  | 8:00 | 13570 |  | 0 |  | 13570
|  |  |  | 9:00 | 13840 |  | 0 |  | 13840
|  |  |  | 10:00 | 14140 |  | 0 |  | 14140
|  |  |  | 11:00 | 14260 |  | 0 |  | 14260
|  |  |  | 12:00 | 14890 |  | 0 |  | 14890
|  |  |  | 13:00 | 15100 |  | 0 |  | 15100
|  |  |  | 14:00 | 14970 |  | 0 |  | 14970
|  |  |  | 15:00 | 15020 |  | 0 |  | 15020
|  |  |  | 16:00 | 14750 |  | 0 |  | 14750
|  |  |  | 17:00 | 14350 |  | 0 |  | 14350
|  |  |  | 18:00 | 14550 |  | 0 |  | 14550
|  |  |  | 18:30 | 15500 |  | 0 |  | 15500
|  |  |  | 19:00 | 16240 |  | 0 |  | 16240
|  |  |  | 19:30 | 16300 |  | 0 |  | 16300
|  |  |  | 20:00 | 16350 |  | 0 |  | 16350
|  |  |  | 21:00 | 16400 |  | 0 |  | 16400
|  |  |  | 22:00 | 16300 |  | 0 |  | 16300
|  |  |  | 23:00 | 16200 |  | 0 |  | 16200
Probable Maximum Temperature: |  |  | 33.10°C
Probable Maximum Demand at Day Peak: |  |  | 14890.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 358.16 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:37 hrs on 09-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-09-2025 | [28 empty] | Date: | 08-09-2025 | [28 empty] | Date: | 08-09-2025 | [28 empty] | Date: | 08-09-2025 | [28 empty] | Date: | 08-09-2025 | [14 empty] | Date: | 08-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 46.3 | 17 | 149 | 125 | 195 | 30 | 55 | 150 | 0 | 300 | 296 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 35 | 26 | 15 | 0 | 330 | 13 | 0 | 0 | 0 | 0 | 66 | 65 | 0 | 12 | 12 | 0 | 222 | 110 | 15 | 260 | 80 | 0 | 19 | 17 | 95 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 125 | 35 | 0 | 350 | 330 | 45 | 199 | 40 | 90 | 90 | 190 | 0 | 19 | 114 | 54 | 43 | 0 | 37 | 315 | 0 | 390 | 0 | 69 | 156 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 100 | 29 | 93 | 0 | 0 | 12 | 8222.3 | 916 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 0 | 1459 | 0 | 40 | 0 | 0 | 50 | 0 | 92 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 194 | 0 | 189 | 0 | 188 | 0 | 360 | 0 | 0 | 172 | 49 | 114 | 0 | 113 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 305 | 1100 | 63 | 7693 | 15915.3 | 108.17
01:00 | 7 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 45.3 | 0 | 149 | 125 | 195 | 30 | 55 | 144 | 0 | 300 | 284 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 17 | 25 | 15 | 0 | 330 | 13 | 0 | 0 | 0 | 0 | 66 | 52 | 0 | 12 | 12 | 0 | 222 | 110 | 21 | 260 | 45 | 0 | 19 | 17 | 92 | 219 | 0 | 0 | 0 | 1130 | 0 | 51 | 125 | 35 | 0 | 355 | 330 | 45 | 186 | 40 | 90 | 90 | 142 | 0 | 19 | 114 | 52 | 8 | 0 | 37 | 305 | 0 | 360 | 0 | 70 | 151 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 98 | 0 | 0 | 12 | 7954.3 | 917 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 1453 | 0 | 40 | 0 | 0 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 14 | 0 | 0 | 185 | 0 | 183 | 0 | 183 | 0 | 330 | 0 | 0 | 173 | 49 | 114 | 0 | 113 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 220 | 0 | 305 | 1090 | 60 | 7544 | 15498.3 | 108.2
02:00 | 7 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 44.5 | 0 | 149 | 124 | 145 | 0 | 55 | 143 | 0 | 300 | 289 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 52 | 0 | 12 | 12 | 0 | 220 | 51 | 25 | 260 | 15 | 0 | 19 | 17 | 91 | 219 | 0 | 0 | 0 | 1142 | 0 | 51 | 125 | 35 | 0 | 355 | 330 | 45 | 191 | 37 | 91 | 90 | 104 | 0 | 19 | 114 | 50 | 8 | 0 | 37 | 310 | 0 | 360 | 0 | 70 | 151 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 103 | 29 | 102 | 0 | 0 | 12 | 7746.5 | 917 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 183 | 0 | 183 | 0 | 338 | 0 | 0 | 171 | 49 | 114 | 0 | 113 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 305 | 1091 | 0 | 7307 | 15053.5 | 108.23
03:00 | 7 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 44.2 | 0 | 149 | 90 | 0 | 0 | 55 | 142 | 0 | 300 | 287 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 52 | 0 | 12 | 12 | 0 | 218 | 0 | 28 | 260 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 80 | 35 | 0 | 354 | 330 | 45 | 191 | 37 | 90 | 90 | 103 | 0 | 19 | 114 | 50 | 8 | 0 | 37 | 305 | 0 | 365 | 0 | 70 | 151 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 103 | 29 | 102 | 0 | 0 | 12 | 7313.2 | 917 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 182 | 0 | 182 | 0 | 340 | 0 | 0 | 172 | 49 | 35 | 0 | 34 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 305 | 1092 | 0 | 7155 | 14468.2 | 108.26
04:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 88 | 60 | 0 | 0 | 51 | 90 | 0 | 300 | 294 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0 | 218 | 0 | 31 | 260 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 30 | 35 | 0 | 355 | 330 | 45 | 191 | 37 | 91 | 90 | 103 | 0 | 19 | 114 | 48 | 8 | 0 | 30 | 305 | 0 | 366 | 0 | 70 | 150 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 103 | 29 | 102 | 0 | 0 | 12 | 7002 | 916 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 183 | 0 | 182 | 0 | 342 | 0 | 0 | 172 | 50 | 35 | 0 | 34 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 255 | 115 | 220 | 0 | 305 | 1091 | 0 | 7130 | 14132 | 108.29
05:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 49 | 30 | 0 | 0 | 17 | 63 | 0 | 300 | 296 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0 | 219 | 0 | 30 | 260 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 35 | 0 | 354 | 330 | 46 | 193 | 34 | 90 | 90 | 103 | 0 | 19 | 114 | 48 | 8 | 0 | 37 | 310 | 0 | 364 | 0 | 70 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 93 | 29 | 102 | 0 | 0 | 12 | 6853 | 916 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 1380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 184 | 0 | 184 | 0 | 346 | 0 | 0 | 172 | 49 | 35 | 0 | 34 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 218 | 115 | 220 | 0 | 305 | 1095 | 0 | 7046 | 13899 | 108.32
06:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 17 | 64 | 0 | 300 | 289 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0.08 | 220 | 0 | 31 | 261 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1130 | 1 | 51 | 0 | 35 | 0 | 357 | 330 | 45 | 187 | 34 | 91 | 90 | 103 | 0 | 19 | 88 | 44 | 8 | 2 | 37 | 305 | 0 | 364 | 0 | 70 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 84 | 29 | 103 | 0 | 0.89 | 12 | 6738.97 | 917 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1227 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 0 | 0 | 0 | 0 | 181 | 0 | 183 | 0 | 183 | 0 | 334 | 0 | 0.06 | 173 | 49 | 35 | 0 | 34 | 0 | 80 | 0 | 0 | 2 | 0 | 0 | 213 | 115 | 220 | 0 | 305 | 1095 | 0 | 6773.48 | 13512.45 | 108.35
07:00 | 0 | 51 | 2 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 17 | 62 | 0 | 300 | 284 | 0 | 0 | 0 | 331 | 0 | 0 | 7 | 17 | 26 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 12 | 12 | 0.7 | 221 | 0 | 16 | 261 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1132 | 4 | 51 | 0 | 35 | 0 | 355 | 330 | 45 | 184 | 28 | 90 | 90 | 104 | 0 | 19 | 52 | 42 | 8 | 11 | 37 | 305 | 0 | 321 | 0 | 70 | 149 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 84 | 29 | 93 | 0 | 5.76 | 12 | 6670.46 | 918 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 1210 | 0 | 1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 3.95 | 178 | 0 | 180 | 0 | 179 | 0 | 329 | 0 | 0.61 | 173 | 49 | 35 | 2 | 34 | 0 | 66 | 0 | 0.5 | 36 | 0.07 | 0 | 211 | 115 | 220 | 0 | 304 | 1090 | 0 | 6813.63 | 13484.09 | 108.38
08:00 | 0 | 51 | 22 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 51 | 59 | 0 | 0 | 17 | 35 | 0 | 300 | 289 | 0 | 0 | 0 | 330 | 0 | 0 | 16 | 17 | 22 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 1.72 | 220 | 0 | 2 | 260 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1156 | 9 | 51 | 0 | 35 | 0 | 350 | 330 | 45 | 192 | 30 | 76 | 90 | 103 | 0 | 19 | 52 | 40 | 8 | 19 | 37 | 305 | 0 | 316 | 0 | 69 | 136 | 0 | 0 | 79 | 30 | 0 | 0 | 166 | 0 | 84 | 29 | 94 | 1 | 25.6 | 12 | 6623.32 | 924 | 263 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1099 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.27 | 51 | 0 | 0 | 6.01 | 182 | 0 | 182 | 0 | 181 | 0 | 343 | 0 | 2.9 | 174 | 50 | 35 | 4 | 34 | 0 | 66 | 0 | 0 | 55 | 0.3 | 0 | 166 | 115 | 220 | 0 | 305 | 1100 | 0 | 6783.48 | 13406.8 | 108.4
09:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 52 | 29 | 0 | 0 | 28 | 94 | 0 | 300 | 294 | 0 | 0 | 0 | 330 | 0 | 0 | 25 | 35 | 22 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 12 | 12 | 2.6 | 220 | 0 | 2 | 260 | 0 | 0 | 18 | 0 | 0 | 219 | 0 | 0 | 0 | 1156 | 15 | 51 | 0 | 35 | 0 | 348 | 330 | 45 | 194 | 33 | 73 | 90 | 103 | 0 | 19 | 52 | 40 | 8 | 57 | 37 | 310 | 0 | 336 | 0 | 69 | 144 | 0 | 0 | 79 | 30 | 0 | 0 | 166 | 0 | 93 | 29 | 81 | 2 | 17.4 | 12 | 6803 | 923 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 1103 | 0 | 1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.21 | 78 | 0 | 0 | 7.85 | 185 | 0 | 189 | 0 | 178 | 0 | 361 | 0 | 0.82 | 174 | 50 | 0 | 10 | 0 | 0 | 66 | 0 | 1 | 123 | 0.28 | 0 | 171 | 115 | 220 | 0 | 305 | 1110 | 0 | 6877.16 | 13680.16 | 108.42
10:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 25 | 0 | 71 | 29 | 50 | 4 | 55 | 142 | 0 | 300 | 303 | 0 | 0 | 15 | 331 | 0 | 0 | 32 | 35 | 21 | 15 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 3.34 | 221 | 0 | 2 | 260 | 15 | 0 | 32 | 1 | 0 | 217 | 0 | 0 | 0 | 1161 | 10 | 43 | 16 | 35 | 0 | 341 | 330 | 44 | 210 | 33 | 73 | 90 | 104 | 0 | 19 | 52 | 40 | 8 | 63 | 37 | 315 | 0 | 336 | 0 | 69 | 150 | 0 | 0 | 79 | 30 | 0 | 0 | 166 | 0 | 93 | 29 | 71 | 2 | 31.34 | 12 | 7091.68 | 924 | 254 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 1110 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7 | 96 | 0 | 0 | 51.78 | 176 | 0 | 181 | 0 | 170 | 0 | 379 | 0 | 5.11 | 174 | 50 | 0 | 13 | 0 | 0 | 66 | 0 | 2.2 | 115 | 0.23 | 0 | 166 | 115 | 220 | 0 | 305 | 1111 | 0 | 6901.02 | 13992.7 | 108.44
11:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 49.6 | 14 | 85 | 86 | 245 | 42 | 55 | 143 | 0 | 300 | 304 | 0 | 0 | 35 | 327 | 0 | 0 | 30 | 17 | 19 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 12 | 0 | 2.23 | 221 | 3 | 2 | 260 | 53 | 0 | 43 | 15 | 15 | 215 | 0 | 0 | 0 | 566 | 16 | 43 | 87 | 35 | 0 | 340 | 330 | 43 | 206 | 33 | 74 | 90 | 105 | 0 | 19 | 17 | 40 | 8 | 74 | 36 | 315 | 0 | 388 | 0 | 69 | 149 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 93 | 38 | 70 | 1 | 42.97 | 12 | 7046.8 | 925 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 1121 | 0 | 1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.01 | 112 | 0 | 0 | 30.6 | 173 | 0 | 168 | 0 | 166 | 0 | 387 | 0 | 2.56 | 172 | 51 | 0 | 19 | 0 | 0 | 66 | 0 | 5.5 | 113 | 0.7 | 0 | 231 | 115 | 220 | 0 | 304 | 1111 | 0 | 7036.37 | 14083.17 | 108.46
12:00 | 5 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 51.4 | 17 | 91 | 105 | 293 | 55 | 55 | 156 | 0 | 350 | 299 | 0 | 0 | 55 | 327 | 0 | 0 | 34 | 17 | 23.4 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 12 | 0 | 4.56 | 172 | 19 | 4 | 262 | 35 | 0 | 46 | 17 | 40 | 214 | 0 | 0 | 0 | 545 | 18 | 51 | 120 | 70 | 0 | 342 | 330 | 41 | 193 | 33 | 74 | 90 | 104 | 0 | 19 | 17 | 42 | 8 | 74 | 35 | 320 | 0 | 369 | 0 | 69 | 158 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 93 | 38 | 70 | 2 | 46.79 | 12 | 7288.15 | 924 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 1189 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.02 | 115 | 0 | 0 | 51.18 | 177 | 0 | 172 | 0 | 192 | 0 | 405 | 0 | 1.95 | 176 | 51 | 0 | 19 | 0 | 0 | 66 | 0 | 5.5 | 72 | 0.75 | 0 | 278 | 115 | 220 | 0 | 304 | 1145 | 0 | 7325.4 | 14613.55 | 108.5
13:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 49.3 | 26 | 110 | 122 | 293 | 55 | 55 | 162 | 0 | 420 | 299 | 0 | 0 | 55 | 320 | 0 | 0 | 33 | 17 | 21 | 15 | 0 | 330 | 1 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 12 | 0 | 1.79 | 172 | 33 | 11 | 266 | 35 | 0 | 50 | 17 | 49 | 214 | 0 | 0 | 0 | 558 | 18 | 51 | 118 | 97 | 0 | 340 | 330 | 41 | 200 | 34 | 75 | 90 | 103 | 0 | 19 | 17 | 44 | 10 | 59 | 36 | 315 | 0 | 385 | 0 | 69 | 156 | 0 | 0 | 83 | 30 | 0 | 0 | 167 | 0 | 84 | 38 | 69 | 2 | 16.42 | 12 | 7467.51 | 925 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 96 | 1200 | 0 | 1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.76 | 115 | 0 | 0 | 24.44 | 175 | 0 | 177 | 0 | 202 | 0 | 406 | 0 | 5.8 | 175 | 50 | 0 | 18 | 0 | 0 | 50 | 0 | 5.9 | 29 | 0.8 | 0 | 275 | 115 | 220 | 0 | 303 | 1222 | 0 | 7361.7 | 14829.21 | 108.56
14:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 48.2 | 35 | 114 | 122 | 294 | 55 | 55 | 162 | 0 | 320 | 299 | 0 | 0 | 35 | 320 | 0 | 0 | 11 | 17 | 7 | 15 | 0 | 345 | 13 | 0 | 0 | 0 | 4 | 65 | 51 | 0 | 12 | 0 | 2.09 | 220 | 32 | 5 | 266 | 35 | 0 | 50 | 17 | 49 | 214 | 0 | 0 | 0 | 601 | 3 | 51 | 118 | 98 | 0 | 344 | 330 | 44 | 203 | 36 | 71 | 90 | 103 | 0 | 19 | 17 | 46 | 10 | 63 | 36 | 320 | 0 | 362 | 0 | 68 | 152 | 0 | 0 | 83 | 30 | 0 | 0 | 167 | 13 | 91 | 38 | 70 | 2 | 16.98 | 12 | 7426.27 | 924 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 88 | 1187 | 0 | 1294.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.43 | 67 | 0 | 0 | 4.37 | 166 | 0 | 185 | 0 | 200 | 0 | 372 | 0 | 0.39 | 176 | 50 | 0 | 32 | 0 | 0 | 50 | 0 | 3.6 | 49 | 0.63 | 0 | 277 | 115 | 220 | 0 | 304 | 1222 | 0 | 7285.11 | 14711.38 | 108.64
15:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 51.4 | 35 | 114 | 30 | 294 | 55 | 54 | 162 | 0 | 320 | 286 | 0 | 0 | 35 | 325 | 0 | 0 | 9 | 17 | 23 | 15 | 0 | 350 | 15 | 0 | 0 | 0 | 4 | 65 | 51 | 0 | 12 | 0 | 2.76 | 220 | 39 | 6 | 260 | 35 | 0 | 50 | 17 | 59 | 212 | 0 | 0 | 0 | 610 | 4 | 51 | 120 | 107 | 0 | 335 | 330 | 43 | 206 | 36 | 69 | 90 | 103 | 0 | 19 | 17 | 46 | 10 | 50 | 36 | 320 | 0 | 390 | 0 | 68 | 155 | 0 | 0 | 83 | 30 | 0 | 0 | 167 | 17 | 84 | 38 | 70 | 0 | 5.99 | 12 | 7373.15 | 924 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1228 | 0 | 1337.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.26 | 28 | 0 | 0 | 3.2 | 185 | 0 | 177 | 0 | 180 | 0 | 398 | 0 | 0.28 | 168 | 52 | 0 | 21 | 0 | 0 | 66 | 0 | 3.2 | 51 | 0 | 0 | 290 | 115 | 220 | 0 | 303 | 1222 | 0 | 7280.35 | 14653.5 | 108.66
16:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 48.9 | 17 | 65 | 30 | 65 | 55 | 55 | 162 | 0 | 320 | 289 | 0 | 0 | 35 | 325 | 0 | 0 | 5 | 17 | 25 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 4 | 65 | 67 | 0 | 12 | 0 | 1.84 | 220 | 50 | 5 | 260 | 35 | 0 | 50 | 17 | 78 | 214 | 0 | 0 | 0 | 612 | 3 | 51 | 117 | 60 | 0 | 349 | 330 | 42 | 188 | 36 | 69 | 90 | 103 | 0 | 19 | 17 | 44 | 14 | 21 | 36 | 310 | 0 | 358 | 0 | 67 | 153 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 17 | 101 | 29 | 70 | 0 | 16.24 | 12 | 6975.98 | 924 | 174 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 1224 | 0 | 1372.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.15 | 20 | 0 | 0 | 6.27 | 186 | 0 | 173 | 0 | 150 | 0 | 327 | 0 | 0.57 | 173 | 52 | 0 | 16 | 0 | 0 | 66 | 0 | 2.6 | 28 | 0.33 | 0 | 261 | 115 | 220 | 0 | 305 | 1214 | 0 | 7111.53 | 14087.51 | 108.66
17:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 47.3 | 17 | 33 | 30 | 65 | 55 | 55 | 157 | 0 | 320 | 291 | 0 | 0 | 35 | 270 | 0 | 0 | 4 | 17 | 28 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 0 | 65 | 67 | 0 | 12 | 0 | 0 | 221 | 51 | 15 | 260 | 35 | 0 | 50 | 17 | 82 | 214 | 0 | 0 | 0 | 630 | 1 | 51 | 120 | 33 | 0 | 300 | 280 | 43 | 210 | 36 | 68 | 90 | 103 | 0 | 19 | 17 | 42 | 16 | 3 | 36 | 315 | 0 | 368 | 0 | 67 | 146 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 2.85 | 12 | 6787.15 | 924 | 163 | 0 | 7 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 1224 | 0 | 1366.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 7 | 0 | 0 | 7.55 | 180 | 0 | 150 | 0 | 150 | 0 | 358 | 0 | 0.74 | 175 | 52 | 0 | 5 | 0 | 0 | 66 | 0 | 1.3 | 17 | 0.04 | 0 | 276 | 115 | 220 | 0 | 305 | 1188 | 0 | 7021.56 | 13808.71 | 108.66
18:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 44.5 | 17 | 45 | 30 | 65 | 55 | 55 | 141 | 0 | 320 | 291 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 17 | 28 | 15 | 0 | 330 | 13 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 0 | 0 | 222 | 48 | 11 | 260 | 35 | 0 | 50 | 17 | 74 | 214 | 0 | 0 | 0 | 890 | 0 | 51 | 128 | 33 | 0 | 300 | 280 | 44 | 186 | 37 | 68 | 90 | 168 | 0 | 19 | 110 | 44 | 12 | 0 | 36 | 300 | 0 | 361 | 0 | 67 | 148 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 38 | 71 | 0 | 0.21 | 12 | 7143.71 | 924 | 151 | 0 | 18 | 12 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1136 | 0 | 1354.4 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 12 | 2 | 0.05 | 0 | 12 | 0 | 0.19 | 175 | 0 | 150 | 0 | 150 | 0 | 333 | 0 | 0.03 | 172 | 50 | 0 | 1 | 0 | 0 | 66 | 0 | 0.1 | 3 | 0 | 0 | 271 | 115 | 220 | 0 | 305 | 1180 | 2 | 6908.77 | 14052.48 | 108.66
19:00 | 16 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 48.2 | 17 | 101 | 123 | 65 | 55 | 55 | 155 | 0 | 350 | 299 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 52 | 27 | 15 | 0 | 345 | 15 | 0 | 0 | 0 | 0 | 66 | 74 | 0 | 12 | 0 | 0 | 222 | 51 | 22 | 265 | 160 | 0 | 50 | 17 | 91 | 215 | 0 | 0 | 0 | 922 | 0 | 51 | 130 | 33 | 0 | 345 | 330 | 44 | 202 | 37 | 81 | 90 | 179 | 0 | 19 | 114 | 48 | 43 | 0 | 36 | 315 | 0 | 390 | 0 | 67 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 38 | 71 | 0 | 0 | 12 | 7932.2 | 926 | 138 | 0 | 22 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1364.15 | 0 | 43 | 0 | 100 | 60 | 0 | 92 | 35 | 35 | 0 | 0 | 28 | 0 | 0 | 171 | 0 | 150 | 0 | 150 | 0 | 377 | 0 | 0 | 175 | 51 | 109 | 0 | 108 | 0 | 66 | 0 | 0 | 0 | 0 | 29 | 277 | 115 | 220 | 0 | 305 | 1180 | 54 | 7624.15 | 15556.35 | 108.66
19:30 | 58 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 46.2 | 17 | 102 | 123 | 65 | 55 | 55 | 147 | 0 | 350 | 297 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 52 | 28 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 0 | 66 | 70 | 0 | 12 | 0 | 0 | 222 | 49 | 17 | 270 | 160 | 0 | 50 | 17 | 92 | 216 | 0 | 0 | 0 | 925 | 0 | 51 | 130 | 33 | 0 | 348 | 330 | 44 | 192 | 37 | 90 | 90 | 179 | 0 | 19 | 114 | 50 | 43 | 0 | 36 | 310 | 0 | 365 | 0 | 67 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 38 | 71 | 0 | 0 | 12 | 7914.2 | 925 | 131 | 0 | 19 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1376.59 | 0 | 47 | 0 | 108 | 108 | 0 | 92 | 35 | 43 | 0 | 0 | 28 | 0 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 345 | 0 | 0 | 173 | 51 | 109 | 0 | 108 | 0 | 66 | 0 | 0 | 0 | 0 | 48 | 276 | 115 | 220 | 0 | 305 | 1180 | 137 | 7749.59 | 15663.79
20:00 | 65 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 46.6 | 17 | 103 | 123 | 65 | 55 | 55 | 149 | 0 | 350 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 52 | 21 | 15 | 0 | 340 | 13 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 12 | 0 | 0 | 222 | 50 | 21 | 262 | 150 | 0 | 50 | 17 | 96 | 217 | 0 | 0 | 0 | 983 | 0 | 51 | 130 | 33 | 0 | 348 | 330 | 44 | 199 | 37 | 89 | 90 | 182 | 0 | 19 | 114 | 52 | 43 | 0 | 36 | 310 | 0 | 390 | 0 | 68 | 155 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 38 | 71 | 0 | 0 | 12 | 8022.6 | 862 | 131 | 0 | 19 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 1366.43 | 0 | 47 | 0 | 113 | 106 | 0 | 92 | 38 | 52 | 0 | 0 | 28 | 0 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 362 | 0 | 0 | 174 | 50 | 114 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 60 | 276 | 115 | 220 | 0 | 305 | 1180 | 140 | 7733.43 | 15756.03 | 108.66
21:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 50.7 | 17 | 50 | 124 | 65 | 55 | 55 | 159 | 0 | 350 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 52 | 26 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 12 | 0 | 0 | 222 | 51 | 22 | 261 | 90 | 0 | 50 | 17 | 103 | 217 | 0 | 0 | 0 | 1099 | 0 | 51 | 125 | 33 | 0 | 348 | 330 | 45 | 199 | 37 | 91 | 90 | 183 | 0 | 19 | 114 | 50 | 43 | 0 | 36 | 315 | 0 | 388 | 0 | 68 | 156 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 8003.7 | 857 | 113 | 0 | 19 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 1280.49 | 0 | 47 | 0 | 113 | 92 | 0 | 92 | 38 | 52 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 351 | 0 | 0 | 178 | 50 | 114 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 64 | 276 | 115 | 220 | 0 | 305 | 1180 | 139 | 7559.49 | 15563.19 | 108.67
22:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 46.3 | 17 | 34 | 124 | 65 | 55 | 55 | 148 | 0 | 350 | 298 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 125 | 20 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 12 | 0 | 0 | 222 | 48 | 25 | 262 | 126 | 0 | 50 | 17 | 94 | 218 | 0 | 0 | 0 | 1192 | 0 | 51 | 125 | 41 | 0 | 351 | 330 | 45 | 190 | 34 | 89 | 90 | 184 | 0 | 19 | 114 | 54 | 52.2 | 0 | 36 | 310 | 0 | 384 | 0 | 69 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 8136.5 | 857 | 110 | 0 | 19 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1177 | 0 | 1211.87 | 0 | 47 | 0 | 113 | 92 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 175 | 50 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 64 | 276 | 115 | 220 | 0 | 305 | 1222 | 133 | 7483.87 | 15620.37 | 108.67
23:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 45.6 | 17 | 34 | 94 | 65 | 55 | 55 | 141 | 0 | 350 | 304 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 142 | 26 | 15 | 0 | 330 | 15 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 12 | 0 | 0 | 222 | 52 | 31 | 262 | 126 | 0 | 50 | 17 | 94 | 218 | 0 | 0 | 0 | 1226 | 0 | 51 | 127 | 43 | 0 | 348 | 330 | 45 | 199 | 34 | 83 | 90 | 180 | 0 | 19 | 114 | 56 | 52.2 | 0 | 36 | 310 | 0 | 390 | 0 | 69 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 8177.8 | 919 | 104 | 0 | 19 | 31 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1104.86 | 0 | 47 | 0 | 113 | 108 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 169 | 50 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 80 | 277 | 115 | 220 | 0 | 305 | 1222 | 140 | 7474.86 | 15652.66 | 108.68
Total KWH | 194544 | 1154880 | 454560 | 0 | 0 | 0 | 0 | 0 | 8460000 | 0 | 0 | 855000 | 297360 | 1859472 | 1832160 | 2482745 | 810421 | 1151624 | 3163680 | 0 | 7975000 | 7119796 | 0 | 0 | 814624 | 7786549 | 0 | 0 | 211904 | 793200 | 570600 | 360000 | 0 | 8043636.36 | 198218 | 0 | 0 | 0 | 14880 | 1436865 | 880076 | 0 | 285120 | 116160 | 24398 | 5150356 | 829673 | 373440 | 6327272.73 | 1119055 | 0 | 839520 | 272368.8 | 1339018 | 5233466 | 0 | 0 | 0 | 22887270 | 90585 | 1227488 | 2181236 | 1120727 | 0 | 8597400 | 7892000 | 1057440 | 4793000 | 846000 | 1937280 | 2148940 | 3036480 | 0 | 443660 | 1789800 | 1120320 | 457642 | 516873 | 872576 | 7580500 | 0 | 9210000 | 0 | 1605600 | 3646964 | 0 | 0 | 1957440 | 718080 | 0 | 0 | 3431460 | 256320 | 2277600 | 770400 | 1868160 | 10800 | 258410 | 298560 | 177738652.89 | 22161455 | 5036832 | 0 | 121920 | 162048 | 912000 | 0 | 0 | 0 | 0 | 0 | 722880 | 28356360 | 0 | 30582225 | 0 | 284816 | 0 | 624576 | 629280 | 0 | 659520 | 225198 | 265507 | 396443 | 752620 | 144171 | 0 | 177752 | 4192273 | 0 | 4245282 | 0 | 4339891 | 0 | 8659709 | 0 | 19440 | 4241000 | 1154181 | 1132345 | 172785 | 1120560 | 0 | 1634850 | 0 | 33995.64 | 718560 | 4656 | 362592 | 6131000 | 2756000 | 5404870 | 0 | 7323636.36 | 27949090.91 | 819600 | 174631919.91 | 352370572.8

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14613.55 | MW | 12:00 Hr. | Energy Generated |  |  | 352.3706 |  | MKWHr.
| Day Peak Demand |  |  | 14794.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.979 |  | MKWHr.
| Evening Peak Generation |  |  | 15756.03 | MW | 20:00 Hr. | Energy Demand |  |  | 358.3496 |  | MKWHr.
| Evening Peak Demand |  |  | 16300.19 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.1 |  | °C
| Minimum Generation of the Day |  |  | 13406.8 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1002 |  | MMCFD
| Maximum Generation of the Day |  |  | 15915.3 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.5382 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.3156 | 0 | 15.8643 | 0 | 0 | 0.2119 | 0 | 0 | 56.3918 | Gas | 138.7022 | Gas | 497186893.8012
| Chattogram Zone |  |  | 5.6069 | 29.2145 | 7.3161 | 0 | 5.1504 | 0.11498 | 0 | 0.01488 | 47.4177 | Coal | 104.3698 | Coal | 625109049.5583
| Cumilla Zone |  |  | 28.1267 | 0 | 10.275 | 0 | 0 | 0.51687 | 1.1203 | 0 | 40.0389 | HFO | 43.6104 | HFO | 799466669.074
| Mymensingh Zone |  |  | 1.8682 | 0 | 3.6029 | 0 | 0 | 0.26921 | 0 | 0 | 5.7402 | HSD | 1.6348 | HSD | 0
| Sylhet Zone |  |  | 28.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.15 | Hydro | 5.1504 | Hydro | 515035.6
| Khulna Zone |  |  | 5.0368 | 28.3564 | 0.28397 | 0 | 0 | 0.72288 | 23.0735 | 0 | 57.4735 | Solar | 4.1121 | Solar | 59759511.8044
| Barishal Zone |  |  | 8.1609 | 41.4037 | 1.1822 | 0 | 0 | 0.004656 | 0 | 0 | 50.7514 | Import | 54.776 | Import | 321602459.1
| Rajshahi Zone |  |  | 21.4372 | 0 | 2.8331 | 0 | 0 | 1.3463 | 30.5822 | 0 | 56.1987 | Wind | 0.01488 | Wind | 219331.2
| Rangpur Zone |  |  | 0 | 5.3952 | 2.2529 | 1.6348 | 0 | 0.92534 | 0 | 0 | 10.2083
| Total |  |  | 138.7022 | 104.3698 | 43.6104 | 1.6348 | 5.1504 | 4.1121 | 54.776 | 0.01488 | 352.3706
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 497186893.8012 |  | Hydro | 515035.6
|  |  |  | Coal | 625109049.5583 |  | Solar | 59759511.8044
|  |  |  | HFO | 799466669.074 |  | Import | 321602459.1
|  |  |  | HSD | 0 |  | Wind | 219331.2
[5 empty] | Total: | 230,38,58,950 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1615 | Peak Hr Flow | 862.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54558399.19 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.5822 | Peak Hr Flow | 1366.43 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2296 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1203 | Peak Hr Flow | 52.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2904 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.864 | Peak Hr Flow | 2280.43 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 180 |  | 5591
|  |  |  | Chattogram |  | 15 |  | 1492
|  |  |  | Cumilla |  | 85 |  | 1502
|  |  |  | Mymensingh |  | 135 |  | 1187
|  |  |  | Sylhet |  | 58 |  | 650
|  |  |  | Khulna |  | 0 |  | 1949
|  |  |  | Barishal |  | 0 |  | 476
|  |  |  | Rajshahi |  | 0 |  | 1704
|  |  |  | Rangpur |  | 0 |  | 1025
|  |  |  | Total |  | 473 |  | 15576
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:50 | Pabna 132/33kV S/S T-1 HT is restored.
|  | 08:50 | Pabna 132/33kV S/S T-1 LT is restored.
| 09:01 | 10:29 | BIPTC S/S 20D09C 20MVA LT Forced S/D Due to Shutdown is taken for emergency maintenance
work on neutral grounding
|  | 09:40 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
| 09:59 | 13:43 | Amnura 132/33kV S/S Amnura - 100MW PPP Scheduled S/D Due to Redhot at Chapainawabganj
100MW line bay.
| 10:20 |  | SS Power Tripped with remarks:- Unit-1 / Generator protection fault
| 10:21 |  | SS Power Synchronized with remarks:- Running U-2
|  | 10:45 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
|  | 10:46 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
| 11:01 | 11:52 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to Red hot problem | [7 empty] | 50.0MW load interrup.
| 11:01 | 11:54 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to Red hot problem | [7 empty] | 50.0MW load interrup.
| 11:16 | 11:50 | BIPTC S/S 20DF22 Scheduled S/D Due to Shutdown is taken for maintenance work
| 12:00 |  | Day peak generation: 14614 MW
| 13:32 | 13:42 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing Dist protn rly relays. | [7 empty] | 10.0MW load interrup.
| 13:55 | 14:43 | Halishahar 132/33kV S/S 415T(TR-2) LT Forced S/D Due to Bpdp station Transformer R Phase
Blast. Now They are maintenance this phase and connection with 33kv TR-02 Secondary
Breaker. For this reason need to shutdown.
| 13:58 | 14:41 | Halishahar 132/33kV S/S 415T(TR-2) HT Forced S/D Due to Bpdp station Transformer R Phase
Blast. Now They are maintenance this phase and connection with 33kv TR-02 Secondary
Breaker. For this reason need to shutdown.
| 16:03 | 16:14 | Cumilla(S) 132/33kV S/S TR-1 LT Tripped showing REF615, RET650 relays Due to 33 KV Kosba | [7 empty] | 40.0MW load
|  |  | Palpara PDB feeder C.B trip | [7 empty] | interrup.
| 17:00 |  | SS Power Synchronized with remarks:- U-1
| 17:00 |  | SS Power Synchronized with remarks:- U-1
| 17:42 | 18:29 | Patuakhali 132/33kV S/S 425T (T-3) HT Forced S/D Due to 33kv bus red-hot Maintenance work. | [7 empty] | 40.0MW load interrup.
| 17:42 | 18:30 | Patuakhali 132/33kV S/S 425T (T-3) LT Forced S/D Due to 33kv bus red-hot Maintenance work. | [7 empty] | 40.0MW load interrup.
| 20:00 |  | Evening Peak Generation 15755 MW.
| 21:54 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 01:30 | 01:39 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing
quadramho relays.
| 01:30 | 01:39 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing
quadramho relays.
| 01:38 | 02:31 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT Forced S/D Due to Red-hot maintenance
at Biral-1, 33 kv Feeder
| 03:06 | 03:09 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing
quadramho relays.
| 05:36 |  | AKSML-Baroaulia 132kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to Emergency high
temperature maintenance at Hathazari ckt-1
| 05:53 |  | Baroaulia-Hathazari 132 kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to Emergency | [7 empty] | 72.0MW load
|  |  | high temperature maintenance | [7 empty] | interrup. Baroaulia
132/33kV end
| 07:00 |  | Min. Gen. 13406 MW
| 07:10 |  | Narail 132/33kV S/S TR1 (403-T) HT Project Work S/D Due to 33 kV Bus extension | [7 empty] | 20.0MW load interrup.
| 07:10 |  | Narail 132/33kV S/S TR1 (403-T) LT Project Work S/D Due to 33kV Bus extension works | [7 empty] | 20.0MW load interrup.
| 07:12 |  | Adani Power Jharkhand Ltd. Unit-1 was shut down due to coal shortage at 07:12 hrs.
| 07:14 |  | Adani unit-1 Shutdown.
| 07:34 |  | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to High temperature at HT bushing ( | [7 empty] | 45.0MW load interrup.
|  |  | Y phase) of T5 | [7 empty] | interrup.
| 07:34 |  | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to High temperature at HT bushing (Y phase) | [7 empty] | 45.0MW load interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 334 | 8460000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7975000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7119796 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 810421 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7786549 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 65 | 194544 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46.6 | 855000 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 1832160 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1151624 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 814624 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 570600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 360000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 454560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 65 | 2482745 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 103 | 1859472 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 1154880 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 149 | 3163680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 211904 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 297360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 8043636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 793200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2551.6 | 56391755.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 272368.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 90585 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 839520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5150356 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5233466 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 96 | 1339018 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 75 | 880076 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1436865 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 285120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 373440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 829673 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 116160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 198218 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 150 | 1119055 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 983 | 22887270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 14880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 262 | 6327272.73 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2234 | 47417741.53
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 199 | 4793000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8597400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7892000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 846000 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1057440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 33 | 1120727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1227488 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 2181236 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 872576 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2148940 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 182 | 3036480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 52 | 1120320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 457642 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 443660 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1789800 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1937280 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 516873 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1797 | 40038862
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1868160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 38 | 770400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 2277600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 258410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298560 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 256320 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 240 | 5740250
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1605600 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3646964 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718080 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1957440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 3431460 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7580500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 9210000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1200 | 28150044
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 862 | 22161455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 19 | 121920 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 41 | 162048 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 131 | 5036832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 722880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1175 | 28356360 | As per info no disruption in coal supply
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2266 | 57473495
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 305 | 7323636.36 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 60 | 362592 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2756000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 27949090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5404870 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 140 | 819600 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6131000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4656 | -
Barishal Area Total |  |  |  |  | 2236 | 2296 | 50751445.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 396443 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 284816 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 225198 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 4192273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 150 | 4245282 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 150 | 4339891 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 362 | 8659709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 144171 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 265507 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 659520 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 106 | 629280 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 624576 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1366.43 | 30582225 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 177752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 752620 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2654.43 | 56198703
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 66 | 1634850 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1154181 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 174 | 4241000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1120560 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33995.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1132345 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 172785 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 718560 | -
Rangpur Area Total |  |  |  |  | 950 | 517 | 10208276.64
Eastern Grid Total |  |  |  |  | 17385.715 | 8022.6 | 177738652.89
Western Grid Total |  |  |  |  | 10444.16 | 7733.43 | 174631919.91
National Grid Total |  |  |  |  | 27829.875 | 15756.03 | 352370572.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-09-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9948.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5152.7 | MW
i) Dhaka area |  |  | 5410.91 |  | MW | i) Khulna area |  |  |  | 1948.6 | MW
ii) Chattogram area |  |  | 1477 |  | MW | ii) Barishal area |  |  |  | 475.5 | MW
iii) Cumilla area |  |  | 1417.08 |  | MW | iii) Rajshahi area |  |  |  | 1703.6 | MW
iv) Mymensingh area |  |  | 1052 |  | MW | iv) Rangpur area |  |  |  | 1025 | MW
v) Sylhet area |  |  | 592 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15101.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 88 | 19:00 | 133 | PHP | 8 | 01:00
2 | AKSML | 127 | 12:00 | 68 | Ishurdi | 87 | 19:30 | 134 | Pabna | 142 | 19:00
3 | Aftabnagar | 44 | 13:00 | 69 | Jaldhaka | 90 | 19:00 | 135 | Palashbari | 122 | 00:00
4 | Agargaon | 149 | 12:00 | 70 | Jamalpur | 125 | 04:00 | 136 | Panchagarh | 67 | 19:00
5 | Agrabad | 106 | 15:00 | 71 | Jashore | 164 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 37 | 23:00 | 72 | Jhenaidah | 146 | 19:30 | 138 | Patuakhali | 78 | 22:00
7 | Ashuganj | 89 | 01:00 | 73 | Joydebpur | 169 | 12:00 | 139 | Payra | 38 | 23:00
8 | BSRM | 151 | 14:00 | 74 | Joypurhat | 68 | 00:00 | 140 | Postogola | 62 | 00:00
9 | Bagerhat | 86 | 21:00 | 75 | Juldah | 17 | 00:00 | 141 | Purbachal | 23 | 22:00
10 | Bajitpur | 101 | 22:00 | 76 | KSRM | 35 | 00:00 | 142 | Purbasadipur | 128 | 19:00
11 | Bakulia | 103 | 19:00 | 77 | Kabirpur | 274 | 11:00 | 143 | Rahanpur | 42 | 00:00
12 | Banani | 58.4 | 12:00 | 78 | Kachua | 102 | 00:00 | 144 | Rahim | 44 | 12:00
13 | Bangabhaban | 26 | 10:00 | 79 | Kallyanpur | 117 | 00:00 | 145 | Rajbari | 90 | 19:00
14 | Barapukuria | 71 | 19:00 | 80 | Kalurghat | 42 | 12:00 | 146 | Rajendrapur | 131 | 18:30
15 | Barguna | 24 | 21:00 | 81 | Kamrangirchar | 80 | 16:00 | 147 | Rajshahi | 118 | 00:00
16 | Barishal | 122 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 114 | 18:30
17 | Barishal-230 | 106 | 18:30 | 83 | Kasba | 38 | 00:00 | 149 | Ramganj | 96 | 02:00
18 | Baroaulia | 68 | 10:00 | 84 | Kazla | 107 | 12:00 | 150 | Rampur | 46 | 00:00
19 | Baroirhat | 70 | 00:00 | 85 | Keranigonj | 102 | 00:00 | 151 | Rangamati | 20 | 18:30
20 | Bashundhara | 220 | 12:00 | 86 | Khagrachori | 34 | 18:30 | 152 | Rangpur | 165 | 19:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 69 | 13:00 | 153 | Ruppur | 9.2 | 10:00
22 | Beanibazar | 82 | 00:00 | 88 | Khulshi | 182 | 22:00 | 154 | SSM | 14 | 23:00
23 | Benapole | 74 | 22:00 | 89 | Kishoreganj | 137 | 23:00 | 155 | Saidpur | 114 | 19:00
24 | Bhaluka | 122 | 18:30 | 90 | Kodda | 288 | 14:00 | 156 | Satkhira | 126 | 21:00
25 | Bhandaria | 60 | 23:00 | 91 | Kulaura | 54 | 18:30 | 157 | Satmasjid | 111 | 18:30
26 | Bhangura | 41 | 20:00 | 92 | Kurigram | 72 | 19:00 | 158 | Savar | 239 | 10:00
27 | Bheramara(GK) | 74 | 19:00 | 93 | Kushtia | 176 | 19:00 | 159 | SevenRings | 20.62 | 19:30
28 | Bhulta | 217 | 15:00 | 94 | Laksam | 35 | 00:00 | 160 | ShahCement | 32 | 08:00
29 | Bog-Sherpur | 82 | 19:00 | 95 | Lakshmipur | 40 | 18:30 | 161 | Shahjadpur | 98 | 20:00
30 | Bogura | 185 | 19:30 | 96 | Lalbag | 60 | 12:00 | 162 | Shahjibazar | 136 | 00:00
31 | Borhanuddin | 93 | 21:00 | 97 | Lalmonirhat | 70 | 18:30 | 163 | Shahmirpur | 65 | 00:00
32 | Brahmanbaria | 142 | 19:00 | 98 | MI_Cement | 13 | 01:00 | 164 | Shariatpur | 100 | 22:00
33 | Cantonment | 156 | 12:00 | 99 | Madanganj | 34 | 00:00 | 165 | Sherpur | 142 | 02:00
34 | Chandina | 17.42 | 21:00 | 100 | Madaripur | 133 | 22:00 | 166 | Shikalbaha | 15 | 14:00
35 | Chandpur | 93 | 19:00 | 101 | Madartek | 106 | 00:00 | 167 | Shitalakhya | 78.2 | 13:00
36 | Chandraghona | 38 | 19:00 | 102 | Madunaghat | 61 | 19:00 | 168 | Sholosohor | 51 | 15:00
37 | Chapai | 76 | 00:00 | 103 | Magura | 71 | 19:00 | 169 | Shyampur | 164 | 00:00
38 | Charsaidpur | 35 | 21:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 129 | 12:00
39 | Chauddagram | 77 | 00:00 | 105 | Maijdee | 16 | 00:00 | 171 | Sirajganj | 126 | 20:00
40 | Chhatak | 42 | 00:00 | 106 | Manikganj | 128 | 02:00 | 172 | Sonargaon | 132 | 23:00
41 | Chowmuhani | 185 | 00:00 | 107 | Maniknagar | 66 | 14:00 | 173 | Sreemongol | 88 | 23:00
42 | Chuadanga | 122 | 23:00 | 108 | Matarbari | 59 | 19:00 | 174 | Sreepur | 100 | 19:00
43 | Coxsbazar | 143 | 13:00 | 109 | Matuail | 77 | 16:00 | 175 | Srinagar | 53.54 | 22:00
44 | Cumilla(N) | 150 | 20:00 | 110 | Millgate | 136 | 12:00 | 176 | Sunamganj | 61 | 00:00
45 | Cumilla(S) | 159 | 18:30 | 111 | Mirpur | 131 | 12:00 | 177 | Sylhet | 52 | 00:00
46 | Daganbhuiyan | N/A | N/A | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 130 | 15:00
47 | Daudkandi | 148 | 00:00 | 113 | Mirzapur | 37 | 00:00 | 179 | TK | 38 | 20:00
48 | Dhaka | 96 | 12:00 | 114 | Mithapukur | 74 | 19:00 | 180 | Tangail | 168 | 20:00
49 | Dhamrai | 130 | 14:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 18:30
50 | Dhanmondi | 151 | 14:00 | 116 | Mogbazar | 117 | 13:00 | 182 | Thakurgaon | 117 | 19:00
51 | Dohazari | 116 | 19:30 | 117 | Mongla | 42 | 23:00 | 183 | Tongi | 124 | 09:00
52 | Faridpur | 192 | 22:00 | 118 | Motijheel | 49 | 12:00 | 184 | Ullahpara | 44 | 20:00
53 | Fatullah | 109 | 10:00 | 119 | Muktagacha | 36 | 03:00 | 185 | Ullon | 61 | 00:00
54 | Fenchuganj | 48 | 01:00 | 120 | Munshiganj | 119 | 00:00 | 186 | Uttara | 91 | 12:00
55 | Feni | 126 | 20:00 | 121 | Muradnagar | 42 | 00:00 | 187 | UttaraNew | 67 | 23:00
56 | GPH | 7 | 19:30 | 122 | Mymensingh | 206 | 22:00 | 188 | Zigatola | 77 | 00:00
57 | Ghatail | 82 | 03:00 | 123 | Naogaon | 148 | 20:00
58 | Ghorashal | 12 | 00:00 | 124 | Narail | 60 | 01:00
59 | Ghorashal-230 | 92 | 00:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 42 | 23:00 | 126 | Narshingdi | 185 | 00:00
61 | Gollamari | 114 | 23:00 | 127 | Natore | 164 | 19:00
62 | Gopalganj | 115 | 19:00 | 128 | Nawabganj | 60.8 | 00:00
63 | Gulshan | 142 | 12:00 | 129 | Netrakona | 140 | 23:00
64 | Halishahar | 72 | 09:00 | 130 | New | 76 | 10:00
65 | HaripurSBU | 169 | 15:00 | 131 | Niamatpur | 82 | 00:00
66 | Hasnabad | 77 | 23:00 | 132 | Noapara | 48 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15915.3 | 81 |  | 15999.95
1:00 | 15498.3 | 126 |  | 15630.3
2:00 | 15053.5 | 69 |  | 15125.5
3:00 | 14468.2 | 59 |  | 14530.2
4:00 | 14132 | 41 |  | 14175
5:00 | 13899 | 34 |  | 13935
6:00 | 13512.45 | 32 |  | 13545.89
7:00 | 13484.09 | 29 |  | 13514.4
8:00 | 13406.8 | 63 |  | 13472.64
9:00 | 13680.16 | 60 |  | 13742.86
10:00 | 13992.7 | 48 |  | 14042.86
11:00 | 14083.17 | 77 |  | 14163.64
12:00 | 14613.55 | 173 |  | 14794.34
13:00 | 14829.21 | 168 |  | 15004.77
14:00 | 14711.38 | 156 |  | 14874.4
15:00 | 14653.5 | 258 |  | 14923.11
16:00 | 14087.51 | 541 |  | 14652.51
17:00 | 13808.71 | 425 |  | 14252.71
18:00 | 14052.48 | 381 |  | 14450.48
19:00 | 15556.35 | 567 |  | 16149.35
19:30 | 15663.79 | 513 |  | 16199.79
20:00 | 15756.03 | 473 |  | 16250.03
21:00 | 15563.19 | 705 |  | 16300.19
22:00 | 15620.37 | 698 |  | 16349.37
23:00 | 15652.66 | 715 |  | 16399.66
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8222.3 | 7693 | 15915.3 | DAILY GENERATION CURVE
00:30 | 8088.3 | 7618.5 | 15706.8
01:00 | 7954.3 | 7544 | 15498.3 | 08-09-2025
01:30 | 7850.4 | 7425.5 | 15275.9
02:00 | 7746.5 | 7307 | 15053.5
02:30 | 7529.85 | 7231 | 14760.85
03:00 | 7313.2 | 7155 | 14468.2
03:30 | 7157.6 | 7142.5 | 14300.1
04:00 | 7002 | 7130 | 14132
04:30 | 6927.5 | 7088 | 14015.5
05:00 | 6853 | 7046 | 13899
05:30 | 6795.985 | 6909.74 | 13705.725
06:00 | 6738.97 | 6773.48 | 13512.45
06:30 | 6704.715 | 6793.555 | 13498.27
07:00 | 6670.46 | 6813.63 | 13484.09
07:30 | 6646.89 | 6798.555 | 13445.445
08:00 | 6623.32 | 6783.48 | 13406.8
08:30 | 6713.16 | 6830.32 | 13543.48
09:00 | 6803 | 6877.16 | 13680.16
09:30 | 6947.34 | 6889.09 | 13836.43
10:00 | 7091.68 | 6901.02 | 13992.7
10:30 | 7069.24 | 6968.695 | 14037.935
11:00 | 7046.8 | 7036.37 | 14083.17
11:30 | 7167.475 | 7180.885 | 14348.36
12:00 | 7288.15 | 7325.4 | 14613.55
12:30 | 7377.83 | 7343.55 | 14721.38
13:00 | 7467.51 | 7361.7 | 14829.21
13:30 | 7446.89 | 7323.405 | 14770.295
14:00 | 7426.27 | 7285.11 | 14711.38
14:30 | 7399.71 | 7282.73 | 14682.44
15:00 | 7373.15 | 7280.35 | 14653.5
15:30 | 7174.565 | 7195.94 | 14370.505
16:00 | 6975.98 | 7111.53 | 14087.51
16:30 | 6881.565 | 7066.545 | 13948.11
17:00 | 6787.15 | 7021.56 | 13808.71
17:30 | 6965.43 | 6965.165 | 13930.595
18:00 | 7143.71 | 6908.77 | 14052.48
18:30 | 7537.955 | 7266.46 | 14804.415
19:00 | 7932.2 | 7624.15 | 15556.35
19:30 | 7914.2 | 7749.59 | 15663.79
20:00 | 8022.6 | 7733.43 | 15756.03
20:30 | 8013.15 | 7646.46 | 15659.61 |  | Executive Engineer
21:00 | 8003.7 | 7559.49 | 15563.19 |  | Network Operation Division
21:30 | 8070.1 | 7521.68 | 15591.78
22:00 | 8136.5 | 7483.87 | 15620.37
22:30 | 8157.15 | 7479.365 | 15636.515
23:00 | 8177.8 | 7474.86 | 15652.66

## En-Curve
QF-LDC-12
Date | 08-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3991 | 1904 | 916 | 38 | 54 | 1459 | 222 | 4550 | 0 | 579 | 2122.3 | 80 | 0 | 0 | 81 | DAILY ENERGY CURVE
00:30 | 3941 | 1893 | 916.5 | 38 | 53 | 1456 | 222 | 4521 | 0 | 562 | 2024.3 | 80 | 0 | 0 | 103.5 | 08-09-2025
01:00 | 3891 | 1882 | 917 | 38 | 52 | 1453 | 222 | 4492 | 0 | 545 | 1926.3 | 80 | 0 | 0 | 126
01:30 | 3896 | 1889.5 | 917 | 38 | 51 | 1452.5 | 221 | 4499 | 0 | 446 | 1785.9 | 80 | 0 | 0 | 97.5 | Energy Generated | 352.3706 |  | MKWHr
02:00 | 3901 | 1897 | 917 | 38 | 50 | 1452 | 220 | 4506 | 0 | 347 | 1645.5 | 80 | 0 | 0 | 69 | Energy not Served | 5.979 |  | MKWHr
02:30 | 3898 | 1895 | 917 | 38 | 50 | 1453.5 | 219 | 4508 | 0 | 330 | 1372.35 | 80 | 0 | 0 | 64 | Total Energy Requirement | 358.3496 |  | MKWHr
03:00 | 3895 | 1893 | 917 | 38 | 50 | 1455 | 218 | 4510 | 0 | 313 | 1099.2 | 80 | 0 | 0 | 59
03:30 | 3897 | 1897.5 | 916.5 | 38 | 49 | 1449 | 218 | 4510 | 0 | 280 | 965.1 | 80 | 0 | 0 | 50
04:00 | 3899 | 1902 | 916 | 38 | 48 | 1443 | 218 | 4510 | 0 | 247 | 831 | 80 | 0 | 0 | 41
04:30 | 3905.5 | 1906.5 | 916 | 38 | 48 | 1411.5 | 218.5 | 4495.5 | 0 | 235.5 | 760.5 | 80 | 0 | 0 | 37.5
05:00 | 3912 | 1911 | 916 | 38 | 48 | 1380 | 219 | 4481 | 0 | 224 | 690 | 80 | 0 | 0 | 34
05:30 | 3903.5 | 1905 | 916.5 | 38 | 46 | 1250.5 | 219.5 | 4467 | 3.725 | 226.5 | 649.5 | 80 | 0 | 0 | 33
06:00 | 3895 | 1899 | 917 | 38 | 44 | 1121 | 220 | 4453 | 7.45 | 229 | 609 | 80 | 0 | 0 | 32
06:30 | 3850 | 1887.5 | 917.5 | 38 | 43 | 1116 | 220.5 | 4441.5 | 71.27 | 242.5 | 597.5 | 73 | 0 | 0 | 30.5
07:00 | 3805 | 1876 | 918 | 38 | 42 | 1111 | 221 | 4430 | 135.09 | 256 | 586 | 66 | 0 | 0 | 29
07:30 | 3804 | 1862 | 921 | 38 | 41 | 1115 | 220.5 | 4370 | 197.445 | 237.5 | 573 | 66 | 0 | 0 | 46
08:00 | 3803 | 1848 | 924 | 38 | 40 | 1119 | 220 | 4310 | 259.8 | 219 | 560 | 66 | 0 | 0 | 63
08:30 | 3825.5 | 1857 | 923.5 | 38 | 40 | 1116.5 | 220 | 4319.5 | 348.98 | 214.5 | 573 | 66 | 0 | 1 | 61.5
09:00 | 3848 | 1866 | 923 | 38 | 40 | 1114 | 220 | 4329 | 438.16 | 210 | 586 | 66 | 0 | 2 | 60
09:30 | 3847 | 1876 | 923.5 | 38 | 40 | 1071.5 | 220.5 | 4333 | 506.43 | 210 | 703.5 | 66 | 0 | 1 | 54
10:00 | 3846 | 1886 | 924 | 38 | 40 | 1029 | 221 | 4337 | 574.7 | 210 | 821 | 66 | 0 | 0 | 48
10:30 | 3863 | 1890.5 | 924.5 | 38 | 40 | 1062 | 221 | 4076.5 | 593.135 | 231 | 1032.3 | 66 | 0 | 0 | 62.5
11:00 | 3880 | 1895 | 925 | 38 | 40 | 1095 | 221 | 3816 | 611.57 | 252 | 1243.6 | 66 | 0 | 0 | 77
11:30 | 3894 | 1938.2 | 924.5 | 38 | 41 | 1155 | 196.5 | 3883 | 608.66 | 275 | 1328.5 | 66 | 0 | 0 | 125
12:00 | 3908 | 1981.4 | 924 | 38 | 42 | 1215 | 172 | 3950 | 605.75 | 298 | 1413.4 | 66 | 0 | 0 | 173
12:30 | 3910 | 2029.7 | 924.5 | 38 | 43 | 1236.5 | 172 | 3999.5 | 546.33 | 324 | 1439.85 | 58 | 0 | 0 | 170.5
13:00 | 3912 | 2078 | 925 | 38 | 44 | 1258 | 172 | 4049 | 486.91 | 350 | 1466.3 | 50 | 0 | 0 | 168
13:30 | 3872.5 | 2028 | 924.5 | 38 | 45 | 1276.345 | 196 | 4066 | 445.7 | 350 | 1476.25 | 50 | 0 | 2 | 162
14:00 | 3833 | 1978 | 924 | 38 | 46 | 1294.69 | 220 | 4083 | 404.49 | 350 | 1486.2 | 50 | 0 | 4 | 156
14:30 | 3846.5 | 1988 | 924 | 38 | 46 | 1316.05 | 220 | 4108 | 334.59 | 304 | 1495.3 | 58 | 0 | 4 | 207
15:00 | 3860 | 1998 | 924 | 38 | 46 | 1337.41 | 220 | 4133 | 264.69 | 258 | 1504.4 | 66 | 0 | 4 | 258
15:30 | 3775.5 | 1960.5 | 924 | 38 | 45 | 1355.01 | 220 | 4117 | 224.345 | 266 | 1375.15 | 66 | 0 | 4 | 399.5
16:00 | 3691 | 1923 | 924 | 38 | 44 | 1372.61 | 220 | 4101 | 184 | 274 | 1245.9 | 66 | 0 | 4 | 541
16:30 | 3624.5 | 1916.5 | 924 | 38 | 43 | 1369.65 | 220.5 | 4105.5 | 129.36 | 277.5 | 1231.6 | 66 | 0 | 2 | 483
17:00 | 3558 | 1910 | 924 | 38 | 42 | 1366.69 | 221 | 4110 | 74.72 | 281 | 1217.3 | 66 | 0 | 0 | 425
17:30 | 3509 | 1900.5 | 924 | 38 | 43 | 1360.545 | 221.5 | 4187 | 40.15 | 333.5 | 1307.4 | 66 | 0 | 0 | 403
18:00 | 3460 | 1891 | 924 | 38 | 44 | 1354.4 | 222 | 4264 | 5.58 | 386 | 1397.5 | 66 | 0 | 0 | 381
18:30 | 3587.5 | 1933 | 925 | 38 | 46 | 1359.275 | 222 | 4312.5 | 2.79 | 526.5 | 1785.85 | 66 | 0 | 0 | 474
19:00 | 3715 | 1975 | 926 | 38 | 48 | 1364.15 | 222 | 4361 | 0 | 667 | 2174.2 | 66 | 0 | 0 | 567
19:30 | 3616 | 1949 | 925 | 38 | 50 | 1376.59 | 222 | 4366 | 0 | 674 | 2381.2 | 66 | 0 | 0 | 513
20:00 | 3668 | 1960 | 862 | 38 | 52 | 1366.43 | 222 | 4405 | 0 | 693 | 2423.6 | 66 | 0 | 0 | 473
20:30 | 3634.5 | 1961.5 | 859.5 | 38 | 51 | 1323.46 | 222 | 4478.5 | 0 | 686 | 2339.15 | 66 | 0 | 0 | 589
21:00 | 3601 | 1963 | 857 | 38 | 50 | 1280.49 | 222 | 4552 | 0 | 679 | 2254.7 | 66 | 0 | 0 | 705
21:30 | 3576.5 | 1961 | 857 | 38 | 52 | 1246.18 | 222 | 4605.5 | 0 | 715 | 2252.6 | 66 | 0 | 0 | 701.5
22:00 | 3552 | 1959 | 857 | 38 | 54 | 1211.87 | 222 | 4659 | 0 | 751 | 2250.5 | 66 | 0 | 0 | 698
22:30 | 3554 | 1969 | 888 | 38 | 55 | 1158.365 | 222 | 4678 | 0 | 744 | 2264.15 | 66 | 0 | 0 | 706.5
23:00 | 3556 | 1979 | 919 | 38 | 56 | 1104.86 | 222 | 4697 | 0 | 737 | 2277.8 | 66 | 0 | 0 | 715
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 02:00 | 370 | 09:00 | Payra | 413 | 06:00 | 409 | 12:00
Ashuganj | 395 | 2:00 | 377 | 9:00 | Rahanpur | 401 | 23:00 | 389 | 00:00
Bhulta | 390 | 01:00 | 373 | 09:00 | Rampal | 400 | 06:00 | 390 | 23:00
Bibiana | 383 | 07:00 | 378 | 09:00
BIPTC | 399 | 05:00 | 388 | 15:00
Bogura | 384 | 22:00 | 370 | 00:00
Gopalganj | 392 | 07:00 | 384 | 20:00
Kaliakoir | 369 | 02:00 | 360 | 09:00
Madunaghat | 389 | 00:00 | 383 | 12:00
Meghnaghat | 379 | 02:00 | 374 | 09:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 02:00 | 218 | 09:00 | Keranigonj | 221 | 02:00 | 216 | 09:00
AKSML | 230 | 20:00 | 224 | 10:00 | Khulna(S) | 229 | 09:00 | 216 | 23:00
Aminbazar | 224 | 06:00 | 220 | 10:00 | Madunaghat | 237 | 09:00 | 226 | 10:00
Ashuganj | 228 | 03:00 | 220 | 09:00 | Madunaghat-400 | 230 | 00:00 | 226 | 10:00
Ashuganj-400 | 228 | 2:00 | 218 | 9:00 | Maniknagar | 217 | 05:00 | 212 | 09:00
Baghabari | 231 | 06:00 | 226 | 14:00 | Meghnaghat | 226 | 02:00 | 223 | 06:00
Barapukuria | 226 | 22:00 | 219 | 13:00 | Meghnaghat-400 | 221 | 02:00 | 216 | 09:00
Barapukuria-230 | 226 | 22:00 | 218 | 14:00 | Mirsorai | 230 | 19:00 | 221 | 10:00
Barishal | 226 | 08:00 | 221 | 00:00 | Rajshahi | 229 | 07:00 | 219 | 13:00
Bheramara | 233 | 13:00 | 222 | 19:00 | Rampal | 228 | 08:00 | 218 | 23:00
Bhulta | 224 | 01:00 | 213 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 02:00 | 221 | 23:00 | Rampura | 222 | 02:00 | 210 | 09:00
BIPTC | 235 | 10:00 | 222 | 15:00 | Shikalbaha | 229 | 17:00 | 224 | 09:00
Bogura | 239 | 22:00 | 230 | 03:00 | Shyampur | 219 | 03:00 | 215 | 10:00
Bogura-400 | 240 | 22:00 | 231 | 00:00 | Siddhirganj | 218 | 03:00 | 215 | 08:00
Borhanuddin | 231 | 07:00 | 226 | 00:00 | Sirajgonj | 239 | 06:00 | 236 | 00:00
BSRM | 228 | 16:00 | 221 | 09:00 | Sreepur | 225 | 19:30 | 220 | 09:00
Cumilla(N) | 221 | 19:30 | 216 | 09:00 | Tongi | 225 | 13:00 | 214 | 09:00
Faridpur | 223 | 08:00 | 216 | 00:00
Fenchuganj | 226 | 06:00 | 223 | 01:00
Ghorashal | 230 | 00:00 | 225 | 01:00
Ghorashal-230 | 224 | 02:00 | 213 | 09:00
Gopalganj | 223 | 06:00 | 218 | 00:00
GPH | 230 | 02:00 | 224 | 13:00
Haripur | 218 | 05:00 | 215 | 09:00
Hasnabad | 220 | 07:00 | 216 | 09:00
Hathazari | 228 | 00:00 | 223 | 08:00
Ishurdi | 233 | 08:00 | 225 | 15:00
Jhenaidah | 229 | 09:00 | 216 | 19:00
Kaliakoir | 230 | 02:00 | 221 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 127 | 16:00 | Lalmonirhat | 129 | 21:00 | 120 | 13:00
Agargaon | 134 | 02:00 | 129 | 12:00 | Madanganj | 128 | 08:00 | 125 | 01:00
Agrabad | 131 | 18:30 | 126 | 14:00 | Madaripur | 133 | 08:00 | 130 | 00:00
AKS | 128 | 19:00 | 125 | 09:00 | Madartek | 137 | 02:00 | 127 | 09:00
Aminbazar | 133 | 01:00 | 128 | 09:00 | Madunaghat | 133 | 17:00 | 130 | 10:00
Amnura | 134 | 06:00 | 125 | 15:00 | Magura | 134 | 09:00 | 122 | 19:00
Ashuganj | 137 | 06:00 | 135 | 00:00 | Mahasthangarh | 132 | 21:00 | 125 | 01:00
Bagerhat | 130 | 08:00 | 118 | 21:00 | Maijdee | 119 | 18:30 | 109 | 00:00
Bajitpur | 129 | 14:00 | 124 | 18:30 | Manikganj | 124 | 06:00 | 118 | 18:30
Bakulia | 132 | 16:00 | 128 | 11:00 | Maniknagar | 131 | 02:00 | 126 | 13:00
Banani | 136 | 01:00 | 128 | 09:00 | Matarbari | 126 | 18:30 | 109 | 00:00
Bangabhaban | 131 | 06:00 | 127 | 10:00 | Matuail | 127 | 19:00 | 124 | 12:00
Barapukuria | 138 | 22:00 | 128 | 13:00 | Millgate | 130 | 01:00 | 123 | 09:00
Barguna | 138 | 19:30 | 131 | 15:00 | Mirpur | 131 | 14:00 | 127 | 08:00
Barishal | 132 | 07:00 | 128 | 15:00 | Mirzapur | 129 | 02:00 | 123 | 09:00
Barishal-230 | 132 | 07:00 | 128 | 00:00 | Mithapukur | 132 | 22:00 | 123 | 13:00
Baroaulia | 130 | 00:00 | 127 | 10:00 | MI_Cement | 129 | 20:00 | 125 | 09:00
Baroirhat | 125 | 18:00 | 117 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 01:00 | 122 | 09:00 | Mogbazar | 137 | 02:00 | 130 | 09:00
BashundharaCement | 128 | 08:00 | 125 | 01:00 | Mongla | 131 | 08:00 | 118 | 23:00
Beanibazar | 125 | 16:00 | 121 | 00:00 | Motijheel | 131 | 06:00 | 127 | 10:00
Benapole | 130 | 09:00 | 116 | 23:00 | Muktagacha | 131 | 16:00 | 122 | 00:00
Bhaluka | 129 | 14:00 | 121 | 18:30 | Munshiganj | 128 | 01:00 | 123 | 09:00
Bhandaria | 127 | 18:00 | 119 | 00:00 | Muradnagar | 124 | 16:00 | 119 | 00:00
Bhangura | 131 | 06:00 | 128 | 00:00 | Mymensingh | 131 | 16:00 | 113 | 22:00
Bheramara | 136 | 08:00 | 131 | 23:00 | Naogaon | 132 | 22:00 | 121 | 01:00
Bheramara(GK) | 136 | 08:00 | 131 | 23:00 | Narail | 134 | 09:00 | 121 | 23:00
Bhulta | 120 | 01:00 | 118 | 00:00 | Narinda | 131 | 2:00 | 126 | 13:00
Bog-Sherpur | 133 | 22:00 | 126 | 15:00 | Narshingdi | 136 | 00:00 | 117 | 11:00
Bogura | 135 | 22:00 | 128 | 13:00 | Natore | 132 | 22:00 | 126 | 00:00
Bogura-230 | 136 | 22:00 | 129 | 00:00 | Nawabganj | 134 | 01:00 | 131 | 10:00
Brahmanbaria | 132 | 06:00 | 127 | 23:00 | Netrakona | 124 | 14:00 | 111 | 23:00
Cantonment | 134 | 02:00 | 129 | 11:00 | New | 130 | 07:00 | 124 | 09:00
Chandina | 127 | 18:00 | 122 | 12:00 | Niamatpur | 136 | 06:00 | 131 | 00:00
Chandpur | 129 | 18:00 | 120 | 14:00 | Noapara | 132 | 08:00 | 122 | 22:00
Chandraghona | 133 | 16:00 | 130 | 11:00 | Pabna | 133 | 06:00 | 127 | 19:00
Chapai | 135 | 23:00 | 128 | 00:00 | Palashbari | 129 | 21:00 | 121 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 19:30 | 125 | 09:00 | Panchagarh | 135 | 22:00 | 120 | 12:00
Chauddagram | 124 | 18:00 | 115 | 13:00 | Patiya | 133 | 16:00 | 126 | 11:00
Chhatak | 125 | 06:00 | 118 | 00:00 | Patuakhali | 138 | 19:30 | 132 | 15:00
Chowmuhani | 119 | 18:30 | 110 | 00:00 | Payra | 137 | 19:30 | 134 | 01:00
Chuadanga | 134 | 09:00 | 118 | 21:00 | PHP | 124 | 18:00 | 115 | 13:00
Coxsbazar | 125 | 18:00 | 109 | 20:00 | Postogola | 131 | 19:30 | 127 | 09:00
Cumilla(N) | 127 | 18:00 | 123 | 00:00 | Purbachal | 136 | 01:00 | 123 | 09:00
Cumilla(S) | 131 | 03:00 | 120 | 15:00 | Purbasadipur | 131 | 02:00 | 120 | 14:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Rahanpur | 137 | 06:00 | 133 | 00:00
Daudkandi | 122 | 16:00 | 116 | 00:00 | Rahanpur-400 | 137 | 06:00 | 133 | 00:00
Dhaka | 137 | 01:00 | 128 | 09:00 | Rahim | 127 | 05:00 | 125 | 09:00
Dhamrai | 129 | 15:00 | 123 | 09:00 | Rajbari | 130 | 07:00 | 125 | 00:00
Dhanmondi | 137 | 07:00 | 128 | 09:00 | Rajendrapur | 137 | 01:00 | 121 | 18:30
Dohazari | 131 | 16:00 | 122 | 00:00 | Rajshahi | 133 | 04:00 | 125 | 15:00
Faridpur | 132 | 08:00 | 127 | 00:00 | Rajshahi-230 | 131 | 06:00 | 125 | 13:00
Fatullah | 130 | 01:00 | 127 | 09:00 | Ramganj | 122 | 18:00 | 113 | 13:00
Fenchuganj | 133 | 06:00 | 131 | 00:00 | Rampur | 132 | 16:00 | 126 | 11:00
Feni | 123 | 08:00 | 115 | 11:00 | Rampura | 136 | 02:00 | 127 | 09:00
Ghatail | 129 | 19:00 | 119 | 00:00 | Rangamati | 132 | 03:00 | 130 | 00:00
Ghorashal | 136 | 00:00 | 130 | 17:00 | Rangpur | 132 | 21:00 | 125 | 13:00
Goalpara | 135 | 09:00 | 124 | 23:00 | Ruppur | 136 | 06:00 | 132 | 00:00
Gollamari | 135 | 07:00 | 126 | 23:00 | Saidpur | 133 | 22:00 | 124 | 13:00
Gopalganj | 133 | 08:00 | 126 | 23:00 | Satkhira | 134 | 10:00 | 119 | 23:00
Gopalganj-400 | 134 | 05:00 | 130 | 22:00 | Satmasjid | 134 | 03:00 | 129 | 10:00
Gulshan | 136 | 05:00 | 128 | 09:00 | Savar | 134 | 14:00 | 125 | 08:00
Halishahar | 133 | 16:00 | 126 | 10:00 | SevenRings | 136 | 01:00 | 129 | 09:00
Haripur | 128 | 03:00 | 125 | 09:00 | ShahCement | 129 | 19:30 | 125 | 09:00
HaripurSBU | 128 | 03:00 | 125 | 08:00 | Shahjadpur | 135 | 01:00 | 132 | 13:00
Hasnabad | 130 | 18:00 | 128 | 01:00 | Shahjibazar | 131 | 04:00 | 127 | 00:00
Hathazari | 132 | 00:00 | 130 | 04:00 | Shahmirpur | 134 | 16:00 | 127 | 11:00
Ishurdi | 136 | 06:00 | 132 | 00:00 | Shariatpur | 132 | 18:00 | 126 | 00:00
Jaldhaka | 130 | 23:00 | 122 | 13:00 | Sherpur | 128 | 17:00 | 115 | 00:00
Jamalpur | 129 | 17:00 | 120 | 00:00 | Shikalbaha | 121 | 02:00 | 117 | 10:00
Jashore | 134 | 09:00 | 121 | 19:00 | Shikalbaha-230 | 133 | 17:00 | 129 | 10:00
Jhenaidah | 136 | 07:00 | 119 | 23:00 | Shitalakhya | 129 | 20:00 | 125 | 09:00
Jhenaidah-230 | 136 | 09:00 | 125 | 23:00 | Sholosohor | 133 | 16:00 | 130 | 09:00
Joydebpur | 140 | 00:00 | 108 | 18:30 | Shyampur | 133 | 19:00 | 129 | 12:00
Joypurhat | 127 | 21:00 | 118 | 00:00 | Shyampur-230 | 131 | 19:30 | 128 | 00:00
Juldah | 134 | 16:00 | 127 | 11:00 | Siddhirganj | 127 | 02:00 | 125 | 09:00
Kabirpur | 134 | 02:00 | 118 | 18:30 | Sirajganj | 129 | 06:00 | 124 | 15:00
Kachua | 127 | 18:30 | 121 | 13:00 | Sonargaon | 125 | 05:00 | 123 | 00:00
Kaliakoir | 134 | 07:00 | 127 | 09:00 | Sreemongol | 130 | 07:00 | 126 | 00:00
Kallyanpur | 132 | 13:00 | 128 | 08:00 | Sreepur | 130 | 19:30 | 125 | 09:00
Kalurghat | 134 | 16:00 | 130 | 10:00 | Srinagar | 135 | 02:00 | 131 | 12:00
Kamrangirchar | 136 | 05:00 | 131 | 09:00 | SSM | 132 | 23:00 | 130 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 122 | 17:00 | 116 | 00:00
Kasba | 124 | 18:00 | 118 | 00:00 | Sylhet | 126 | 07:00 | 122 | 00:00
Kazla | 131 | 06:00 | 126 | 12:00 | Sylhet-132 | 126 | 08:00 | 124 | 00:00
Keranigonj | 135 | 02:00 | 131 | 18:30 | Tangail | 127 | 12:00 | 119 | 22:00
Khagrachori | 132 | 07:00 | 128 | 10:00 | Taraganj | 131 | 18:00 | 122 | 13:00
Khulna | 134 | 08:00 | 125 | 22:00 | Thakurgaon | 135 | 22:00 | 119 | 12:00
Khulna(S) | 136 | 09:00 | 126 | 22:00 | TK | 133 | 16:00 | 130 | 03:00
Khulshi | 130 | 16:00 | 125 | 11:00 | Tongi | 132 | 04:00 | 126 | 09:00
Kishoreganj | 128 | 14:00 | 120 | 23:00 | Ullahpara | 131 | 07:00 | 127 | 15:00
Kodda | 137 | 01:00 | 122 | 23:00 | Ullon | 136 | 01:00 | 127 | 09:00
KSRM | 132 | 16:00 | 128 | 00:00 | Uttara | 132 | 02:00 | 127 | 09:00
Kulaura | 132 | 07:00 | 129 | 00:00 | UttaraNew | 132 | 01:00 | 126 | 08:00
Kurigram | 128 | 21:00 | 120 | 19:00 | Zigatola | 135 | 03:00 | 130 | 10:00
Kushtia | 131 | 09:00 | 125 | 23:00
Laksam | 127 | 18:00 | 120 | 00:00
Lakshmipur | 119 | 18:00 | 106 | 00:00
Lalbag | 135 | 02:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division