## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-09-2025 | during | 10-09-2025 | during | 10-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 352 | 400.75 | 400.75 | 363 | 363 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 306 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 39 | 330 | 335 | 335 | 332 | 332 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 65 | 7 | 102 | 7 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 48.5 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 108 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 0 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 15 | 15 | 15 | 15 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 47 | 95 | 47 | 95 | 65 | 65 | Fuel Shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 30 | 149 | 51 | 149 | 34 | 102 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 51 | 87.5 | 87.5 | 51 | 51 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 153 | 72 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 10 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.76 | 524.76 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 52 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2171.5 | 2637 | 5438.34 | 5645.34 | 3374.26 | 3576.26
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 218 | 214 | 219 | 214 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 98 | 93 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 39 | 72 | 48 | 78 | 48 | 78 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 66 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 11 | 100 | 100 | 12 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 22 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.93 | 0 | 4.56 | 0 | 4.56 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 155 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 32 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 86 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 134 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1155 | 1130 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 5 | 5 | 5 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 262 | 264 | 260 | 260 | 260 | 260 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2197.93 | 2669 | 3284.28 | 3314.72 | 2944.92 | 2988.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 195 | 176 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 24 | 37 | 46.7 | 46.7 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 44 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 23 | 26 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 118 | 123 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 101 | 167 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 97 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 91 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 52 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1583 | 1738.2 | 2434.56 | 2379.56 | 2121.36 | 2066.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-09-2025 | during | 10-09-2025 | during | 10-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 60 | 63 | 157.5 | 157.5 | 102 | 102 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 28 | 32 | 32 | 32 | 32 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 83 | 100 | 109 | 109 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22.67 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 206.67 | 220 | 422 | 375 | 319 | 272
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 70 | 69 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 0 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 370 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1207 | 868 | 1280 | 1280 | 1155 | 1155
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 836 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 22 | 22 | 22 | 22 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 102 | 108 | 410 | 410 | 267 | 267 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1198 | 736 | 750 | 750 | 1234.2 | 1234.2 | Due to coal supply disruption as vessel got stuck
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2362 | 1773 | 3138 | 3048 | 3284.2 | 3194.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 302 | 349 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 99 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1112 | 1222 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 49 | 128 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 305 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2074.19 | 2438 | 2162 | 2161 | 2132 | 2131
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 52.75 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 132 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 154 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 135 | 220 | 220 | 220 | 220 | Low gas pressure
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 387 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 92 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.41 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 744 | 741.82 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 31.36 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 83 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1744.52 | 2026.82 | 2499.64 | 2332.99 | 2426.26 | 2259.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 66 | 66 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 51 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 144 | 166 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 85 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.2 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 96 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 3 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 138 | 0 | 112.31 | 0 | 112.31 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 586.2 | 511 | 630.91 | 482 | 630.91 | 482
System Total |  |  |  |  | 28823.2 | 27829.875 | 14133.01 | 14881.02 | 21289.73 | 21018.61 | 18387.91 | 18124.79
Forecast Scenario (10-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14500 |  | 1650 |  | 16250
|  |  |  | 1:00 | 14300 |  | 1450 |  | 15850
|  |  |  | 2:00 | 14500 |  | 850 |  | 15400
|  |  |  | 3:00 | 14450 |  | 750 |  | 15230
|  |  |  | 4:00 | 14300 |  | 450 |  | 14750
|  |  |  | 5:00 | 14250 |  | 200 |  | 14450
|  |  |  | 6:00 | 13900 |  | 150 |  | 14050
|  |  |  | 7:00 | 13800 |  | 100 |  | 13900
|  |  |  | 8:00 | 13800 |  | 100 |  | 13900
|  |  |  | 9:00 | 13900 |  | 150 |  | 14100
|  |  |  | 10:00 | 14100 |  | 100 |  | 14220
|  |  |  | 11:00 | 14200 |  | 300 |  | 14500
|  |  |  | 12:00 | 14200 |  | 500 |  | 14750
|  |  |  | 13:00 | 14100 |  | 850 |  | 15000
|  |  |  | 14:00 | 14100 |  | 950 |  | 15100
|  |  |  | 15:00 | 14150 |  | 1000 |  | 15200
|  |  |  | 16:00 | 14100 |  | 950 |  | 15100
|  |  |  | 17:00 | 13800 |  | 850 |  | 14700
|  |  |  | 18:00 | 13700 |  | 850 |  | 14600
|  |  |  | 18:30 | 14500 |  | 850 |  | 15400
|  |  |  | 19:00 | 14800 |  | 1250 |  | 16100
|  |  |  | 19:30 | 14900 |  | 1350 |  | 16300
|  |  |  | 20:00 | 15000 |  | 1300 |  | 16350
|  |  |  | 21:00 | 15000 |  | 1300 |  | 16350
|  |  |  | 22:00 | 14900 |  | 1450 |  | 16400
|  |  |  | 23:00 | 14700 |  | 1600 |  | 16400
Probable Maximum Temperature: |  |  | 33.50°C
Probable Maximum Demand at Day Peak: |  |  | 14750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1300
Probable Maximum Demand at Evening Peak: |  |  | 16350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 356.11 MKWHr. |  | 262 | 120 | 200 | 185 | 125 | 160 | 22 | 100 | 125 | 1300
*** This report is generated digitally from Operation Information System (OIS) at 07:42 hrs on 10-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-09-2025 | [28 empty] | Date: | 09-09-2025 | [28 empty] | Date: | 09-09-2025 | [28 empty] | Date: | 09-09-2025 | [28 empty] | Date: | 09-09-2025 | [14 empty] | Date: | 09-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 49.6 | 17 | 34 | 62 | 45 | 55 | 55 | 148 | 0 | 350 | 305 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 35 | 26 | 15 | 0 | 350 | 28 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 12 | 0 | 0 | 222 | 95 | 31 | 265 | 126 | 0 | 33 | 17 | 68 | 217 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 43 | 0 | 348 | 330 | 45 | 203 | 34 | 72 | 90 | 181 | 0 | 19 | 114 | 54 | 43 | 0 | 36 | 315 | 0 | 390 | 0 | 69 | 157 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 8016.6 | 919 | 103 | 0 | 19 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 997.33 | 0 | 47 | 0 | 113 | 113 | 0 | 92 | 30 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 169 | 50 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 110 | 277 | 115 | 220 | 0 | 305 | 1222 | 142 | 7408.33 | 15424.93 | 108.71
01:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 47.4 | 0 | 22 | 30 | 47 | 55 | 55 | 153 | 0 | 350 | 294 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 35 | 27 | 15 | 0 | 330 | 45 | 0 | 0 | 0 | 0 | 66 | 76 | 0 | 12 | 0 | 0 | 222 | 105 | 30 | 262 | 53 | 0 | 32 | 17 | 65 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 43 | 0 | 352 | 330 | 45 | 188 | 34 | 82 | 90 | 137 | 0 | 19 | 114 | 52 | 8 | 0 | 37 | 310 | 0 | 376 | 0 | 70 | 155 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 7784.4 | 919 | 99 | 0 | 19 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 1012.99 | 0 | 47 | 0 | 113 | 113 | 0 | 92 | 30 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 170 | 50 | 114 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 110 | 273 | 115 | 220 | 0 | 305 | 1222 | 134 | 7395.99 | 15180.39 | 108.74
02:00 | 7 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 44.9 | 0 | 17 | 30 | 47 | 30 | 55 | 143 | 0 | 350 | 302 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 35 | 27 | 15 | 0 | 335 | 42 | 0 | 0 | 0 | 0 | 66 | 76 | 0 | 12 | 0 | 0 | 222 | 68 | 30 | 261 | 17 | 0 | 32 | 17 | 62 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 43 | 0 | 350 | 330 | 45 | 199 | 31 | 90 | 90 | 103 | 0 | 19 | 114 | 50 | 8 | 0 | 37 | 305 | 0 | 390 | 0 | 70 | 148 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 7644.9 | 931 | 97 | 0 | 19 | 22 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 0 | 1025.12 | 0 | 47 | 0 | 50 | 113 | 0 | 92 | 28 | 8 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 166 | 50 | 114 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 96 | 278 | 115 | 220 | 0 | 305 | 1222 | 140 | 7280.12 | 14925.02 | 108.76
03:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 47.8 | 0 | 17 | 30 | 47 | 30 | 55 | 152 | 0 | 350 | 294 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 35 | 27 | 15 | 0 | 320 | 45 | 0 | 0 | 0 | 0 | 66 | 76 | 0 | 12 | 0 | 0 | 221 | 65 | 31 | 260 | 17 | 0 | 33 | 8 | 63 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 43 | 0 | 353 | 330 | 45 | 195 | 31 | 89 | 90 | 104 | 0 | 19 | 114 | 50 | 8 | 0 | 37 | 310 | 0 | 390 | 0 | 70 | 157 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 102 | 29 | 71 | 0 | 0 | 12 | 7652.8 | 931 | 100 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 1032.33 | 0 | 47 | 0 | 50 | 50 | 0 | 0 | 28 | 0 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 168 | 50 | 114 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 16 | 276 | 115 | 220 | 0 | 305 | 1222 | 134 | 7021.33 | 14674.13 | 108.79
04:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 47 | 0 | 17 | 30 | 47 | 15 | 55 | 151 | 0 | 350 | 292 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 35 | 27 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 76 | 0 | 12 | 0 | 0 | 220 | 66 | 31 | 263 | 0 | 0 | 33 | 0 | 64 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 43 | 0 | 352 | 330 | 45 | 191 | 27 | 90 | 90 | 103 | 0 | 19 | 114 | 48 | 8 | 0 | 37 | 310 | 0 | 386 | 0 | 70 | 155 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 85 | 0 | 0 | 12 | 7471 | 932 | 100 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 1047.26 | 0 | 47 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 166 | 50 | 114 | 0 | 49 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 305 | 1222 | 66 | 6802.26 | 14273.26 | 108.82
05:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 44.2 | 0 | 17 | 30 | 47 | 15 | 55 | 144 | 0 | 350 | 291 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 35 | 27 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 76 | 0 | 12 | 0 | 0 | 220 | 64 | 37 | 262 | 0 | 0 | 33 | 0 | 61 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 43 | 0 | 354 | 330 | 45 | 188 | 27 | 90 | 90 | 104 | 0 | 19 | 114 | 48 | 8 | 0 | 37 | 305 | 0 | 359 | 0 | 70 | 150 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 85 | 0 | 0 | 12 | 7410.2 | 932 | 100 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 0 | 1137.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 166 | 50 | 70 | 0 | 49 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 305 | 1224 | 60 | 6715.67 | 14125.87 | 108.84
06:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 43.4 | 0 | 17 | 30 | 47 | 0 | 55 | 72 | 0 | 300 | 290 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 20 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 52 | 39 | 0 | 12 | 0 | 0 | 219 | 34 | 37 | 260 | 0 | 0 | 33 | 0 | 34 | 222 | 0 | 0 | 0 | 1224 | 1 | 51 | 40 | 43 | 0 | 354 | 330 | 45 | 187 | 27 | 90 | 90 | 104 | 0 | 19 | 70 | 44 | 8 | 0 | 37 | 305 | 0 | 361 | 0 | 70 | 148 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 86 | 0 | 0.88 | 12 | 6991.28 | 931 | 101 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 1173.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0.07 | 164 | 50 | 35 | 0 | 34 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 180 | 0 | 305 | 1222 | 0 | 6536.85 | 13528.13 | 108.86
07:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 45.6 | 0 | 17 | 30 | 47 | 0 | 55 | 35 | 0 | 300 | 307 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 35 | 20 | 15 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 66 | 39 | 0 | 12 | 0 | 0.59 | 222 | 31 | 23 | 265 | 0 | 0 | 33 | 0 | 29 | 222 | 0 | 0 | 0 | 1224 | 6 | 51 | 40 | 45 | 0 | 348 | 330 | 45 | 200 | 27 | 89 | 90 | 104 | 0 | 19 | 52 | 42 | 8 | 2 | 37 | 310 | 0 | 389 | 0 | 70 | 155 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 70 | 0 | 6.4 | 12 | 7057.59 | 931 | 100 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1194 | 0 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2 | 15 | 0 | 0 | 10 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0.88 | 164 | 50 | 35 | 4 | 0 | 0 | 66 | 0 | 0 | 2 | 0.04 | 0 | 277 | 115 | 180 | 0 | 306 | 1224 | 0 | 6349.12 | 13406.71 | 108.88
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 49.2 | 0 | 17 | 29 | 47 | 0 | 55 | 33 | 0 | 300 | 295 | 0 | 0 | 7 | 331 | 0 | 0 | 13 | 35 | 10 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 39 | 0 | 12 | 0 | 1.19 | 222 | 33 | 3 | 262 | 0 | 0 | 33 | 0 | 61 | 222 | 0 | 0 | 0 | 1170 | 11 | 51 | 51 | 16 | 0 | 300 | 330 | 45 | 195 | 27 | 72 | 90 | 104 | 0 | 19 | 52 | 38 | 8 | 22 | 37 | 315 | 0 | 336 | 0 | 70 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 69 | 1 | 10.19 | 12 | 6909.58 | 932 | 108 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 1200 | 0 | 758.01 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 16.29 | 47 | 0 | 0 | 25 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 2.44 | 164 | 51 | 35 | 14 | 20 | 0 | 66 | 0 | 0 | 5 | 0.17 | 0 | 274 | 115 | 180 | 0 | 305 | 1200 | 16 | 6300.91 | 13210.49 | 108.88
09:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 47 | 0 | 17 | 29 | 47 | 10 | 55 | 102 | 0 | 300 | 293 | 0 | 0 | 17 | 331 | 0 | 0 | 20 | 35 | 21 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 39 | 0 | 12 | 0 | 2.03 | 222 | 32 | 3 | 262 | 35 | 0 | 33 | 0 | 94 | 219 | 0 | 0 | 0 | 1140 | 18 | 51 | 85 | 16 | 0 | 300 | 330 | 45 | 192 | 29 | 69 | 90 | 104 | 0 | 19 | 52 | 34 | 8 | 32 | 37 | 310 | 0 | 364 | 0 | 70 | 153 | 0 | 0 | 79 | 30 | 0 | 0 | 166 | 0 | 84 | 29 | 69 | 1 | 12.3 | 12 | 7106.33 | 932 | 105 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1196 | 0 | 758 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 43.93 | 66 | 0 | 0 | 29.47 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 2.17 | 175 | 51 | 70 | 5 | 35 | 0 | 66 | 0 | 0.3 | 36 | 0.27 | 0 | 273 | 115 | 220 | 0 | 303 | 1120 | 47 | 6451.14 | 13557.47 | 108.88
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 46 | 0 | 17 | 30 | 47 | 50 | 55 | 120 | 0 | 300 | 304 | 0 | 0 | 35 | 328 | 0 | 0 | 24 | 35 | 21 | 15 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 66 | 39 | 0 | 12 | 0 | 3.68 | 222 | 32 | 4 | 262 | 35 | 0 | 22 | 0 | 96 | 216 | 0 | 0 | 0 | 1165 | 12 | 51 | 105 | 16 | 0 | 300 | 330 | 44 | 200 | 29 | 69 | 90 | 104 | 0 | 19 | 52 | 36 | 8 | 30 | 29 | 310 | 0 | 389 | 0 | 70 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 29 | 65 | 1 | 23.66 | 12 | 7281.34 | 932 | 102 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1190 | 0 | 736 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 52.24 | 104 | 0 | 0 | 36.71 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 1.82 | 146 | 51 | 70 | 14 | 69 | 0 | 66 | 0 | 0.8 | 109 | 0.56 | 0 | 275 | 115 | 220 | 0 | 303 | 1108 | 49 | 6597.13 | 13878.47 | 108.88
11:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 48.5 | 10 | 30 | 30 | 47 | 55 | 55 | 153 | 0 | 380 | 300 | 0 | 0 | 35 | 39 | 0 | 0 | 29 | 35 | 21 | 15 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 66 | 39 | 0 | 12 | 0 | 3.93 | 222 | 32 | 4 | 262 | 35 | 0 | 45 | 1 | 98 | 217 | 0 | 0 | 0 | 1155 | 6 | 51 | 118 | 23 | 0 | 344 | 330 | 40 | 195 | 24 | 69 | 90 | 101 | 0 | 19 | 52 | 38 | 8 | 52 | 29 | 315 | 0 | 385 | 0 | 70 | 160 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 83 | 28 | 60 | 1 | 22.67 | 12 | 7366.1 | 932 | 102 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 1198 | 0 | 744 | 0 | 0 | 0 | 50 | 92 | 0 | 0 | 0 | 0 | 52.75 | 83 | 0 | 0 | 31.36 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 1.41 | 144 | 52 | 96 | 3 | 85 | 0 | 66 | 0 | 2.2 | 138 | 0.19 | 0 | 276 | 115 | 220 | 0 | 302 | 1112 | 49 | 6766.91 | 14133.01 | 108.89
12:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 48.1 | 17 | 34 | 30 | 47 | 55 | 55 | 155 | 0 | 420 | 299 | 0 | 0 | 35 | 24 | 0 | 0 | 28 | 35 | 20 | 15 | 0 | 535 | 0 | 0 | 0 | 0 | 3 | 66 | 55 | 0 | 11 | 0 | 4.28 | 222 | 34 | 4 | 262 | 35 | 0 | 46 | 14 | 100 | 212 | 0 | 0 | 0 | 1165 | 10 | 51 | 122 | 23 | 0 | 349 | 330 | 41 | 204 | 24 | 70 | 90 | 103 | 0 | 19 | 52 | 38 | 8 | 65 | 28 | 0 | 0 | 391 | 0 | 69 | 158 | 0 | 0 | 81 | 30 | 0 | 0 | 167 | 17 | 83 | 28 | 59 | 1 | 15.64 | 12 | 7283.02 | 933 | 98 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1070 | 0 | 738 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 43 | 50.53 | 95 | 0 | 0 | 25.66 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 2.35 | 169 | 50 | 96 | 8 | 104 | 0 | 67 | 0 | 0 | 118 | 0.68 | 0 | 278 | 115 | 220 | 0 | 303 | 1117 | 75 | 6802.22 | 14085.24 | 108.9
13:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 49.2 | 17 | 34 | 30 | 47 | 55 | 55 | 154 | 0 | 420 | 279 | 0 | 0 | 35 | 32 | 0 | 0 | 17 | 35 | 0 | 15 | 0 | 500 | 13 | 10 | 0 | 0 | 3 | 66 | 62 | 0 | 11 | 0 | 3.91 | 222 | 70 | 10 | 262 | 35 | 0 | 50 | 17 | 97 | 214 | 0 | 0 | 0 | 1097 | 13 | 51 | 125 | 25 | 0 | 355 | 330 | 43 | 180 | 26 | 69 | 90 | 104 | 8 | 19 | 52 | 60 | 8 | 35 | 28 | 0 | 0 | 377 | 0 | 70 | 156 | 0 | 0 | 83 | 30 | 0 | 0 | 167 | 17 | 82 | 28 | 59 | 1 | 21.95 | 12 | 7196.06 | 932 | 97 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 771 | 0 | 740 | 0 | 0 | 0 | 113 | 113 | 0 | 49 | 0 | 52 | 53.24 | 79 | 0 | 0 | 32.15 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 2.38 | 170 | 50 | 95 | 10 | 106 | 0 | 66 | 0 | 4 | 125 | 0.84 | 80 | 260 | 115 | 220 | 0 | 303 | 1180 | 109 | 6725.61 | 13921.67 | 108.9
14:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 47 | 17 | 83 | 30 | 47 | 55 | 17 | 108 | 0 | 380 | 282 | 0 | 0 | 35 | 240 | 0 | 0 | 30 | 35 | 0 | 15 | 0 | 480 | 28 | 32 | 0 | 0 | 2 | 66 | 75 | 0 | 11 | 0 | 2.05 | 220 | 99 | 11 | 268 | 35 | 0 | 50 | 17 | 99 | 219 | 0 | 0 | 0 | 1129 | 3 | 51 | 118 | 25 | 0 | 350 | 330 | 42 | 186 | 22 | 73 | 90 | 102 | 8 | 19 | 52 | 56 | 16 | 38 | 36 | 0 | 0 | 364 | 0 | 69 | 149 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 17 | 82 | 28 | 59 | 1 | 20.7 | 12 | 7379.75 | 932 | 92 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 754 | 0 | 745.34 | 0 | 0 | 0 | 113 | 113 | 0 | 49 | 0 | 52 | 57.01 | 77 | 0 | 0 | 23.08 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 1.6 | 169 | 50 | 95 | 11 | 107 | 0 | 66 | 0 | 5.5 | 115 | 0.32 | 110 | 231 | 115 | 220 | 0 | 303 | 1119 | 125 | 6631.85 | 14011.6 | 108.9
15:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 17 | 105 | 30 | 47 | 55 | 17 | 54 | 0 | 380 | 306 | 0 | 0 | 35 | 330 | 0 | 0 | 10 | 35 | 9 | 15 | 0 | 400 | 50 | 32 | 0 | 0 | 5 | 66 | 67 | 0 | 11 | 0 | 3.3 | 218 | 105 | 4 | 260 | 35 | 0 | 50 | 17 | 101 | 217 | 0 | 0 | 0 | 1155 | 1 | 51 | 118 | 40 | 0 | 344 | 330 | 43 | 201 | 31 | 71 | 90 | 104 | 8 | 19 | 52 | 56 | 16 | 49 | 36 | 0 | 0 | 390 | 0 | 69 | 146 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 81 | 28 | 59 | 1 | 33.14 | 12 | 7438.44 | 932 | 94 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 756 | 0 | 737.92 | 0 | 0 | 0 | 113 | 113 | 0 | 49 | 0 | 52 | 26.33 | 31 | 0 | 0 | 19.21 | 130 | 0 | 130 | 0 | 130 | 0 | 360 | 0 | 1.26 | 167 | 50 | 95 | 11 | 107 | 0 | 66 | 0 | 3.9 | 122 | 0.25 | 110 | 277 | 115 | 220 | 0 | 303 | 1125 | 92 | 6608.87 | 14047.31 | 108.9
16:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 105 | 30 | 47 | 55 | 17 | 54 | 0 | 380 | 292 | 0 | 0 | 35 | 330 | 0 | 0 | 4 | 35 | 0 | 15 | 0 | 350 | 20 | 77 | 0 | 0 | 0 | 66 | 67 | 0 | 11 | 0 | 0.95 | 219 | 110 | 5 | 260 | 35 | 0 | 50 | 17 | 95 | 216 | 0 | 0 | 0 | 1155 | 1 | 51 | 122 | 61 | 0 | 344 | 330 | 44 | 196 | 32 | 72 | 90 | 104 | 0 | 19 | 52 | 42 | 16 | 26 | 28 | 20 | 0 | 380 | 0 | 69 | 152 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 81 | 28 | 59 | 1 | 21.75 | 12 | 7356.7 | 932 | 98 | 0 | 13 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 756 | 0 | 737.21 | 0 | 0 | 0 | 113 | 113 | 0 | 49 | 0 | 52 | 9.74 | 56 | 0 | 0 | 10 | 130 | 0 | 130 | 0 | 130 | 0 | 357 | 0 | 1.07 | 165 | 50 | 95 | 15 | 111 | 0 | 66 | 0 | 3.8 | 59 | 0.34 | 80 | 277 | 115 | 220 | 0 | 304 | 1180 | 87 | 6592.16 | 13948.86 | 108.9
17:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 105 | 30 | 47 | 55 | 17 | 54 | 0 | 330 | 289 | 0 | 0 | 17 | 328 | 0 | 0 | 2 | 35 | 0 | 15 | 0 | 320 | 74 | 83 | 0 | 0 | 0 | 66 | 72 | 0 | 11 | 0 | 0.33 | 220 | 108 | 14 | 260 | 35 | 0 | 50 | 17 | 96 | 215 | 0 | 0 | 0 | 1131 | 0 | 51 | 127 | 83 | 0 | 349 | 330 | 43 | 190 | 32 | 72 | 90 | 103 | 0 | 19 | 52 | 46 | 25 | 13 | 29 | 20 | 0 | 362 | 0 | 69 | 155 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 81 | 28 | 61 | 0 | 10.71 | 12 | 7307.04 | 932 | 100 | 0 | 18 | 52 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 738 | 0 | 733.07 | 0 | 0 | 0 | 113 | 113 | 0 | 49 | 0 | 52 | 5.39 | 11 | 24 | 0 | 4.58 | 130 | 0 | 130 | 0 | 130 | 0 | 343 | 0 | 0.39 | 168 | 50 | 109 | 4 | 112 | 0 | 66 | 0 | 1.5 | 15 | 0.11 | 80 | 272 | 115 | 180 | 0 | 304 | 1120 | 84 | 6401.04 | 13708.08 | 108.9
18:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 20 | 105 | 75 | 65 | 55 | 17 | 54 | 0 | 300 | 303 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 35 | 0 | 15 | 0 | 320 | 82 | 95 | 0 | 0 | 0 | 66 | 72 | 0 | 11 | 0 | 0 | 220 | 101 | 20 | 260 | 98 | 0 | 50 | 17 | 91 | 217 | 0 | 0 | 0 | 1110 | 0 | 51 | 125 | 86 | 0 | 310 | 315 | 45 | 189 | 34 | 79 | 90 | 118 | 0 | 19 | 97 | 46 | 34 | 0 | 36 | 60 | 0 | 366 | 0 | 69 | 149 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 100 | 28 | 61 | 0 | 0.12 | 12 | 7393.12 | 932 | 105 | 0 | 18 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 734 | 0 | 740.79 | 0 | 0 | 0 | 113 | 113 | 0 | 63 | 0 | 52 | 0.33 | 0 | 21 | 0 | 0.35 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0.05 | 167 | 51 | 115 | 0 | 106 | 0 | 66 | 0 | 0.1 | 1 | 0 | 80 | 225 | 100 | 180 | 0 | 304 | 1050 | 86 | 6230.62 | 13623.74 | 108.9
19:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 35 | 136 | 108 | 65 | 55 | 35 | 72 | 0 | 350 | 305 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 142 | 4 | 15 | 0 | 400 | 95 | 155 | 0 | 0 | 0 | 66 | 72 | 6 | 11 | 0 | 0 | 172 | 110 | 19 | 260 | 145 | 0 | 50 | 17 | 101 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 123 | 50 | 0 | 346 | 330 | 44 | 165 | 37 | 90 | 90 | 169 | 0 | 19 | 97 | 48 | 52.2 | 0 | 36 | 0 | 0 | 390 | 0 | 69 | 156 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 17 | 100 | 28 | 61 | 0 | 0 | 12 | 8064.2 | 932 | 105 | 0 | 23 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 736.99 | 0 | 32 | 0 | 113 | 113 | 0 | 92 | 22 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 402 | 0 | 0 | 167 | 50 | 115 | 0 | 111 | 0 | 66 | 0 | 0 | 0 | 0 | 99 | 276 | 115 | 220 | 0 | 304 | 1140 | 133 | 6660.99 | 14725.19 | 108.91
19:30 | 50 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 35 | 149 | 108 | 95 | 55 | 35 | 72 | 0 | 350 | 304 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 400 | 95 | 155 | 0 | 0 | 0 | 66 | 72 | 17 | 11 | 0 | 0 | 172 | 110 | 22 | 260 | 140 | 0 | 50 | 17 | 92 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 124 | 26 | 0 | 348 | 330 | 44 | 175 | 37 | 90 | 90 | 170 | 0 | 19 | 97 | 48 | 52.2 | 0 | 36 | 0 | 0 | 360 | 0 | 69 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 100 | 28 | 64 | 0 | 0 | 12 | 8091.2 | 836 | 106 | 0 | 20 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 739 | 0 | 738.35 | 0 | 48 | 0 | 113 | 113 | 0 | 92 | 36 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 402 | 0 | 0 | 168 | 51 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 99 | 275 | 115 | 220 | 0 | 350 | 1210 | 133 | 6689.35 | 14780.55
20:00 | 65 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 35 | 149 | 108 | 95 | 55 | 35 | 72 | 0 | 350 | 306 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 400 | 86 | 155 | 0 | 0 | 2 | 66 | 72 | 17 | 11 | 0 | 0 | 222 | 110 | 22 | 264 | 134 | 0 | 50 | 17 | 93 | 218 | 0 | 0 | 0 | 1130 | 0 | 51 | 123 | 26 | 0 | 353 | 330 | 44 | 176 | 37 | 91 | 90 | 167 | 0 | 19 | 97 | 46 | 52.2 | 0 | 36 | 0 | 0 | 370 | 0 | 69 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 17 | 100 | 28 | 63 | 0 | 0 | 12 | 8132.2 | 836 | 108 | 0 | 20 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 741.82 | 0 | 48 | 0 | 113 | 113 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 132 | 0 | 154 | 0 | 135 | 0 | 387 | 0 | 0 | 166 | 51 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 99 | 305 | 115 | 220 | 0 | 349 | 1222 | 128 | 6748.82 | 14881.02 | 108.91
21:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 19 | 115 | 108 | 95 | 55 | 35 | 72 | 0 | 350 | 307 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 108 | 23 | 15 | 0 | 400 | 85 | 138 | 0 | 0 | 0 | 66 | 73 | 54.36 | 11 | 0 | 0 | 222 | 110 | 31 | 264 | 140 | 0 | 50 | 17 | 94 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 127 | 8 | 0 | 352 | 330 | 44 | 211 | 35 | 91 | 90 | 178 | 0 | 19 | 97 | 50 | 52.2 | 0 | 36 | 0 | 0 | 386 | 0 | 69 | 154 | 0 | 0 | 81 | 30 | 0 | 0 | 167 | 17 | 100 | 28 | 64 | 0 | 0 | 12 | 8135.56 | 796 | 108 | 0 | 18 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 745.32 | 0 | 47 | 0 | 113 | 113 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 161 | 0 | 172 | 0 | 130 | 0 | 355 | 0 | 0 | 166 | 51 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 99 | 306 | 115 | 220 | 0 | 350 | 1212 | 140 | 6718.32 | 14853.88 | 108.91
22:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 17 | 106 | 108 | 95 | 55 | 35 | 72 | 0 | 300 | 305 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 90 | 21 | 15 | 0 | 375 | 96 | 140 | 0 | 0 | 0 | 66 | 73 | 54.36 | 0 | 0 | 0 | 221 | 110 | 31 | 264 | 156 | 0 | 40 | 17 | 101 | 220 | 0 | 0 | 0 | 1180 | 0 | 51 | 130 | 8 | 0 | 345 | 330 | 44 | 207 | 32 | 90 | 90 | 187 | 0 | 19 | 97 | 52 | 52.2 | 0 | 36 | 0 | 0 | 391 | 0 | 69 | 158 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 109 | 28 | 64 | 0 | 0 | 12 | 8099.56 | 796 | 108 | 0 | 18 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 741.95 | 0 | 47 | 0 | 113 | 113 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 140 | 0 | 130 | 0 | 130 | 0 | 390 | 0 | 0 | 170 | 52 | 115 | 0 | 113 | 0 | 66 | 0 | 0 | 0 | 0 | 99 | 306 | 115 | 220 | 0 | 304 | 1212 | 150 | 6675.95 | 14775.51 | 108.92
23:00 | 7 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 106 | 92 | 95 | 55 | 35 | 35 | 0 | 300 | 296 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 35 | 27.5 | 15 | 0 | 350 | 95 | 173 | 0 | 0 | 1 | 66 | 74 | 54.36 | 0 | 0 | 0 | 220 | 107 | 31 | 260 | 148 | 0 | 39 | 17 | 98 | 220 | 0 | 0 | 0 | 1162 | 0 | 51 | 132 | 51 | 0 | 352 | 330 | 44 | 196 | 36 | 89 | 90 | 189 | 0 | 19 | 97 | 52 | 52.2 | 0 | 36 | 15 | 0 | 392 | 0 | 69 | 156 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 111 | 28 | 70 | 0 | 0 | 0 | 8012.06 | 923 | 105 | 0 | 16 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 740.63 | 0 | 47 | 0 | 113 | 113 | 0 | 92 | 38 | 52 | 0 | 0 | 21 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 171 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 181 | 115 | 220 | 0 | 304 | 1212 | 140 | 6558.63 | 14570.69 | 108.93
Total KWH | 176688 | 1077120 | 597600 | 0 | 0 | 0 | 0 | 0 | 8517600 | 0 | 0 | 777240 | 287280 | 1513440 | 1126080 | 1439716 | 1028651 | 1039974 | 2355840 | 0 | 8396000 | 7170647 | 0 | 0 | 714744 | 6846685 | 0 | 0 | 196723 | 1178400 | 358800 | 361800 | 0 | 8962727.27 | 991091 | 1159200 | 0 | 0 | 20160 | 1573310 | 1531816 | 219504 | 251520 | 0 | 25602 | 5258691 | 1983855 | 479040 | 6283636.36 | 1329818 | 0 | 983520 | 263237.4 | 2053273 | 5076203 | 0 | 0 | 0 | 28309088 | 69930 | 1249120 | 2721527 | 936727 | 0 | 8555500 | 7952000 | 1051200 | 4755000 | 732168 | 1936320 | 2106810 | 3006720 | 31080 | 430440 | 1917480 | 1127040 | 528302 | 376991 | 813056 | 3993340 | 0 | 9441000 | 0 | 1623480 | 3695891 | 0 | 0 | 1970880 | 719712 | 0 | 0 | 4428090 | 297720 | 2191200 | 686400 | 1544640 | 9250 | 187720 | 278400 | 183281454.03 | 22125090 | 2486016 | 0 | 181440 | 322560 | 912000 | 0 | 0 | 0 | 0 | 0 | 528480 | 23105450 | 0 | 19553818 | 0 | 463739 | 0 | 1818528 | 2107680 | 0 | 989024 | 262302 | 743323 | 371034 | 684473 | 248099 | 0 | 250504 | 3332909 | 0 | 3457500 | 0 | 3416091 | 0 | 8261600 | 0 | 17640 | 4058000 | 1154181 | 2300878 | 100205 | 2157158 | 0 | 1445062.5 | 0 | 23928.6 | 985680 | 3154 | 1413696 | 6546000 | 2738000 | 5364410 | 0 | 7388352 | 28714181.82 | 2265600 | 162297786.92 | 345579240.95

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14133.01 | MW | 11:00 Hr. | Energy Generated |  |  | 345.5792 |  | MKWHr.
| Day Peak Demand |  |  | 14582.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 15.456 |  | MKWHr.
| Evening Peak Generation |  |  | 14881.02 | MW | 20:00 Hr. | Energy Demand |  |  | 361.0352 |  | MKWHr.
| Evening Peak Demand |  |  | 16248.02 | MW | 20:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 13210.49 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 964.93 |  | MMCFD
| Maximum Generation of the Day |  |  | 15424.93 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.0255 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6143 | 0 | 13.3128 | 0 | 0 | 0.19672 | 0 | 0 | 54.1238 | Gas | 130.412 | Gas | 468537220.2259
| Chattogram Zone |  |  | 5.5552 | 34.5927 | 12.3401 | 0 | 5.2587 | 0.095532 | 0 | 0.02016 | 57.8625 | Coal | 105.5589 | Coal | 630766400.0846
| Cumilla Zone |  |  | 27.769 | 0 | 10.9545 | 0 | 0 | 0.37699 | 1.127 | 0 | 40.2275 | HFO | 55.3351 | HFO | 1022196428.072
| Mymensingh Zone |  |  | 1.5446 | 0 | 3.4537 | 0 | 0 | 0.19697 | 0 | 0 | 5.1953 | HSD | 1.4451 | HSD | 0
| Sylhet Zone |  |  | 25.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.8724 | Hydro | 5.2587 | Hydro | 525869.1
| Khulna Zone |  |  | 2.486 | 23.1055 | 0.504 | 0 | 0 | 0.52848 | 23.0371 | 0 | 49.661 | Solar | 3.8313 | Solar | 56073700.236
| Barishal Zone |  |  | 8.1024 | 42.6485 | 3.6793 | 0 | 0 | 0.003154 | 0 | 0 | 54.4334 | Import | 43.7179 | Import | 249477775.04
| Rajshahi Zone |  |  | 18.4681 | 0 | 6.6327 | 0 | 0 | 1.3237 | 19.5538 | 0 | 45.9783 | Wind | 0.02016 | Wind | 297158.4
| Rangpur Zone |  |  | 0 | 5.2122 | 4.458 | 1.4451 | 0 | 1.1098 | 0 | 0 | 12.2251
| Total |  |  | 130.412 | 105.5589 | 55.3351 | 1.4451 | 5.2587 | 3.8313 | 43.7179 | 0.02016 | 345.5792
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 468537220.2259 |  | Hydro | 525869.1
|  |  |  | Coal | 630766400.0846 |  | Solar | 56073700.236
|  |  |  | HFO | 1022196428.072 |  | Import | 249477775.04
|  |  |  | HSD | 0 |  | Wind | 297158.4
[5 empty] | Total: | 242,78,74,551 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1251 | Peak Hr Flow | 836.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48830066.43 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 19.5538 | Peak Hr Flow | 741.82 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1948 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.127 | Peak Hr Flow | 46.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2626 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.8059 | Peak Hr Flow | 1623.82 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 265 |  | 5501
|  |  |  | Chattogram |  | 120 |  | 1518
|  |  |  | Cumilla |  | 203 |  | 1507
|  |  |  | Mymensingh |  | 185 |  | 1286
|  |  |  | Sylhet |  | 125 |  | 661
|  |  |  | Khulna |  | 160 |  | 1779
|  |  |  | Barishal |  | 25 |  | 458
|  |  |  | Rajshahi |  | 100 |  | 1688
|  |  |  | Rangpur |  | 125 |  | 1025
|  |  |  | Total |  | 1308 |  | 15423
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:52 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 08:54 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 09:44 | 18:15 | BIPTC S/S Baharampur-3 Scheduled S/D
|  | 10:14 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
|  | 10:14 | Chandpur 132/33kV S/S 33 kV T-5 section is restored.
| 11:00 |  | Day peak Generation is 14129 MW
|  | 12:01 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
|  | 14:20 | Rahanpur 400/132kV S/S Bus Reactor 400 KV is restored.
| 17:50 | 18:39 | Chhatak 132/33kV S/S T-3 HT Forced S/D Due to Maintanance Oil leakage of 132 kv SF6 CB of
T-3
|  | 18:09 | Chandpur 132/33kV S/S 422T(T-5) HT is restored.
|  | 18:09 | Chandpur 132/33kV S/S 422T(T-5) LT is restored.
| 18:11 |  | Chandpur 132/33kV S/S 412T (T-2) LT Forced S/D
| 18:12 |  | Chandpur 132/33kV S/S 200KVA Aux. T-2 HT Forced S/D
| 20:13 | 20:50 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Forced S/D from Ashuganj 230/132/33kV end Due to Wave
trap problem.
| 22:27 |  | Summit Bibiana-2 GT was sync.
| 00:21 |  | Summit Bibiana-2 ST was sync.
| 03:48 | 04:31 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Corrective maintenance work for PBS 33kv | [7 empty] | 40.0MW load
|  |  | Langulbanbdo feeder Y-phase source DS flashing. Work done by PBS. | [7 empty] | interrup.
| 07:00 |  | Minimum Gen. is 13776 MW.
| 07:23 |  | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to work of PDB
| 07:23 |  | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to work of PDB | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 352 | 8517600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8396000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 7170647 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1028651 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 6846685 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 65 | 176688 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 777240 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 108 | 1126080 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 1039974 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 714744 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 358800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 361800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 597600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 1439716 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1513440 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 1077120 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 2355840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 196723 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 287280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 8962727.27 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1178400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2637 | 54123755.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 263237.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 69930 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 983520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5258691 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5076203 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 93 | 2053273 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 1531816 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1573310 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 11 | 251520 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 479040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 155 | 1159200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 219504 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1983855 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 86 | 991091 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 134 | 1329818 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1130 | 28309088 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 20160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 264 | 6283636.36 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2669 | 57862494.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 176 | 4755000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8555500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7952000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 732168 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1051200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 26 | 936727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249120 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 2721527 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 813056 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2106810 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 167 | 3006720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1127040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 528302 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 430440 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1917480 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 31080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 1936320 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 376991 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1738.2 | 40227481
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 63 | 1544640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 686400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 100 | 2191200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 187720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 278400 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 297720 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 220 | 5195330
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 69 | 1623480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3695891 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719712 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1970880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4428090 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 3993340 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 9441000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 868 | 25872393
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 836 | 22125090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 181440 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 322560 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 108 | 2486016 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 528480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 736 | 23105450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1773 | 49661036
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 349 | 7388352 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 99 | 1413696 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2738000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 28714181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5364410 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 128 | 2265600 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 305 | 6546000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3154 | -
Barishal Area Total |  |  |  |  | 2236 | 2438 | 54433393.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 371034 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 463739 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 262302 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 132 | 3332909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 154 | 3457500 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 135 | 3416091 | Low gas pressure
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 387 | 8261600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 248099 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 743323 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 989024 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2107680 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1818528 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 741.82 | 19553818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 250504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 684473 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2026.82 | 45978264
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 66 | 1445062.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1154181 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 166 | 4058000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2157158 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23928.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2300878 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 100205 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 985680 | -
Rangpur Area Total |  |  |  |  | 950 | 511 | 12225093.1
Eastern Grid Total |  |  |  |  | 17385.715 | 8132.2 | 183281454.03
Western Grid Total |  |  |  |  | 10444.16 | 6748.82 | 162297786.92
National Grid Total |  |  |  |  | 27829.875 | 14881.02 | 345579240.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-09-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9574.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4539.6 | MW
i) Dhaka area |  |  | 5235.87 |  | MW | i) Khulna area |  |  |  | 1619 | MW
ii) Chattogram area |  |  | 1398 |  | MW | ii) Barishal area |  |  |  | 433 | MW
iii) Cumilla area |  |  | 1303.88 |  | MW | iii) Rajshahi area |  |  |  | 1587.6 | MW
iv) Mymensingh area |  |  | 1101 |  | MW | iv) Rangpur area |  |  |  | 900 | MW
v) Sylhet area |  |  | 536 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14114.35 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 88 | 18:30 | 133 | PHP | 8 | 05:00
2 | AKSML | 153 | 04:00 | 68 | Ishurdi | 85 | 19:00 | 134 | Pabna | 125 | 20:00
3 | Aftabnagar | 42 | 00:00 | 69 | Jaldhaka | 92 | 19:00 | 135 | Palashbari | 122 | 02:00
4 | Agargaon | 150 | 13:00 | 70 | Jamalpur | 113 | 06:00 | 136 | Panchagarh | 62 | 19:00
5 | Agrabad | 104 | 12:00 | 71 | Jashore | 158 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 33 | 04:00 | 72 | Jhenaidah | 133 | 00:00 | 138 | Patuakhali | 78 | 00:00
7 | Ashuganj | 95 | 03:00 | 73 | Joydebpur | 156 | 18:00 | 139 | Payra | 36 | 21:00
8 | BSRM | 148 | 10:00 | 74 | Joypurhat | 70 | 20:00 | 140 | Postogola | 61 | 00:00
9 | Bagerhat | 83 | 01:00 | 75 | Juldah | 15.5 | 16:00 | 141 | Purbachal | 24 | 13:00
10 | Bajitpur | 102 | 18:30 | 76 | KSRM | 29 | 14:00 | 142 | Purbasadipur | 123 | 19:00
11 | Bakulia | 104 | 15:00 | 77 | Kabirpur | 213 | 18:00 | 143 | Rahanpur | 44 | 02:00
12 | Banani | 58 | 12:00 | 78 | Kachua | 92 | 00:00 | 144 | Rahim | 37 | 10:00
13 | Bangabhaban | 26 | 10:00 | 79 | Kallyanpur | 117 | 00:00 | 145 | Rajbari | 89 | 00:00
14 | Barapukuria | 64 | 03:00 | 80 | Kalurghat | 44 | 15:00 | 146 | Rajendrapur | 123 | 09:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 83 | 17:00 | 147 | Rajshahi | 114 | 01:00
16 | Barishal | 121 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 108 | 19:00
17 | Barishal-230 | 102 | 00:00 | 83 | Kasba | 34 | 02:00 | 149 | Ramganj | 98 | 03:00
18 | Baroaulia | 70 | 11:00 | 84 | Kazla | 106 | 19:00 | 150 | Rampur | 43 | 00:00
19 | Baroirhat | 58 | 23:00 | 85 | Keranigonj | 85 | 01:00 | 151 | Rangamati | 17 | 10:00
20 | Bashundhara | 223 | 13:00 | 86 | Khagrachori | 30 | 19:00 | 152 | Rangpur | 142 | 19:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 70 | 21:00 | 153 | Ruppur | 9.2 | 10:00
22 | Beanibazar | 84 | 01:00 | 88 | Khulshi | 200 | 15:00 | 154 | SSM | 14 | 00:00
23 | Benapole | 70 | 01:00 | 89 | Kishoreganj | 135 | 00:00 | 155 | Saidpur | 101 | 12:00
24 | Bhaluka | 143 | 11:00 | 90 | Kodda | 280 | 08:00 | 156 | Satkhira | 124 | 00:00
25 | Bhandaria | 60 | 00:00 | 91 | Kulaura | 52 | 02:00 | 157 | Satmasjid | 111 | 19:00
26 | Bhangura | 38 | 01:00 | 92 | Kurigram | 58 | 00:00 | 158 | Savar | 239 | 09:00
27 | Bheramara(GK) | 71 | 00:00 | 93 | Kushtia | 165 | 00:00 | 159 | SevenRings | 21.07 | 16:00
28 | Bhulta | 202 | 00:00 | 94 | Laksam | 35 | 23:00 | 160 | ShahCement | 31 | 11:00
29 | Bog-Sherpur | 84 | 02:00 | 95 | Lakshmipur | 35 | 01:00 | 161 | Shahjadpur | 92 | 12:00
30 | Bogura | 175 | 21:00 | 96 | Lalbag | 51 | 01:00 | 162 | Shahjibazar | 131 | 02:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 60 | 02:00 | 163 | Shahmirpur | 69 | 00:00
32 | Brahmanbaria | 134 | 01:00 | 98 | MI_Cement | 11.5 | 21:00 | 164 | Shariatpur | 97 | 00:00
33 | Cantonment | 154 | 13:00 | 99 | Madanganj | 40 | 18:30 | 165 | Sherpur | 120 | 00:00
34 | Chandina | 43.53 | 23:00 | 100 | Madaripur | 128 | 00:00 | 166 | Shikalbaha | 15 | 16:00
35 | Chandpur | 94 | 00:00 | 101 | Madartek | 102 | 23:00 | 167 | Shitalakhya | 76.7 | 13:00
36 | Chandraghona | 34 | 00:00 | 102 | Madunaghat | 66 | 19:30 | 168 | Sholosohor | 50 | 15:00
37 | Chapai | 72 | 02:00 | 103 | Magura | 66 | 00:00 | 169 | Shyampur | 170 | 11:00
38 | Charsaidpur | 36 | 00:00 | 104 | Mahasthangarh | 88 | 00:00 | 170 | Siddhirganj | 123 | 18:30
39 | Chauddagram | 71 | 04:00 | 105 | Maijdee | 16 | 05:00 | 171 | Sirajganj | 123 | 19:00
40 | Chhatak | 40 | 01:00 | 106 | Manikganj | 126 | 02:00 | 172 | Sonargaon | 129 | 01:00
41 | Chowmuhani | 175 | 05:00 | 107 | Maniknagar | 66 | 12:00 | 173 | Sreemongol | 87 | 00:00
42 | Chuadanga | 120 | 00:00 | 108 | Matarbari | 52 | 02:00 | 174 | Sreepur | 95 | 11:00
43 | Coxsbazar | 134 | 06:00 | 109 | Matuail | 74 | 09:00 | 175 | Srinagar | 49.68 | 00:00
44 | Cumilla(N) | 152 | 00:00 | 110 | Millgate | 129 | 12:00 | 176 | Sunamganj | 60 | 01:00
45 | Cumilla(S) | 156 | 16:00 | 111 | Mirpur | 141 | 11:00 | 177 | Sylhet | 52 | 01:00
46 | Daganbhuiyan | N/A | N/A | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 113 | 00:00
47 | Daudkandi | 156 | 01:00 | 113 | Mirzapur | 35 | 05:00 | 179 | TK | 39 | 19:00
48 | Dhaka | 98 | 11:00 | 114 | Mithapukur | 70 | 00:00 | 180 | Tangail | 168 | 13:00
49 | Dhamrai | 128 | 09:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 00:00
50 | Dhanmondi | 131 | 13:00 | 116 | Mogbazar | 119.4 | 13:00 | 182 | Thakurgaon | 110 | 00:00
51 | Dohazari | 113 | 00:00 | 117 | Mongla | 47 | 18:30 | 183 | Tongi | 121 | 18:30
52 | Faridpur | 192 | 00:00 | 118 | Motijheel | 50 | 18:30 | 184 | Ullahpara | 45 | 19:30
53 | Fatullah | 110 | 16:00 | 119 | Muktagacha | 31 | 00:00 | 185 | Ullon | 61 | 00:00
54 | Fenchuganj | 46 | 00:00 | 120 | Munshiganj | 126 | 00:00 | 186 | Uttara | 94 | 13:00
55 | Feni | 126 | 23:00 | 121 | Muradnagar | 41 | 01:00 | 187 | UttaraNew | 66 | 00:00
56 | GPH | 20 | 17:00 | 122 | Mymensingh | 216 | 22:00 | 188 | Zigatola | 78 | 00:00
57 | Ghatail | 76 | 00:00 | 123 | Naogaon | 150 | 20:00
58 | Ghorashal | 15 | 19:00 | 124 | Narail | 56 | 18:30
59 | Ghorashal-230 | 90 | 00:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 42 | 00:00 | 126 | Narshingdi | 179 | 01:00
61 | Gollamari | 114 | 00:00 | 127 | Natore | 165 | 21:00
62 | Gopalganj | 110 | 00:00 | 128 | Nawabganj | 65.6 | 01:00
63 | Gulshan | 140 | 12:00 | 129 | Netrakona | 133 | 19:00
64 | Halishahar | 83 | 15:00 | 130 | New | 80 | 13:00
65 | HaripurSBU | 150 | 10:00 | 131 | Niamatpur | 82 | 21:00
66 | Hasnabad | 85 | 01:00 | 132 | Noapara | 49 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15424.93 | 693 |  | 16148.93
1:00 | 15180.39 | 469 |  | 15670.39
2:00 | 14925.02 | 187 |  | 15120.02
3:00 | 14674.13 | 169 |  | 14850.74
4:00 | 14273.26 | 140 |  | 14419.56
5:00 | 14125.87 | 119 |  | 14250.23
6:00 | 13528.13 | 109 |  | 13642.04
7:00 | 13406.71 | 92 |  | 13502.85
8:00 | 13210.49 | 125 |  | 13341.12
9:00 | 13557.47 | 138 |  | 13701.68
10:00 | 13878.47 | 92 |  | 13974.61
11:00 | 14133.01 | 259 |  | 14404.01
12:00 | 14085.24 | 476 |  | 14582.24
13:00 | 13921.67 | 938 |  | 14901.67
14:00 | 14011.6 | 899 |  | 14951.06
15:00 | 14047.31 | 913 |  | 15001.4
16:00 | 13948.86 | 912 |  | 14901.9
17:00 | 13708.08 | 855 |  | 14601.56
18:00 | 13623.74 | 838 |  | 14499.45
19:00 | 14725.19 | 1281 |  | 16064.19
19:30 | 14780.55 | 1356 |  | 16197.57
20:00 | 14881.02 | 1308 |  | 16248.02
21:00 | 14853.88 | 1334 |  | 16247.88
22:00 | 14775.51 | 1457 |  | 16298.51
23:00 | 14570.69 | 1653 |  | 16297.69
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8016.6 | 7408.33 | 15424.93 | DAILY GENERATION CURVE
00:30 | 7900.5 | 7402.16 | 15302.66
01:00 | 7784.4 | 7395.99 | 15180.39 | 09-09-2025
01:30 | 7714.65 | 7338.055 | 15052.705
02:00 | 7644.9 | 7280.12 | 14925.02
02:30 | 7648.85 | 7150.725 | 14799.575
03:00 | 7652.8 | 7021.33 | 14674.13
03:30 | 7561.9 | 6911.795 | 14473.695
04:00 | 7471 | 6802.26 | 14273.26
04:30 | 7440.6 | 6758.965 | 14199.565
05:00 | 7410.2 | 6715.67 | 14125.87
05:30 | 7200.74 | 6626.26 | 13827
06:00 | 6991.28 | 6536.85 | 13528.13
06:30 | 7024.435 | 6442.985 | 13467.42
07:00 | 7057.59 | 6349.12 | 13406.71
07:30 | 6983.585 | 6325.015 | 13308.6
08:00 | 6909.58 | 6300.91 | 13210.49
08:30 | 7007.955 | 6376.025 | 13383.98
09:00 | 7106.33 | 6451.14 | 13557.47
09:30 | 7193.835 | 6524.135 | 13717.97
10:00 | 7281.34 | 6597.13 | 13878.47
10:30 | 7323.72 | 6682.02 | 14005.74
11:00 | 7366.1 | 6766.91 | 14133.01
11:30 | 7324.56 | 6784.565 | 14109.125
12:00 | 7283.02 | 6802.22 | 14085.24
12:30 | 7239.54 | 6763.915 | 14003.455
13:00 | 7196.06 | 6725.61 | 13921.67
13:30 | 7287.905 | 6678.73 | 13966.635
14:00 | 7379.75 | 6631.85 | 14011.6
14:30 | 7409.095 | 6620.36 | 14029.455
15:00 | 7438.44 | 6608.87 | 14047.31
15:30 | 7397.57 | 6600.515 | 13998.085
16:00 | 7356.7 | 6592.16 | 13948.86
16:30 | 7331.87 | 6496.6 | 13828.47
17:00 | 7307.04 | 6401.04 | 13708.08
17:30 | 7350.08 | 6315.83 | 13665.91
18:00 | 7393.12 | 6230.62 | 13623.74
18:30 | 7728.66 | 6445.805 | 14174.465
19:00 | 8064.2 | 6660.99 | 14725.19
19:30 | 8091.2 | 6689.35 | 14780.55
20:00 | 8132.2 | 6748.82 | 14881.02
20:30 | 8133.88 | 6733.57 | 14867.45 |  | Executive Engineer
21:00 | 8135.56 | 6718.32 | 14853.88 |  | Network Operation Division
21:30 | 8117.56 | 6697.135 | 14814.695
22:00 | 8099.56 | 6675.95 | 14775.51
22:30 | 8055.81 | 6617.29 | 14673.1
23:00 | 8012.06 | 6558.63 | 14570.69

## En-Curve
QF-LDC-12
Date | 09-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3570 | 2008 | 919 | 38 | 54 | 997.33 | 222 | 4712 | 0 | 589 | 2249.6 | 66 | 0 | 0 | 693 | DAILY ENERGY CURVE
00:30 | 3551 | 1989 | 919 | 38 | 53 | 1005.16 | 222 | 4703 | 0 | 565.5 | 2191 | 66 | 0 | 0 | 581 | 09-09-2025
01:00 | 3532 | 1970 | 919 | 38 | 52 | 1012.99 | 222 | 4694 | 0 | 542 | 2132.4 | 66 | 0 | 0 | 469
01:30 | 3536 | 1970.5 | 925 | 38 | 51 | 1019.055 | 222 | 4687 | 0 | 537 | 2001.15 | 66 | 0 | 0 | 328 | Energy Generated | 345.5792 |  | MKWHr
02:00 | 3540 | 1971 | 931 | 38 | 50 | 1025.12 | 222 | 4680 | 0 | 532 | 1869.9 | 66 | 0 | 0 | 187 | Energy not Served | 15.456 |  | MKWHr
02:30 | 3551.5 | 1967 | 931 | 38 | 50 | 1028.725 | 221.5 | 4690 | 0 | 465.5 | 1790.35 | 66 | 0 | 0 | 178 | Total Energy Requirement | 361.0352 |  | MKWHr
03:00 | 3563 | 1963 | 931 | 38 | 50 | 1032.33 | 221 | 4700 | 0 | 399 | 1710.8 | 66 | 0 | 0 | 169
03:30 | 3560.5 | 1961 | 931.5 | 38 | 49 | 1039.795 | 220.5 | 4697 | 0 | 385 | 1525.4 | 66 | 0 | 0 | 154.5
04:00 | 3558 | 1959 | 932 | 38 | 48 | 1047.26 | 220 | 4694 | 0 | 371 | 1340 | 66 | 0 | 0 | 140
04:30 | 3537.5 | 1956.5 | 932 | 38 | 48 | 1092.465 | 220 | 4686.5 | 0 | 339.5 | 1283.1 | 66 | 0 | 0 | 129.5
05:00 | 3517 | 1954 | 932 | 38 | 48 | 1137.67 | 220 | 4679 | 0 | 308 | 1226.2 | 66 | 0 | 0 | 119
05:30 | 3478 | 1904 | 931.5 | 38 | 46 | 1155.445 | 219.5 | 4668 | 1.255 | 280 | 1039.3 | 66 | 0 | 0 | 114
06:00 | 3439 | 1854 | 931 | 38 | 44 | 1173.22 | 219 | 4657 | 2.51 | 252 | 852.4 | 66 | 0 | 0 | 109
06:30 | 3459 | 1878.5 | 931 | 38 | 43 | 1051.11 | 220.5 | 4680.5 | 36.31 | 259 | 804.5 | 66 | 0 | 0 | 100.5
07:00 | 3479 | 1903 | 931 | 38 | 42 | 929 | 222 | 4704 | 70.11 | 266 | 756.6 | 66 | 0 | 0 | 92
07:30 | 3452 | 1853.5 | 931.5 | 38 | 40 | 843.505 | 222 | 4665 | 137.195 | 265.5 | 794.4 | 66 | 0 | 0 | 108.5
08:00 | 3425 | 1804 | 932 | 38 | 38 | 758.01 | 222 | 4626 | 204.28 | 265 | 832.2 | 66 | 0 | 0 | 125
08:30 | 3432 | 1824.5 | 932 | 38 | 36 | 758.005 | 222 | 4573 | 258.375 | 265 | 979.1 | 66 | 0 | 0 | 131.5
09:00 | 3439 | 1845 | 932 | 38 | 34 | 758 | 222 | 4520 | 312.47 | 265 | 1126 | 66 | 0 | 0 | 138
09:30 | 3445.5 | 1858.5 | 932 | 38 | 35 | 747 | 222 | 4510 | 404.47 | 270.5 | 1189 | 66 | 0 | 0 | 115
10:00 | 3452 | 1872 | 932 | 38 | 36 | 736 | 222 | 4500 | 496.47 | 276 | 1252 | 66 | 0 | 0 | 92
10:30 | 3336 | 1975.5 | 932 | 38 | 37 | 740 | 222 | 4500.5 | 507.49 | 275.5 | 1375.75 | 66 | 0 | 0 | 175.5
11:00 | 3220 | 2079 | 932 | 38 | 38 | 744 | 222 | 4501 | 518.51 | 275 | 1499.5 | 66 | 0 | 0 | 259
11:30 | 3224 | 1982.5 | 932.5 | 38 | 38 | 741 | 222 | 4457.5 | 507.325 | 282.5 | 1615.8 | 66.5 | 0 | 1.5 | 367.5
12:00 | 3228 | 1886 | 933 | 38 | 38 | 738 | 222 | 4414 | 496.14 | 290 | 1732.1 | 67 | 0 | 3 | 476
12:30 | 3215.5 | 1853.5 | 932.5 | 38 | 49 | 739 | 222 | 4253.5 | 482.305 | 318 | 1830.65 | 66.5 | 0 | 3 | 707
13:00 | 3203 | 1821 | 932 | 38 | 60 | 740 | 222 | 4093 | 468.47 | 346 | 1929.2 | 66 | 0 | 3 | 938
13:30 | 3279.5 | 1789.5 | 932 | 38 | 58 | 742.67 | 221 | 4058 | 453.365 | 356.5 | 1969.6 | 66 | 0 | 2.5 | 918.5
14:00 | 3356 | 1758 | 932 | 38 | 56 | 745.34 | 220 | 4023 | 438.26 | 367 | 2010 | 66 | 0 | 2 | 899
14:30 | 3455 | 1737.5 | 932 | 38 | 56 | 741.63 | 219 | 4058 | 391.325 | 363 | 1968.5 | 66 | 0 | 3.5 | 906
15:00 | 3554 | 1717 | 932 | 38 | 56 | 737.92 | 218 | 4093 | 344.39 | 359 | 1927 | 66 | 0 | 5 | 913
15:30 | 3554.5 | 1705 | 932 | 38 | 49 | 737.565 | 218.5 | 4120 | 286.52 | 371.5 | 1917 | 66 | 0 | 2.5 | 912.5
16:00 | 3555 | 1693 | 932 | 38 | 42 | 737.21 | 219 | 4147 | 228.65 | 384 | 1907 | 66 | 0 | 0 | 912
16:30 | 3543 | 1648 | 932 | 38 | 44 | 735.14 | 219.5 | 4095 | 150.33 | 417.5 | 1940 | 66 | 0 | 0 | 883.5
17:00 | 3531 | 1603 | 932 | 38 | 46 | 733.07 | 220 | 4043 | 72.01 | 451 | 1973 | 66 | 0 | 0 | 855
17:30 | 3457.5 | 1617.5 | 932 | 38 | 46 | 736.93 | 220 | 3972 | 37.98 | 475.5 | 2066.5 | 66 | 0 | 0 | 846.5
18:00 | 3384 | 1632 | 932 | 38 | 46 | 740.79 | 220 | 3901 | 3.95 | 500 | 2160 | 66 | 0 | 0 | 838
18:30 | 3494 | 1674.5 | 932 | 38 | 47 | 738.89 | 196 | 4008 | 1.975 | 612.5 | 2365.6 | 66 | 0 | 0 | 1059.5
19:00 | 3604 | 1717 | 932 | 38 | 48 | 736.99 | 172 | 4115 | 0 | 725 | 2571.2 | 66 | 0 | 0 | 1281
19:30 | 3578 | 1686 | 836 | 38 | 48 | 738.35 | 172 | 4213 | 0 | 747 | 2658.2 | 66 | 0 | 0 | 1356
20:00 | 3615 | 1686 | 836 | 38 | 46 | 741.82 | 222 | 4223 | 0 | 754 | 2651.2 | 66 | 0 | 2 | 1308
20:30 | 3647 | 1694.5 | 816 | 38 | 48 | 743.57 | 222 | 4234 | 0 | 733.5 | 2623.88 | 66 | 0 | 1 | 1321
21:00 | 3679 | 1703 | 796 | 38 | 50 | 745.32 | 222 | 4245 | 0 | 713 | 2596.56 | 66 | 0 | 0 | 1334
21:30 | 3669.5 | 1667 | 796 | 38 | 51 | 743.635 | 221.5 | 4244.5 | 0 | 704 | 2613.56 | 66 | 0 | 0 | 1395.5
22:00 | 3660 | 1631 | 796 | 38 | 52 | 741.95 | 221 | 4244 | 0 | 695 | 2630.56 | 66 | 0 | 0 | 1457
22:30 | 3635 | 1645.25 | 859.5 | 38 | 52 | 741.29 | 220.5 | 4171.5 | 0 | 659 | 2617.56 | 33 | 0 | 0.5 | 1555
23:00 | 3610 | 1659.5 | 923 | 38 | 52 | 740.63 | 220 | 4099 | 0 | 623 | 2604.56 | 0 | 0 | 1 | 1653
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 19:30 | 368 | 11:00 | Payra | 414 | 18:00 | 410 | 00:00
Ashuganj | 402 | 20:00 | 372 | 10:00 | Rahanpur | 403 | 12:00 | 387 | 19:00
Bhulta | 398 | 19:30 | 371 | 11:00 | Rampal | 403 | 14:00 | 390 | 00:00
Bibiana | 383 | 05:00 | 375 | 12:00
BIPTC | 399 | 21:00 | 386 | 13:00
Bogura | 389 | 12:00 | 375 | 19:00
Gopalganj | 398 | 12:00 | 385 | 00:00
Kaliakoir | 371 | 19:00 | 359 | 11:00
Madunaghat | 395 | 20:00 | 387 | 11:00
Meghnaghat | 382 | 19:30 | 372 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 05:00 | 217 | 11:00 | Keranigonj | 222 | 19:30 | 214 | 11:00
AKSML | 233 | 19:00 | 225 | 11:00 | Khulna(S) | 230 | 18:00 | 216 | 00:00
Aminbazar | 224 | 05:00 | 220 | 11:00 | Madunaghat | 236 | 18:30 | 228 | 11:00
Ashuganj | 233 | 19:30 | 222 | 10:00 | Madunaghat-400 | 237 | 20:00 | 229 | 07:00
Ashuganj-400 | 233 | 19:30 | 222 | 10:00 | Maniknagar | 218 | 19:30 | 210 | 11:00
Baghabari | 235 | 22:00 | 228 | 00:00 | Meghnaghat | 226 | 14:00 | 222 | 23:00
Barapukuria | 229 | 11:00 | 221 | 07:00 | Meghnaghat-400 | 223 | 19:30 | 216 | 11:00
Barapukuria-230 | 229 | 11:00 | 221 | 07:00 | Mirsorai | 237 | 19:30 | 224 | 02:00
Barishal | 230 | 13:00 | 222 | 00:00 | Rajshahi | 232 | 13:00 | 222 | 07:00
Bheramara | 234 | 20:00 | 223 | 00:00 | Rampal | 230 | 13:00 | 218 | 00:00
Bhulta | 228 | 19:30 | 210 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 18:00 | 221 | 00:00 | Rampura | 226 | 20:00 | 207 | 11:00
BIPTC | 236 | 20:00 | 223 | 00:00 | Shikalbaha | 237 | 19:00 | 227 | 11:00
Bogura | 244 | 12:00 | 235 | 05:00 | Shyampur | 222 | 20:00 | 214 | 11:00
Bogura-400 | 242 | 12:00 | 234 | 19:00 | Siddhirganj | 220 | 18:00 | 213 | 11:00
Borhanuddin | 233 | 13:00 | 228 | 00:00 | Sirajgonj | 241 | 13:00 | 238 | 00:00
BSRM | 234 | 19:30 | 223 | 02:00 | Sreepur | 230 | 19:30 | 222 | 00:00
Cumilla(N) | 225 | 19:30 | 216 | 11:00 | Tongi | 227 | 19:30 | 213 | 11:00
Faridpur | 225 | 19:30 | 217 | 00:00
Fenchuganj | 229 | 18:00 | 222 | 01:00
Ghorashal | 225 | 00:00 | 220 | 10:00
Ghorashal-230 | 228 | 20:00 | 212 | 11:00
Gopalganj | 227 | 18:00 | 219 | 00:00
GPH | 232 | 16:00 | 227 | 00:00
Haripur | 219 | 19:30 | 212 | 11:00
Hasnabad | 222 | 19:30 | 215 | 11:00
Hathazari | 231 | 18:00 | 224 | 08:00
Ishurdi | 236 | 20:00 | 225 | 02:00
Jhenaidah | 230 | 13:00 | 217 | 00:00
Kaliakoir | 232 | 19:30 | 221 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 19:00 | 124 | 10:00 | Lalmonirhat | 131 | 10:00 | 125 | 07:00
Agargaon | 135 | 05:00 | 128 | 11:00 | Madanganj | 129 | 19:30 | 125 | 10:00
Agrabad | 133 | 17:00 | 128 | 10:00 | Madaripur | 135 | 13:00 | 130 | 00:00
AKS | 131 | 18:30 | 126 | 09:00 | Madartek | 138 | 20:00 | 124 | 11:00
Aminbazar | 133 | 04:00 | 128 | 12:00 | Madunaghat | 136 | 17:00 | 131 | 03:00
Amnura | 137 | 20:00 | 128 | 02:00 | Magura | 134 | 13:00 | 123 | 00:00
Ashuganj | 140 | 14:00 | 135 | 00:00 | Mahasthangarh | 136 | 12:00 | 128 | 07:00
Bagerhat | 130 | 13:00 | 120 | 4:00 | Maijdee | 123 | 19:00 | 123 | 5:00
Bajitpur | 130 | 13:00 | 124 | 01:00 | Manikganj | 127 | 15:00 | 118 | 11:00
Bakulia | 136 | 19:00 | 130 | 00:00 | Maniknagar | 131 | 03:00 | 125 | 11:00
Banani | 138 | 19:30 | 126 | 11:00 | Matarbari | 125 | 12:00 | 109 | 01:00
Bangabhaban | 131 | 05:00 | 125 | 11:00 | Matuail | 128 | 18:00 | 124 | 11:00
Barapukuria | 140 | 11:00 | 130 | 07:00 | Millgate | 131 | 19:00 | 122 | 10:00
Barguna | 140 | 20:00 | 132 | 06:00 | Mirpur | 131 | 04:00 | 127 | 09:00
Barishal | 137 | 14:00 | 129 | 04:00 | Mirzapur | 131 | 19:00 | 124 | 00:00
Barishal-230 | 137 | 14:00 | 120 | 05:00 | Mithapukur | 136 | 13:00 | 125 | 07:00
Baroaulia | 135 | 19:00 | 130 | 00:00 | MI_Cement | 130 | 19:30 | 125 | 11:00
Baroirhat | 129 | 19:00 | 120 | 07:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 19:30 | 122 | 11:00 | Mogbazar | 139 | 20:00 | 125 | 11:00
BashundharaCement | 129 | 19:30 | 125 | 11:00 | Mongla | 131 | 13:00 | 119 | 00:00
Beanibazar | 127 | 19:00 | 121 | 01:00 | Motijheel | 131 | 05:00 | 125 | 11:00
Benapole | 130 | 13:00 | 118 | 00:00 | Muktagacha | 130 | 19:00 | 121 | 23:00
Bhaluka | 131 | 19:30 | 123 | 01:00 | Munshiganj | 129 | 19:30 | 125 | 11:00
Bhandaria | 136 | 23:00 | 120 | 00:00 | Muradnagar | 127 | 18:30 | 119 | 02:00
Bhangura | 132 | 13:00 | 129 | 02:00 | Mymensingh | 130 | 19:00 | 115 | 07:00
Bheramara | 136 | 05:00 | 131 | 01:00 | Naogaon | 132 | 12:00 | 125 | 07:00
Bheramara(GK) | 135 | 13:00 | 131 | 00:00 | Narail | 135 | 19:30 | 122 | 00:00
Bhulta | 121 | 19:00 | 118 | 11:00 | Narinda | 131 | 03:00 | 125 | 11:00
Bog-Sherpur | 135 | 11:00 | 129 | 07:00 | Narshingdi | 140 | 20:00 | 114 | 10:00
Bogura | 138 | 12:00 | 130 | 07:00 | Natore | 135 | 13:00 | 129 | 04:00
Bogura-230 | 138 | 12:00 | 132 | 05:00 | Nawabganj | 136 | 20:00 | 130 | 11:00
Brahmanbaria | 134 | 16:00 | 127 | 00:00 | Netrakona | 124 | 12:00 | 113 | 01:00
Cantonment | 134 | 04:00 | 128 | 11:00 | New | 132 | 19:30 | 123 | 11:00
Chandina | 130 | 18:00 | 123 | 02:00 | Niamatpur | 137 | 11:00 | 131 | 15:00
Chandpur | 134 | 19:00 | 123 | 02:00 | Noapara | 134 | 18:00 | 122 | 01:00
Chandraghona | 136 | 18:00 | 130 | 03:00 | Pabna | 133 | 13:00 | 128 | 02:00
Chapai | 135 | 00:00 | 130 | 18:30 | Palashbari | 133 | 13:00 | 125 | 03:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 19:30 | 125 | 11:00 | Panchagarh | 138 | 11:00 | 128 | 07:00
Chauddagram | 128 | 19:00 | 118 | 03:00 | Patiya | 135 | 18:00 | 128 | 00:00
Chhatak | 127 | 09:00 | 118 | 02:00 | Patuakhali | 140 | 18:30 | 133 | 06:00
Chowmuhani | 124 | 18:30 | 114 | 05:00 | Payra | 137 | 01:00 | 134 | 07:00
Chuadanga | 133 | 20:00 | 120 | 00:00 | PHP | 129 | 19:30 | 118 | 11:00
Coxsbazar | 124 | 19:00 | 110 | 00:00 | Postogola | 131 | 05:00 | 127 | 11:00
Cumilla(N) | 130 | 18:00 | 123 | 02:00 | Purbachal | 138 | 19:30 | 122 | 11:00
Cumilla(S) | 132 | 04:00 | 122 | 01:00 | Purbasadipur | 135 | 13:00 | 127 | 07:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Rahanpur | 138 | 00:00 | 132 | 19:00
Daudkandi | 125 | 19:00 | 116 | 01:00 | Rahanpur-400 | 138 | 00:00 | 132 | 21:00
Dhaka | 140 | 20:00 | 126 | 11:00 | Rahim | 128 | 18:00 | 124 | 12:00
Dhamrai | 132 | 18:00 | 125 | 11:00 | Rajbari | 133 | 18:00 | 125 | 00:00
Dhanmondi | 139 | 19:30 | 125 | 11:00 | Rajendrapur | 141 | 19:30 | 122 | 11:00
Dohazari | 131 | 12:00 | 123 | 00:00 | Rajshahi | 133 | 20:00 | 128 | 04:00
Faridpur | 134 | 18:00 | 128 | 00:00 | Rajshahi-230 | 133 | 14:00 | 127 | 07:00
Fatullah | 132 | 20:00 | 126 | 11:00 | Ramganj | 127 | 19:00 | 115 | 03:00
Fenchuganj | 135 | 19:30 | 130 | 01:00 | Rampur | 133 | 17:00 | 127 | 11:00
Feni | 127 | 19:00 | 116 | 03:00 | Rampura | 139 | 20:00 | 125 | 11:00
Ghatail | 128 | 19:00 | 120 | 21:00 | Rangamati | 135 | 18:00 | 130 | 10:00
Ghorashal | 139 | 19:30 | 128 | 11:00 | Rangpur | 135 | 11:00 | 126 | 07:00
Goalpara | 136 | 18:00 | 125 | 00:00 | Ruppur | 136 | 13:00 | 132 | 00:00
Gollamari | 136 | 13:00 | 127 | 00:00 | Saidpur | 136 | 13:00 | 128 | 08:00
Gopalganj | 135 | 18:00 | 127 | 00:00 | Satkhira | 132 | 18:00 | 120 | 00:00
Gopalganj-400 | 136 | 13:00 | 131 | 00:00 | Satmasjid | 134 | 04:00 | 128 | 12:00
Gulshan | 139 | 20:00 | 125 | 11:00 | Savar | 133 | 03:00 | 127 | 14:00
Halishahar | 136 | 19:30 | 130 | 00:00 | SevenRings | 138 | 19:00 | 128 | 11:00
Haripur | 129 | 19:30 | 126 | 09:00 | ShahCement | 130 | 19:30 | 125 | 11:00
HaripurSBU | 129 | 19:30 | 126 | 09:00 | Shahjadpur | 135 | 09:00 | 133 | 01:00
Hasnabad | 132 | 19:30 | 127 | 10:00 | Shahjibazar | 134 | 14:00 | 127 | 00:00
Hathazari | 135 | 14:00 | 131 | 11:00 | Shahmirpur | 136 | 18:00 | 130 | 00:00
Ishurdi | 137 | 13:00 | 132 | 02:00 | Shariatpur | 134 | 13:00 | 126 | 00:00
Jaldhaka | 135 | 13:00 | 128 | 05:00 | Sherpur | 125 | 19:00 | 117 | 07:00
Jamalpur | 129 | 19:00 | 119 | 07:00 | Shikalbaha | 125 | 17:00 | 119 | 02:00
Jashore | 134 | 13:00 | 121 | 00:00 | Shikalbaha-230 | 136 | 17:00 | 131 | 00:00
Jhenaidah | 136 | 14:00 | 120 | 00:00 | Shitalakhya | 130 | 19:30 | 125 | 11:00
Jhenaidah-230 | 136 | 13:00 | 126 | 00:00 | Sholosohor | 136 | 18:00 | 131 | 10:00
Joydebpur | 140 | 19:00 | 122 | 11:00 | Shyampur | 132 | 18:00 | 125 | 11:00
Joypurhat | 130 | 12:00 | 123 | 19:00 | Shyampur-230 | 132 | 18:00 | 126 | 11:00
Juldah | 136 | 19:00 | 130 | 00:00 | Siddhirganj | 129 | 19:30 | 124 | 12:00
Kabirpur | 135 | 19:00 | 119 | 11:00 | Sirajganj | 132 | 13:00 | 127 | 07:00
Kachua | 132 | 18:00 | 121 | 02:00 | Sonargaon | 127 | 14:00 | 122 | 10:00
Kaliakoir | 135 | 19:00 | 128 | 02:00 | Sreemongol | 132 | 19:30 | 126 | 00:00
Kallyanpur | 132 | 05:00 | 128 | 11:00 | Sreepur | 134 | 19:30 | 127 | 00:00
Kalurghat | 137 | 19:30 | 131 | 11:00 | Srinagar | 136 | 06:00 | 131 | 11:00
Kamrangirchar | 136 | 19:30 | 130 | 11:00 | SSM | 138 | 22:00 | 130 | 07:00
Kaptai | 137 | 18:00 | 134 | 1:00 | Sunamganj | 125 | 08:00 | 115 | 01:00
Kasba | 126 | 18:00 | 118 | 02:00 | Sylhet | 128 | 18:00 | 123 | 01:00
Kazla | 131 | 05:00 | 125 | 12:00 | Sylhet-132 | 128 | 09:00 | 124 | 00:00
Keranigonj | 136 | 05:00 | 130 | 11:00 | Tangail | 127 | 19:00 | 119 | 13:00
Khagrachori | 134 | 18:00 | 130 | 00:00 | Taraganj | 134 | 11:00 | 124 | 07:00
Khulna | 136 | 15:00 | 125 | 00:00 | Thakurgaon | 138 | 13:00 | 126 | 07:00
Khulna(S) | 136 | 13:00 | 126 | 00:00 | TK | 136 | 18:00 | 131 | 00:00
Khulshi | 133 | 18:00 | 127 | 10:00 | Tongi | 134 | 18:30 | 124 | 11:00
Kishoreganj | 128 | 14:00 | 121 | 00:00 | Ullahpara | 134 | 13:00 | 129 | 07:00
Kodda | 136 | 19:00 | 121 | 08:00 | Ullon | 139 | 20:00 | 125 | 11:00
KSRM | 136 | 20:00 | 130 | 08:00 | Uttara | 132 | 04:00 | 126 | 11:00
Kulaura | 133 | 14:00 | 129 | 00:00 | UttaraNew | 132 | 04:00 | 126 | 11:00
Kurigram | 133 | 11:00 | 123 | 07:00 | Zigatola | 135 | 05:00 | 130 | 12:00
Kushtia | 131 | 13:00 | 125 | 00:00
Laksam | 132 | 19:30 | 121 | 03:00
Lakshmipur | 125 | 19:30 | 112 | 03:00
Lalbag | 136 | 06:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division