## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-09-2025 | during | 13-09-2025 | during | 13-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 365 | 365 | 365 | 365 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 369 | 366 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 97 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 50 | 0 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 48.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 60 | 123 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 5 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 21.7 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 22 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 18 | 68 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 52 | 87.5 | 87.5 | 51 | 70 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 60 | 147 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 3 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 530 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2033.5 | 2549.9 | 5890.54 | 5924.54 | 5624.88 | 5677.88
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 214 | 214 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 97 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 70 | 48 | 72 | 48 | 78 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 34 | 38 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.53 | 0 | 4.1 | 0 | 4.1 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1150 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 26 | 0 | 2 | 3 | 2 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 267 | 265 | 260 | 260 | 260 | 260 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1780.53 | 2170 | 3111.96 | 3137.86 | 2763.46 | 2795.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 190 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 356 | 349 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 10 | 3 | 250 | 250 | 250 | 250 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 44 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 61 | 172 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 80 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 14 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 180 | 200 | 200 | 80 | 180 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 24 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 89 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1352 | 1861.2 | 2689.56 | 2629.56 | 2386.56 | 2426.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-09-2025 | during | 13-09-2025 | during | 13-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 50 | 104 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 32 | 32 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 77 | 77 | 77 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 12.72 | 0 | 30.37 | 0 | 30.37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 167.72 | 202 | 352.77 | 320.5 | 359.77 | 327.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 38 | 70 | 70 | 70 | 70 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 371 | 389 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1162 | 1202 | 1278 | 1278 | 1216 | 1216
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 893 | 779 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 188 | 245 | 410 | 410 | 410 | 410
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 51 | 0 | 30 | 0 | 30 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 962 | 1141 | 1234.2 | 1234.2 | 1234 | 1234
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2132 | 2203 | 3562.2 | 3532.2 | 3367 | 3337
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 304 | 351 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1055 | 1100 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 167 | 275 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.7 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1861.7 | 2078 | 2162 | 2161 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 48.46 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 150 | 187 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 179 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 180 | 220 | 220 | 220 | 220
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 342 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 22 | 22 | 18 | 18 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 40 | 95 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.12 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 752.16 | 765.27 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 19.76 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 73 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1687.5 | 1992.27 | 2493.59 | 2326.99 | 2416.21 | 2249.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 0 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 161 | 150 | 150 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.2 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 96 | 0 | 150.1 | 0 | 150.1 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 409.2 | 389 | 631.7 | 448 | 651.7 | 468
System Total |  |  |  |  | 28823.2 | 27829.875 | 12586.15 | 14647.37 | 22172.32 | 21758.65 | 20932.58 | 20643.91
Forecast Scenario (13-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14400 |  | 0 |  | 14400
|  |  |  | 1:00 | 14150 |  | 0 |  | 14150
|  |  |  | 2:00 | 13800 |  | 0 |  | 13800
|  |  |  | 3:00 | 13430 |  | 0 |  | 13430
|  |  |  | 4:00 | 13150 |  | 0 |  | 13150
|  |  |  | 5:00 | 12860 |  | 0 |  | 12860
|  |  |  | 6:00 | 12300 |  | 0 |  | 12300
|  |  |  | 7:00 | 12350 |  | 0 |  | 12350
|  |  |  | 8:00 | 12290 |  | 0 |  | 12290
|  |  |  | 9:00 | 12210 |  | 0 |  | 12210
|  |  |  | 10:00 | 12100 |  | 0 |  | 12100
|  |  |  | 11:00 | 12370 |  | 0 |  | 12370
|  |  |  | 12:00 | 12770 |  | 0 |  | 12770
|  |  |  | 13:00 | 13240 |  | 0 |  | 13240
|  |  |  | 14:00 | 13480 |  | 0 |  | 13480
|  |  |  | 15:00 | 13490 |  | 0 |  | 13490
|  |  |  | 16:00 | 13270 |  | 0 |  | 13270
|  |  |  | 17:00 | 12900 |  | 0 |  | 12900
|  |  |  | 18:00 | 12950 |  | 0 |  | 12950
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 15300 |  | 0 |  | 15300
|  |  |  | 19:30 | 15630 |  | 0 |  | 15630
|  |  |  | 20:00 | 15450 |  | 0 |  | 15450
|  |  |  | 21:00 | 15590 |  | 0 |  | 15590
|  |  |  | 22:00 | 15520 |  | 0 |  | 15520
|  |  |  | 23:00 | 15520 |  | 0 |  | 15520
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 12770.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15630.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15630.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.89 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:53 hrs on 13-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-09-2025 | [28 empty] | Date: | 12-09-2025 | [28 empty] | Date: | 12-09-2025 | [28 empty] | Date: | 12-09-2025 | [28 empty] | Date: | 12-09-2025 | [14 empty] | Date: | 12-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 48.5 | 17 | 132 | 123 | 294 | 55 | 55 | 158 | 0 | 360 | 286 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 35 | 27.5 | 21 | 0 | 350 | 0 | 190 | 0 | 0 | 2 | 66 | 73 | 0 | 0 | 0 | 0 | 222 | 18 | 35 | 262 | 0 | 0 | 32 | 17 | 21 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 16 | 205 | 353 | 330 | 45 | 194 | 31 | 75 | 90 | 86 | 0 | 19 | 97 | 52 | 16 | 0 | 36 | 310 | 0 | 367 | 0 | 69 | 157 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 114 | 29 | 44 | 0 | 0 | 18 | 8403 | 860 | 115 | 0 | 14 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 739.95 | 0 | 48 | 0 | 113 | 113 | 0 | 91 | 30 | 52 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 160 | 0 | 150 | 0 | 404 | 0 | 0 | 170 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 350 | 1222 | 17 | 7144.15 | 15547.15 | 108.59
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 46.4 | 0 | 132 | 123 | 294 | 15 | 55 | 35 | 0 | 360 | 288 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 17 | 27.5 | 21 | 0 | 350 | 0 | 150 | 0 | 0 | 9 | 51 | 73 | 0 | 0 | 0 | 0 | 222 | 30 | 36 | 261 | 0 | 0 | 32 | 17 | 31 | 221 | 0 | 0 | 0 | 1170 | 0 | 51 | 133 | 16 | 205 | 356 | 330 | 45 | 192 | 25 | 72 | 90 | 87 | 0 | 13 | 97 | 48 | 16 | 0 | 37 | 305 | 0 | 364 | 0 | 69 | 152 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 17 | 76 | 9 | 46 | 0 | 0 | 18 | 8030.9 | 931 | 118 | 0 | 14 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1209 | 0 | 734.7 | 0 | 48 | 0 | 113 | 113 | 0 | 91 | 30 | 52 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 130 | 0 | 353 | 0 | 0 | 172 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 288 | 115 | 220 | 0 | 342 | 1222 | 17 | 7065.7 | 15096.6 | 108.59
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 46 | 0 | 132 | 123 | 294 | 15 | 55 | 35 | 0 | 420 | 68 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 17 | 27.5 | 21 | 0 | 450 | 0 | 150 | 0 | 0 | 1 | 66 | 73 | 0 | 0 | 0 | 0 | 220 | 30 | 37 | 260 | 0 | 0 | 32 | 17 | 30 | 221 | 0 | 0 | 0 | 1122 | 0 | 51 | 132 | 16 | 205 | 356 | 330 | 45 | 191 | 25 | 72 | 90 | 86 | 0 | 17 | 97 | 48 | 16 | 0 | 36 | 310 | 0 | 358 | 0 | 69 | 154 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 45 | 0 | 0 | 18 | 7916.5 | 931 | 116 | 0 | 14 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 750.53 | 0 | 48 | 0 | 113 | 113 | 0 | 91 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 130 | 0 | 130 | 0 | 338 | 0 | 0 | 172 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 272 | 115 | 220 | 0 | 303 | 1120 | 17 | 6841.53 | 14758.03 | 108.59
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 46 | 0 | 117 | 123 | 230 | 0 | 55 | 35 | 0 | 450 | 0 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 17 | 27.5 | 21 | 0 | 526 | 0 | 0 | 0 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 0 | 220 | 32 | 37 | 262 | 0 | 0 | 32 | 17 | 30 | 221 | 0 | 0 | 0 | 1170 | 0 | 51 | 132 | 16 | 205 | 350 | 330 | 45 | 203 | 25 | 72 | 90 | 86 | 0 | 19 | 97 | 46 | 16 | 0 | 36 | 305 | 0 | 390 | 0 | 69 | 154 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 51 | 0 | 0 | 18 | 7788.5 | 932 | 124 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 0 | 743.73 | 0 | 48 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 130 | 0 | 130 | 0 | 375 | 0 | 0 | 168 | 49 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 303 | 1095 | 17 | 6374.73 | 14163.23 | 108.6
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 48.5 | 0 | 105 | 123 | 45 | 0 | 55 | 35 | 0 | 450 | 0 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 17 | 27.5 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 0 | 220 | 31 | 37 | 262 | 0 | 0 | 32 | 17 | 29 | 221 | 0 | 0 | 0 | 1160 | 0 | 51 | 100 | 40 | 205 | 354 | 330 | 45 | 195 | 25 | 72 | 90 | 86 | 0 | 19 | 84 | 46 | 16 | 0 | 36 | 310 | 0 | 386 | 0 | 69 | 156 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 51 | 0 | 0 | 18 | 7564 | 933 | 134 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 0 | 747.46 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 353 | 0 | 0 | 168 | 49 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 303 | 1095 | 17 | 6212.46 | 13776.46 | 108.61
05:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 46 | 0 | 105 | 108 | 45 | 0 | 55 | 35 | 0 | 450 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 17 | 27.5 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 0 | 0 | 0 | 0 | 217 | 30 | 37 | 262 | 0 | 0 | 32 | 17 | 31 | 222 | 0 | 0 | 0 | 1115 | 0 | 51 | 80 | 60 | 205 | 356 | 330 | 45 | 195 | 25 | 68 | 90 | 86 | 0 | 19 | 98 | 44 | 16 | 0 | 36 | 305 | 0 | 372 | 0 | 69 | 153 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 51 | 0 | 0 | 18 | 7390.5 | 932 | 140 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 747.66 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 344 | 0 | 0 | 170 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 301 | 1100 | 0 | 6150.66 | 13541.16 | 108.62
06:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 44.1 | 0 | 85 | 76 | 15 | 0 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 17 | 21.8 | 21 | 0 | 480 | 0 | 0 | 0 | 0 | 7 | 33 | 30 | 0 | 0 | 0 | 0.02 | 174 | 29 | 36 | 262 | 0 | 0 | 32 | 0 | 29 | 224 | 0 | 0 | 0 | 1040 | 1 | 43 | 24 | 61 | 205 | 333 | 300 | 45 | 186 | 25 | 68 | 90 | 86 | 0 | 19 | 88 | 38 | 16 | 0 | 36 | 300 | 0 | 383 | 0 | 69 | 150 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 0 | 77 | 9 | 50 | 0 | 0.26 | 18 | 6861.18 | 933 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 746.97 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 331 | 0 | 0.02 | 171 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 242 | 115 | 180 | 0 | 301 | 1050 | 0 | 5918.24 | 12779.42 | 108.66
07:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 23 | 0 | 51 | 60 | 15 | 0 | 0 | 31 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 17 | 21.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 10 | 0 | 15 | 0 | 0 | 0 | 0.23 | 199 | 0 | 31 | 262 | 0 | 0 | 32 | 0 | 0 | 223 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 61 | 205 | 300 | 300 | 45 | 193 | 25 | 69 | 90 | 87 | 0 | 19 | 34 | 40 | 16 | 1 | 7 | 305 | 0 | 363 | 0 | 69 | 155 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 51 | 0 | 2.34 | 18 | 6496.07 | 932 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1034 | 0 | 748.25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 4.73 | 13 | 0 | 0 | 5.15 | 130 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 0.46 | 170 | 48 | 35 | 2 | 34 | 0 | 0 | 0 | 0.4 | 32 | 0.09 | 0 | 228 | 100 | 180 | 0 | 303 | 1020 | 0 | 5873.08 | 12369.15 | 108.7
08:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 17 | 21.8 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.81 | 210 | 0 | 24 | 262 | 0 | 0 | 32 | 0 | 0 | 223 | 0 | 0 | 0 | 980 | 8 | 51 | 0 | 61 | 205 | 300 | 300 | 45 | 192 | 22 | 50 | 90 | 51 | 0 | 12 | 26 | 37 | 16 | 4 | 0 | 310 | 0 | 368 | 0 | 69 | 149 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 0 | 77 | 9 | 50 | 0 | 3.61 | 18 | 6312.22 | 933 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1006 | 0 | 748.15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10.64 | 64 | 0 | 0 | 11.32 | 130 | 0 | 130 | 0 | 130 | 0 | 339 | 0 | 0.88 | 170 | 48 | 35 | 7 | 41 | 0 | 0 | 0 | 0.8 | 65 | 0.02 | 0 | 217 | 100 | 180 | 0 | 305 | 1000 | 0 | 5936.81 | 12249.03 | 108.74
09:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 17 | 21.8 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 215 | 0 | 33 | 260 | 0 | 0 | 29 | 0 | 0 | 222 | 0 | 0 | 0 | 950 | 6 | 51 | 0 | 61 | 150 | 300 | 300 | 45 | 192 | 19 | 34 | 90 | 34 | 0 | 12 | 0 | 34 | 0 | 9 | 0 | 305 | 0 | 369 | 0 | 69 | 149 | 0 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 51 | 1 | 5.21 | 18 | 6059.68 | 933 | 173 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 970 | 0 | 741.82 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 13.03 | 47 | 0 | 0 | 11.67 | 130 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 1.59 | 170 | 48 | 35 | 19 | 61 | 0 | 0 | 0 | 1.4 | 106 | 0.12 | 0 | 168 | 100 | 180 | 0 | 304 | 1000 | 0 | 5922.63 | 11982.31 | 108.76
10:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 6 | 17 | 21.8 | 14 | 0 | 410 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.14 | 176 | 0 | 34 | 265 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 900 | 10 | 51 | 0 | 61 | 80 | 355 | 300 | 45 | 197 | 25 | 32 | 90 | 31 | 0 | 12 | 0 | 34 | 0 | 21 | 0 | 310 | 0 | 386 | 0 | 68 | 157 | 0 | 0 | 81 | 30 | 0 | 0 | 165 | 0 | 77 | 9 | 50 | 1 | 13.33 | 18 | 6019.27 | 902 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 907 | 0 | 749.04 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 9.72 | 49 | 0 | 0 | 16.69 | 130 | 0 | 130 | 0 | 130 | 0 | 355 | 0 | 2.13 | 168 | 48 | 35 | 28 | 70 | 0 | 0 | 0 | 2.4 | 118 | 0.25 | 0 | 170 | 100 | 180 | 0 | 304 | 1000 | 0 | 5892.23 | 11911.5 | 108.8
11:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 11 | 17 | 21.8 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 4.07 | 174 | 0 | 34 | 267 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 900 | 8 | 51 | 0 | 61 | 40 | 354 | 330 | 44 | 197 | 34 | 32 | 90 | 33 | 0 | 12 | 0 | 38 | 0 | 54 | 0 | 320 | 0 | 386 | 0 | 38 | 159 | 0 | 0 | 84 | 30 | 0 | 0 | 165 | 0 | 77 | 9 | 50 | 1 | 9.29 | 18 | 6231.16 | 893 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 909 | 0 | 746.81 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 21.64 | 109 | 0 | 0 | 19.2 | 140 | 0 | 130 | 0 | 130 | 0 | 353 | 0 | 2.13 | 168 | 48 | 35 | 26 | 34 | 0 | 0 | 0 | 0 | 108 | 0.25 | 0 | 171 | 115 | 220 | 0 | 304 | 1000 | 0 | 5992.03 | 12223.19 | 108.83
12:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 3 | 18 | 60 | 0 | 0 | 17 | 60 | 0 | 450 | 0 | 0 | 0 | 5 | 331 | 0 | 0 | 23 | 52 | 21.5 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 1.53 | 218 | 0 | 34 | 267 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 16 | 51 | 0 | 61 | 10 | 356 | 330 | 44 | 190 | 34 | 35 | 90 | 50 | 0 | 18 | 24 | 40 | 0 | 19 | 0 | 315 | 0 | 371 | 0 | 38 | 158 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 50 | 1 | 12.72 | 18 | 6495.75 | 893 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 962 | 0 | 752.16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 48.46 | 73 | 0 | 0 | 19.76 | 150 | 0 | 130 | 0 | 130 | 0 | 342 | 0 | 2.12 | 169 | 48 | 35 | 24 | 34 | 0 | 0 | 0 | 3.2 | 96 | 0.7 | 0 | 167 | 115 | 220 | 0 | 304 | 1055 | 0 | 6090.4 | 12586.15 | 108.82
13:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 40.2 | 17 | 50 | 76 | 15 | 0 | 17 | 65 | 0 | 450 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 28 | 52 | 21.2 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.95 | 218 | 0 | 37 | 268 | 0 | 0 | 16 | 0 | 0 | 219 | 0 | 0 | 0 | 1070 | 15 | 51 | 20 | 61 | 0 | 350 | 330 | 44 | 195 | 31 | 68 | 90 | 70 | 0 | 18 | 39 | 44 | 0 | 49 | 0 | 315 | 0 | 374 | 0 | 38 | 158 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 50 | 1 | 20.05 | 18 | 6810.4 | 894 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 1114 | 0 | 748.8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 55.39 | 76 | 0 | 0 | 17.41 | 150 | 0 | 130 | 0 | 130 | 0 | 353 | 0 | 2.05 | 168 | 48 | 35 | 33 | 34 | 0 | 0 | 0 | 3.2 | 143 | 0.32 | 0 | 199 | 115 | 220 | 0 | 304 | 1120 | 0 | 6425.17 | 13235.57 | 108.82
14:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 60 | 0 | 0 | 17 | 64 | 0 | 450 | 0 | 0 | 0 | 0 | 328 | 36 | 0 | 19 | 52 | 21.5 | 7 | 0 | 470 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1.99 | 218 | 0 | 42 | 268 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 0 | 1060 | 9 | 51 | 0 | 61 | 50 | 300 | 300 | 43 | 200 | 34 | 72 | 90 | 123 | 6 | 19 | 46 | 42 | 0 | 49 | 0 | 310 | 0 | 321 | 0 | 38 | 140 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 50 | 1 | 36.23 | 18 | 6543.72 | 894 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1078 | 0 | 748.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.64 | 80 | 0 | 0 | 54.46 | 150 | 0 | 130 | 0 | 130 | 0 | 363 | 0 | 3.11 | 167 | 44 | 35 | 10 | 0 | 0 | 0 | 0 | 5.2 | 96 | 0.33 | 0 | 181 | 115 | 180 | 0 | 304 | 1000 | 0 | 6085.51 | 12629.23 | 108.82
15:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 34 | 45 | 0 | 0 | 20 | 69 | 0 | 450 | 0 | 0 | 0 | 0 | 326 | 36 | 0 | 8 | 52 | 21.5 | 7 | 0 | 465 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.63 | 218 | 0 | 42 | 266 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 0 | 1050 | 12 | 51 | 0 | 61 | 265 | 300 | 300 | 44 | 205 | 31 | 72 | 90 | 127 | 8 | 19 | 46 | 42 | 0 | 46 | 0 | 320 | 0 | 386 | 0 | 38 | 152 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 50 | 2 | 27.91 | 18 | 6782.04 | 894 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1012 | 0 | 757.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.05 | 50 | 0 | 0 | 43.54 | 150 | 0 | 130 | 0 | 130 | 0 | 383 | 0 | 2.88 | 170 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 3.9 | 45 | 0.41 | 0 | 171 | 100 | 220 | 0 | 304 | 1000 | 0 | 5907.39 | 12689.43 | 108.82
16:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 17 | 16 | 0 | 450 | 0 | 0 | 0 | 0 | 328 | 36 | 0 | 4 | 52 | 21.7 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.88 | 218 | 0 | 42 | 267 | 0 | 0 | 6 | 0 | 0 | 195 | 0 | 0 | 0 | 1030 | 10 | 51 | 0 | 61 | 240 | 331 | 310 | 43 | 192 | 34 | 72 | 90 | 131 | 8 | 19 | 44 | 40 | 0 | 4 | 0 | 310 | 0 | 366 | 0 | 38 | 155 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 50 | 1 | 16.87 | 18 | 6607.45 | 893 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1001 | 0 | 758.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 9 | 0 | 0 | 34.99 | 150 | 0 | 130 | 0 | 130 | 0 | 344 | 0 | 1.94 | 165 | 0 | 35 | 9 | 0 | 0 | 0 | 0 | 1.2 | 28 | 0.34 | 0 | 168 | 100 | 220 | 0 | 303 | 997 | 0 | 5761.24 | 12368.69 | 108.82
17:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 20 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 35 | 21.7 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.21 | 218 | 0 | 42 | 265 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 920 | 2 | 51 | 0 | 61 | 270 | 350 | 330 | 43 | 189 | 34 | 76 | 90 | 120 | 9 | 19 | 45 | 54 | 0 | 10 | 0 | 305 | 0 | 350 | 0 | 40 | 150 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 55 | 1 | 2.64 | 16 | 6391.55 | 894 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 985 | 0 | 762.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 3 | 0 | 0 | 13.94 | 150 | 0 | 130 | 0 | 130 | 0 | 335 | 0 | 0 | 167 | 0 | 35 | 3 | 0 | 0 | 0 | 0 | 0.7 | 14 | 0.07 | 0 | 164 | 115 | 220 | 0 | 303 | 894 | 0 | 5601.07 | 11992.62 | 108.82
18:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 18 | 52 | 0 | 0 | 25 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 52 | 21.7 | 7 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 219 | 0 | 42 | 264 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1060 | 0 | 51 | 0 | 61 | 140 | 280 | 290 | 44 | 209 | 34 | 89 | 90 | 119 | 8 | 19 | 54 | 58 | 8 | 0 | 0 | 300 | 0 | 356 | 0 | 40 | 139 | 0 | 0 | 33 | 30 | 0 | 0 | 167 | 0 | 77 | 9 | 97 | 0 | 0 | 0 | 6231.7 | 893 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 984 | 0 | 767.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0.31 | 150 | 0 | 130 | 0 | 130 | 0 | 388 | 0 | 0.03 | 166 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 185 | 100 | 180 | 0 | 303 | 890 | 0 | 5576.42 | 11808.12 | 108.82
19:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 38.5 | 25 | 96 | 123 | 125 | 11 | 35 | 143 | 0 | 370 | 0 | 0 | 0 | 40 | 300 | 36 | 0 | 0 | 108 | 21.7 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 66 | 38 | 0 | 0 | 0 | 0 | 219 | 22 | 37 | 263 | 0 | 0 | 12 | 0 | 65 | 220 | 0 | 0 | 0 | 1080 | 0 | 51 | 73 | 130 | 5 | 300 | 330 | 44 | 186 | 34 | 89 | 90 | 161 | 8 | 19 | 98 | 46 | 43 | 0 | 12 | 310 | 0 | 356 | 0 | 37 | 149 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 10 | 77 | 9 | 103 | 0 | 0 | 0 | 7395.2 | 893 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 753.69 | 0 | 0 | 0 | 25 | 20 | 0 | 94 | 12 | 0 | 0 | 0 | 14 | 0 | 0 | 187 | 0 | 196 | 0 | 205 | 0 | 324 | 0 | 0 | 164 | 0 | 110 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 180 | 0 | 349 | 1105 | 11 | 6506.69 | 13901.89 | 108.82
19:30 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 47 | 35 | 100 | 123 | 75 | 15 | 35 | 140 | 0 | 370 | 0 | 0 | 0 | 55 | 300 | 36 | 0 | 0 | 108 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 66 | 70 | 0 | 0 | 0 | 0 | 219 | 30 | 37 | 264 | 0 | 0 | 18 | 0 | 88 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 120 | 137 | 3 | 300 | 330 | 44 | 186 | 34 | 89 | 90 | 161 | 8 | 19 | 98 | 46 | 52.2 | 0 | 14 | 305 | 0 | 362 | 0 | 37 | 137 | 0 | 0 | 84 | 30 | 0 | 0 | 167 | 34 | 77 | 9 | 103 | 0 | 0 | 0 | 7564.2 | 893 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 769.07 | 0 | 0 | 0 | 50 | 70 | 0 | 94 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 178 | 0 | 180 | 0 | 198 | 0 | 326 | 0 | 0 | 161 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 180 | 0 | 350 | 1216 | 17 | 6705.07 | 14269.27
20:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 43.9 | 35 | 94 | 123 | 30 | 15 | 35 | 138 | 0 | 450 | 0 | 0 | 0 | 55 | 331 | 37 | 0 | 0 | 125 | 20.2 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 66 | 70 | 0 | 0 | 0 | 0 | 220 | 30 | 37 | 265 | 0 | 0 | 19 | 4 | 94 | 220 | 0 | 0 | 0 | 1145 | 0 | 51 | 80 | 165 | 3 | 344 | 330 | 44 | 198 | 34 | 89 | 90 | 165 | 9 | 19 | 98 | 48 | 52.2 | 0 | 14 | 300 | 0 | 388 | 0 | 37 | 135 | 0 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 103 | 0 | 0 | 0 | 7810.3 | 779 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 766.32 | 0 | 0 | 0 | 50 | 70 | 0 | 95 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 178 | 0 | 184 | 0 | 182 | 0 | 348 | 0 | 0 | 161 | 0 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 180 | 0 | 350 | 1114 | 17 | 6529.32 | 14339.62 | 108.82
21:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 48.2 | 35 | 68 | 123 | 30 | 15 | 35 | 147 | 0 | 450 | 0 | 0 | 0 | 55 | 330 | 97 | 0 | 0 | 125 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 66 | 70 | 0 | 0 | 0 | 0 | 220 | 17 | 38 | 265 | 0 | 0 | 19 | 8 | 97 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 172 | 3 | 349 | 330 | 44 | 200 | 34 | 89 | 90 | 180 | 8 | 19 | 98 | 48 | 52.2 | 0 | 14 | 320 | 0 | 389 | 0 | 38 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 12 | 7985.1 | 779 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1141 | 0 | 765.27 | 0 | 0 | 0 | 50 | 70 | 0 | 95 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 187 | 0 | 179 | 0 | 180 | 0 | 414 | 0 | 0 | 161 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 351 | 1100 | 17 | 6662.27 | 14647.37 | 108.82
22:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 47.4 | 22 | 68 | 123 | 0 | 0 | 35 | 151 | 0 | 450 | 15 | 0 | 0 | 55 | 330 | 98 | 0 | 0 | 125 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 66 | 69 | 0 | 0 | 0 | 0 | 220 | 15 | 38 | 265 | 0 | 0 | 19 | 8 | 51 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 172 | 140 | 352 | 330 | 44 | 200 | 34 | 89 | 90 | 178 | 9 | 19 | 98 | 50 | 52.2 | 0 | 14 | 310 | 0 | 388 | 0 | 37 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 167 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 8030.3 | 779 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 763.01 | 0 | 0 | 0 | 35 | 70 | 0 | 95 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 188 | 0 | 186 | 0 | 188 | 0 | 414 | 0 | 0 | 161 | 0 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 350 | 1098 | 17 | 6657.01 | 14687.31 | 108.82
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 51 | 17 | 68 | 123 | 0 | 0 | 35 | 160 | 0 | 450 | 20 | 0 | 0 | 55 | 210 | 36 | 0 | 0 | 125 | 21.7 | 22 | 0 | 550 | 0 | 0 | 0 | 0 | 1 | 66 | 62 | 0 | 0 | 0 | 0 | 220 | 15 | 38 | 267 | 0 | 0 | 19 | 8 | 51 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 80 | 61 | 200 | 351 | 330 | 45 | 187 | 34 | 84 | 90 | 188 | 8 | 19 | 98 | 50 | 52.2 | 0 | 15 | 320 | 0 | 391 | 0 | 37 | 159 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 103 | 0 | 0 | 18 | 7855.9 | 823 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 771.91 | 0 | 0 | 0 | 35 | 70 | 0 | 95 | 37 | 0 | 0 | 0 | 14 | 0 | 0 | 198 | 0 | 193 | 0 | 196 | 0 | 414 | 0 | 0 | 164 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 350 | 1138 | 17 | 6886.91 | 14742.81 | 108.82
Total KWH | 0 | 1255680 | 161280 | 0 | 0 | 0 | 0 | 0 | 8715600 | 0 | 0 | 659520 | 184680 | 1524240 | 2125920 | 1411865 | 113963 | 629632 | 1464480 | 0 | 10087000 | 542633 | 0 | 0 | 601304 | 7448031 | 642000 | 0 | 107228 | 1261200 | 537000 | 384120 | 0 | 11315454.55 | 0 | 414000 | 0 | 0 | 135840 | 732634 | 775920 | 0 | 0 | 0 | 19801 | 5295447 | 370507 | 912960 | 6385454.55 | 0 | 0 | 456480 | 132861.6 | 660727 | 5133891 | 0 | 0 | 0 | 25674543 | 85185 | 1224096 | 1269600 | 1655999 | 3446800 | 8360300 | 7772000 | 1063680 | 4767000 | 717984 | 1663680 | 2149040 | 2597280 | 94080 | 411070 | 1550400 | 1054080 | 418123 | 291682 | 328512 | 7551000 | 0 | 9288000 | 0 | 1224000 | 3667663.64 | 0 | 0 | 1959360 | 719424 | 0 | 59000 | 3428730 | 72720 | 1852800 | 216000 | 1478400 | 9500 | 149090 | 383760 | 171253935.34 | 21512727 | 4585536 | 0 | 31680 | 66240 | 912000 | 0 | 0 | 0 | 0 | 0 | 372240 | 25730900 | 0 | 18261818 | 0 | 140202 | 0 | 591360 | 739104 | 0 | 1336432 | 211008 | 108835 | 193414 | 567130 | 42896 | 0 | 232504 | 3930909 | 0 | 3770891 | 0 | 3920218 | 0 | 8803563 | 0 | 19920 | 4131000 | 742690 | 1627368 | 174970 | 1457961 | 0 | 0 | 0 | 29700.24 | 870480 | 3235 | 297120 | 5585000 | 2636000 | 5261560 | 0 | 7613784 | 25994181.82 | 175200 | 152681777.06 | 323935712.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12586.15 | MW | 12:00 Hr. | Energy Generated |  |  | 323.9357 |  | MKWHr.
| Day Peak Demand |  |  | 12586.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.867 |  | MKWHr.
| Evening Peak Generation |  |  | 14647.37 | MW | 21:00 Hr. | Energy Demand |  |  | 326.8027 |  | MKWHr.
| Evening Peak Demand |  |  | 14750.83 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 11911.5 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1055.74 |  | MMCFD
| Maximum Generation of the Day |  |  | 15547.15 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.1388 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.6718 | 0 | 11.3938 | 0 | 0 | 0.10723 | 0 | 0 | 51.1728 | Gas | 139.5709 | Gas | 500646671.3259
| Chattogram Zone |  |  | 6.0469 | 32.06 | 3.5431 | 0 | 5.2954 | 0.10499 | 0 | 0.13584 | 47.1863 | Coal | 101.8576 | Coal | 606802022.4734
| Cumilla Zone |  |  | 31.568 | 0 | 7.9217 | 0 | 0 | 0.29168 | 1.0541 | 0 | 40.8354 | HFO | 32.2093 | HFO | 593216597.888
| Mymensingh Zone |  |  | 1.4784 | 0 | 2.5253 | 0 | 0 | 0.15859 | 0 | 0 | 4.1623 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8972 | Hydro | 5.2954 | Hydro | 529544.7
| Khulna Zone |  |  | 4.5855 | 25.7309 | 0.09792 | 0 | 0 | 0.37224 | 22.4247 | 0 | 53.2113 | Solar | 3.1261 | Solar | 47888646.8604
| Barishal Zone |  |  | 7.8976 | 39.193 | 0.47232 | 0 | 0 | 0.003235 | 0 | 0 | 47.5661 | Import | 41.7406 | Import | 237482634.91
| Rajshahi Zone |  |  | 20.4256 | 0 | 3.1698 | 0 | 0 | 1.013 | 18.2618 | 0 | 42.8702 | Wind | 0.13584 | Wind | 2002281.6
| Rangpur Zone |  |  | 0 | 4.8737 | 3.0853 | 0 | 0 | 1.0752 | 0 | 0 | 9.0342
| Total |  |  | 139.5709 | 101.8576 | 32.2093 | 0 | 5.2954 | 3.1261 | 41.7406 | 0.13584 | 323.9357
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 500646671.3259 |  | Hydro | 529544.7
|  |  |  | Coal | 606802022.4734 |  | Solar | 47888646.8604
|  |  |  | HFO | 593216597.888 |  | Import | 237482634.91
|  |  |  | HSD | 0 |  | Wind | 2002281.6
[5 empty] | Total: | 198,85,68,399 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5127 | Peak Hr Flow | 779.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42329617.5 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.2618 | Peak Hr Flow | 765.27 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1740 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0541 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2282 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.8286 | Peak Hr Flow | 1592.27 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4743
|  |  |  | Chattogram |  | 0 |  | 1415
|  |  |  | Cumilla |  | 0 |  | 1434
|  |  |  | Mymensingh |  | 99 |  | 1252
|  |  |  | Sylhet |  | 0 |  | 623
|  |  |  | Khulna |  | 0 |  | 1766
|  |  |  | Barishal |  | 0 |  | 450
|  |  |  | Rajshahi |  | 0 |  | 1500
|  |  |  | Rangpur |  | 0 |  | 965
|  |  |  | Total |  | 99 |  | 14148
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 09:01 | Bogura 230/132kV S/S 132KV Main 1 is restored.
|  | 09:13 | Bogura-Bogura (New)) 132 kV Ckt-2 is restored.
|  | 09:20 | Niamatpur 132/33kV S/S Transformer-1(407T) HT is restored.
|  | 09:20 | Niamatpur 132/33kV S/S Transformer-1(407T) LT is restored.
| 09:21 | 12:38 | Ishwardi-Natore 132kV Ckt-1 Project Work S/D from Natore 132/33kV end Due to Requested
by ALDC. and from Ishurdi 132/33kV end Due to Bonpara s/s Lilo
| 09:23 | 11:42 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Loop maintenance
| 09:24 | 11:41 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Loop Maintenance works
| 09:26 | 12:38 | Ishwardi-Natore 132kV Ckt-2 Project Work S/D from Natore 132/33kV end. and from Ishurdi
132/33kV end Due to Bonpara s/s Lilo
| 10:01 | 14:41 | Patuakhali 132/33kV S/S 425T (T-3) LT Project Work S/D Due to Installation annunciator
| 10:02 | 14:40 | Patuakhali 132/33kV S/S 425T (T-3) HT Project Work S/D Due to Installation annunciator
|  | 10:03 | Meghnaghat 230/132kV S/S Bus2 is restored.
|  | 11:45 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 11:47 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT is restored.
|  | 11:48 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT is restored.
|  | 11:49 | Jashore-Noapara 132kV Ckt-1 is restored.
|  | 11:50 | Jashore-Noapara 132kV Ckt-2 is restored.
| 12:00 |  | Day Peak Generation: 12582 MW.
| 14:39 |  | Barapukuria PS Unit-1 tripped during changeover.
|  | 17:16 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 19:30 |  | HVDC schedule has been changed from 950 MW to 834 MW. At, 22:30, schedule will be changed
from 834 MW to 877 MW and will continue till midnight.
| 21:00 |  | Evening Peak Generation 14646 MW.
| 21:23 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 21:35 |  | Meghnaghat Summit 335 MW CCPP GT-1 was sync.
| 21:35 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 21:35 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- None
| 21:52 | 22:58 | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to 33kV secondary bus isolator
R-phase red hot maintenance work.
| 22:05 |  | Barapukuria PS Unit-1 was sync.
| 22:33 |  | Siddhirganj 335 MW CCPP ST tripped due to exciter alarm
| 00:15 |  | Meghnaghat Summit 335 MW CCPP ST was sync.
| 00:15 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- None
| 00:15 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
| 02:47 |  | Siddhirganj 335 MW CCPP ST was sync.
| 04:49 | 04:51 | Rajbari 132/33kV S/S Transformer-3 LT Tripped showing O/C relays Due to Sajjankanda | [7 empty] | 6.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 06:00 |  | Coxsbazar 132/33kV S/S 405T-T1 HT Scheduled S/D Due to TR-1 33(33kV bushing to incomer 2 | [7 empty] | 46.0MW load
|  |  | cable installation ) | [7 empty] | interrup.
| 06:16 | 07:33 | Khulshi 132/33kV S/S 405T (T1) LT Forced S/D Due to 33/0.44kV station supply
Transformer's Bus Isolator R Phase Red hot maintenance.
| 06:16 | 07:32 | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to 33/0.44kV Station supply
Transformer's 33kV Bus connector Red-hot maintenance work.
| 07:00 |  | Minimum Generation 12489 MW.
| 07:08 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Project Work S/D | [7 empty] | 40.0MW load
interrup.
| 07:08 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Project Work S/D Due to None | [7 empty] | 40.0MW load
interrup.
| 07:09 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Project Work S/D
| 07:09 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Project Work S/D | [7 empty] | 20.0MW load
interrup.
| 07:09 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Project Work S/D | [7 empty] | 40.0MW load
interrup.
| 07:09 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Project Work S/D | [7 empty] | 40.0MW load
interrup.
| 07:10 |  | Chuadanga 132/33kV S/S Jhenaidah-Chuadanga Ckt-2 Project Work S/D | [7 empty] | 100.0MW load
interrup.
| 07:11 |  | Chuadanga-Jhenaidah 132 kV Ckt-1 Project Work S/D from Chuadanga 132/33kV end. and from | [7 empty] | 100.0MW load
|  |  | Jhenaidah 230/132kVend. | [7 empty] | interrup. Chuadanga
132/33kV end
| 07:13 |  | Jhenaidah 132/33kV S/S Jhenaidah-Chuadanga, 132kV Circuit-2(L8) Project Work S/D Due to | [7 empty] | 47.0MW load
|  |  | None | [7 empty] | interrup.
| 07:52 |  | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
project work and from Bogura 400/230kV end Due to Tower aviation painting work
(Barapukuria side)
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 366 | 8715600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10087000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 542633 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 113963 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 642000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7448031 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.2 | 659520 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 2125920 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 629632 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 601304 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.7 | 537000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 384120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 161280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 1411865 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 68 | 1524240 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 1255680 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 147 | 1464480 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 107228 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 184680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 11315454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1261200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2549.9 | 51172830.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 132861.6 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 85185 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 456480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5295447 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5133891 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 660727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 775920 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 732634 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 38 | 912960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 414000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 370507 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 25674543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 135840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6385454.55 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2170 | 47186251.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4767000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 349 | 8360300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7772000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 3 | 3446800 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 717984 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1063680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 172 | 1655999 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1224096 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1269600 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 14 | 328512 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2149040 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 2597280 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1054080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 418123 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 411070 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1550400 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 94080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1663680 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 291682 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1861.2 | 40835406
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 104 | 1478400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 216000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1852800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 149090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 383760 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 72720 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 202 | 4162270
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 1224000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3667663.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719424 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1959360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 3428730 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 59000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7551000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 389 | 9288000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1202 | 27897177.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 779 | 21512727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 31680 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 66240 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 245 | 4585536 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 372240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1141 | 25730900 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2203 | 53211323
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 351 | 7613784 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 297120 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2636000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 25994181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5261560 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 175200 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 5585000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3235 | -
Barishal Area Total |  |  |  |  | 2236 | 2078 | 47566080.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 193414 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 140202 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 211008 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 187 | 3930909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 179 | 3770891 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 3920218 | Low gas pressure
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8803563 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 42896 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 108835 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1336432 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 739104 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 591360 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 765.27 | 18261818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 232504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 567130 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1992.27 | 42870204
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 742690 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 4131000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1457961 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29700.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1627368 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 174970 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 870480 | -
Rangpur Area Total |  |  |  |  | 950 | 389 | 9034169.24
Eastern Grid Total |  |  |  |  | 17385.715 | 7985.1 | 171253935.34
Western Grid Total |  |  |  |  | 10444.16 | 6662.27 | 152681777.06
National Grid Total |  |  |  |  | 27829.875 | 14647.37 | 323935712.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-09-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9368.9 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4681.4 | MW
i) Dhaka area |  |  | 4743.08 |  | MW | i) Khulna area |  |  |  | 1766 | MW
ii) Chattogram area |  |  | 1415.4 |  | MW | ii) Barishal area |  |  |  | 450 | MW
iii) Cumilla area |  |  | 1434.42 |  | MW | iii) Rajshahi area |  |  |  | 1500.4 | MW
iv) Mymensingh area |  |  | 1153 |  | MW | iv) Rangpur area |  |  |  | 965 | MW
v) Sylhet area |  |  | 623 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14050.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 79 | 23:00 | 133 | PHP | 8 | 04:00
2 | AKSML | 129.6 | 14:00 | 68 | Ishurdi | 78 | 00:00 | 134 | Pabna | 126 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 76 | 19:00 | 135 | Palashbari | 126 | 00:00
4 | Agargaon | 124 | 00:00 | 70 | Jamalpur | 112 | 21:00 | 136 | Panchagarh | 57 | 18:30
5 | Agrabad | 88 | 20:00 | 71 | Jashore | 148 | 00:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 132 | 19:30 | 138 | Patuakhali | 68.5 | 00:00
7 | Ashuganj | 85 | 01:00 | 73 | Joydebpur | 144 | 00:00 | 139 | Payra | 36 | 00:00
8 | BSRM | 153 | 21:00 | 74 | Joypurhat | 60 | 01:00 | 140 | Postogola | 59 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 16.5 | 00:00 | 141 | Purbachal | 22 | 13:00
10 | Bajitpur | 95 | 00:00 | 76 | KSRM | 31 | 16:00 | 142 | Purbasadipur | 127 | 00:00
11 | Bakulia | 87 | 00:00 | 77 | Kabirpur | 214 | 00:00 | 143 | Rahanpur | 41 | 22:00
12 | Banani | 33.6 | 18:30 | 78 | Kachua | 96 | 22:00 | 144 | Rahim | 30 | 00:00
13 | Bangabhaban | 5 | 10:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 83 | 22:00
14 | Barapukuria | 62 | 00:00 | 80 | Kalurghat | 34 | 00:00 | 146 | Rajendrapur | 139 | 21:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 73 | 00:00 | 147 | Rajshahi | 111 | 00:00
16 | Barishal | 116 | 01:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 104 | 00:00
17 | Barishal-230 | 98 | 22:00 | 83 | Kasba | 37 | 20:00 | 149 | Ramganj | 106 | 21:00
18 | Baroaulia | 66 | 20:00 | 84 | Kazla | 99 | 00:00 | 150 | Rampur | 53 | 21:00
19 | Baroirhat | 65 | 00:00 | 85 | Keranigonj | 85 | 00:00 | 151 | Rangamati | 17 | 18:30
20 | Bashundhara | 181 | 00:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Rangpur | 145 | 01:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 61 | 00:00 | 153 | Ruppur | 7.8 | 09:00
22 | Beanibazar | 84 | 00:00 | 88 | Khulshi | 163 | 00:00 | 154 | SSM | 16 | 01:00
23 | Benapole | 68 | 00:00 | 89 | Kishoreganj | 133 | 19:30 | 155 | Saidpur | 106 | 00:00
24 | Bhaluka | 139 | 18:30 | 90 | Kodda | 282 | 00:00 | 156 | Satkhira | 132 | 00:00
25 | Bhandaria | 56 | 00:00 | 91 | Kulaura | 53 | 00:00 | 157 | Satmasjid | 99 | 00:00
26 | Bhangura | 38 | 00:00 | 92 | Kurigram | 70 | 18:30 | 158 | Savar | 177 | 00:00
27 | Bheramara(GK) | 70 | 00:00 | 93 | Kushtia | 162 | 00:00 | 159 | SevenRings | 7.61 | 23:00
28 | Bhulta | 202 | 00:00 | 94 | Laksam | 35 | 22:00 | 160 | ShahCement | 31 | 00:00
29 | Bog-Sherpur | 80 | 01:00 | 95 | Lakshmipur | 38 | 23:00 | 161 | Shahjadpur | 82 | 00:00
30 | Bogura | 158 | 19:00 | 96 | Lalbag | 50 | 02:00 | 162 | Shahjibazar | 136 | 00:00
31 | Borhanuddin | 94 | 01:00 | 97 | Lalmonirhat | 60 | 00:00 | 163 | Shahmirpur | 53 | 00:00
32 | Brahmanbaria | 137 | 00:00 | 98 | MI_Cement | 16 | 12:00 | 164 | Shariatpur | 93 | 00:00
33 | Cantonment | 132 | 13:00 | 99 | Madanganj | 38 | 00:00 | 165 | Sherpur | 124 | 09:00
34 | Chandina | 39.4 | 19:30 | 100 | Madaripur | 120 | 00:00 | 166 | Shikalbaha | 17 | 00:00
35 | Chandpur | 84 | 22:00 | 101 | Madartek | 96 | 00:00 | 167 | Shitalakhya | 56.3 | 13:00
36 | Chandraghona | 35 | 21:00 | 102 | Madunaghat | 54 | 02:00 | 168 | Sholosohor | 45 | 00:00
37 | Chapai | 68 | 23:00 | 103 | Magura | 65 | 22:00 | 169 | Shyampur | 164 | 00:00
38 | Charsaidpur | 21 | 00:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Siddhirganj | 107 | 00:00
39 | Chauddagram | 72 | 21:00 | 105 | Maijdee | 15 | 06:00 | 171 | Sirajganj | 108 | 01:00
40 | Chhatak | 42 | 00:00 | 106 | Manikganj | 130 | 00:00 | 172 | Sonargaon | 121 | 07:00
41 | Chowmuhani | 181 | 15:00 | 107 | Maniknagar | 58 | 00:00 | 173 | Sreemongol | 86 | 00:00
42 | Chuadanga | 118 | 00:00 | 108 | Matarbari | 50 | 00:00 | 174 | Sreepur | 91 | 00:00
43 | Coxsbazar | 133 | 23:00 | 109 | Matuail | 70 | 00:00 | 175 | Srinagar | 50.33 | 22:00
44 | Cumilla(N) | 149 | 13:00 | 110 | Millgate | 93 | 00:00 | 176 | Sunamganj | 64 | 00:00
45 | Cumilla(S) | 136 | 00:00 | 111 | Mirpur | 115 | 13:00 | 177 | Sylhet | 55 | 00:00
46 | Daganbhuiyan | N/A | N/A | 112 | Mirsorai | 9 | 00:00 | 178 | Sylhet-132 | 120 | 00:00
47 | Daudkandi | 148 | 19:00 | 113 | Mirzapur | 35 | 06:00 | 179 | TK | 37 | 00:00
48 | Dhaka | 42 | 00:00 | 114 | Mithapukur | 76 | 00:00 | 180 | Tangail | 170 | 20:00
49 | Dhamrai | 136 | 00:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 00:00
50 | Dhanmondi | 114 | 18:30 | 116 | Mogbazar | 85.9 | 00:00 | 182 | Thakurgaon | 108 | 19:00
51 | Dohazari | 101 | 18:30 | 117 | Mongla | 33 | 12:00 | 183 | Tongi | 105 | 00:00
52 | Faridpur | 170 | 01:00 | 118 | Motijheel | 37 | 00:00 | 184 | Ullahpara | 40 | 01:00
53 | Fatullah | 88 | 00:00 | 119 | Muktagacha | 36 | 00:00 | 185 | Ullon | 57 | 00:00
54 | Fenchuganj | 47 | 00:00 | 120 | Munshiganj | 114 | 21:00 | 186 | Uttara | 77 | 18:30
55 | Feni | 117 | 23:00 | 121 | Muradnagar | 44 | 21:00 | 187 | UttaraNew | 62 | 00:00
56 | GPH | 92 | 10:00 | 122 | Mymensingh | 205 | 21:00 | 188 | Zigatola | 70 | 00:00
57 | Ghatail | 82 | 11:00 | 123 | Naogaon | 142 | 00:00
58 | Ghorashal | 15 | 00:00 | 124 | Narail | 60 | 00:00
59 | Ghorashal-230 | 95 | 01:00 | 125 | Narinda | 55 | 00:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 185 | 02:00
61 | Gollamari | 110 | 00:00 | 127 | Natore | 157 | 00:00
62 | Gopalganj | 106 | 21:00 | 128 | Nawabganj | 59.6 | 22:00
63 | Gulshan | 88 | 18:30 | 129 | Netrakona | 149 | 21:00
64 | Halishahar | 59.5 | 09:00 | 130 | New | 62 | 00:00
65 | HaripurSBU | 142 | 02:00 | 131 | Niamatpur | 79 | 22:00
66 | Hasnabad | 82 | 00:00 | 132 | Noapara | 48 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15547.15 | 339 |  | 15901.41
1:00 | 15096.6 | 310 |  | 15420.55
2:00 | 14758.03 | 280 |  | 15050.63
3:00 | 14163.23 | 265 |  | 14440.16
4:00 | 13776.46 | 244 |  | 14031.44
5:00 | 13541.16 | 220 |  | 13771.06
6:00 | 12779.42 | 165 |  | 12951.85
7:00 | 12369.15 | 157 |  | 12533.15
8:00 | 12249.03 | 149 |  | 12404.74
9:00 | 11982.31 | 97 |  | 12083.68
10:00 | 11911.5 | 31 |  | 11943.9
11:00 | 12223.19 | 0 |  | 12223.19
12:00 | 12586.15 | 0 |  | 12586.15
13:00 | 13235.57 | 36 |  | 13273.57
14:00 | 12629.23 | 0 |  | 12629.23
15:00 | 12689.43 | 0 |  | 12689.43
16:00 | 12368.69 | 0 |  | 12368.69
17:00 | 11992.62 | 0 |  | 11992.62
18:00 | 11808.12 | 50 |  | 11860.37
19:00 | 13901.89 | 143 |  | 14051.33
19:30 | 14269.27 | 106 |  | 14380.04
20:00 | 14339.62 | 88 |  | 14431.58
21:00 | 14647.37 | 99 |  | 14750.83
22:00 | 14687.31 | 99 |  | 14790.77
23:00 | 14742.81 | 95 |  | 14842.09
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8403 | 7144.15 | 15547.15 | DAILY GENERATION CURVE
00:30 | 8216.95 | 7104.925 | 15321.875
01:00 | 8030.9 | 7065.7 | 15096.6 | 12-09-2025
01:30 | 7973.7 | 6953.615 | 14927.315
02:00 | 7916.5 | 6841.53 | 14758.03
02:30 | 7852.5 | 6608.13 | 14460.63
03:00 | 7788.5 | 6374.73 | 14163.23
03:30 | 7676.25 | 6293.595 | 13969.845
04:00 | 7564 | 6212.46 | 13776.46
04:30 | 7477.25 | 6181.56 | 13658.81
05:00 | 7390.5 | 6150.66 | 13541.16
05:30 | 7125.84 | 6034.45 | 13160.29
06:00 | 6861.18 | 5918.24 | 12779.42
06:30 | 6678.625 | 5895.66 | 12574.285
07:00 | 6496.07 | 5873.08 | 12369.15
07:30 | 6404.145 | 5904.945 | 12309.09
08:00 | 6312.22 | 5936.81 | 12249.03
08:30 | 6185.95 | 5929.72 | 12115.67
09:00 | 6059.68 | 5922.63 | 11982.31
09:30 | 6039.475 | 5907.43 | 11946.905
10:00 | 6019.27 | 5892.23 | 11911.5
10:30 | 6125.215 | 5942.13 | 12067.345
11:00 | 6231.16 | 5992.03 | 12223.19
11:30 | 6363.455 | 6041.215 | 12404.67
12:00 | 6495.75 | 6090.4 | 12586.15
12:30 | 6653.075 | 6257.785 | 12910.86
13:00 | 6810.4 | 6425.17 | 13235.57
13:30 | 6677.06 | 6255.34 | 12932.4
14:00 | 6543.72 | 6085.51 | 12629.23
14:30 | 6662.88 | 5996.45 | 12659.33
15:00 | 6782.04 | 5907.39 | 12689.43
15:30 | 6694.745 | 5834.315 | 12529.06
16:00 | 6607.45 | 5761.24 | 12368.69
16:30 | 6499.5 | 5681.155 | 12180.655
17:00 | 6391.55 | 5601.07 | 11992.62
17:30 | 6311.625 | 5588.745 | 11900.37
18:00 | 6231.7 | 5576.42 | 11808.12
18:30 | 6813.45 | 6041.555 | 12855.005
19:00 | 7395.2 | 6506.69 | 13901.89
19:30 | 7564.2 | 6705.07 | 14269.27
20:00 | 7810.3 | 6529.32 | 14339.62
20:30 | 7897.7 | 6595.795 | 14493.495 |  | Executive Engineer
21:00 | 7985.1 | 6662.27 | 14647.37 |  | Network Operation Division
21:30 | 8007.7 | 6659.64 | 14667.34
22:00 | 8030.3 | 6657.01 | 14687.31
22:30 | 7943.1 | 6771.96 | 14715.06
23:00 | 7855.9 | 6886.91 | 14742.81

## En-Curve
QF-LDC-12
Date | 12-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3910 | 1981.5 | 860 | 38 | 52 | 739.95 | 222 | 4818.2 | 0 | 645 | 2278.5 | 0 | 0 | 2 | 339 | DAILY ENERGY CURVE
00:30 | 3851.5 | 1975 | 895.5 | 38 | 50 | 737.325 | 222 | 4765.1 | 0 | 617.5 | 2164.45 | 0 | 0 | 5.5 | 324.5 | 12-09-2025
01:00 | 3793 | 1968.5 | 931 | 38 | 48 | 734.7 | 222 | 4712 | 0 | 590 | 2050.4 | 0 | 0 | 9 | 310
01:30 | 3778.5 | 1944.5 | 931 | 38 | 48 | 742.615 | 221 | 4585 | 0 | 593 | 2040.7 | 0 | 0 | 5 | 295 | Energy Generated | 323.9357 |  | MKWHr
02:00 | 3764 | 1920.5 | 931 | 38 | 48 | 750.53 | 220 | 4458 | 0 | 596 | 2031 | 0 | 0 | 1 | 280 | Energy not Served | 2.867 |  | MKWHr
02:30 | 3806 | 1938 | 931.5 | 38 | 47 | 747.13 | 220 | 4477 | 0 | 561 | 1694.5 | 0 | 0 | 0.5 | 272.5 | Total Energy Requirement | 326.8027 |  | MKWHr
03:00 | 3848 | 1955.5 | 932 | 38 | 46 | 743.73 | 220 | 4496 | 0 | 526 | 1358 | 0 | 0 | 0 | 265
03:30 | 3828 | 1968 | 932.5 | 38 | 46 | 745.595 | 220 | 4493 | 0 | 502 | 1196.75 | 0 | 0 | 0 | 254.5
04:00 | 3808 | 1980.5 | 933 | 38 | 46 | 747.46 | 220 | 4490 | 0 | 478 | 1035.5 | 0 | 0 | 0 | 244
04:30 | 3796.5 | 1986.5 | 932.5 | 38 | 45 | 747.56 | 218.5 | 4464.5 | 0 | 445 | 984.75 | 0 | 0 | 0 | 232
05:00 | 3785 | 1992.5 | 932 | 38 | 44 | 747.66 | 217 | 4439 | 0 | 412 | 934 | 0 | 0 | 0 | 220
05:30 | 3740.5 | 1941.65 | 932.5 | 38 | 41 | 747.315 | 195.5 | 4302.5 | 1.775 | 378.5 | 837.55 | 0 | 0 | 3.5 | 192.5
06:00 | 3696 | 1890.8 | 933 | 38 | 38 | 746.97 | 174 | 4166 | 3.55 | 345 | 741.1 | 0 | 0 | 7 | 165
06:30 | 3684.5 | 1878.15 | 932.5 | 38 | 39 | 747.61 | 186.5 | 4115.5 | 35.975 | 272 | 636.05 | 0 | 0 | 8.5 | 161
07:00 | 3673 | 1865.5 | 932 | 38 | 40 | 748.25 | 199 | 4065 | 68.4 | 199 | 531 | 0 | 0 | 10 | 157
07:30 | 3663.5 | 1862.15 | 932.5 | 38 | 38.5 | 748.2 | 204.5 | 4026.5 | 135.24 | 188 | 465.5 | 0 | 0 | 6.5 | 153
08:00 | 3654 | 1858.8 | 933 | 38 | 37 | 748.15 | 210 | 3988 | 202.08 | 177 | 400 | 0 | 0 | 3 | 149
08:30 | 3628.5 | 1834.3 | 933 | 38 | 35.5 | 744.985 | 212.5 | 3929 | 226.885 | 173 | 358.5 | 0 | 0 | 1.5 | 123
09:00 | 3603 | 1809.8 | 933 | 38 | 34 | 741.82 | 215 | 3870 | 251.69 | 169 | 317 | 0 | 0 | 0 | 97
09:30 | 3627.5 | 1818.3 | 917.5 | 38 | 34 | 745.43 | 195.5 | 3816 | 279.675 | 169 | 303 | 0 | 0 | 3 | 64
10:00 | 3652 | 1826.8 | 902 | 38 | 34 | 749.04 | 176 | 3762 | 307.66 | 169 | 289 | 0 | 0 | 6 | 31
10:30 | 3668.5 | 1910.3 | 897.5 | 38 | 36 | 747.925 | 175 | 3764.5 | 363.62 | 178 | 272 | 0 | 0 | 16 | 15.5
11:00 | 3685 | 1993.8 | 893 | 38 | 38 | 746.81 | 174 | 3767 | 419.58 | 187 | 255 | 0 | 0 | 26 | 0
11:30 | 3661.5 | 1993.65 | 893 | 38 | 39 | 749.485 | 196 | 3869.5 | 405.535 | 204.5 | 328.5 | 0 | 0 | 26 | 0
12:00 | 3638 | 1993.5 | 893 | 38 | 40 | 752.16 | 218 | 3972 | 391.49 | 222 | 402 | 0 | 0 | 26 | 0
12:30 | 3643 | 1994.85 | 893.5 | 38 | 42 | 750.48 | 218 | 4131.5 | 448.43 | 230 | 504.6 | 0 | 0 | 16.5 | 18
13:00 | 3648 | 1996.2 | 894 | 38 | 44 | 748.8 | 218 | 4291 | 505.37 | 238 | 607.2 | 0 | 0 | 7 | 36
13:30 | 3604.5 | 1937.35 | 894 | 38 | 43 | 748.785 | 218 | 4196.5 | 475.665 | 210 | 557.1 | 0 | 0 | 9.5 | 18
14:00 | 3561 | 1878.5 | 894 | 38 | 42 | 748.77 | 218 | 4102 | 445.96 | 182 | 507 | 0 | 0 | 12 | 0
14:30 | 3716.5 | 1907.5 | 894 | 38 | 42 | 753.19 | 218 | 4037.5 | 375.14 | 157 | 514 | 0 | 0 | 6.5 | 0
15:00 | 3872 | 1936.5 | 894 | 38 | 42 | 757.61 | 218 | 3973 | 304.32 | 132 | 521 | 0 | 0 | 1 | 0
15:30 | 3855 | 1925.1 | 893.5 | 38 | 41 | 757.99 | 218 | 3952 | 228.47 | 132 | 485.5 | 0 | 0 | 2.5 | 0
16:00 | 3838 | 1913.7 | 893 | 38 | 40 | 758.37 | 218 | 3931 | 152.62 | 132 | 450 | 0 | 0 | 4 | 0
16:30 | 3829 | 1893.7 | 893.5 | 38 | 47 | 760.36 | 218 | 3814.5 | 111.595 | 123.5 | 447 | 0 | 0 | 4.5 | 0
17:00 | 3820 | 1873.7 | 894 | 38 | 54 | 762.35 | 218 | 3698 | 70.57 | 115 | 444 | 0 | 0 | 5 | 0
17:30 | 3773.5 | 1755.7 | 893.5 | 38 | 56 | 765.165 | 218.5 | 3775 | 36.005 | 133 | 453.5 | 0 | 0 | 2.5 | 25
18:00 | 3727 | 1637.7 | 893 | 38 | 58 | 767.98 | 219 | 3852 | 1.44 | 151 | 463 | 0 | 0 | 0 | 50
18:30 | 3759.5 | 1745.2 | 893 | 38 | 52 | 760.835 | 219 | 4089 | 0.72 | 339 | 958.75 | 0 | 0 | 0 | 96.5
19:00 | 3792 | 1852.7 | 893 | 38 | 46 | 753.69 | 219 | 4326 | 0 | 527 | 1454.5 | 0 | 0 | 0 | 143
19:30 | 3769 | 1856 | 893 | 38 | 46 | 769.07 | 219 | 4459 | 0 | 569 | 1651.2 | 0 | 0 | 0 | 106
20:00 | 3901 | 2037.2 | 779 | 38 | 48 | 766.32 | 220 | 4418 | 0 | 597 | 1535.1 | 0 | 0 | 0 | 88
20:30 | 3992.5 | 2082.95 | 779 | 38 | 48 | 765.795 | 220 | 4430.5 | 0 | 597 | 1539.75 | 0 | 0 | 0 | 93.5
21:00 | 4084 | 2128.7 | 779 | 38 | 48 | 765.27 | 220 | 4443 | 0 | 597 | 1544.4 | 0 | 0 | 0 | 99
21:30 | 4163.5 | 2130.7 | 779 | 38 | 49 | 764.14 | 220 | 4440 | 0 | 596.5 | 1486.5 | 0 | 0 | 0 | 99
22:00 | 4243 | 2132.7 | 779 | 38 | 50 | 763.01 | 220 | 4437 | 0 | 596 | 1428.6 | 0 | 0 | 0 | 99
22:30 | 4195.5 | 2096.7 | 801 | 38 | 50 | 767.46 | 220 | 4518 | 0 | 592.5 | 1435.4 | 0 | 0 | 0.5 | 97
23:00 | 4148 | 2060.7 | 823 | 38 | 50 | 771.91 | 220 | 4599 | 0 | 589 | 1442.2 | 0 | 0 | 1 | 95
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 06:00 | 372 | 23:00 | Payra | 415 | 17:00 | 409 | 23:00
Ashuganj | 414 | 17:00 | 390 | 12:00 | Rahanpur | 398 | 09:00 | 388 | 22:00
Bhulta | 409 | 17:00 | 389 | 13:00 | Rampal | 405 | 17:00 | 391 | 23:00
Bibiana | 387 | 17:00 | 380 | 23:00
BIPTC | 402 | 05:00 | 394 | 11:00
Bogura | 390 | 09:00 | 377 | 22:00
Gopalganj | 398 | 16:00 | 385 | 23:00
Kaliakoir | 377 | 04:00 | 366 | 23:00
Madunaghat | 391 | 06:00 | 387 | 13:00
Meghnaghat | 383 | 18:00 | 375 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 221 | 13:00 | Keranigonj | 223 | 17:00 | 218 | 13:00
AKSML | 231 | 06:00 | 224 | 23:00 | Khulna(S) | 233 | 10:00 | 218 | 00:00
Aminbazar | 228 | 18:00 | 223 | 11:00 | Madunaghat | 232 | 19:30 | 227 | 12:00
Ashuganj | 235 | 17:00 | 228 | 12:00 | Madunaghat-400 | 232 | 06:00 | 228 | 13:00
Ashuganj-400 | 234 | 17:00 | 224 | 12:00 | Maniknagar | 219 | 16:00 | 214 | 23:00
Baghabari | 235 | 15:00 | 227 | 00:00 | Meghnaghat | 225 | 02:00 | 222 | 12:00
Barapukuria | 221 | 07:00 | 213 | 15:00 | Meghnaghat-400 | 223 | 19:00 | 218 | 12:00
Barapukuria-230 | 221 | 7:00 | 212 | 14:00 | Mirsorai | 228 | 06:00 | 223 | 03:00
Barishal | 229 | 08:00 | 220 | 23:00 | Rajshahi | 230 | 10:00 | 220 | 18:30
Bheramara | 234 | 10:00 | 223 | 23:00 | Rampal | 232 | 17:00 | 219 | 00:00
Bhulta | 233 | 17:00 | 214 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 18:00 | 222 | 23:00 | Rampura | 231 | 06:00 | 220 | 13:00
BIPTC | 237 | 10:00 | 223 | 23:00 | Shikalbaha | 230 | 02:00 | 225 | 13:00
Bogura | 233 | 09:00 | 225 | 22:00 | Shyampur | 222 | 18:30 | 216 | 23:00
Bogura-400 | 232 | 09:00 | 224 | 22:00 | Siddhirganj | 221 | 17:00 | 217 | 11:00
Borhanuddin | 233 | 08:00 | 227 | 23:00 | Sirajgonj | 240 | 17:00 | 235 | 23:00
BSRM | 228 | 06:00 | 223 | 03:00 | Sreepur | 230 | 17:00 | 224 | 03:00
Cumilla(N) | 224 | 18:00 | 218 | 11:00 | Tongi | 230 | 04:00 | 223 | 12:00
Faridpur | 227 | 17:00 | 216 | 23:00
Fenchuganj | 230 | 09:00 | 224 | 00:00
Ghorashal | 235 | 00:00 | 230 | 22:00
Ghorashal-230 | 230 | 02:00 | 221 | 13:00
Gopalganj | 228 | 17:00 | 219 | 23:00
GPH | 230 | 06:00 | 225 | 00:00
Haripur | 220 | 17:00 | 216 | 03:00
Hasnabad | 224 | 17:00 | 219 | 23:00
Hathazari | 229 | 04:00 | 222 | 23:00
Ishurdi | 237 | 10:00 | 225 | 23:00
Jhenaidah | 232 | 10:00 | 216 | 23:00
Kaliakoir | 234 | 02:00 | 227 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 03:00 | 127 | 13:00 | Lalmonirhat | 126 | 10:00 | 121 | 00:00
Agargaon | 136 | 07:00 | 132 | 13:00 | Madanganj | 130 | 18:30 | 127 | 08:00
Agrabad | 132 | 06:00 | 128 | 10:00 | Madaripur | 135 | 11:00 | 129 | 23:00
AKS | 130 | 05:00 | 127 | 13:00 | Madartek | 138 | 06:00 | 128 | 11:00
Aminbazar | 134 | 18:00 | 130 | 11:00 | Madunaghat | 134 | 19:00 | 131 | 11:00
Amnura | 135 | 09:00 | 127 | 18:30 | Magura | 136 | 10:00 | 122 | 23:00
Ashuganj | 142 | 08:00 | 138 | 00:00 | Mahasthangarh | 129 | 09:00 | 122 | 22:00
Bagerhat | 133 | 10:00 | 119 | 00:00 | Maijdee | 119 | 18:00 | 115 | 15:00
Bajitpur | 133 | 17:00 | 125 | 23:00 | Manikganj | 129 | 04:00 | 124 | 23:00
Bakulia | 133 | 19:00 | 128 | 23:00 | Maniknagar | 132 | 06:00 | 129 | 12:00
Banani | 138 | 05:00 | 125 | 13:00 | Matarbari | 118 | 16:00 | 110 | 23:00
Bangabhaban | 132 | 05:00 | 130 | 00:00 | Matuail | 130 | 19:00 | 126 | 11:00
Barapukuria | 134 | 06:00 | 126 | 15:00 | Millgate | 134 | 02:00 | 129 | 23:00
Barguna | 135 | 07:00 | 131 | 00:00 | Mirpur | 133 | 19:00 | 128 | 11:00
Barishal | 135 | 03:00 | 128 | 23:00 | Mirzapur | 130 | 00:00 | 125 | 23:00
Barishal-230 | 135 | 08:00 | 127 | 23:00 | Mithapukur | 128 | 09:00 | 123 | 15:00
Baroaulia | 133 | 06:00 | 128 | 11:00 | MI_Cement | 158 | 02:00 | 127 | 11:00
Baroirhat | 126 | 06:00 | 119 | 03:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 03:00 | 128 | 12:00 | Mogbazar | 139 | 05:00 | 127 | 13:00
BashundharaCement | 130 | 18:30 | 127 | 08:00 | Mongla | 134 | 11:00 | 121 | 00:00
Beanibazar | 127 | 06:00 | 121 | 00:00 | Motijheel | 132 | 05:00 | 123 | 19:00
Benapole | 134 | 10:00 | 119 | 00:00 | Muktagacha | 128 | 19:00 | 118 | 23:00
Bhaluka | 132 | 17:00 | 124 | 01:00 | Munshiganj | 131 | 18:30 | 127 | 03:00
Bhandaria | 130 | 07:00 | 119 | 23:00 | Muradnagar | 125 | 06:00 | 120 | 11:00
Bhangura | 134 | 15:00 | 128 | 02:00 | Mymensingh | 128 | 19:00 | 115 | 23:00
Bheramara | 137 | 10:00 | 131 | 00:00 | Naogaon | 127 | 08:00 | 120 | 22:00
Bheramara(GK) | 138 | 17:00 | 131 | 00:00 | Narail | 136 | 10:00 | 121 | 23:00
Bhulta | 124 | 17:00 | 120 | 00:00 | Narinda | 132 | 6:00 | 129 | 12:00
Bog-Sherpur | 131 | 09:00 | 126 | 23:00 | Narshingdi | 139 | 00:00 | 117 | 00:00
Bogura | 131 | 01:00 | 126 | 22:00 | Natore | 131 | 08:00 | 120 | 23:00
Bogura-230 | 132 | 02:00 | 126 | 22:00 | Nawabganj | 137 | 08:00 | 133 | 13:00
Brahmanbaria | 137 | 08:00 | 131 | 00:00 | Netrakona | 126 | 16:00 | 112 | 23:00
Cantonment | 136 | 17:00 | 132 | 12:00 | New | 136 | 17:00 | 130 | 23:00
Chandina | 129 | 18:00 | 123 | 23:00 | Niamatpur | 137 | 08:00 | 131 | 23:00
Chandpur | 130 | 18:00 | 119 | 10:00 | Noapara | 137 | 10:00 | 126 | 09:00
Chandraghona | 134 | 06:00 | 131 | 11:00 | Pabna | 136 | 16:00 | 128 | 00:00
Chapai | 135 | 08:00 | 130 | 22:00 | Palashbari | 126 | 08:00 | 119 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 18:30 | 128 | 01:00 | Panchagarh | 135 | 02:00 | 121 | 00:00
Chauddagram | 125 | 06:00 | 117 | 11:00 | Patiya | 131 | 06:00 | 127 | 23:00
Chhatak | 128 | 06:00 | 119 | 00:00 | Patuakhali | 136 | 22:00 | 133 | 00:00
Chowmuhani | 120 | 17:00 | 112 | 04:00 | Payra | 136 | 07:00 | 134 | 00:00
Chuadanga | 135 | 17:00 | 119 | 23:00 | PHP | 125 | 06:00 | 117 | 11:00
Coxsbazar | 119 | 11:00 | 111 | 23:00 | Postogola | 133 | 18:00 | 130 | 18:30
Cumilla(N) | 129 | 18:00 | 123 | 11:00 | Purbachal | 138 | 05:00 | 127 | 13:00
Cumilla(S) | 133 | 06:00 | 121 | 10:00 | Purbasadipur | 130 | 02:00 | 123 | 13:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Rahanpur | 137 | 08:00 | 133 | 21:00
Daudkandi | 123 | 08:00 | 116 | 23:00 | Rahanpur-400 | 137 | 09:00 | 133 | 22:00
Dhaka | 138 | 02:00 | 129 | 12:00 | Rahim | 129 | 17:00 | 127 | 01:00
Dhamrai | 133 | 17:00 | 129 | 23:00 | Rajbari | 133 | 09:00 | 125 | 23:00
Dhanmondi | 139 | 06:00 | 127 | 13:00 | Rajendrapur | 138 | 02:00 | 125 | 00:00
Dohazari | 127 | 06:00 | 123 | 12:00 | Rajshahi | 131 | 06:00 | 123 | 23:00
Faridpur | 135 | 06:00 | 128 | 23:00 | Rajshahi-230 | 131 | 06:00 | 125 | 22:00
Fatullah | 133 | 19:00 | 129 | 11:00 | Ramganj | 124 | 18:00 | 120 | 01:00
Fenchuganj | 135 | 06:00 | 131 | 00:00 | Rampur | 131 | 03:00 | 127 | 12:00
Feni | 124 | 04:00 | 116 | 11:00 | Rampura | 138 | 02:00 | 128 | 12:00
Ghatail | 126 | 00:00 | 117 | 23:00 | Rangamati | 133 | 05:00 | 130 | 13:00
Ghorashal | 139 | 18:00 | 134 | 13:00 | Rangpur | 130 | 09:00 | 124 | 22:00
Goalpara | 139 | 17:00 | 126 | 23:00 | Ruppur | 139 | 17:00 | 131 | 01:00
Gollamari | 139 | 17:00 | 127 | 00:00 | Saidpur | 130 | 17:00 | 123 | 13:00
Gopalganj | 135 | 08:00 | 126 | 23:00 | Satkhira | 136 | 18:00 | 120 | 00:00
Gopalganj-400 | 137 | 17:00 | 130 | 23:00 | Satmasjid | 135 | 06:00 | 133 | 00:00
Gulshan | 138 | 06:00 | 128 | 13:00 | Savar | 134 | 18:30 | 128 | 11:00
Halishahar | 133 | 06:00 | 129 | 09:00 | SevenRings | 139 | 02:00 | 134 | 12:00
Haripur | 130 | 18:30 | 127 | 00:00 | ShahCement | 131 | 18:30 | 128 | 01:00
HaripurSBU | 130 | 18:30 | 127 | 00:00 | Shahjadpur | 138 | 17:00 | 132 | 00:00
Hasnabad | 132 | 17:00 | 130 | 00:00 | Shahjibazar | 136 | 07:00 | 129 | 00:00
Hathazari | 134 | 03:00 | 130 | 23:00 | Shahmirpur | 132 | 06:00 | 129 | 12:00
Ishurdi | 139 | 10:00 | 132 | 00:00 | Shariatpur | 134 | 08:00 | 126 | 23:00
Jaldhaka | 127 | 06:00 | 120 | 22:00 | Sherpur | 124 | 00:00 | 110 | 23:00
Jamalpur | 129 | 00:00 | 114 | 23:00 | Shikalbaha | 122 | 05:00 | 118 | 13:00
Jashore | 135 | 10:00 | 119 | 23:00 | Shikalbaha-230 | 133 | 02:00 | 130 | 13:00
Jhenaidah | 138 | 10:00 | 120 | 00:00 | Shitalakhya | 131 | 18:30 | 127 | 11:00
Jhenaidah-230 | 138 | 17:00 | 125 | 23:00 | Sholosohor | 133 | 02:00 | 130 | 12:00
Joydebpur | 142 | 01:00 | 129 | 23:00 | Shyampur | 133 | 18:30 | 130 | 02:00
Joypurhat | 126 | 09:00 | 117 | 23:00 | Shyampur-230 | 133 | 19:00 | 128 | 13:00
Juldah | 132 | 01:00 | 129 | 12:00 | Siddhirganj | 130 | 17:00 | 127 | 02:00
Kabirpur | 136 | 19:00 | 126 | 23:00 | Sirajganj | 131 | 03:00 | 124 | 22:00
Kachua | 128 | 19:00 | 120 | 11:00 | Sonargaon | 128 | 17:00 | 124 | 00:00
Kaliakoir | 136 | 17:00 | 131 | 08:00 | Sreemongol | 134 | 08:00 | 127 | 00:00
Kallyanpur | 135 | 18:30 | 130 | 10:00 | Sreepur | 134 | 17:00 | 128 | 01:00
Kalurghat | 134 | 19:30 | 131 | 02:00 | Srinagar | 137 | 06:00 | 134 | 00:00
Kamrangirchar | 137 | 06:00 | 134 | 00:00 | SSM | 136 | 08:00 | 132 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 126 | 06:00 | 116 | 00:00
Kasba | 125 | 06:00 | 120 | 11:00 | Sylhet | 129 | 09:00 | 123 | 00:00
Kazla | 132 | 18:00 | 129 | 00:00 | Sylhet-132 | 128 | 09:00 | 124 | 00:00
Keranigonj | 138 | 17:00 | 134 | 01:00 | Tangail | 127 | 00:00 | 119 | 23:00
Khagrachori | 132 | 06:00 | 129 | 13:00 | Taraganj | 128 | 04:00 | 121 | 15:00
Khulna | 137 | 10:00 | 125 | 23:00 | Thakurgaon | 133 | 02:00 | 123 | 13:00
Khulna(S) | 139 | 10:00 | 127 | 00:00 | TK | 135 | 05:00 | 130 | 12:00
Khulshi | 130 | 05:00 | 127 | 13:00 | Tongi | 136 | 04:00 | 133 | 11:00
Kishoreganj | 129 | 16:00 | 120 | 23:00 | Ullahpara | 134 | 17:00 | 127 | 22:00
Kodda | 137 | 19:00 | 128 | 12:00 | Ullon | 139 | 06:00 | 126 | 13:00
KSRM | 132 | 00:00 | 128 | 15:00 | Uttara | 132 | 00:00 | 128 | 11:00
Kulaura | 134 | 08:00 | 130 | 00:00 | UttaraNew | 133 | 19:00 | 128 | 13:00
Kurigram | 128 | 09:00 | 120 | 00:00 | Zigatola | 138 | 19:00 | 134 | 13:00
Kushtia | 135 | 17:00 | 125 | 00:00
Laksam | 128 | 18:00 | 119 | 11:00
Lakshmipur | 120 | 06:00 | 111 | 02:00
Lalbag | 137 | 06:00 | 134 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division