## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-09-2025 | [28 empty] | Date: | 13-09-2025 | [28 empty] | Date: | 13-09-2025 | [28 empty] | Date: | 13-09-2025 | [28 empty] | Date: | 13-09-2025 | [14 empty] | Date: | 13-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 50.3 | 17 | 69 | 107 | 0 | 0 | 35 | 161 | 0 | 450 | 45 | 0 | 0 | 55 | 28 | 98 | 0 | 0 | 125 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 66 | 62 | 0 | 0 | 0 | 0 | 220 | 15 | 42 | 267 | 0 | 0 | 19 | 8 | 50 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 8 | 210 | 355 | 330 | 45 | 202 | 31 | 70 | 90 | 187 | 9 | 19 | 98 | 50 | 52.2 | 0 | 14 | 310 | 0 | 386 | 0 | 37 | 159 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 7730.2 | 823 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 756.11 | 0 | 0 | 0 | 70 | 91 | 0 | 95 | 30 | 0 | 0 | 0 | 14 | 0 | 0 | 198 | 0 | 192 | 0 | 195 | 0 | 414 | 0 | 0 | 165 | 40 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 350 | 1222 | 17 | 7063.31 | 14793.51 | 108.82
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 47.3 | 0 | 69 | 108 | 0 | 0 | 35 | 154 | 0 | 450 | 151 | 0 | 0 | 55 | 25 | 99 | 0 | 0 | 125 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 6 | 66 | 54 | 0 | 0 | 0 | 0 | 221 | 15 | 42 | 266 | 0 | 0 | 19 | 8 | 49 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 8 | 210 | 356 | 330 | 45 | 207 | 31 | 72 | 90 | 132 | 13 | 19 | 98 | 48 | 52.2 | 0 | 14 | 310 | 0 | 361 | 0 | 38 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 7632.2 | 893 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 768.51 | 0 | 0 | 0 | 35 | 113 | 0 | 95 | 30 | 0 | 0 | 0 | 14 | 0 | 0 | 191 | 0 | 186 | 0 | 189 | 0 | 400 | 0 | 0 | 164 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 300 | 1222 | 17 | 6998.51 | 14630.71 | 108.82
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 46 | 0 | 69 | 90 | 0 | 0 | 35 | 146 | 0 | 450 | 151 | 0 | 0 | 17 | 25 | 99 | 0 | 0 | 90 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 5 | 66 | 54 | 0 | 0 | 0 | 0 | 219 | 14 | 38 | 268 | 0 | 0 | 19 | 0 | 46 | 220 | 0 | 0 | 0 | 1137 | 0 | 51 | 40 | 8 | 210 | 356 | 330 | 45 | 207 | 31 | 72 | 90 | 111 | 10 | 19 | 98 | 46 | 52.2 | 0 | 14 | 305 | 0 | 367 | 0 | 38 | 153 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 7425.9 | 894 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 766.41 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 183 | 0 | 186 | 0 | 406 | 0 | 0 | 164 | 43 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 300 | 1100 | 17 | 6468.41 | 13894.31 | 108.81
03:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 37 | 90 | 0 | 0 | 35 | 35 | 0 | 450 | 151 | 0 | 0 | 0 | 95 | 99 | 0 | 0 | 70 | 21.7 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 66 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 40 | 268 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1153 | 0 | 51 | 13 | 8 | 210 | 356 | 330 | 45 | 214 | 31 | 72 | 90 | 107 | 11 | 19 | 98 | 44 | 52.2 | 0 | 14 | 305 | 0 | 381 | 0 | 38 | 151 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 7138.9 | 894 | 257 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1138 | 0 | 768.25 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 181 | 0 | 184 | 0 | 405 | 0 | 0 | 167 | 43 | 70 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 115 | 220 | 0 | 300 | 1095 | 0 | 6375.25 | 13514.15 | 108.81
04:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 0 | 0 | 350 | 151 | 0 | 0 | 0 | 331 | 37 | 0 | 0 | 70 | 21.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 42 | 268 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 210 | 356 | 330 | 45 | 214 | 31 | 71 | 90 | 104 | 8 | 19 | 98 | 44 | 25 | 0 | 14 | 315 | 0 | 366 | 0 | 38 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 104 | 0 | 0 | 18 | 6989.7 | 893 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 765.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 186 | 0 | 189 | 0 | 400 | 0 | 0 | 168 | 43 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 115 | 220 | 0 | 300 | 1100 | 0 | 6120.33 | 13110.03 | 108.81
05:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 350 | 151 | 0 | 0 | 0 | 333 | 36 | 0 | 0 | 70 | 21.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 42 | 267 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1130 | 0 | 51 | 0 | 8 | 210 | 356 | 330 | 45 | 214 | 31 | 70 | 90 | 103 | 8 | 19 | 98 | 44 | 25 | 0 | 14 | 310 | 0 | 366 | 0 | 38 | 152 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 105 | 0 | 0 | 18 | 6910.7 | 893 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 760.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 182 | 0 | 185 | 0 | 403 | 0 | 0 | 163 | 46 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 300 | 1100 | 0 | 6083.15 | 12993.85 | 108.8
06:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 350 | 151 | 0 | 0 | 0 | 334 | 36 | 0 | 0 | 70 | 21.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.08 | 217 | 0 | 42 | 266 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 990 | 1 | 51 | 0 | 8 | 230 | 356 | 300 | 45 | 189 | 31 | 71 | 90 | 104 | 8 | 19 | 98 | 42 | 25 | 0 | 14 | 305 | 0 | 362 | 0 | 38 | 152 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 105 | 0 | 0 | 18 | 6714.78 | 894 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 913 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 186 | 0 | 182 | 0 | 184 | 0 | 396 | 0 | 0 | 165 | 44 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 300 | 1000 | 0 | 5924.25 | 12639.03 | 108.8
07:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 350 | 151 | 0 | 0 | 0 | 335 | 36 | 0 | 3 | 70 | 21.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 38 | 215 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1000 | 4 | 51 | 0 | 8 | 235 | 355 | 330 | 45 | 193 | 28 | 69 | 90 | 102 | 8 | 19 | 47 | 40 | 8 | 3 | 14 | 300 | 0 | 363 | 0 | 38 | 150 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 105 | 0 | 1.39 | 15 | 6624.09 | 894 | 274 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 883 | 0 | 758.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 10 | 0 | 0 | 3.39 | 184 | 0 | 182 | 0 | 182 | 0 | 405 | 0 | 0.3 | 163 | 43 | 35 | 2 | 0 | 0 | 0 | 0 | 0.1 | 12 | 0.07 | 0 | 169 | 115 | 220 | 0 | 300 | 980 | 0 | 5868.13 | 12492.22 | 108.8
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 52 | 45 | 0 | 0 | 0 | 0 | 0 | 350 | 150 | 0 | 0 | 0 | 334 | 36 | 0 | 8 | 35 | 18.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.43 | 218 | 0 | 14 | 260 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 997 | 4 | 51 | 0 | 8 | 235 | 355 | 330 | 45 | 193 | 28 | 68 | 90 | 104 | 9 | 19 | 32 | 38 | 8 | 19 | 14 | 305 | 0 | 364 | 0 | 38 | 152 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 105 | 1 | 4.31 | 18 | 6684.44 | 893 | 279 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 890 | 0 | 769.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.59 | 20 | 0 | 0 | 9.23 | 186 | 0 | 183 | 0 | 183 | 0 | 406 | 0 | 0.88 | 161 | 42 | 35 | 5 | 0 | 0 | 0 | 0 | 0.7 | 30 | 0.27 | 0 | 168 | 115 | 220 | 0 | 303 | 900 | 0 | 5901.18 | 12585.62 | 108.79
09:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 55 | 75 | 0 | 0 | 17 | 0 | 0 | 350 | 150 | 0 | 0 | 0 | 332 | 36 | 0 | 19 | 35 | 21.7 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 2.21 | 218 | 0 | 3 | 268 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 988 | 9 | 51 | 0 | 0 | 235 | 352 | 330 | 44 | 200 | 31 | 52 | 90 | 104 | 8 | 19 | 31 | 32 | 8 | 28 | 14 | 315 | 0 | 374 | 0 | 38 | 158 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 105 | 1 | 10.27 | 18 | 6804.18 | 893 | 279 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 901 | 0 | 769.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.54 | 47 | 0 | 0 | 17.27 | 190 | 0 | 208 | 0 | 189 | 0 | 405 | 0 | 1.66 | 163 | 42 | 35 | 9 | 34 | 0 | 0 | 0 | 1.6 | 72 | 0.36 | 0 | 168 | 115 | 220 | 0 | 303 | 890 | 0 | 6104.63 | 12908.81 | 108.78
10:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 70 | 75 | 0 | 0 | 20 | 16 | 0 | 350 | 149 | 0 | 0 | 0 | 330 | 36 | 0 | 32 | 35 | 20 | 22 | 0 | 510 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.04 | 218 | 0 | 4 | 266 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1004 | 10 | 43 | 0 | 0 | 235 | 348 | 330 | 28 | 212 | 33 | 51 | 90 | 107 | 8 | 6 | 32 | 28 | 8 | 37 | 14 | 315 | 0 | 384 | 0 | 38 | 162 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 65 | 2 | 20.68 | 18 | 6830.72 | 893 | 274 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 903 | 0 | 767.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.81 | 68 | 0 | 0 | 24.35 | 193 | 0 | 210 | 0 | 191 | 0 | 414 | 0 | 1.95 | 162 | 44 | 35 | 10 | 34 | 0 | 0 | 0 | 3 | 50 | 0.33 | 0 | 171 | 115 | 220 | 0 | 303 | 890 | 0 | 6150.56 | 12981.28 | 108.77
11:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 12 | 14 | 70 | 90 | 30 | 0 | 35 | 50 | 0 | 350 | 147 | 0 | 0 | 0 | 329 | 36 | 0 | 15 | 35 | 20 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.51 | 218 | 0 | 2 | 268 | 0 | 0 | 21 | 0 | 0 | 219 | 0 | 0 | 0 | 1052 | 16 | 43 | 0 | 0 | 220 | 346 | 330 | 20 | 204 | 34 | 50 | 90 | 133 | 11 | 6 | 17 | 32 | 8 | 46 | 14 | 320 | 0 | 387 | 0 | 38 | 158 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 65 | 2 | 25.45 | 18 | 6994.96 | 893 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 952 | 0 | 750.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.84 | 46 | 0 | 0 | 50.64 | 193 | 0 | 209 | 0 | 191 | 0 | 414 | 0 | 4.63 | 162 | 44 | 35 | 17 | 34 | 0 | 0 | 0 | 4.6 | 78 | 0.73 | 0 | 167 | 115 | 220 | 0 | 303 | 910 | 0 | 6240.61 | 13235.57 | 108.75
12:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 25 | 17 | 70 | 96 | 60 | 0 | 35 | 82 | 0 | 350 | 146 | 0 | 0 | 0 | 326 | 36 | 0 | 5 | 35 | 20 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.35 | 219 | 4 | 4 | 269 | 0 | 0 | 42 | 0 | 6 | 219 | 0 | 0 | 0 | 1172 | 4 | 43 | 0 | 0 | 205 | 339 | 330 | 20 | 202 | 33 | 51 | 90 | 132 | 10 | 17 | 17 | 34 | 8 | 45 | 14 | 320 | 0 | 400 | 0 | 38 | 160 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 75 | 9 | 65 | 1 | 32.71 | 18 | 7264.06 | 893 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 1063 | 0 | 745.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.22 | 65 | 0 | 0 | 49.22 | 197 | 0 | 206 | 0 | 198 | 0 | 414 | 0 | 6.49 | 161 | 44 | 35 | 38 | 34 | 0 | 0 | 0 | 1.5 | 68 | 0.06 | 0 | 175 | 115 | 220 | 0 | 302 | 1000 | 0 | 6431.12 | 13695.18 | 108.74
13:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 44.2 | 17 | 70 | 105 | 115 | 0 | 37 | 141 | 0 | 380 | 147 | 0 | 0 | 0 | 328 | 36 | 0 | 14 | 35 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1.5 | 219 | 16 | 7 | 267 | 0 | 0 | 45 | 0 | 31 | 218 | 0 | 0 | 0 | 1150 | 17 | 43 | 12 | 0 | 185 | 348 | 330 | 20 | 198 | 34 | 51 | 90 | 141 | 5 | 17 | 45 | 38 | 8 | 45 | 14 | 320 | 0 | 377 | 0 | 38 | 159 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 65 | 1 | 45.92 | 18 | 7435.62 | 893 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1132 | 0 | 747.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.47 | 108 | 0 | 0 | 49.57 | 197 | 0 | 195 | 0 | 194 | 0 | 400 | 0 | 4.1 | 160 | 45 | 35 | 37 | 34 | 0 | 0 | 0 | 5.4 | 148 | 0.16 | 0 | 196 | 115 | 180 | 0 | 302 | 1084 | 0 | 6606.51 | 14042.13 | 108.73
14:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 45.2 | 17 | 70 | 105 | 145 | 0 | 37 | 145 | 0 | 380 | 147 | 0 | 0 | 0 | 324 | 0 | 0 | 3 | 35 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1.55 | 219 | 15 | 5 | 265 | 0 | 0 | 46 | 0 | 47 | 218 | 0 | 0 | 0 | 1123 | 18 | 43 | 68 | 0 | 155 | 346 | 330 | 20 | 194 | 34 | 50 | 90 | 156 | 0 | 19 | 43 | 38 | 25 | 30 | 20 | 310 | 0 | 369 | 0 | 38 | 153 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 0 | 33 | 2 | 25.41 | 18 | 7354.16 | 894 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 1148 | 0 | 747.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.79 | 64 | 0 | 0 | 45.21 | 184 | 0 | 177 | 0 | 174 | 0 | 342 | 0 | 5.14 | 160 | 45 | 35 | 27 | 34 | 0 | 0 | 0 | 5.6 | 87 | 0.29 | 0 | 246 | 115 | 180 | 0 | 302 | 1090 | 0 | 6480.29 | 13834.45 | 108.72
15:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 45.7 | 17 | 70 | 105 | 145 | 0 | 37 | 162 | 0 | 380 | 146 | 0 | 0 | 0 | 326 | 0 | 0 | 7 | 35 | 21.2 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 2.03 | 220 | 15 | 4 | 265 | 0 | 0 | 48 | 0 | 46 | 218 | 0 | 0 | 0 | 1157 | 6 | 51 | 80 | 0 | 145 | 352 | 330 | 16 | 196 | 32 | 63 | 90 | 155 | 0 | 7 | 63 | 48 | 25 | 17 | 21 | 310 | 0 | 386 | 0 | 38 | 155 | 6 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 73 | 9 | 57 | 0 | 13.36 | 18 | 7453.29 | 893 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 1176 | 0 | 743.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.73 | 36 | 0 | 0 | 15.47 | 172 | 0 | 170 | 0 | 167 | 0 | 363 | 0 | 4.48 | 165 | 45 | 35 | 24 | 34 | 0 | 0 | 0 | 2.2 | 64 | 0.31 | 0 | 248 | 115 | 180 | 0 | 304 | 1095 | 0 | 6392.3 | 13845.59 | 108.72
16:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 47.4 | 17 | 70 | 105 | 145 | 0 | 37 | 162 | 0 | 380 | 146 | 0 | 0 | 0 | 332 | 0 | 0 | 3 | 35 | 20.2 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.35 | 220 | 15 | 2 | 265 | 0 | 0 | 50 | 0 | 47 | 219 | 0 | 0 | 0 | 1144 | 3 | 51 | 80 | 0 | 155 | 351 | 300 | 6 | 213 | 20 | 68 | 90 | 144 | 0 | 19 | 63 | 44 | 25 | 16 | 28 | 310 | 0 | 380 | 0 | 38 | 156 | 6 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 76 | 9 | 28 | 0 | 22.69 | 18 | 7384.64 | 893 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 1180 | 0 | 724.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.95 | 24 | 0 | 0 | 30.35 | 174 | 0 | 172 | 0 | 169 | 0 | 396 | 0 | 2.48 | 164 | 45 | 35 | 12 | 34 | 0 | 0 | 0 | 3.5 | 24 | 0.14 | 0 | 196 | 115 | 180 | 0 | 304 | 1098 | 0 | 6286.79 | 13671.43 | 108.72
17:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 38 | 17 | 64 | 60 | 145 | 0 | 37 | 162 | 0 | 420 | 147 | 0 | 0 | 0 | 332 | 0 | 0 | 2 | 35 | 20.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 49 | 8 | 0 | 0 | 0 | 0.06 | 220 | 14 | 13 | 265 | 0 | 0 | 50 | 10 | 17 | 220 | 0 | 0 | 0 | 1138 | 1 | 51 | 60 | 0 | 155 | 354 | 300 | 5 | 213 | 20 | 68 | 90 | 139 | 0 | 19 | 43 | 42 | 25 | 5 | 29 | 305 | 0 | 360 | 0 | 38 | 153 | 5 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 76 | 9 | 28 | 0 | 6.83 | 18 | 7285.39 | 893 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1108 | 0 | 740.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 13 | 0 | 0 | 4 | 170 | 0 | 168 | 0 | 165 | 0 | 389 | 0 | 0.4 | 163 | 45 | 35 | 2 | 0 | 0 | 0 | 0 | 0.5 | 14 | 0.09 | 0 | 164 | 115 | 180 | 0 | 304 | 1094 | 0 | 6030.67 | 13316.06 | 108.72
18:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 15 | 17 | 52 | 107 | 145 | 0 | 37 | 162 | 0 | 420 | 148 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 125 | 20.5 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 49 | 16 | 0 | 0 | 0 | 0 | 219 | 15 | 8 | 265 | 0 | 0 | 50 | 17 | 14 | 220 | 0 | 0 | 0 | 1149 | 0 | 51 | 60 | 0 | 145 | 320 | 300 | 5 | 211 | 20 | 72 | 90 | 138 | 0 | 19 | 45 | 44 | 25 | 0 | 36 | 310 | 0 | 395 | 0 | 38 | 147 | 5 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 76 | 9 | 28 | 0 | 0 | 18 | 7436.5 | 893 | 197 | 0 | 10 | 13 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1064 | 0 | 741.19 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 15 | 0 | 0 | 170 | 0 | 169 | 0 | 166 | 0 | 393 | 0 | 0 | 164 | 45 | 35 | 0 | 14 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 175 | 115 | 180 | 0 | 304 | 1050 | 0 | 5980.29 | 13416.79 | 108.72
19:00 | 5 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 37.8 | 33 | 96 | 107 | 245 | 28 | 37 | 162 | 0 | 450 | 149 | 0 | 0 | 40 | 331 | 0 | 0 | 0 | 125 | 25 | 21 | 0 | 450 | 11 | 15 | 0 | 0 | 3 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 15 | 23 | 265 | 0 | 0 | 50 | 17 | 16 | 222 | 0 | 0 | 0 | 1160 | 0 | 51 | 92 | 0 | 135 | 355 | 330 | 5 | 192 | 20 | 89 | 90 | 173 | 0 | 19 | 98 | 48 | 37 | 0 | 36 | 310 | 0 | 370 | 0 | 38 | 159 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 14 | 76 | 9 | 28 | 0 | 0 | 18 | 8017.8 | 893 | 173 | 0 | 34 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 729.4 | 0 | 0 | 0 | 50 | 40 | 0 | 94 | 31 | 44 | 0 | 0 | 20 | 0 | 0 | 189 | 0 | 182 | 0 | 192 | 0 | 414 | 0 | 0 | 165 | 45 | 110 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 283 | 115 | 220 | 0 | 321 | 1140 | 17 | 6861.4 | 14879.2 | 108.72
19:30 | 16 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 48 | 35 | 132 | 107 | 294 | 55 | 37 | 162 | 0 | 450 | 149 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 125 | 25.7 | 21 | 0 | 450 | 13 | 15 | 0 | 0 | 6 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 15 | 24 | 266 | 0 | 0 | 50 | 17 | 15 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 115 | 0 | 115 | 355 | 330 | 5 | 182 | 20 | 89 | 90 | 161 | 0 | 19 | 98 | 48 | 52.2 | 0 | 36 | 310 | 0 | 385 | 0 | 38 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 76 | 9 | 28 | 0 | 0 | 18 | 8182.9 | 826 | 172 | 0 | 30 | 56 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 728.97 | 0 | 0 | 0 | 109 | 90 | 0 | 94 | 36 | 52 | 0 | 0 | 20 | 0 | 0 | 183 | 0 | 174 | 0 | 190 | 0 | 414 | 0 | 0 | 164 | 44 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 307 | 115 | 220 | 0 | 322 | 1232 | 17 | 7089.97 | 15272.87
20:00 | 24 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 48.1 | 35 | 132 | 107 | 294 | 55 | 37 | 162 | 0 | 450 | 149 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 125 | 26.2 | 21 | 0 | 455 | 15 | 15 | 0 | 0 | 9 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 15 | 26 | 267 | 0 | 0 | 50 | 17 | 15 | 222 | 0 | 0 | 0 | 1160 | 0 | 51 | 112 | 0 | 115 | 355 | 330 | 5 | 182 | 20 | 90 | 90 | 157 | 0 | 19 | 98 | 50 | 52.2 | 0 | 37 | 305 | 0 | 385 | 0 | 38 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 76 | 9 | 28 | 0 | 0 | 18 | 8190.5 | 779 | 151 | 0 | 30 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 728.06 | 0 | 0 | 0 | 113 | 105 | 0 | 94 | 38 | 52 | 0 | 0 | 20 | 0 | 0 | 183 | 0 | 170 | 0 | 191 | 0 | 414 | 0 | 0 | 164 | 44 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 307 | 115 | 220 | 0 | 322 | 1244 | 17 | 7058.26 | 15248.76 | 108.72
21:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 51 | 26 | 132 | 107 | 294 | 55 | 37 | 162 | 0 | 400 | 151 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 380 | 16 | 0 | 0 | 0 | 1 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 15 | 27 | 267 | 0 | 0 | 50 | 17 | 28 | 223 | 0 | 0 | 0 | 1149 | 0 | 51 | 125 | 0 | 119 | 355 | 330 | 5 | 181 | 10 | 89 | 90 | 164 | 0 | 19 | 98 | 50 | 52.2 | 0 | 37 | 315 | 0 | 370 | 0 | 38 | 160 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 76 | 9 | 27 | 0 | 0 | 18 | 8054.2 | 779 | 140 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 726.8 | 0 | 0 | 0 | 113 | 113 | 0 | 94 | 38 | 52 | 0 | 0 | 20 | 0 | 0 | 174 | 0 | 159 | 0 | 190 | 0 | 405 | 0 | 0 | 164 | 44 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 307 | 115 | 220 | 0 | 351 | 1240 | 17 | 7091 | 15145.2 | 108.72
22:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 44.6 | 17 | 132 | 107 | 294 | 55 | 37 | 162 | 0 | 400 | 150 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 380 | 13 | 0 | 0 | 0 | 3 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 14 | 30 | 265 | 0 | 0 | 50 | 17 | 60 | 223 | 0 | 0 | 0 | 1134 | 0 | 51 | 125 | 0 | 105 | 320 | 300 | 5 | 197 | 5 | 88 | 90 | 180 | 0 | 19 | 98 | 50 | 52.2 | 0 | 37 | 305 | 0 | 370 | 0 | 38 | 150 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 76 | 9 | 11 | 0 | 0 | 18 | 7911.8 | 779 | 110 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 720.08 | 0 | 0 | 0 | 113 | 113 | 0 | 94 | 31 | 52 | 0 | 0 | 20 | 0 | 0 | 166 | 0 | 179 | 0 | 183 | 0 | 414 | 0 | 0 | 164 | 44 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 115 | 220 | 0 | 350 | 1232 | 17 | 7066.08 | 14977.88 | 108.72
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 48.2 | 17 | 132 | 107 | 294 | 55 | 37 | 162 | 0 | 400 | 150 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 450 | 15 | 0 | 0 | 0 | 0 | 49 | 70 | 0 | 0 | 0 | 0 | 219 | 15 | 36 | 268 | 0 | 0 | 33 | 17 | 67 | 222 | 0 | 0 | 0 | 1206 | 0 | 51 | 132 | 0 | 100 | 320 | 300 | 5 | 214 | 5 | 88 | 90 | 180 | 0 | 19 | 98 | 50 | 52.2 | 0 | 37 | 310 | 0 | 370 | 0 | 38 | 149 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 75 | 9 | 11 | 0 | 0 | 18 | 8096.4 | 859 | 81 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 727.69 | 0 | 0 | 0 | 113 | 113 | 0 | 94 | 31 | 52 | 0 | 0 | 20 | 0 | 0 | 130 | 0 | 130 | 0 | 156 | 0 | 414 | 0 | 0 | 167 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 350 | 1232 | 17 | 7049.89 | 15146.29 | 108.72
Total KWH | 75888 | 1198080 | 411360 | 0 | 0 | 0 | 0 | 0 | 8726400 | 0 | 0 | 654480 | 291960 | 1748736 | 2054400 | 2563538 | 309913 | 673811 | 2432160 | 0 | 9363000 | 3491985 | 0 | 0 | 419601 | 6963148 | 739000 | 0 | 126453 | 1820400 | 519600 | 515520 | 0 | 11321363.64 | 87818 | 32618 | 0 | 0 | 194880 | 666768 | 538944 | 0 | 0 | 0 | 16320 | 5041385 | 242544 | 564960 | 6370909.09 | 0 | 0 | 683520 | 139692.6 | 625599 | 5208378 | 0 | 0 | 0 | 26863634 | 102060 | 1221956 | 1326472 | 66909 | 4299000 | 8698000 | 7840000 | 577440 | 4906000 | 627048 | 1667520 | 2141010 | 3271200 | 126840 | 425430 | 1668960 | 1036800 | 730954 | 273909 | 526248 | 7546500 | 0 | 9413000 | 0 | 888138 | 3729763.63 | 141576 | 0 | 2009280 | 714720 | 0 | 275000 | 4427410 | 104400 | 1797600 | 204000 | 1489920 | 8700 | 221840 | 445440 | 178649809.96 | 21176000 | 5391360 | 0 | 159840 | 217920 | 912000 | 0 | 0 | 0 | 0 | 0 | 558720 | 26080000 | 0 | 0 | 0 | 63056 | 0 | 739008 | 790272 | 0 | 742848 | 192090 | 280334 | 227666 | 563980 | 130933 | 0 | 320992 | 4401364 | 0 | 4531291 | 0 | 4600973 | 0 | 9696800 | 0 | 30960 | 4008000 | 1003636 | 1508908 | 159381 | 1381728 | 0 | 0 | 0 | 29766.96 | 626400 | 3078 | 429600 | 5373000 | 2761000 | 5353620 | 0 | 7548336 | 26658909.09 | 156000 | 138809770.05 | 317459580.01

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-09-2025 | during | 14-09-2025 | during | 14-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 373 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 146 | 149 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 36 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 0 | 102 | 0 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 25 | 48 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 96 | 107 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 37 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 25.7 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 70 | 87.5 | 87.5 | 51 | 70 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 82 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 450 | 584 | 584 | 528 | 528 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 125 | 160 | 160 | 125 | 125 | -
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2304 | 2950.7 | 5789.54 | 5871.54 | 3278.75 | 3379.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 2 | 0 | 2 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 42 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 223 | 214 | 219 | 219 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 6 | 15 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 70 | 48 | 78 | 48 | 78 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 24 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.35 | 0 | 4.22 | 0 | 4.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 4 | 15 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 13 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1172 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 6 | 2 | 6 | 2 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 269 | 266 | 265 | 265 | 265 | 265 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1953.35 | 2142 | 3001.08 | 3052.86 | 2765.58 | 2812.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 205 | 115 | 250 | 250 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 20 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 5 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 115 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 132 | 161 | 200 | 200 | 80 | 180 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 17.83 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 89 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 45 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1590 | 1766.2 | 2672.89 | 2629.56 | 2293.56 | 2343.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-09-2025 | during | 14-09-2025 | during | 14-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 65 | 28 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 32 | 32 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 76 | 77 | 77 | 109 | 109 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 32.71 | 0 | 30.37 | 0 | 30.37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 12 | 12 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 200.71 | 148 | 352.77 | 320.5 | 359.77 | 327.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 38 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 385 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1216 | 1176 | 1276 | 1276 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 893 | 826 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 22 | 22 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 56 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 262 | 172 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1063 | 1224 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2343 | 2346 | 3622.2 | 3552.2 | 3407.2 | 3337.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 302 | 322 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 12 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1232 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 175 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.06 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1812.06 | 2225 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 13.22 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 183 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 206 | 174 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 22 | 22 | 18 | 18 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 95 | 95 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6.49 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 745.63 | 728.97 | 1435.88 | 1435.88 | 1436 | 1436 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.22 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 65 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1894.56 | 2090.97 | 3184.47 | 3017.87 | 3082.21 | 2915.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 44 | 44 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 164 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.5 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 38 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 68 | 0 | 153.86 | 0 | 153.86 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 381.5 | 428 | 633.46 | 448 | 633.46 | 448
System Total |  |  |  |  | 28823.2 | 27829.875 | 13695.18 | 15272.87 | 22694.41 | 22329.53 | 19075.53 | 18817.98
Forecast Scenario (14-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15100 |  | 210 |  | 15330
|  |  |  | 1:00 | 14750 |  | 140 |  | 14900
|  |  |  | 2:00 | 14250 |  | 120 |  | 14380
|  |  |  | 3:00 | 13710 |  | 140 |  | 13860
|  |  |  | 4:00 | 13370 |  | 120 |  | 13500
|  |  |  | 5:00 | 13220 |  | 80 |  | 13310
|  |  |  | 6:00 | 12730 |  | 40 |  | 12780
|  |  |  | 7:00 | 12600 |  | 0 |  | 12600
|  |  |  | 8:00 | 12360 |  | 0 |  | 12360
|  |  |  | 9:00 | 12650 |  | 0 |  | 12650
|  |  |  | 10:00 | 12900 |  | 0 |  | 12900
|  |  |  | 11:00 | 13400 |  | 0 |  | 13400
|  |  |  | 12:00 | 13500 |  | 0 |  | 13500
|  |  |  | 13:00 | 13900 |  | 0 |  | 13900
|  |  |  | 14:00 | 14000 |  | 0 |  | 14000
|  |  |  | 15:00 | 14100 |  | 0 |  | 14100
|  |  |  | 16:00 | 14100 |  | 0 |  | 14100
|  |  |  | 17:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:00 | 13600 |  | 0 |  | 13600
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15460 |  | 0 |  | 15460
|  |  |  | 19:30 | 15590 |  | 0 |  | 15590
|  |  |  | 20:00 | 15640 |  | 0 |  | 15640
|  |  |  | 21:00 | 15640 |  | 0 |  | 15640
|  |  |  | 22:00 | 15690 |  | 0 |  | 15690
|  |  |  | 23:00 | 15690 |  | 0 |  | 15690
Probable Maximum Temperature: |  |  | 31.40°C
Probable Maximum Demand at Day Peak: |  |  | 13980.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15640.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15640.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.14 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:01 hrs on 14-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13695.18 | MW | 12:00 Hr. | Energy Generated |  |  | 335.6989 |  | MKWHr.
| Day Peak Demand |  |  | 13695.18 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.501 |  | MKWHr.
| Evening Peak Generation |  |  | 15272.87 | MW | 19:30 Hr. | Energy Demand |  |  | 338.1999 |  | MKWHr.
| Evening Peak Demand |  |  | 15669.79 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.6 |  | °C
| Minimum Generation of the Day |  |  | 12492.22 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1015.32 |  | MMCFD
| Maximum Generation of the Day |  |  | 15272.87 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.2534 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.64 | 0 | 14.6543 | 0 | 0 | 0.12645 | 0 | 0 | 56.4208 | Gas | 145.5879 | Gas | 519144633.5021
| Chattogram Zone |  |  | 5.7733 | 33.2345 | 3.0175 | 0 | 5.0414 | 0.11838 | 0 | 0.19488 | 47.38 | Coal | 103.9064 | Coal | 620631322.0881
| Cumilla Zone |  |  | 30.8028 | 0 | 9.3182 | 0 | 0 | 0.27391 | 1.0368 | 0 | 41.4317 | HFO | 36.334 | HFO | 671150493.648
| Mymensingh Zone |  |  | 1.4899 | 0 | 2.5514 | 0 | 0 | 0.23054 | 0 | 0 | 4.2719 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.1454 | Hydro | 5.0414 | Hydro | 504138.5
| Khulna Zone |  |  | 5.3914 | 26.08 | 0.37776 | 0 | 0 | 0.55872 | 22.088 | 0 | 54.4958 | Solar | 3.2702 | Solar | 49360842.4316
| Barishal Zone |  |  | 8.1146 | 39.5802 | 0.5856 | 0 | 0 | 0.003078 | 0 | 0 | 48.2835 | Import | 41.3641 | Import | 235590117.31
| Rajshahi Zone |  |  | 23.2304 | 0 | 2.9385 | 0 | 0 | 1.1436 | 18.2393 | 0 | 45.5519 | Wind | 0.19488 | Wind | 2872531.2
| Rangpur Zone |  |  | 0 | 5.0116 | 2.8906 | 0 | 0 | 0.81555 | 0 | 0 | 8.7178
| Total |  |  | 145.5879 | 103.9064 | 36.334 | 0 | 5.0414 | 3.2702 | 41.3641 | 0.19488 | 335.6989
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 519144633.5021 |  | Hydro | 504138.5
|  |  |  | Coal | 620631322.0881 |  | Solar | 49360842.4316
|  |  |  | HFO | 671150493.648 |  | Import | 235590117.31
|  |  |  | HSD | 0 |  | Wind | 2872531.2
[5 empty] | Total: | 209,92,54,078 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.176 | Peak Hr Flow | 826.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46542381.17 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.2393 | Peak Hr Flow | 728.97 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2182 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0368 | Peak Hr Flow | 48.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2524 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.4521 | Peak Hr Flow | 1602.97 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5430
|  |  |  | Chattogram |  | 0 |  | 1434
|  |  |  | Cumilla |  | 10 |  | 1387
|  |  |  | Mymensingh |  | 126 |  | 1207
|  |  |  | Sylhet |  | 0 |  | 598
|  |  |  | Khulna |  | 30 |  | 1812
|  |  |  | Barishal |  | 10 |  | 437
|  |  |  | Rajshahi |  | 75 |  | 1524
|  |  |  | Rangpur |  | 35 |  | 1023
|  |  |  | Total |  | 286 |  | 14852
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 12:00 |  | Day Peak Generation: 13692 MW.
| 12:50 | 14:33 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS red hot maintenance | [7 empty] | 22.0MW load
interrup.
| 12:50 | 14:32 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS red hot maintenance | [7 empty] | 22.0MW load
interrup.
| 12:50 | 14:42 | Siddhirganj 132/33kV S/S 132kV MTR 2 Forced S/D Due to maintenance work
| 12:50 | 14:42 | Siddhirganj 230/132kV S/S MTR 2 HT Scheduled S/D Due to Oil refilled in OLTC
| 13:20 |  | Siddhirganj 2x120 MW GT-1 and GT-2 were shut down at 12:57 hrs. and 13:20
hrs. respectively.
|  | 14:04 | Coxsbazar 132/33kV S/S 405T-T1 HT is restored.
| 15:15 | 15:50 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to For 33 kV GCB gas refill
work.
| 15:16 | 15:49 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to For 33 kV GCB gas refill
work.
| 15:38 | 17:48 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kV Bus DS Red Hot Maintanence | [7 empty] | 115.0MW load
|  |  | of 33 kV Hi-Tec Feeder. | [7 empty] | interrup.
| 15:38 | 17:47 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kV Red Hot Maintanence of Hi - | [7 empty] | 115.0MW load
|  |  | Tec feeder | [7 empty] | interrup.
|  | 17:42 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
| 17:44 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
|  | 18:24 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT is restored.
|  | 18:25 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT is restored.
|  | 18:27 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 18:27 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
|  | 18:28 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 18:28 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
| 18:32 |  | Candpur (Desh)- Chandpur 132kV Ckt-2 Forced S/D from Chandpur 132/33kV end.
| 18:32 |  | Candpur (Desh)- Chandpur 132kV Ckt-1 Forced S/D from Chandpur 132/33kV end.
| 19:03 |  | Korerhat–Choumohoni 230 kV ckt-4 ( for the first time) and Choumohoni–Kachua 230 kV ckt-2
were switched ON at 19:03 hrs. Power is now flowing from Korerhat to Kachua through
Korerhat–Choumohoni–Kachua line and Kachua 230/132 kV T-1 & T-2 transformers.
|  | 19:08 | Jhenaidah 132/33kV S/S Jhenaidah-Chuadanga, 132kV Circuit-2(L8) is restored.
| 19:30 |  | Evening Peak Generation: 15271 MW.
| 22:35 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Demand full load.
| 01:14 |  | Adani Power Jharkhand Ltd. Unit-1 was sync.
| 02:28 |  | Bheramara 410 MW CCPP Shutdown with remarks:- STG
| 02:39 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GTG
| 02:48 |  | Bheramara 410 MW was forced shut down due to low gas pressure.
| 07:00 |  | Minimum Generation 12612 MW.
| 07:15 |  | Jhenaidah 132/33kV S/S Transformer T-3 LT Forced S/D Due to Due to Red Hot maintenance | [7 empty] | 28.0MW load
|  |  | taken by pbs | [7 empty] | interrup.
| 07:16 |  | Jhenaidah 132/33kV S/S Transformer T-3 HT Forced S/D Due to Due to Red Hot maintenance | [7 empty] | 28.0MW load
|  |  | taken by pbs | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8726400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9363000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 149 | 3491985 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 309913 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 739000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 6963148 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 75888 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48 | 654480 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 107 | 2054400 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 37 | 673811 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 419601 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25.7 | 519600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 515520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 411360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2563538 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1748736 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1198080 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2432160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 126453 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 291960 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 11321363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1820400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2950.7 | 56420796.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 139692.6 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 102060 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 683520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5041385 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5208378 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 15 | 625599 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 538944 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 666768 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 564960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 32618 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 242544 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 87818 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26863634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 194880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 266 | 6370909.09 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2142 | 47380029.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 182 | 4906000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8698000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7840000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 115 | 4299000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 627048 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 577440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 66909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1221956 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 1326472 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 526248 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2141010 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 161 | 3271200 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1036800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 730954 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 425430 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1668960 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 126840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1667520 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 273909 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1766.2 | 41431696
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 28 | 1489920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 204000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 76 | 1797600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 221840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 445440 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 104400 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 148 | 4271900
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 888138 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3729763.63 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714720 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2009280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4427410 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 275000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 141576 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7546500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 9413000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1176 | 29145387.63
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 826 | 21176000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 159840 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 56 | 217920 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 172 | 5391360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 558720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1224 | 26080000 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2346 | 54495840
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 322 | 7548336 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 12 | 429600 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2761000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 26658909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5353620 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 156000 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5373000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3078 | -
Barishal Area Total |  |  |  |  | 2236 | 2225 | 48283543.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 227666 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 63056 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 192090 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 183 | 4401364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4531291 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4600973 | Low gas pressure
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9696800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 130933 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 280334 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 742848 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 790272 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 109 | 739008 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 728.97 | 18239327 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 320992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 563980 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2090.97 | 45551894
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 44 | 1003636 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 4008000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1381728 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29766.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1508908 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 159381 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 626400 | -
Rangpur Area Total |  |  |  |  | 950 | 428 | 8717819.96
Eastern Grid Total |  |  |  |  | 17385.715 | 8182.9 | 178649809.96
Western Grid Total |  |  |  |  | 10444.16 | 7089.97 | 157049097.05
National Grid Total |  |  |  |  | 27829.875 | 15272.87 | 335698907.01
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-09-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9919.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4646.2 | MW
i) Dhaka area |  |  | 5429.9 |  | MW | i) Khulna area |  |  |  | 1782 | MW
ii) Chattogram area |  |  | 1434 |  | MW | ii) Barishal area |  |  |  | 427 | MW
iii) Cumilla area |  |  | 1376.58 |  | MW | iii) Rajshahi area |  |  |  | 1449.2 | MW
iv) Mymensingh area |  |  | 1081 |  | MW | iv) Rangpur area |  |  |  | 988 | MW
v) Sylhet area |  |  | 598 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14565.68 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 18:30 | 133 | PHP | 8 | 02:00
2 | AKSML | 136 | 08:00 | 68 | Ishurdi | 84 | 19:00 | 134 | Pabna | 122 | 23:00
3 | Aftabnagar | 40 | 20:00 | 69 | Jaldhaka | 87 | 18:30 | 135 | Palashbari | 120 | 19:30
4 | Agargaon | 130 | 13:00 | 70 | Jamalpur | 114 | 12:00 | 136 | Panchagarh | 59 | 19:00
5 | Agrabad | 96 | 18:30 | 71 | Jashore | 150 | 18:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 33 | 23:00 | 72 | Jhenaidah | 136 | 19:00 | 138 | Patuakhali | 66 | 00:00
7 | Ashuganj | 83 | 00:00 | 73 | Joydebpur | 154 | 09:00 | 139 | Payra | 36 | 22:00
8 | BSRM | 148 | 00:00 | 74 | Joypurhat | 65 | 20:00 | 140 | Postogola | 60 | 13:00
9 | Bagerhat | 83 | 18:30 | 75 | Juldah | 17 | 11:00 | 141 | Purbachal | 22 | 14:00
10 | Bajitpur | 99 | 21:00 | 76 | KSRM | 30 | 20:00 | 142 | Purbasadipur | 127 | 20:00
11 | Bakulia | 94 | 18:00 | 77 | Kabirpur | 273 | 12:00 | 143 | Rahanpur | 42 | 22:00
12 | Banani | 44 | 13:00 | 78 | Kachua | 96 | 20:00 | 144 | Rahim | 45 | 18:00
13 | Bangabhaban | 11 | 11:00 | 79 | Kallyanpur | 108 | 18:30 | 145 | Rajbari | 87 | 23:00
14 | Barapukuria | 68 | 23:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajendrapur | 135 | 07:00
15 | Barguna | 22 | 23:00 | 81 | Kamrangirchar | 82 | 13:00 | 147 | Rajshahi | 105 | 00:00
16 | Barishal | 115 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 104 | 13:00
17 | Barishal-230 | 104 | 18:30 | 83 | Kasba | 36 | 20:00 | 149 | Ramganj | 108 | 21:00
18 | Baroaulia | 66 | 16:00 | 84 | Kazla | 107 | 14:00 | 150 | Rampur | 51 | 01:00
19 | Baroirhat | 62 | 18:30 | 85 | Keranigonj | 92 | 18:30 | 151 | Rangamati | 16 | 18:30
20 | Bashundhara | 200 | 13:00 | 86 | Khagrachori | 28 | 19:00 | 152 | Rangpur | 136 | 00:00
21 | BashundharaCement | 2 | 18:30 | 87 | Khulna | 64 | 12:00 | 153 | Ruppur | 6.2 | 11:00
22 | Beanibazar | 74 | 00:00 | 88 | Khulshi | 188 | 14:00 | 154 | SSM | 2 | 00:00
23 | Benapole | 67 | 23:00 | 89 | Kishoreganj | 135 | 21:00 | 155 | Saidpur | 101 | 22:00
24 | Bhaluka | 156 | 19:00 | 90 | Kodda | 291 | 15:00 | 156 | Satkhira | 131 | 21:00
25 | Bhandaria | 59 | 22:00 | 91 | Kulaura | 51 | 00:00 | 157 | Satmasjid | 108 | 13:00
26 | Bhangura | 40 | 18:30 | 92 | Kurigram | 64 | 19:00 | 158 | Savar | 236 | 15:00
27 | Bheramara(GK) | 69 | 22:00 | 93 | Kushtia | 182 | 18:30 | 159 | SevenRings | 20.6 | 13:00
28 | Bhulta | 217 | 21:00 | 94 | Laksam | 36 | 22:00 | 160 | ShahCement | 29 | 12:00
29 | Bog-Sherpur | 78 | 00:00 | 95 | Lakshmipur | 39 | 00:00 | 161 | Shahjadpur | 92 | 19:30
30 | Bogura | 153 | 19:00 | 96 | Lalbag | 53 | 20:00 | 162 | Shahjibazar | 120 | 00:00
31 | Borhanuddin | 94 | 21:00 | 97 | Lalmonirhat | 64 | 18:30 | 163 | Shahmirpur | 65 | 16:00
32 | Brahmanbaria | 133 | 21:00 | 98 | MI_Cement | 16.2 | 17:00 | 164 | Shariatpur | 90 | 20:00
33 | Cantonment | 142 | 13:00 | 99 | Madanganj | 40 | 23:00 | 165 | Sherpur | 118 | 08:00
34 | Chandina | 41.81 | 21:00 | 100 | Madaripur | 113 | 00:00 | 166 | Shikalbaha | 22 | 11:00
35 | Chandpur | 90 | 22:00 | 101 | Madartek | 95.54 | 22:00 | 167 | Shitalakhya | 76.2 | 16:00
36 | Chandraghona | 34 | 19:00 | 102 | Madunaghat | 55 | 19:00 | 168 | Sholosohor | 46 | 15:00
37 | Chapai | 67 | 23:00 | 103 | Magura | 67 | 18:30 | 169 | Shyampur | 166 | 13:00
38 | Charsaidpur | 21 | 12:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Siddhirganj | 125 | 15:00
39 | Chauddagram | 72 | 22:00 | 105 | Maijdee | 15 | 22:00 | 171 | Sirajganj | 114 | 19:00
40 | Chhatak | 40 | 00:00 | 106 | Manikganj | 122 | 19:00 | 172 | Sonargaon | 126 | 16:00
41 | Chowmuhani | 181 | 22:00 | 107 | Maniknagar | 62 | 13:00 | 173 | Sreemongol | 80 | 00:00
42 | Chuadanga | 130 | 23:00 | 108 | Matarbari | 51 | 19:00 | 174 | Sreepur | 102 | 18:30
43 | Coxsbazar | 140 | 19:00 | 109 | Matuail | 75 | 15:00 | 175 | Srinagar | 50.71 | 22:00
44 | Cumilla(N) | 118 | 19:30 | 110 | Millgate | 108 | 15:00 | 176 | Sunamganj | 62 | 00:00
45 | Cumilla(S) | 153 | 18:30 | 111 | Mirpur | 127 | 18:30 | 177 | Sylhet | 49 | 00:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 11 | 19:00 | 178 | Sylhet-132 | 119 | 18:30
47 | Daudkandi | 152 | 21:00 | 113 | Mirzapur | 35 | 02:00 | 179 | TK | 35 | 23:00
48 | Dhaka | 72 | 13:00 | 114 | Mithapukur | 76 | 00:00 | 180 | Tangail | 162 | 00:00
49 | Dhamrai | 130 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 18:30
50 | Dhanmondi | 138 | 13:00 | 116 | Mogbazar | 94.1 | 13:00 | 182 | Thakurgaon | 110 | 19:30
51 | Dohazari | 100 | 19:30 | 117 | Mongla | 40 | 19:30 | 183 | Tongi | 127 | 11:00
52 | Faridpur | 171 | 21:00 | 118 | Motijheel | 44 | 13:00 | 184 | Ullahpara | 40 | 20:00
53 | Fatullah | 107 | 15:00 | 119 | Muktagacha | 36 | 00:00 | 185 | Ullon | 56 | 22:00
54 | Fenchuganj | 44 | 03:00 | 120 | Munshiganj | 116 | 00:00 | 186 | Uttara | 79 | 18:30
55 | Feni | 116 | 18:30 | 121 | Muradnagar | 44 | 22:00 | 187 | UttaraNew | 59 | 00:00
56 | GPH | 95 | 11:00 | 122 | Mymensingh | 205 | 00:00 | 188 | Zigatola | 74 | 13:00
57 | Ghatail | 82 | 06:00 | 123 | Naogaon | 139 | 20:00
58 | Ghorashal | 14 | 19:00 | 124 | Narail | 61.5 | 23:00
59 | Ghorashal-230 | 82 | 02:00 | 125 | Narinda | 76 | 13:00
60 | Goalpara | 42 | 13:00 | 126 | Narshingdi | 189 | 21:00
61 | Gollamari | 102 | 00:00 | 127 | Natore | 141 | 00:00
62 | Gopalganj | 110.3 | 19:00 | 128 | Nawabganj | 62 | 22:00
63 | Gulshan | 110 | 13:00 | 129 | Netrakona | 141 | 21:00
64 | Halishahar | 70 | 16:00 | 130 | New | 68 | 14:00
65 | HaripurSBU | 165 | 20:00 | 131 | Niamatpur | 78 | 23:00
66 | Hasnabad | 85 | 20:00 | 132 | Noapara | 46 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14793.51 | 113 |  | 14911.6
1:00 | 14630.71 | 87 |  | 14721.71
2:00 | 13894.31 | 54 |  | 13950.31
3:00 | 13514.15 | 45 |  | 13561.15
4:00 | 13110.03 | 39 |  | 13151.03
5:00 | 12993.85 | 35 |  | 13030.85
6:00 | 12639.03 | 31 |  | 12671.03
7:00 | 12492.22 | 39 |  | 12533.22
8:00 | 12585.62 | 0 |  | 12585.62
9:00 | 12908.81 | 0 |  | 12908.81
10:00 | 12981.28 | 0 |  | 12981.28
11:00 | 13235.57 | 0 |  | 13235.57
12:00 | 13695.18 | 0 |  | 13695.18
13:00 | 14042.13 | 0 |  | 14042.13
14:00 | 13834.45 | 75 |  | 13912.83
15:00 | 13845.59 | 51 |  | 13898.89
16:00 | 13671.43 | 0 |  | 13671.43
17:00 | 13316.06 | 0 |  | 13316.06
18:00 | 13416.79 | 109 |  | 13530.7
19:00 | 14879.2 | 241 |  | 15131.05
19:30 | 15272.87 | 286 |  | 15571.74
20:00 | 15248.76 | 327 |  | 15590.48
21:00 | 15145.2 | 502 |  | 15669.79
22:00 | 14977.88 | 490 |  | 15489.88
23:00 | 15146.29 | 263 |  | 15421.29
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7730.2 | 7063.31 | 14793.51 | DAILY GENERATION CURVE
00:30 | 7681.2 | 7030.91 | 14712.11
01:00 | 7632.2 | 6998.51 | 14630.71 | 13-09-2025
01:30 | 7529.05 | 6733.46 | 14262.51
02:00 | 7425.9 | 6468.41 | 13894.31
02:30 | 7282.4 | 6421.83 | 13704.23
03:00 | 7138.9 | 6375.25 | 13514.15
03:30 | 7064.3 | 6247.79 | 13312.09
04:00 | 6989.7 | 6120.33 | 13110.03
04:30 | 6950.2 | 6101.74 | 13051.94
05:00 | 6910.7 | 6083.15 | 12993.85
05:30 | 6812.74 | 6003.7 | 12816.44
06:00 | 6714.78 | 5924.25 | 12639.03
06:30 | 6669.435 | 5896.19 | 12565.625
07:00 | 6624.09 | 5868.13 | 12492.22
07:30 | 6654.265 | 5884.655 | 12538.92
08:00 | 6684.44 | 5901.18 | 12585.62
08:30 | 6744.31 | 6002.905 | 12747.215
09:00 | 6804.18 | 6104.63 | 12908.81
09:30 | 6817.45 | 6127.595 | 12945.045
10:00 | 6830.72 | 6150.56 | 12981.28
10:30 | 6912.84 | 6195.585 | 13108.425
11:00 | 6994.96 | 6240.61 | 13235.57
11:30 | 7129.51 | 6335.865 | 13465.375
12:00 | 7264.06 | 6431.12 | 13695.18
12:30 | 7349.84 | 6518.815 | 13868.655
13:00 | 7435.62 | 6606.51 | 14042.13
13:30 | 7394.89 | 6543.4 | 13938.29
14:00 | 7354.16 | 6480.29 | 13834.45
14:30 | 7403.725 | 6436.295 | 13840.02
15:00 | 7453.29 | 6392.3 | 13845.59
15:30 | 7418.965 | 6339.545 | 13758.51
16:00 | 7384.64 | 6286.79 | 13671.43
16:30 | 7335.015 | 6158.73 | 13493.745
17:00 | 7285.39 | 6030.67 | 13316.06
17:30 | 7360.945 | 6005.48 | 13366.425
18:00 | 7436.5 | 5980.29 | 13416.79
18:30 | 7727.15 | 6420.845 | 14147.995
19:00 | 8017.8 | 6861.4 | 14879.2
19:30 | 8182.9 | 7089.97 | 15272.87
20:00 | 8190.5 | 7058.26 | 15248.76
20:30 | 8122.35 | 7074.63 | 15196.98 |  | Executive Engineer
21:00 | 8054.2 | 7091 | 15145.2 |  | Network Operation Division
21:30 | 7983 | 7078.54 | 15061.54
22:00 | 7911.8 | 7066.08 | 14977.88
22:30 | 8004.1 | 7057.985 | 15062.085
23:00 | 8096.4 | 7049.89 | 15146.29

## En-Curve
QF-LDC-12
Date | 13-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4045 | 2006.7 | 823 | 38 | 50 | 756.11 | 220 | 4809.2 | 0 | 553 | 1485.5 | 0 | 0 | 7 | 113 | DAILY ENERGY CURVE
00:30 | 4011 | 2058.2 | 858 | 38 | 49 | 762.31 | 220.5 | 4721.6 | 0 | 546.5 | 1440.5 | 0 | 0 | 6.5 | 100 | 13-09-2025
01:00 | 3977 | 2109.7 | 893 | 38 | 48 | 768.51 | 221 | 4634 | 0 | 540 | 1395.5 | 0 | 0 | 6 | 87
01:30 | 3976.5 | 2103.7 | 893.5 | 38 | 47 | 767.46 | 220 | 4530 | 0 | 465 | 1215.85 | 0 | 0 | 5.5 | 70.5 | Energy Generated | 335.6989 |  | MKWHr
02:00 | 3976 | 2097.7 | 894 | 38 | 46 | 766.41 | 219 | 4426 | 0 | 390 | 1036.2 | 0 | 0 | 5 | 54 | Energy not Served | 2.501 |  | MKWHr
02:30 | 4018 | 2097.7 | 894 | 38 | 45 | 767.33 | 219 | 4397.5 | 0 | 353 | 868.7 | 0 | 0 | 6 | 49.5 | Total Energy Requirement | 338.1999 |  | MKWHr
03:00 | 4060 | 2097.7 | 894 | 38 | 44 | 768.25 | 219 | 4369 | 0 | 316 | 701.2 | 0 | 0 | 7 | 45
03:30 | 4154.5 | 2041.2 | 893.5 | 38 | 44 | 766.79 | 218.5 | 4288 | 0 | 263.5 | 598.6 | 0 | 0 | 5.5 | 42
04:00 | 4249 | 1984.7 | 893 | 38 | 44 | 765.33 | 218 | 4207 | 0 | 211 | 496 | 0 | 0 | 4 | 39
04:30 | 4241 | 1980.2 | 893 | 38 | 44 | 762.74 | 218 | 4185 | 0 | 187.5 | 495 | 0 | 0 | 7.5 | 37
05:00 | 4233 | 1975.7 | 893 | 38 | 44 | 760.15 | 218 | 4163 | 0 | 164 | 494 | 0 | 0 | 11 | 35
05:30 | 4212 | 1973.2 | 893.5 | 38 | 43 | 765.075 | 217.5 | 4004 | 6.165 | 156 | 495 | 0 | 0 | 13 | 33
06:00 | 4191 | 1970.7 | 894 | 38 | 42 | 770 | 217 | 3845 | 12.33 | 148 | 496 | 0 | 0 | 15 | 31
06:30 | 4211 | 1965.2 | 894 | 38 | 41 | 764.345 | 217 | 3799 | 33.08 | 148 | 442.5 | 0 | 0 | 12.5 | 35
07:00 | 4231 | 1959.7 | 894 | 38 | 40 | 758.69 | 217 | 3753 | 53.83 | 148 | 389 | 0 | 0 | 10 | 39
07:30 | 4237.5 | 1947.7 | 893.5 | 38 | 39 | 764.1 | 217.5 | 3737 | 111.12 | 146 | 400.5 | 0 | 0 | 7 | 19.5
08:00 | 4244 | 1935.7 | 893 | 38 | 38 | 769.51 | 218 | 3721 | 168.41 | 144 | 412 | 0 | 0 | 4 | 0
08:30 | 4274 | 1935.2 | 893 | 38 | 35 | 769.355 | 218 | 3722 | 250.16 | 172 | 430 | 0 | 0 | 10.5 | 0
09:00 | 4304 | 1934.7 | 893 | 38 | 32 | 769.2 | 218 | 3723 | 331.91 | 200 | 448 | 0 | 0 | 17 | 0
09:30 | 4299 | 1922.35 | 893 | 38 | 30 | 768.16 | 218 | 3733 | 364.535 | 200 | 466.5 | 0 | 0 | 12.5 | 0
10:00 | 4294 | 1910 | 893 | 38 | 28 | 767.12 | 218 | 3743 | 397.16 | 200 | 485 | 0 | 0 | 8 | 0
10:30 | 4280 | 1899.5 | 893 | 38 | 30 | 758.645 | 218 | 3800.5 | 424.28 | 207.5 | 554 | 0 | 0 | 5 | 0
11:00 | 4266 | 1889 | 893 | 38 | 32 | 750.17 | 218 | 3858 | 451.4 | 215 | 623 | 0 | 0 | 2 | 0
11:30 | 4264 | 1912.5 | 893 | 38 | 33 | 747.9 | 218.5 | 4022 | 434.475 | 218 | 676.5 | 0 | 0 | 7.5 | 0
12:00 | 4262 | 1936 | 893 | 38 | 34 | 745.63 | 219 | 4186 | 417.55 | 221 | 730 | 0 | 0 | 13 | 0
12:30 | 4223.5 | 1892.5 | 893 | 38 | 36 | 746.72 | 219 | 4261 | 476.835 | 225.5 | 840.6 | 0 | 0 | 16 | 0
13:00 | 4185 | 1849 | 893 | 38 | 38 | 747.81 | 219 | 4336 | 536.12 | 230 | 951.2 | 0 | 0 | 19 | 0
13:30 | 4058.5 | 1844 | 893.5 | 38 | 38 | 747.535 | 219 | 4357.5 | 472.555 | 233 | 1012.2 | 0 | 0 | 24.5 | 37.5
14:00 | 3932 | 1839 | 894 | 38 | 38 | 747.26 | 219 | 4379 | 408.99 | 236 | 1073.2 | 0 | 0 | 30 | 75
14:30 | 3949.5 | 1834.1 | 893.5 | 38 | 43 | 745.185 | 219.5 | 4417 | 333.785 | 236.5 | 1106.95 | 0 | 0 | 23 | 63
15:00 | 3967 | 1829.2 | 893 | 38 | 48 | 743.11 | 220 | 4455 | 258.58 | 237 | 1140.7 | 0 | 0 | 16 | 51
15:30 | 3951.5 | 1830.7 | 893 | 38 | 46 | 733.74 | 220 | 4425.5 | 225.02 | 240.5 | 1141.55 | 0 | 0 | 13 | 25.5
16:00 | 3936 | 1832.2 | 893 | 38 | 44 | 724.37 | 220 | 4396 | 191.46 | 244 | 1142.4 | 0 | 0 | 10 | 0
16:30 | 3904.5 | 1853.35 | 893 | 38 | 43 | 732.66 | 220 | 4338.5 | 129.535 | 250.5 | 1084.7 | 0 | 0 | 6 | 0
17:00 | 3873 | 1874.5 | 893 | 38 | 42 | 740.95 | 220 | 4281 | 67.61 | 257 | 1027 | 0 | 0 | 2 | 0
17:30 | 3864 | 1896.5 | 893 | 38 | 43 | 741.07 | 219.5 | 4248.5 | 34.355 | 366 | 1021.5 | 0 | 0 | 1 | 54.5
18:00 | 3855 | 1918.5 | 893 | 38 | 44 | 741.19 | 219 | 4216 | 1.1 | 475 | 1016 | 0 | 0 | 0 | 109
18:30 | 3896.5 | 1946.25 | 893 | 38 | 46 | 735.295 | 219 | 4399 | 0.55 | 587 | 1385.9 | 0 | 0 | 1.5 | 175
19:00 | 3938 | 1974 | 893 | 38 | 48 | 729.4 | 219 | 4582 | 0 | 699 | 1755.8 | 0 | 0 | 3 | 241
19:30 | 3904 | 1971.7 | 826 | 38 | 48 | 728.97 | 219 | 4719 | 0 | 718 | 2094.2 | 0 | 0 | 6 | 286
20:00 | 3874 | 1974.2 | 779 | 38 | 50 | 728.06 | 219 | 4742.2 | 0 | 706 | 2129.3 | 0 | 0 | 9 | 327
20:30 | 3851 | 1920.6 | 779 | 38 | 50 | 727.43 | 219 | 4749.2 | 0 | 704 | 2153.75 | 0 | 0 | 5 | 414.5
21:00 | 3828 | 1867 | 779 | 38 | 50 | 726.8 | 219 | 4756.2 | 0 | 702 | 2178.2 | 0 | 0 | 1 | 502
21:30 | 3751.5 | 1858 | 779 | 38 | 50 | 723.44 | 219 | 4734.6 | 0 | 698.5 | 2207.5 | 0 | 0 | 2 | 496
22:00 | 3675 | 1849 | 779 | 38 | 50 | 720.08 | 219 | 4713 | 0 | 695 | 2236.8 | 0 | 0 | 3 | 490
22:30 | 3623 | 1889 | 819 | 38 | 50 | 723.885 | 219 | 4760.6 | 0 | 695 | 2243.1 | 0 | 0 | 1.5 | 376.5
23:00 | 3571 | 1929 | 859 | 38 | 50 | 727.69 | 219 | 4808.2 | 0 | 695 | 2249.4 | 0 | 0 | 0 | 263
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 06:00 | 370 | 12:00 | Payra | 414 | 06:00 | 409 | 00:00
Ashuganj | 407 | 7:00 | 389 | 12:00 | Rahanpur | 404 | 22:00 | 388 | 02:00
Bhulta | 403 | 21:00 | 381 | 12:00 | Rampal | 404 | 07:00 | 391 | 00:00
Bibiana | 386 | 06:00 | 379 | 12:00
BIPTC | 404 | 07:00 | 394 | 23:00
Bogura | 398 | 22:00 | 377 | 02:00
Gopalganj | 397 | 06:00 | 386 | 00:00
Kaliakoir | 373 | 07:00 | 361 | 12:00
Madunaghat | 391 | 07:00 | 386 | 00:00
Meghnaghat | 384 | 06:00 | 374 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 07:00 | 217 | 12:00 | Keranigonj | 224 | 06:00 | 214 | 12:00
AKSML | 230 | 07:00 | 222 | 12:00 | Khulna(S) | 232 | 09:00 | 219 | 00:00
Aminbazar | 228 | 05:00 | 218 | 12:00 | Madunaghat | 230 | 22:00 | 225 | 12:00
Ashuganj | 235 | 21:00 | 223 | 12:00 | Madunaghat-400 | 231 | 07:00 | 227 | 12:00
Ashuganj-400 | 235 | 21:00 | 223 | 12:00 | Maniknagar | 219 | 08:00 | 212 | 12:00
Baghabari | 233 | 21:00 | 227 | 00:00 | Meghnaghat | 226 | 08:00 | 220 | 11:00
Barapukuria | 224 | 18:30 | 215 | 08:00 | Meghnaghat-400 | 223 | 06:00 | 216 | 12:00
Barapukuria-230 | 224 | 18:30 | 215 | 08:00 | Mirsorai | 227 | 08:00 | 221 | 12:00
Barishal | 228 | 07:00 | 221 | 00:00 | Rajshahi | 229 | 19:30 | 218 | 13:00
Bheramara | 232 | 21:00 | 225 | 00:00 | Rampal | 231 | 08:00 | 219 | 00:00
Bhulta | 231 | 06:00 | 214 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 02:00 | 222 | 12:00 | Rampura | 230 | 06:00 | 213 | 12:00
BIPTC | 234 | 09:00 | 225 | 23:00 | Shikalbaha | 228 | 01:00 | 223 | 12:00
Bogura | 237 | 21:00 | 225 | 02:00 | Shyampur | 222 | 06:00 | 214 | 12:00
Bogura-400 | 236 | 22:00 | 224 | 02:00 | Siddhirganj | 221 | 08:00 | 214 | 12:00
Borhanuddin | 233 | 08:00 | 227 | 00:00 | Sirajgonj | 240 | 21:00 | 235 | 02:00
BSRM | 227 | 08:00 | 221 | 11:00 | Sreepur | 229 | 21:00 | 221 | 12:00
Cumilla(N) | 223 | 06:00 | 215 | 12:00 | Tongi | 229 | 21:00 | 218 | 13:00
Faridpur | 225 | 06:00 | 217 | 00:00
Fenchuganj | 230 | 06:00 | 225 | 00:00
Ghorashal | 235 | 00:00 | 230 | 07:00
Ghorashal-230 | 230 | 21:00 | 217 | 12:00
Gopalganj | 226 | 06:00 | 219 | 00:00
GPH | 228 | 06:00 | 224 | 11:00
Haripur | 221 | 06:00 | 214 | 12:00
Hasnabad | 223 | 04:00 | 214 | 11:00
Hathazari | 227 | 17:00 | 221 | 13:00
Ishurdi | 234 | 06:00 | 226 | 01:00
Jhenaidah | 232 | 09:00 | 217 | 23:00
Kaliakoir | 234 | 21:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 123 | 12:00 | Lalmonirhat | 129 | 18:30 | 122 | 03:00
Agargaon | 137 | 06:00 | 129 | 12:00 | Madanganj | 129 | 20:00 | 124 | 12:00
Agrabad | 129 | 01:00 | 127 | 00:00 | Madaripur | 135 | 10:00 | 129 | 00:00
AKS | 129 | 07:00 | 126 | 10:00 | Madartek | 134 | 22:00 | 123 | 12:00
Aminbazar | 134 | 01:00 | 128 | 12:00 | Madunaghat | 132 | 02:00 | 130 | 11:00
Amnura | 137 | 18:30 | 124 | 13:00 | Magura | 137 | 08:00 | 123 | 23:00
Ashuganj | 141 | 06:00 | 137 | 12:00 | Mahasthangarh | 132 | 21:00 | 122 | 02:00
Bagerhat | 133 | 07:00 | 120 | 23:00 | Maijdee | 118 | 10:00 | 111 | 00:00
Bajitpur | 129 | 04:00 | 125 | 19:00 | Manikganj | 129 | 06:00 | 119 | 12:00
Bakulia | 130 | 01:00 | 128 | 12:00 | Maniknagar | 133 | 06:00 | 126 | 12:00
Banani | 134 | 05:00 | 123 | 12:00 | Matarbari | 121 | 09:00 | 107 | 21:00
Bangabhaban | 132 | 05:00 | 126 | 12:00 | Matuail | 128.5 | 07:00 | 124 | 12:00
Barapukuria | 136 | 18:30 | 127 | 04:00 | Millgate | 134 | 05:00 | 127 | 11:00
Barguna | 134 | 06:00 | 131 | 00:00 | Mirpur | 132 | 01:00 | 126 | 12:00
Barishal | 133 | 06:00 | 127 | 00:00 | Mirzapur | 129 | 09:00 | 125 | 12:00
Barishal-230 | 134 | 07:00 | 128 | 00:00 | Mithapukur | 132 | 18:30 | 123 | 02:00
Baroaulia | 130 | 04:00 | 128 | 12:00 | MI_Cement | 131 | 06:00 | 124 | 12:00
Baroirhat | 124 | 07:00 | 120 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 134 | 05:00 | 123 | 12:00 | Mogbazar | 135 | 05:00 | 125 | 12:00
BashundharaCement | 129 | 20:00 | 124 | 12:00 | Mongla | 133 | 07:00 | 122 | 00:00
Beanibazar | 128 | 07:00 | 122 | 00:00 | Motijheel | 132 | 04:00 | 126 | 12:00
Benapole | 131 | 08:00 | 120 | 00:00 | Muktagacha | 129 | 14:00 | 119 | 22:00
Bhaluka | 132 | 07:00 | 122 | 13:00 | Munshiganj | 129 | 05:00 | 124 | 11:00
Bhandaria | 129 | 09:00 | 119 | 00:00 | Muradnagar | 125 | 06:00 | 120 | 12:00
Bhangura | 132 | 01:00 | 128 | 00:00 | Mymensingh | 129 | 14:00 | 117 | 12:00
Bheramara | 136 | 06:00 | 133 | 00:00 | Naogaon | 129 | 18:30 | 119 | 02:00
Bheramara(GK) | 136 | 06:00 | 133 | 00:00 | Narail | 137 | 09:00 | 123 | 23:00
Bhulta | 121 | 00:00 | 118 | 11:00 | Narinda | 133 | 06:00 | 126 | 12:00
Bog-Sherpur | 133 | 21:00 | 125 | 02:00 | Narshingdi | 139 | 21:00 | 117 | 11:00
Bogura | 135 | 22:00 | 125 | 13:00 | Natore | 131 | 19:30 | 121 | 13:00
Bogura-230 | 135 | 21:00 | 125 | 02:00 | Nawabganj | 138 | 06:00 | 130 | 12:00
Brahmanbaria | 135 | 06:00 | 131 | 00:00 | Netrakona | 125 | 07:00 | 114 | 00:00
Cantonment | 137 | 06:00 | 129 | 12:00 | New | 134 | 04:00 | 125 | 12:00
Chandina | 127 | 06:00 | 123 | 12:00 | Niamatpur | 137 | 22:00 | 132 | 12:00
Chandpur | 133 | 19:30 | 124 | 00:00 | Noapara | 135 | 08:00 | 124 | 23:00
Chandraghona | 133 | 06:00 | 130 | 12:00 | Pabna | 133 | 06:00 | 130 | 00:00
Chapai | 137 | 18:30 | 131 | 00:00 | Palashbari | 129 | 18:30 | 119 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 02:00 | 124 | 12:00 | Panchagarh | 136 | 18:30 | 124 | 12:00
Chauddagram | 125 | 19:00 | 119 | 12:00 | Patiya | 130 | 06:00 | 126 | 15:00
Chhatak | 126 | 06:00 | 120 | 00:00 | Patuakhali | 135 | 17:00 | 132 | 22:00
Chowmuhani | 121 | 19:00 | 113 | 22:00 | Payra | 136 | 06:00 | 134 | 00:00
Chuadanga | 133 | 07:00 | 118 | 23:00 | PHP | 124 | 06:00 | 117 | 18:30
Coxsbazar | 123 | 09:00 | 109 | 19:00 | Postogola | 133 | 06:00 | 127 | 11:00
Cumilla(N) | 128 | 06:00 | 123 | 12:00 | Purbachal | 134 | 06:00 | 122 | 12:00
Cumilla(S) | 132 | 04:00 | 122 | 12:00 | Purbasadipur | 131 | 18:00 | 121 | 12:00
Daganbhuiyan | 121 | 06:00 | 116 | 12:00 | Rahanpur | 138 | 18:30 | 133 | 01:00
Daudkandi | 123 | 18:00 | 117 | 00:00 | Rahanpur-400 | 139 | 22:00 | 133 | 03:00
Dhaka | 134 | 03:00 | 124 | 12:00 | Rahim | 129 | 07:00 | 124 | 12:00
Dhamrai | 133 | 06:00 | 125 | 11:00 | Rajbari | 132 | 06:00 | 125 | 00:00
Dhanmondi | 135 | 06:00 | 123 | 12:00 | Rajendrapur | 137 | 22:00 | 124 | 13:00
Dohazari | 126 | 07:00 | 122 | 15:00 | Rajshahi | 131 | 19:30 | 123 | 00:00
Faridpur | 136 | 17:00 | 128 | 00:00 | Rajshahi-230 | 132 | 21:00 | 123 | 13:00
Fatullah | 132 | 06:00 | 126 | 12:00 | Ramganj | 124 | 19:00 | 115 | 01:00
Fenchuganj | 137 | 06:00 | 132 | 01:00 | Rampur | 131 | 07:00 | 125 | 12:00
Feni | 124 | 19:00 | 116 | 12:00 | Rampura | 134 | 06:00 | 123 | 12:00
Ghatail | 127 | 14:00 | 118 | 22:00 | Rangamati | 132 | 01:00 | 129 | 12:00
Ghorashal | 138 | 21:00 | 131 | 13:00 | Rangpur | 132 | 21:00 | 125 | 00:00
Goalpara | 137 | 08:00 | 127 | 00:00 | Ruppur | 136 | 04:00 | 133 | 13:00
Gollamari | 137 | 06:00 | 128 | 00:00 | Saidpur | 131 | 18:30 | 124 | 08:00
Gopalganj | 135 | 06:00 | 127 | 00:00 | Satkhira | 134 | 09:00 | 121 | 23:00
Gopalganj-400 | 136 | 02:00 | 130 | 00:00 | Satmasjid | 136 | 06:00 | 129 | 13:00
Gulshan | 134 | 22:00 | 123 | 12:00 | Savar | 134 | 20:00 | 126 | 10:00
Halishahar | 132 | 06:00 | 126 | 15:00 | SevenRings | 138 | 22:00 | 130 | 12:00
Haripur | 130 | 06:00 | 125 | 11:00 | ShahCement | 130 | 02:00 | 124 | 12:00
HaripurSBU | 130 | 06:00 | 125 | 11:00 | Shahjadpur | 135 | 04:00 | 132 | 10:00
Hasnabad | 132 | 03:00 | 126 | 11:00 | Shahjibazar | 136 | 06:00 | 130 | 00:00
Hathazari | 132 | 04:00 | 129 | 15:00 | Shahmirpur | 132 | 23:00 | 127 | 12:00
Ishurdi | 137 | 06:00 | 134 | 00:00 | Shariatpur | 134 | 06:00 | 127 | 00:00
Jaldhaka | 128 | 04:00 | 121 | 08:00 | Sherpur | 126 | 14:00 | 114 | 06:00
Jamalpur | 128 | 15:00 | 118 | 07:00 | Shikalbaha | 123 | 02:00 | 117 | 16:00
Jashore | 136 | 09:00 | 124 | 19:00 | Shikalbaha-230 | 132 | 07:00 | 128 | 12:00
Jhenaidah | 138 | 07:00 | 122 | 13:00 | Shitalakhya | 131 | 06:00 | 124 | 12:00
Jhenaidah-230 | 139 | 08:00 | 126 | 23:00 | Sholosohor | 132 | 01:00 | 130 | 11:00
Joydebpur | 138 | 22:00 | 125 | 08:00 | Shyampur | 133 | 06:00 | 126 | 12:00
Joypurhat | 127 | 21:00 | 119 | 00:00 | Shyampur-230 | 132 | 05:00 | 126 | 12:00
Juldah | 130 | 02:00 | 128 | 12:00 | Siddhirganj | 130 | 03:00 | 124 | 12:00
Kabirpur | 134 | 16:00 | 120 | 12:00 | Sirajganj | 130 | 06:00 | 125 | 00:00
Kachua | 132 | 19:00 | 123 | 00:00 | Sonargaon | 128 | 04:00 | 123 | 11:00
Kaliakoir | 135 | 16:00 | 128 | 12:00 | Sreemongol | 133 | 06:00 | 128 | 00:00
Kallyanpur | 134 | 03:00 | 128 | 12:00 | Sreepur | 133 | 07:00 | 127 | 13:00
Kalurghat | 133 | 06:00 | 130 | 12:00 | Srinagar | 137 | 02:00 | 131 | 12:00
Kamrangirchar | 137 | 08:00 | 130 | 12:00 | SSM | 135 | 17:00 | 131 | 12:00
Kaptai | 134 | 9:00 | 132 | 6:00 | Sunamganj | 125 | 10:00 | 117 | 00:00
Kasba | 125 | 06:00 | 119 | 12:00 | Sylhet | 129 | 07:00 | 125 | 00:00
Kazla | 132 | 06:00 | 126 | 13:00 | Sylhet-132 | 129 | 07:00 | 125 | 00:00
Keranigonj | 138 | 06:00 | 131 | 12:00 | Tangail | 126 | 09:00 | 121 | 22:00
Khagrachori | 132 | 07:00 | 128 | 12:00 | Taraganj | 131 | 18:00 | 124 | 07:00
Khulna | 136 | 09:00 | 126 | 00:00 | Thakurgaon | 134 | 18:30 | 122 | 04:00
Khulna(S) | 138 | 09:00 | 128 | 00:00 | TK | 133 | 06:00 | 130 | 01:00
Khulshi | 129 | 05:00 | 125 | 12:00 | Tongi | 136 | 05:00 | 128 | 11:00
Kishoreganj | 129 | 07:00 | 122 | 13:00 | Ullahpara | 132 | 21:00 | 128 | 00:00
Kodda | 137 | 22:00 | 126 | 12:00 | Ullon | 134 | 06:00 | 123 | 12:00
KSRM | 131 | 07:00 | 127 | 12:00 | Uttara | 133 | 02:00 | 127 | 12:00
Kulaura | 134 | 07:00 | 130 | 00:00 | UttaraNew | 133 | 01:00 | 126 | 12:00
Kurigram | 130 | 18:30 | 120 | 08:00 | Zigatola | 137 | 02:00 | 130 | 12:00
Kushtia | 132 | 09:00 | 127 | 13:00
Laksam | 131 | 21:00 | 122 | 01:00
Lakshmipur | 119 | 06:00 | 112 | 00:00
Lalbag | 138 | 06:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division