## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-09-2025 | during | 15-09-2025 | during | 15-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 346 | 339 | 400.75 | 400.75 | 377 | 377 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 298 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 99 | 99 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 7 | 0 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 45.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 95 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 37 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 102 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 87.5 | 87.5 | 51 | 70 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 115 | 148 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 3 | 0 | 3 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 32 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 400 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 115 | 160 | 160 | 125 | 125 | -
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2075 | 2554.2 | 5542.54 | 5546.54 | 3881.2 | 3904.2
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 10 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 126 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 220 | 195 | 195 | 195 | 195 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 15 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 62 | 56 | 64 | 48 | 56 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 18 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.03 | 0 | 3.65 | 0 | 3.65 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1129 | 1202 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 4 | 12 | 5 | 12 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 211 | 262 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1744.03 | 2127 | 3108.51 | 3109.86 | 2752.01 | 2753.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 190 | 184 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 354 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 300 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 155 | 150 | 270 | 270 | 270 | 270 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 5 | 46.7 | 46.7 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 45 | 45 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 75 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 136 | 200 | 200 | 80 | 180 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 28 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 42 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1452 | 1675 | 2699.56 | 2649.56 | 2173.36 | 2232.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-09-2025 | during | 15-09-2025 | during | 15-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 105 | 105 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.78 | 0 | 30.37 | 0 | 30.37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 18 | 18 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 28 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 118.78 | 132 | 352.27 | 320.5 | 258.27 | 226.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 68 | 70 | 70 | 70 | 70 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 5 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 342 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1180 | 1179 | 1276 | 1276 | 1181 | 1181
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 894 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 5 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 279 | 279 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 963 | 1121 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1915 | 2057 | 3627.2 | 3552.2 | 2735.2 | 2660.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 296 | 296 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 135 | 135 | FGMO
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 277 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.09 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2048.09 | 2169 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 5.66 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 13 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 130 | 214 | 214 | 198 | 198 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 195 | 195 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 388 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 18 | 18 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.36 | 0 | 5.55 | 0 | 5.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1439.49 | 1457.02 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 4.83 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 33 | 0 | 85 | 0 | 85 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2261.34 | 2324.02 | 3169.42 | 3017.87 | 3051.04 | 2899.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 44 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 172 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 51 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.2 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 91 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 2 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 13 | 0 | 129.69 | 0 | 129.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 230.2 | 361 | 609.29 | 448 | 589.29 | 428
System Total |  |  |  |  | 28823.2 | 27829.875 | 13024.44 | 14578.22 | 22546.79 | 22081.53 | 18703.37 | 18366.11
Forecast Scenario (15-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14000 |  | 0 |  | 14000
|  |  |  | 1:00 | 13700 |  | 0 |  | 13700
|  |  |  | 2:00 | 13300 |  | 0 |  | 13300
|  |  |  | 3:00 | 12800 |  | 0 |  | 12800
|  |  |  | 4:00 | 12500 |  | 0 |  | 12500
|  |  |  | 5:00 | 12400 |  | 0 |  | 12400
|  |  |  | 6:00 | 12000 |  | 0 |  | 12000
|  |  |  | 7:00 | 11900 |  | 0 |  | 11900
|  |  |  | 8:00 | 11700 |  | 0 |  | 11700
|  |  |  | 9:00 | 12000 |  | 0 |  | 12000
|  |  |  | 10:00 | 12000 |  | 0 |  | 12000
|  |  |  | 11:00 | 12100 |  | 0 |  | 12100
|  |  |  | 12:00 | 12700 |  | 0 |  | 12700
|  |  |  | 13:00 | 12900 |  | 0 |  | 12900
|  |  |  | 14:00 | 12700 |  | 0 |  | 12700
|  |  |  | 15:00 | 13000 |  | 0 |  | 13000
|  |  |  | 16:00 | 12800 |  | 0 |  | 12800
|  |  |  | 17:00 | 12700 |  | 0 |  | 12700
|  |  |  | 18:00 | 13300 |  | 0 |  | 13300
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 15000 |  | 0 |  | 15000
|  |  |  | 19:30 | 14800 |  | 0 |  | 14800
|  |  |  | 20:00 | 14700 |  | 0 |  | 14700
|  |  |  | 21:00 | 14700 |  | 0 |  | 14700
|  |  |  | 22:00 | 14300 |  | 0 |  | 14300
|  |  |  | 23:00 | 14200 |  | 0 |  | 14200
Probable Maximum Temperature: |  |  | 30.70°C
Probable Maximum Demand at Day Peak: |  |  | 12700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 313.40 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:03 hrs on 15-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-09-2025 | [28 empty] | Date: | 14-09-2025 | [28 empty] | Date: | 14-09-2025 | [28 empty] | Date: | 14-09-2025 | [28 empty] | Date: | 14-09-2025 | [14 empty] | Date: | 14-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 50 | 17 | 133 | 109 | 294 | 55 | 37 | 162 | 0 | 400 | 150 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 108 | 24.5 | 21 | 0 | 420 | 16 | 0 | 0 | 0 | 0 | 49 | 61 | 0 | 0 | 0 | 0 | 220 | 15 | 37 | 265 | 0 | 0 | 33 | 17 | 67 | 223 | 0 | 0 | 0 | 1212 | 0 | 51 | 135 | 0 | 100 | 320 | 300 | 5 | 214 | 5 | 74 | 90 | 180 | 0 | 19 | 98 | 50 | 52.2 | 0 | 29 | 315 | 0 | 390 | 0 | 38 | 160 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 77 | 9 | 11 | 0 | 0 | 18 | 8099.7 | 823 | 64 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 723.81 | 0 | 35 | 0 | 113 | 113 | 0 | 94 | 30 | 52 | 0 | 0 | 20 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 167 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 350 | 1232 | 17 | 7001.01 | 15100.71 | 108.72
01:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 47.8 | 0 | 132 | 109 | 294 | 55 | 37 | 162 | 0 | 350 | 150 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 370 | 15 | 0 | 0 | 0 | 5 | 49 | 45 | 0 | 0 | 0 | 0 | 220 | 15 | 37 | 266 | 0 | 0 | 33 | 17 | 64 | 223 | 0 | 0 | 0 | 1218 | 0 | 51 | 135 | 0 | 100 | 320 | 300 | 5 | 215 | 5 | 70 | 90 | 131 | 0 | 19 | 98 | 50 | 52.2 | 0 | 29 | 310 | 0 | 383 | 0 | 38 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 77 | 9 | 11 | 0 | 0 | 18 | 7805 | 894 | 51 | 0 | 29 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 717.24 | 0 | 37 | 0 | 113 | 113 | 0 | 94 | 30 | 52 | 0 | 0 | 14 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 380 | 0 | 0 | 168 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 115 | 220 | 0 | 300 | 1222 | 17 | 6942.44 | 14747.44 | 108.72
02:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 46.8 | 0 | 132 | 108 | 195 | 0 | 37 | 162 | 0 | 350 | 151 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 320 | 13 | 0 | 0 | 0 | 0 | 49 | 45 | 0 | 0 | 0 | 0 | 220 | 14 | 37 | 267 | 0 | 0 | 33 | 17 | 63 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 0 | 105 | 320 | 300 | 5 | 216 | 5 | 72 | 90 | 104 | 0 | 19 | 98 | 48 | 52.2 | 0 | 29 | 305 | 0 | 362 | 0 | 38 | 155 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 77 | 9 | 11 | 0 | 0 | 18 | 7530 | 894 | 44 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 829.51 | 0 | 43 | 0 | 0 | 0 | 0 | 94 | 22 | 0 | 0 | 0 | 14 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 380 | 0 | 0 | 166 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 307 | 115 | 220 | 0 | 302 | 1222 | 17 | 6703.71 | 14233.71 | 108.72
03:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 46.4 | 0 | 132 | 109 | 30 | 0 | 17 | 35 | 0 | 400 | 151 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 52 | 23 | 21 | 0 | 320 | 13 | 0 | 0 | 0 | 0 | 49 | 45 | 0 | 0 | 0 | 0 | 219 | 14 | 37 | 268 | 0 | 0 | 33 | 17 | 63 | 223 | 0 | 0 | 0 | 1200 | 0 | 51 | 135 | 0 | 70 | 320 | 300 | 5 | 179 | 5 | 72 | 90 | 104 | 0 | 19 | 98 | 46 | 52.2 | 0 | 23 | 310 | 0 | 349 | 0 | 38 | 152 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 78 | 9 | 11 | 0 | 0 | 18 | 7141.6 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1221 | 0 | 992.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 169 | 43 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 307 | 115 | 220 | 0 | 302 | 1222 | 17 | 6575.91 | 13717.51 | 108.72
04:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 46 | 0 | 76 | 109 | 15 | 0 | 17 | 35 | 0 | 400 | 151 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 52 | 23.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 49 | 0 | 0 | 0 | 0 | 0 | 219 | 15 | 37 | 267 | 0 | 0 | 33 | 17 | 15 | 222 | 0 | 0 | 0 | 1150 | 0 | 51 | 50 | 0 | 2 | 320 | 300 | 5 | 196 | 5 | 71 | 90 | 103 | 0 | 19 | 98 | 44 | 52.2 | 0 | 29 | 325 | 0 | 386 | 0 | 38 | 156 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 11 | 0 | 0 | 18 | 6898.7 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1171 | 0 | 1140.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 170 | 43 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 230 | 115 | 220 | 0 | 302 | 1120 | 17 | 6473.75 | 13372.45 | 108.72
05:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 46 | 0 | 53 | 109 | 15 | 0 | 17 | 35 | 0 | 400 | 151 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 35 | 23.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 220 | 14 | 38 | 267 | 0 | 0 | 33 | 17 | 15 | 223 | 0 | 0 | 0 | 1090 | 0 | 51 | 10 | 0 | 100 | 320 | 300 | 5 | 193 | 5 | 72 | 90 | 104 | 0 | 19 | 98 | 44 | 25 | 0 | 29 | 310 | 0 | 371 | 0 | 38 | 143 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 8 | 77 | 9 | 11 | 0 | 0 | 18 | 6743.5 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 1197.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 171 | 42 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 228 | 115 | 220 | 0 | 302 | 1100 | 17 | 6480.39 | 13223.89 | 108.72
06:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 44 | 0 | 46 | 75 | 0 | 0 | 17 | 35 | 0 | 370 | 153 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 40 | 269 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 1078 | 0 | 51 | 10 | 0 | 180 | 280 | 300 | 5 | 185 | 5 | 34 | 90 | 103 | 0 | 19 | 98 | 38 | 0 | 0 | 0 | 305 | 0 | 352 | 0 | 38 | 137 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 17 | 77 | 9 | 11 | 0 | 0 | 18 | 6426 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 0 | 1277.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 370 | 0 | 0 | 171 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 246 | 115 | 220 | 0 | 302 | 1085 | 0 | 6312.47 | 12738.47 | 108.72
07:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 34 | 109 | 0 | 0 | 17 | 0 | 0 | 370 | 153 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 17 | 25 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 34 | 267 | 0 | 0 | 7 | 0 | 0 | 221 | 0 | 0 | 0 | 1040 | 2 | 51 | 0 | 0 | 260 | 280 | 300 | 5 | 180 | 5 | 0 | 90 | 104 | 6 | 19 | 98 | 38 | 0 | 5 | 0 | 305 | 0 | 352 | 0 | 38 | 136 | 8 | 0 | 84 | 30 | 0 | 0 | 165 | 17 | 77 | 9 | 11 | 0 | 0 | 14 | 6250 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1100 | 0 | 1390.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 3 | 0 | 0 | 0.41 | 130 | 0 | 130 | 0 | 130 | 0 | 330 | 0 | 0.06 | 170 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0.1 | 14 | 0.02 | 0 | 265 | 115 | 180 | 0 | 302 | 1080 | 0 | 6364.23 | 12614.23 | 108.72
08:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 34 | 45 | 0 | 0 | 18 | 0 | 0 | 340 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 17 | 25 | 21 | 0 | 375 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.23 | 173 | 0 | 3 | 270 | 0 | 0 | 6 | 0 | 0 | 186 | 0 | 0 | 0 | 1042 | 4 | 51 | 0 | 0 | 275 | 280 | 300 | 5 | 218 | 5 | 0 | 90 | 104 | 8 | 19 | 70 | 36 | 0 | 17 | 0 | 305 | 0 | 385 | 0 | 38 | 142 | 8 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 11 | 0 | 1.45 | 18 | 6129.68 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 988 | 0 | 1449.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 8 | 0 | 0 | 0.31 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0.04 | 170 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0.1 | 21 | 0.08 | 0 | 226 | 115 | 180 | 0 | 303 | 1048 | 0 | 6239.82 | 12369.5 | 108.73
09:00 | 0 | 52 | 22 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 37 | 30 | 0 | 0 | 35 | 15 | 0 | 340 | 150 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 17 | 23.2 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 173 | 0 | 2 | 268 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1002 | 8 | 51 | 0 | 0 | 275 | 355 | 300 | 5 | 194 | 5 | 0 | 90 | 103 | 9 | 19 | 70 | 34 | 0 | 22 | 0 | 320 | 0 | 384 | 0 | 38 | 146 | 8 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 9 | 0 | 4.69 | 18 | 6327.53 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 953 | 0 | 1451.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.57 | 8 | 0 | 0 | 0.4 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 121 | 43 | 35 | 0 | 0 | 0 | 0 | 0 | 0.3 | 2 | 0.24 | 0 | 216 | 115 | 220 | 0 | 302 | 1104 | 0 | 6283.41 | 12610.94 | 108.73
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 46 | 15 | 0 | 0 | 35 | 14 | 0 | 340 | 152 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 17 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 126 | 0 | 2 | 268 | 0 | 0 | 8 | 0 | 0 | 224 | 0 | 0 | 0 | 980 | 10 | 51 | 0 | 0 | 245 | 354 | 300 | 5 | 190 | 5 | 0 | 90 | 103 | 9 | 19 | 45 | 34 | 0 | 23 | 0 | 310 | 0 | 368 | 0 | 38 | 140 | 8 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 5 | 0 | 3.49 | 18 | 6152.27 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 940 | 0 | 1436.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 8 | 0 | 0 | 1.21 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0.11 | 147 | 44 | 35 | 0 | 0 | 0 | 0 | 0 | 0.9 | 2 | 0.3 | 0 | 166 | 115 | 220 | 0 | 302 | 1210 | 0 | 6343.55 | 12495.82 | 108.73
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 14 | 50 | 15 | 15 | 0 | 35 | 15 | 0 | 340 | 153 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 17 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.74 | 126 | 0 | 2 | 266 | 0 | 0 | 27 | 0 | 0 | 223 | 0 | 0 | 0 | 935 | 13 | 51 | 0 | 0 | 205 | 355 | 300 | 5 | 194 | 5 | 0 | 90 | 102 | 0 | 13 | 48 | 34 | 0 | 31 | 0 | 305 | 0 | 383 | 0 | 38 | 137 | 6 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 5 | 0 | 5.15 | 18 | 6110.89 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 928 | 0 | 1445.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 17 | 0 | 0 | 2.7 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0.14 | 169 | 44 | 0 | 1 | 0 | 0 | 0 | 0 | 1.9 | 6 | 0.3 | 0 | 167 | 115 | 220 | 0 | 295 | 1244 | 0 | 6373.36 | 12484.25 | 108.74
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 50 | 16 | 45 | 0 | 35 | 115 | 0 | 340 | 151 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 17 | 23 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.03 | 126 | 0 | 6 | 211 | 0 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 0 | 1129 | 15 | 51 | 0 | 0 | 155 | 354 | 300 | 5 | 190 | 5 | 0 | 90 | 104 | 0 | 13 | 105 | 38 | 0 | 42 | 0 | 315 | 0 | 388 | 0 | 38 | 157 | 5 | 0 | 81 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 0 | 0 | 14.78 | 18 | 6569.81 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 963 | 0 | 1439.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.66 | 33 | 0 | 0 | 4.83 | 130 | 0 | 130 | 0 | 130 | 0 | 388 | 0 | 0.36 | 169 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 2.2 | 13 | 0.09 | 0 | 173 | 115 | 220 | 0 | 296 | 1244 | 0 | 6454.63 | 13024.44 | 108.74
13:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 15 | 17 | 50 | 45 | 145 | 0 | 38 | 137 | 0 | 340 | 153 | 0 | 0 | 17 | 300 | 0 | 0 | 6 | 17 | 21.2 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 172 | 0 | 13 | 213 | 0 | 0 | 40 | 0 | 27 | 220 | 0 | 0 | 0 | 1117 | 7 | 51 | 24 | 0 | 139 | 320 | 300 | 5 | 175 | 5 | 0 | 90 | 103 | 0 | 13 | 114 | 36 | 0 | 53 | 0 | 310 | 0 | 350 | 0 | 38 | 148 | 5 | 0 | 84 | 30 | 0 | 0 | 166 | 0 | 77 | 9 | 0 | 1 | 20.61 | 18 | 6668.46 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 1026 | 0 | 1448.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.77 | 45 | 0 | 0 | 7.29 | 130 | 0 | 130 | 0 | 130 | 0 | 320 | 0 | 0.65 | 169 | 48 | 20 | 2 | 0 | 0 | 0 | 0 | 4.2 | 42 | 0.08 | 0 | 162 | 115 | 220 | 0 | 296 | 1244 | 0 | 6552.9 | 13221.36 | 108.75
14:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 15 | 17 | 50 | 45 | 75 | 0 | 39 | 108 | 0 | 300 | 160 | 0 | 0 | 17 | 270 | 0 | 0 | 4 | 17 | 21 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.41 | 172 | 0 | 6 | 218 | 0 | 0 | 0 | 0 | 17 | 218 | 0 | 0 | 0 | 1050 | 15 | 51 | 24 | 0 | 155 | 300 | 280 | 5 | 215 | 5 | 0 | 90 | 104 | 0 | 19 | 85 | 42 | 0 | 43 | 0 | 305 | 0 | 336 | 0 | 38 | 142 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 0 | 1 | 23.52 | 18 | 6355.93 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 1048 | 0 | 1443.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.65 | 34 | 0 | 0 | 12.24 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0.99 | 172 | 48 | 35 | 4 | 0 | 0 | 0 | 0 | 4.8 | 46 | 0.17 | 0 | 171 | 115 | 180 | 0 | 297 | 1244 | 0 | 6516.51 | 12872.44 | 108.78
15:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 15.7 | 17 | 50 | 45 | 30 | 0 | 37 | 106 | 0 | 350 | 175 | 0 | 0 | 17 | 326 | 0 | 0 | 3 | 17 | 21 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 220 | 0 | 2 | 270 | 0 | 0 | 41 | 0 | 17 | 219 | 0 | 0 | 0 | 1045 | 14 | 51 | 24 | 0 | 175 | 280 | 270 | 5 | 215 | 5 | 0 | 90 | 103 | 0 | 19 | 81 | 42 | 0 | 34 | 0 | 315 | 0 | 386 | 0 | 38 | 152 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 0 | 1 | 17.48 | 18 | 6601.34 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 1030 | 0 | 1351.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 17 | 0 | 0 | 12.74 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 1.1 | 171 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 2.9 | 55 | 0.18 | 0 | 219 | 115 | 220 | 0 | 296 | 1244 | 0 | 6433.72 | 13035.06 | 108.78
16:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 14.6 | 17 | 51 | 45 | 30 | 0 | 37 | 97 | 0 | 350 | 270 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 17 | 21 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 220 | 0 | 5 | 270 | 0 | 0 | 50 | 0 | 14 | 219 | 0 | 0 | 0 | 932 | 1 | 43 | 24 | 0 | 220 | 280 | 270 | 5 | 190 | 5 | 0 | 90 | 104 | 0 | 18 | 74 | 38 | 0 | 13 | 0 | 310 | 0 | 355 | 0 | 38 | 153 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 0 | 0 | 9.75 | 18 | 6497.44 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 912 | 0 | 1313.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.31 | 28 | 0 | 0 | 14.2 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 1.38 | 171 | 47 | 0 | 4 | 0 | 0 | 0 | 0 | 3.3 | 46 | 0.14 | 0 | 215 | 115 | 220 | 0 | 297 | 1244 | 0 | 6275.22 | 12772.66 | 108.79
17:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 15 | 17 | 51 | 80 | 30 | 0 | 37 | 99 | 0 | 300 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 17 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0.17 | 218 | 0 | 16 | 267 | 0 | 0 | 50 | 0 | 15 | 220 | 0 | 0 | 0 | 940 | 0 | 51 | 24 | 0 | 205 | 280 | 270 | 5 | 192 | 5 | 0 | 90 | 107 | 0 | 16 | 75 | 34 | 0 | 5 | 0 | 305 | 0 | 356 | 0 | 48 | 154 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 0 | 0 | 1.35 | 18 | 6494.52 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 819 | 0 | 1219.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 9 | 0 | 0 | 5.61 | 130 | 0 | 130 | 0 | 130 | 0 | 330 | 0 | 0.63 | 170 | 47 | 0 | 3 | 0 | 0 | 0 | 0 | 0.4 | 18 | 0.06 | 0 | 218 | 115 | 220 | 0 | 297 | 1244 | 0 | 6049.96 | 12544.48 | 108.79
18:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 35 | 18 | 62 | 111 | 30 | 45 | 37 | 125 | 0 | 300 | 297 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 218 | 1 | 19 | 262 | 0 | 0 | 50 | 2 | 14 | 182 | 0 | 0 | 0 | 1009 | 0 | 51 | 24 | 0 | 205 | 280 | 270 | 5 | 190 | 5 | 29 | 90 | 155 | 0 | 19 | 76 | 40 | 3 | 0 | 13 | 305 | 0 | 300 | 0 | 58 | 140 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 6 | 77 | 9 | 0 | 0 | 0 | 18 | 6723 | 894 | 0 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 0 | 0 | 0.8 | 926 | 0 | 1376.93 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0.04 | 0 | 0 | 0 | 0.08 | 130 | 0 | 130 | 0 | 130 | 0 | 330 | 0 | 0.03 | 171 | 47 | 10 | 0 | 20 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 215 | 115 | 180 | 0 | 296 | 1244 | 17 | 6318.98 | 13041.98 | 108.79
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 45.2 | 32 | 102 | 95 | 95 | 55 | 37 | 148 | 0 | 300 | 298 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 115 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 50 | 62 | 0 | 0 | 0 | 0 | 219 | 15 | 18 | 262 | 0 | 0 | 50 | 10 | 15 | 220 | 0 | 0 | 0 | 1202 | 0 | 51 | 75 | 0 | 150 | 356 | 330 | 5 | 184 | 5 | 51 | 90 | 136 | 0 | 19 | 114 | 44 | 28 | 0 | 37 | 310 | 0 | 342 | 0 | 68 | 155 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 28 | 77 | 9 | 0 | 0 | 0 | 18 | 7667.2 | 893 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 0 | 1457.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 172 | 47 | 91 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 296 | 1244 | 17 | 6911.02 | 14578.22 | 108.79
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 49 | 35 | 105 | 111 | 95 | 55 | 37 | 152 | 0 | 300 | 300 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 1 | 50 | 69 | 0 | 0 | 0 | 0 | 219 | 14 | 25 | 262 | 0 | 0 | 50 | 17 | 8 | 220 | 0 | 0 | 0 | 1179 | 0 | 51 | 20 | 0 | 135 | 280 | 280 | 5 | 216 | 5 | 68 | 90 | 100 | 0 | 19 | 114 | 42 | 52.2 | 0 | 37 | 315 | 0 | 346 | 0 | 68 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 0 | 0 | 0 | 18 | 7434.2 | 894 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 1461.81 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 173 | 47 | 97 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 315 | 1244 | 17 | 6948.81 | 14383.01 | 108.79
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 45.6 | 35 | 105 | 111 | 30 | 55 | 37 | 146 | 0 | 300 | 300 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 108 | 26 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 61 | 0 | 0 | 0 | 0 | 220 | 0 | 29 | 260 | 0 | 0 | 50 | 17 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 20 | 0 | 185 | 280 | 280 | 5 | 217 | 5 | 63 | 90 | 100 | 0 | 19 | 114 | 44 | 8 | 0 | 37 | 300 | 0 | 350 | 0 | 68 | 153 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 0 | 0 | 0 | 18 | 7251.6 | 894 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 1459.8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 172 | 48 | 96 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 315 | 1244 | 17 | 6959.8 | 14211.4 | 108.79
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 47 | 24 | 70 | 111 | 30 | 15 | 37 | 150 | 0 | 300 | 292 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 90 | 26 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 50 | 61 | 0 | 0 | 0 | 0 | 220 | 0 | 31 | 260 | 0 | 0 | 50 | 17 | 0 | 220 | 0 | 0 | 0 | 1158 | 0 | 51 | 20 | 0 | 195 | 280 | 280 | 5 | 217 | 5 | 67 | 90 | 100 | 0 | 19 | 114 | 44 | 8 | 0 | 37 | 315 | 0 | 344 | 0 | 68 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 0 | 0 | 0 | 18 | 7185 | 893 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 1458.19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 132 | 0 | 141 | 0 | 414 | 0 | 0 | 172 | 48 | 96 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 315 | 1244 | 17 | 7047.19 | 14232.19 | 108.79
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 45.3 | 17 | 51 | 93 | 0 | 0 | 37 | 143 | 0 | 300 | 294 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 90 | 25 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 49 | 61 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 260 | 0 | 0 | 50 | 8 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 15 | 0 | 195 | 280 | 280 | 5 | 216 | 5 | 67 | 90 | 100 | 0 | 19 | 114 | 46 | 0 | 0 | 37 | 305 | 0 | 366 | 0 | 68 | 152 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 0 | 0 | 0 | 18 | 7057.3 | 893 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 1458.12 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 132 | 0 | 142 | 0 | 414 | 0 | 0 | 168 | 48 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 315 | 1244 | 17 | 6923.12 | 13980.42 | 108.79
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 47.5 | 17 | 51 | 93 | 0 | 0 | 37 | 149 | 0 | 300 | 293 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 90 | 23 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 2 | 49 | 61 | 0 | 0 | 0 | 0 | 220 | 0 | 34 | 260 | 0 | 0 | 39 | 8 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 0 | 205 | 280 | 280 | 5 | 216 | 5 | 67 | 90 | 100 | 0 | 19 | 114 | 48 | 0 | 0 | 37 | 315 | 0 | 366 | 0 | 68 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 0 | 0 | 0 | 18 | 7069.5 | 894 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 1456.08 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 132 | 0 | 144 | 0 | 414 | 0 | 0 | 171 | 48 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 312 | 1170 | 17 | 6852.08 | 13921.58 | 108.78
Total KWH | 0 | 1189440 | 544320 | 0 | 0 | 0 | 0 | 0 | 8308800 | 0 | 0 | 661320 | 290520 | 1613952 | 1887360 | 1367455 | 258111 | 786904 | 2183040 | 0 | 8228000 | 4827491 | 0 | 0 | 315461 | 7400985 | 0 | 0 | 30946 | 1230000 | 546600 | 488160 | 0 | 9165454.55 | 47673 | 0 | 0 | 0 | 66240 | 670432 | 433840 | 0 | 0 | 0 | 13199 | 4744405 | 129635 | 511680 | 6269090.91 | 0 | 0 | 854400 | 173732.4 | 404799 | 5144167 | 0 | 0 | 0 | 26219997 | 97335 | 1251620 | 884872 | 0 | 4236200 | 7773100 | 7106000 | 132960 | 4906000 | 143568 | 822720 | 2166170 | 2628480 | 42000 | 391290 | 2219580 | 988800 | 352373 | 291055 | 382880 | 7532000 | 0 | 9108000 | 0 | 1004160 | 3584863.63 | 170064 | 0 | 2006400 | 720192 | 0 | 202000 | 3429550 | 223560 | 1833600 | 218400 | 82560 | 3700 | 102380 | 444960 | 164491002.49 | 21626909 | 151488 | 0 | 36000 | 69248 | 912000 | 0 | 0 | 0 | 0 | 0 | 294480 | 25309100 | 0 | 31347013 | 0 | 78053 | 0 | 178848 | 177600 | 0 | 487056 | 141808 | 66134 | 65668 | 207230 | 29802 | 0 | 61504 | 3347545 | 0 | 3392664 | 0 | 3424536 | 0 | 8960800 | 0 | 5160 | 4087000 | 1033745 | 1134793 | 24915 | 988339 | 0 | 0 | 0 | 20759.88 | 254160 | 1767 | 594432 | 5750000 | 2737000 | 5401560 | 0 | 7294545.45 | 29154909.09 | 218400 | 159066971.42 | 323557973.91

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13024.44 | MW | 12:00 Hr. | Energy Generated |  |  | 323.558 |  | MKWHr.
| Day Peak Demand |  |  | 13024.44 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.651 |  | MKWHr.
| Evening Peak Generation |  |  | 14578.22 | MW | 19:00 Hr. | Energy Demand |  |  | 325.209 |  | MKWHr.
| Evening Peak Demand |  |  | 14720.34 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 12369.5 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 945.88 |  | MMCFD
| Maximum Generation of the Day |  |  | 15100.71 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.0899 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.9655 | 0 | 12.3279 | 0 | 0 | 0.030946 | 0 | 0 | 51.3243 | Gas | 127.9836 | Gas | 454178511.4168
| Chattogram Zone |  |  | 5.6558 | 32.4891 | 2.7145 | 0 | 4.7444 | 0.11053 | 0 | 0.06624 | 45.7806 | Coal | 105.1184 | Coal | 627765999.6345
| Cumilla Zone |  |  | 28.1069 | 0 | 7.3329 | 0 | 0 | 0.29106 | 0.9888 | 0 | 36.7197 | HFO | 29.2963 | HFO | 542056869.142
| Mymensingh Zone |  |  | 0.08256 | 0 | 2.7205 | 0 | 0 | 0.10608 | 0 | 0 | 2.9092 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7572 | Hydro | 4.7444 | Hydro | 474440.5
| Khulna Zone |  |  | 0.15149 | 25.3091 | 0.10525 | 0 | 0 | 0.29448 | 22.5389 | 0 | 48.3992 | Solar | 1.4743 | Solar | 22126402.3548
| Barishal Zone |  |  | 8.1386 | 42.1995 | 0.81283 | 0 | 0 | 0.001767 | 0 | 0 | 51.1526 | Import | 54.8747 | Import | 322863568.28
| Rajshahi Zone |  |  | 19.1255 | 0 | 1.1593 | 0 | 0 | 0.33956 | 31.347 | 0 | 51.9714 | Wind | 0.06624 | Wind | 976377.6
| Rangpur Zone |  |  | 0 | 5.1207 | 2.1231 | 0 | 0 | 0.29983 | 0 | 0 | 7.5437
| Total |  |  | 127.9836 | 105.1184 | 29.2963 | 0 | 4.7444 | 1.4743 | 54.8747 | 0.06624 | 323.558
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 454178511.4168 |  | Hydro | 474440.5
|  |  |  | Coal | 627765999.6345 |  | Solar | 22126402.3548
|  |  |  | HFO | 542056869.142 |  | Import | 322863568.28
|  |  |  | HSD | 0 |  | Wind | 976377.6
[5 empty] | Total: | 197,04,42,168 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6269 | Peak Hr Flow | 893.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50928373.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.347 | Peak Hr Flow | 1457.02 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2180 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9888 | Peak Hr Flow | 44.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2796 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.9627 | Peak Hr Flow | 2394.02 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5168
|  |  |  | Chattogram |  | 0 |  | 1450
|  |  |  | Cumilla |  | 0 |  | 1346
|  |  |  | Mymensingh |  | 136 |  | 1137
|  |  |  | Sylhet |  | 0 |  | 520
|  |  |  | Khulna |  | 0 |  | 1736
|  |  |  | Barishal |  | 0 |  | 433
|  |  |  | Rajshahi |  | 0 |  | 1388
|  |  |  | Rangpur |  | 0 |  | 934
|  |  |  | Total |  | 136 |  | 14112
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:28 | Jhenaidah 132/33kV S/S Transformer T-3 HT is restored.
|  | 08:29 | Jhenaidah 132/33kV S/S Transformer T-3 LT is restored.
| 09:02 | 10:55 | Chowmuhani 132/33kV S/S TR3 Scheduled S/D Due to 33 KV Dotter Hat Feeder Y Phase Red Hot | [7 empty] | 35.0MW load
|  |  | Maintenance at 33 KV Bus Point | [7 empty] | interrup.
| 09:17 | 12:08 | Bheramara 230/132kV S/S GTG (NW) Forced S/D Due to 1-20-89B DS maintenace
| 11:10 | 13:22 | Chuadanga 132/33kV S/S Jhenaidah-Chuadanga Ckt-2 Scheduled S/D Due to Maintenance work
| 11:11 |  | Jhenaidah 132/33kV S/S Jhenaidah-Chuadanga, 132kV Circuit-2(L8) Forced S/D | [7 empty] | 43.0MW load
interrup.
|  | 11:24 | Candpur (Desh)- Chandpur 132kV Ckt-1 is restored.
|  | 11:32 | Candpur (Desh)- Chandpur 132kV Ckt-2 is restored.
| 11:33 | 17:35 | Rampur 230/132/33 S/S 132kV BUS-02 Project Work S/D Due to Interlock wiring modification
purpose
| 11:48 | 12:26 | Barapukuria-Rangpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing REL
511 relays Due to Zone 01 trip
| 11:48 | 12:29 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing
Siemens siprotec relays Due to Zone 01 trip
| 12:00 |  | Day peak Generation is 13021 MW
| 12:10 |  | Chandpur 132/33kV S/S 115MW CPGL Power Plant Incomer (L5) Scheduled S/D Due to
Maintenance work
| 13:22 | 14:09 | Chuadanga-Jhenaidah 132 kV Ckt-1 Tripped from Chuadanga 132/33kV end showing Differential
relay relays.
| 13:41 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 13:41 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- None
| 14:34 | 18:07 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to Red Hot
| 14:34 | 18:07 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to Red Hot
| 19:00 |  | Evening Peak Generation 14578 MW
| 19:32 |  | Bashundhara-Tongi 132 kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Main
prot.trip C-Phase relays.
| 19:34 |  | Tongi-Basundhara 132 kV cable ckt-2 tripped showing distance (blue-phase) relay due to
flashing in cable at Tongi end.
| 21:00 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
| 03:15 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to low voltage.
| 07:00 |  | Minimum Generation 11915 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 339 | 8308800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8228000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 4827491 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 258111 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7400985 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45.2 | 661320 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 95 | 1887360 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 37 | 786904 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 315461 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 546600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 488160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 544320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 1367455 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 102 | 1613952 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1189440 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 148 | 2183040 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 30946 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 32 | 290520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9165454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 115 | 1230000 | -
Dhaka Area Total |  |  |  |  | 6657.724 | 2554.2 | 51324319.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 10 | 173732.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 97335 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 854400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 4744405 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5144167 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 15 | 404799 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 433840 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 670432 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 511680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | MaintenanceShutdown at Shikalbaha 132kV SubStation
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 129635 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 47673 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1202 | 26219997 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 66240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 262 | 6269090.91 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2127 | 45780625.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 184 | 4906000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 7773100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7106000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 150 | 4236200 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 5 | 143568 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 132960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1251620 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 75 | 884872 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 382880 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2166170 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2628480 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 44 | 988800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 28 | 352373 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 391290 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2219580 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 42000 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 822720 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 291055 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1675 | 36719668
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 82560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 218400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1833600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 102380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 444960 | To be dispatched 18 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 28 | 223560 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 132 | 2909160
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1004160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3584863.63 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720192 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2006400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 3429550 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 202000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 170064 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7532000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 342 | 9108000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1179 | 27757229.63
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 21626909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 36000 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 69248 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 151488 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 294480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1121 | 25309100 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2057 | 48399225
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 296 | 7294545.45 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 594432 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2737000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29154909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5401560 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 218400 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5750000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1767 | -
Barishal Area Total |  |  |  |  | 2236 | 2169 | 51152613.54
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 65668 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 78053 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 141808 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3347545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3392664 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3424536 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8960800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 29802 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 66134 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 487056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 177600 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 178848 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1457.02 | 31347013 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 61504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 207230 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2324.02 | 51971421
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1033745 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 172 | 4087000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 51 | 988339 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20759.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 91 | 1134793 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 24915 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 254160 | -
Rangpur Area Total |  |  |  |  | 950 | 361 | 7543711.88
Eastern Grid Total |  |  |  |  | 17385.715 | 7667.2 | 164491002.49
Western Grid Total |  |  |  |  | 10444.16 | 6911.02 | 159066971.42
National Grid Total |  |  |  |  | 27829.875 | 14578.22 | 323557973.91
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-09-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9485.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4490.7 | MW
i) Dhaka area |  |  | 5167.79 |  | MW | i) Khulna area |  |  |  | 1735.7 | MW
ii) Chattogram area |  |  | 1450.5 |  | MW | ii) Barishal area |  |  |  | 433 | MW
iii) Cumilla area |  |  | 1346.18 |  | MW | iii) Rajshahi area |  |  |  | 1388 | MW
iv) Mymensingh area |  |  | 1001 |  | MW | iv) Rangpur area |  |  |  | 934 | MW
v) Sylhet area |  |  | 520 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13976.17 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 18:30 | 133 | PHP | 9 | 07:00
2 | AKSML | 139 | 02:00 | 68 | Ishurdi | 72 | 00:00 | 134 | Pabna | 119 | 01:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 81 | 00:00 | 135 | Palashbari | 122 | 01:00
4 | Agargaon | 129 | 10:00 | 70 | Jamalpur | 96 | 18:30 | 136 | Panchagarh | 56 | 19:00
5 | Agrabad | 96 | 18:30 | 71 | Jashore | 142 | 00:00 | 137 | Patiya | 0 | 00:00
6 | Amnura | 32 | 00:00 | 72 | Jhenaidah | 132 | 00:00 | 138 | Patuakhali | 62 | 00:00
7 | Ashuganj | 83 | 00:00 | 73 | Joydebpur | 152 | 09:00 | 139 | Payra | 36 | 00:00
8 | BSRM | 165 | 17:00 | 74 | Joypurhat | 62 | 00:00 | 140 | Postogola | 60 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 16.5 | 14:00 | 141 | Purbachal | 21 | 00:00
10 | Bajitpur | 91 | 00:00 | 76 | KSRM | 28 | 19:30 | 142 | Purbasadipur | 128 | 00:00
11 | Bakulia | 90 | 18:00 | 77 | Kabirpur | 261 | 09:00 | 143 | Rahanpur | 42 | 00:00
12 | Banani | 47 | 13:00 | 78 | Kachua | 94 | 00:00 | 144 | Rahim | 50 | 00:00
13 | Bangabhaban | 24 | 11:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 84 | 00:00
14 | Barapukuria | 65 | 00:00 | 80 | Kalurghat | 40 | 11:00 | 146 | Rajendrapur | 129 | 20:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 83 | 13:00 | 147 | Rajshahi | 104 | 00:00
16 | Barishal | 115 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 100 | 13:00
17 | Barishal-230 | 100 | 00:00 | 83 | Kasba | 33 | 01:00 | 149 | Ramganj | 110 | 18:30
18 | Baroaulia | 64 | 22:00 | 84 | Kazla | 103 | 00:00 | 150 | Rampur | 41 | 00:00
19 | Baroirhat | 61 | 19:00 | 85 | Keranigonj | 89 | 00:00 | 151 | Rangamati | 16 | 18:30
20 | Bashundhara | 191 | 13:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rangpur | 137 | 19:30
21 | BashundharaCement | 8 | 11:00 | 87 | Khulna | 65 | 13:00 | 153 | Ruppur | 7.8 | 09:00
22 | Beanibazar | 72 | 00:00 | 88 | Khulshi | 169 | 23:00 | 154 | SSM | 14 | 23:00
23 | Benapole | 63 | 00:00 | 89 | Kishoreganj | 128 | 00:00 | 155 | Saidpur | 104 | 19:00
24 | Bhaluka | 146 | 00:00 | 90 | Kodda | 295 | 09:00 | 156 | Satkhira | 127 | 00:00
25 | Bhandaria | 55 | 23:00 | 91 | Kulaura | 46 | 00:00 | 157 | Satmasjid | 101 | 00:00
26 | Bhangura | 38 | 00:00 | 92 | Kurigram | 60 | 19:00 | 158 | Savar | 236 | 12:00
27 | Bheramara(GK) | 64 | 00:00 | 93 | Kushtia | 162 | 01:00 | 159 | SevenRings | 16.95 | 21:00
28 | Bhulta | 219 | 12:00 | 94 | Laksam | 36 | 00:00 | 160 | ShahCement | 30 | 03:00
29 | Bog-Sherpur | 72 | 01:00 | 95 | Lakshmipur | 32 | 21:00 | 161 | Shahjadpur | 84 | 19:00
30 | Bogura | 154 | 01:00 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 116 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 55 | 00:00 | 163 | Shahmirpur | 62 | 02:00
32 | Brahmanbaria | 123 | 01:00 | 98 | MI_Cement | 17.8 | 16:00 | 164 | Shariatpur | 92 | 00:00
33 | Cantonment | 140 | 12:00 | 99 | Madanganj | 39 | 00:00 | 165 | Sherpur | 104 | 18:00
34 | Chandina | 40.18 | 00:00 | 100 | Madaripur | 115 | 00:00 | 166 | Shikalbaha | 21 | 00:00
35 | Chandpur | 88 | 00:00 | 101 | Madartek | 97 | 00:00 | 167 | Shitalakhya | 74.5 | 13:00
36 | Chandraghona | 33 | 19:30 | 102 | Madunaghat | 70 | 18:30 | 168 | Sholosohor | 44 | 19:00
37 | Chapai | 63 | 21:00 | 103 | Magura | 64 | 00:00 | 169 | Shyampur | 174 | 11:00
38 | Charsaidpur | 21 | 12:00 | 104 | Mahasthangarh | 80 | 00:00 | 170 | Siddhirganj | 119 | 11:00
39 | Chauddagram | 70 | 00:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sirajganj | 104 | 19:30
40 | Chhatak | 40 | 01:00 | 106 | Manikganj | 121 | 00:00 | 172 | Sonargaon | 124 | 04:00
41 | Chowmuhani | 181 | 19:00 | 107 | Maniknagar | 62 | 13:00 | 173 | Sreemongol | 69 | 00:00
42 | Chuadanga | 123 | 00:00 | 108 | Matarbari | 51 | 18:30 | 174 | Sreepur | 87 | 00:00
43 | Coxsbazar | 138 | 18:30 | 109 | Matuail | 72 | 00:00 | 175 | Srinagar | 46.57 | 00:00
44 | Cumilla(N) | 111 | 00:00 | 110 | Millgate | 111 | 10:00 | 176 | Sunamganj | 59 | 00:00
45 | Cumilla(S) | 144 | 14:00 | 111 | Mirpur | 119 | 12:00 | 177 | Sylhet | 47 | 00:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 106 | 00:00
47 | Daudkandi | 149 | 00:00 | 113 | Mirzapur | 36 | 00:00 | 179 | TK | 35 | 00:00
48 | Dhaka | 88 | 11:00 | 114 | Mithapukur | 72 | 00:00 | 180 | Tangail | 162 | 06:00
49 | Dhamrai | 124 | 15:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 22 | 00:00
50 | Dhanmondi | 133.4 | 13:00 | 116 | Mogbazar | 96.1 | 13:00 | 182 | Thakurgaon | 102 | 01:00
51 | Dohazari | 106 | 18:30 | 117 | Mongla | 48 | 07:00 | 183 | Tongi | 124 | 12:00
52 | Faridpur | 170 | 00:00 | 118 | Motijheel | 41 | 13:00 | 184 | Ullahpara | 37 | 18:00
53 | Fatullah | 106 | 12:00 | 119 | Muktagacha | 28 | 13:00 | 185 | Ullon | 56 | 00:00
54 | Fenchuganj | 38 | 00:00 | 120 | Munshiganj | 117 | 01:00 | 186 | Uttara | 76 | 18:30
55 | Feni | 114 | 19:30 | 121 | Muradnagar | 40 | 01:00 | 187 | UttaraNew | 58 | 00:00
56 | GPH | 82 | 17:00 | 122 | Mymensingh | 196 | 00:00 | 188 | Zigatola | 70 | 00:00
57 | Ghatail | 60 | 00:00 | 123 | Naogaon | 134 | 00:00
58 | Ghorashal | 14 | 00:00 | 124 | Narail | 60 | 00:00
59 | Ghorashal-230 | 85 | 19:00 | 125 | Narinda | 74 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 171 | 00:00
61 | Gollamari | 108 | 00:00 | 127 | Natore | 135 | 01:00
62 | Gopalganj | 102.7 | 19:00 | 128 | Nawabganj | 56.4 | 00:00
63 | Gulshan | 114 | 10:00 | 129 | Netrakona | 136 | 19:00
64 | Halishahar | 69 | 09:00 | 130 | New | 64 | 10:00
65 | HaripurSBU | 163 | 11:00 | 131 | Niamatpur | 76 | 00:00
66 | Hasnabad | 77 | 00:00 | 132 | Noapara | 46 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15100.71 | 221 |  | 15331.71
1:00 | 14747.44 | 147 |  | 14901.06
2:00 | 14233.71 | 141 |  | 14381.06
3:00 | 13717.51 | 138 |  | 13861.72
4:00 | 13372.45 | 123 |  | 13500.99
5:00 | 13223.89 | 83 |  | 13310.63
6:00 | 12738.47 | 40 |  | 12780.27
7:00 | 12614.23 | 0 |  | 12614.23
8:00 | 12369.5 | 0 |  | 12369.5
9:00 | 12610.94 | 0 |  | 12610.94
10:00 | 12495.82 | 0 |  | 12495.82
11:00 | 12484.25 | 0 |  | 12484.25
12:00 | 13024.44 | 0 |  | 13024.44
13:00 | 13221.36 | 0 |  | 13221.36
14:00 | 12872.44 | 0 |  | 12872.44
15:00 | 13035.06 | 0 |  | 13035.06
16:00 | 12772.66 | 0 |  | 12772.66
17:00 | 12544.48 | 0 |  | 12544.48
18:00 | 13041.98 | 57 |  | 13101.55
19:00 | 14578.22 | 136 |  | 14720.34
19:30 | 14383.01 | 132 |  | 14520.95
20:00 | 14211.4 | 134 |  | 14351.43
21:00 | 14232.19 | 141 |  | 14379.19
22:00 | 13980.42 | 138 |  | 14124.42
23:00 | 13921.58 | 152 |  | 14080.58
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 14-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3579 | 1914.5 | 823 | 38 | 50 | 723.81 | 220 | 4811.2 | 0 | 697 | 2244.2 | 0 | 0 | 0 | 221 | DAILY ENERGY CURVE
00:30 | 3522 | 1858.75 | 858.5 | 38 | 50 | 720.525 | 220 | 4784.7 | 0 | 667.5 | 2201.6 | 0 | 0 | 2.5 | 184 | 14-09-2025
01:00 | 3465 | 1803 | 894 | 38 | 50 | 717.24 | 220 | 4758.2 | 0 | 638 | 2159 | 0 | 0 | 5 | 147
01:30 | 3444.5 | 1776 | 894 | 38 | 49 | 773.375 | 220 | 4761.7 | 0 | 605 | 1926.5 | 0 | 0 | 2.5 | 144 | Energy Generated | 323.558 |  | MKWHr
02:00 | 3424 | 1749 | 894 | 38 | 48 | 829.51 | 220 | 4765.2 | 0 | 572 | 1694 | 0 | 0 | 0 | 141 | Energy not Served | 1.651 |  | MKWHr
02:30 | 3405.5 | 1775 | 894 | 38 | 47 | 911.21 | 219.5 | 4748.6 | 0 | 455 | 1481.8 | 0 | 0 | 0 | 139.5 | Total Energy Requirement | 325.209 |  | MKWHr
03:00 | 3387 | 1801 | 894 | 38 | 46 | 992.91 | 219 | 4732 | 0 | 338 | 1269.6 | 0 | 0 | 0 | 138
03:30 | 3395.5 | 1850.75 | 893.5 | 38 | 45 | 1066.83 | 219 | 4592.5 | 0 | 310 | 1121.9 | 0 | 0 | 12 | 130.5
04:00 | 3404 | 1900.5 | 893 | 38 | 44 | 1140.75 | 219 | 4453 | 0 | 282 | 974.2 | 0 | 0 | 24 | 123
04:30 | 3430.5 | 1887 | 893.5 | 38 | 44 | 1169.07 | 219.5 | 4402 | 0 | 273.5 | 929.1 | 0 | 0 | 12 | 103
05:00 | 3457 | 1873.5 | 894 | 38 | 44 | 1197.39 | 220 | 4351 | 0 | 265 | 884 | 0 | 0 | 0 | 83
05:30 | 3415.5 | 1843.25 | 894 | 38 | 41 | 1237.42 | 220 | 4335.5 | 0.01 | 224.5 | 730 | 0 | 0 | 2 | 61.5
06:00 | 3374 | 1813 | 894 | 38 | 38 | 1277.45 | 220 | 4320 | 0.02 | 184 | 576 | 0 | 0 | 4 | 40
06:30 | 3379 | 1802 | 893.5 | 38 | 38 | 1334.185 | 197 | 4293 | 20.665 | 181 | 497 | 0 | 0 | 3 | 20
07:00 | 3384 | 1791 | 893 | 38 | 38 | 1390.92 | 174 | 4266 | 41.31 | 178 | 418 | 0 | 0 | 2 | 0
07:30 | 3392.5 | 1749.5 | 893.5 | 38 | 37 | 1420.35 | 173.5 | 4177.5 | 63.015 | 146 | 398.5 | 0 | 0 | 2.5 | 0
08:00 | 3401 | 1708 | 894 | 38 | 36 | 1449.78 | 173 | 4089 | 84.72 | 114 | 379 | 0 | 0 | 3 | 0
08:30 | 3501.5 | 1747.1 | 893.5 | 38 | 35 | 1450.84 | 173 | 4049 | 86.78 | 117.5 | 396.5 | 0 | 0 | 1.5 | 0
09:00 | 3602 | 1786.2 | 893 | 38 | 34 | 1451.9 | 173 | 4009 | 88.84 | 121 | 414 | 0 | 0 | 0 | 0
09:30 | 3567.5 | 1779.6 | 893.5 | 38 | 34 | 1444.445 | 149.5 | 4033 | 92.335 | 115 | 406.5 | 0 | 0 | 0 | 0
10:00 | 3533 | 1773 | 894 | 38 | 34 | 1436.99 | 126 | 4057 | 95.83 | 109 | 399 | 0 | 0 | 0 | 0
10:30 | 3518.5 | 1765.5 | 894 | 38 | 34 | 1441.195 | 126 | 4052.5 | 111.34 | 100 | 404.5 | 0 | 0 | 4.5 | 0
11:00 | 3504 | 1758 | 894 | 38 | 34 | 1445.4 | 126 | 4048 | 126.85 | 91 | 410 | 0 | 0 | 9 | 0
11:30 | 3507.5 | 1823.5 | 894 | 38 | 36 | 1442.445 | 126 | 4138.5 | 142.9 | 91.5 | 508.5 | 0 | 0 | 5.5 | 0
12:00 | 3511 | 1889 | 894 | 38 | 38 | 1439.49 | 126 | 4229 | 158.95 | 92 | 607 | 0 | 0 | 2 | 0
12:30 | 3396.5 | 1862.1 | 894 | 38 | 37 | 1444.2 | 149 | 4252 | 205.1 | 115 | 729 | 0 | 0 | 1 | 0
13:00 | 3282 | 1835.2 | 894 | 38 | 36 | 1448.91 | 172 | 4275 | 251.25 | 138 | 851 | 0 | 0 | 0 | 0
13:30 | 3269.5 | 1777.6 | 893.5 | 38 | 39 | 1446.285 | 172 | 4261.5 | 241.015 | 138 | 770.5 | 0 | 0 | 0 | 0
14:00 | 3257 | 1720 | 893 | 38 | 42 | 1443.66 | 172 | 4248 | 230.78 | 138 | 690 | 0 | 0 | 0 | 0
14:30 | 3316.5 | 1770.5 | 893 | 38 | 42 | 1397.71 | 196 | 4286 | 209.69 | 138 | 666.35 | 0 | 0 | 0 | 0
15:00 | 3376 | 1821 | 893 | 38 | 42 | 1351.76 | 220 | 4324 | 188.6 | 138 | 642.7 | 0 | 0 | 0 | 0
15:30 | 3375 | 1863.5 | 893 | 38 | 40 | 1332.825 | 220 | 4206 | 168.385 | 138 | 629.15 | 0 | 0 | 0 | 0
16:00 | 3374 | 1906 | 893 | 38 | 38 | 1313.89 | 220 | 4088 | 148.17 | 138 | 615.6 | 0 | 0 | 0 | 0
16:30 | 3389 | 1876.5 | 893 | 38 | 36 | 1266.54 | 219 | 4045 | 103.73 | 172 | 619.8 | 0 | 0 | 0 | 0
17:00 | 3404 | 1847 | 893 | 38 | 34 | 1219.19 | 218 | 4002 | 59.29 | 206 | 624 | 0 | 0 | 0 | 0
17:30 | 3321 | 1809.5 | 893.5 | 38 | 37 | 1298.06 | 218 | 4086 | 30.17 | 310 | 752 | 0 | 0 | 0 | 28.5
18:00 | 3238 | 1772 | 894 | 38 | 40 | 1376.93 | 218 | 4170 | 1.05 | 414 | 880 | 0 | 0 | 0 | 57
18:30 | 3395 | 1842 | 893.5 | 38 | 42 | 1416.975 | 218.5 | 4395.5 | 0.525 | 468 | 1098.1 | 0 | 0 | 2 | 96.5
19:00 | 3552 | 1912 | 893 | 38 | 44 | 1457.02 | 219 | 4621 | 0 | 522 | 1316.2 | 0 | 0 | 4 | 136
19:30 | 3332 | 1878 | 894 | 38 | 42 | 1461.81 | 219 | 4610 | 0 | 571 | 1336.2 | 0 | 0 | 1 | 132
20:00 | 3359 | 1858 | 894 | 38 | 44 | 1459.8 | 220 | 4600 | 0 | 554 | 1184.6 | 0 | 0 | 0 | 134
20:30 | 3411 | 1864.5 | 893.5 | 38 | 44 | 1458.995 | 220 | 4597 | 0 | 545 | 1148.8 | 0 | 0 | 1 | 137.5
21:00 | 3463 | 1871 | 893 | 38 | 44 | 1458.19 | 220 | 4594 | 0 | 536 | 1113 | 0 | 0 | 2 | 141
21:30 | 3479 | 1864.5 | 893 | 38 | 45 | 1458.155 | 220 | 4594.5 | 0 | 507.5 | 1001.65 | 0 | 0 | 5 | 139.5
22:00 | 3495 | 1858 | 893 | 38 | 46 | 1458.12 | 220 | 4595 | 0 | 479 | 890.3 | 0 | 0 | 8 | 138
22:30 | 3506.5 | 1865 | 893.5 | 38 | 47 | 1457.1 | 220 | 4558.5 | 0 | 479 | 881.4 | 0 | 0 | 5 | 145
23:00 | 3518 | 1872 | 894 | 38 | 48 | 1456.08 | 220 | 4522 | 0 | 479 | 872.5 | 0 | 0 | 2 | 152
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8099.7 | 7001.01 | 15100.71 | DAILY GENERATION CURVE
00:30 | 7952.35 | 6971.725 | 14924.075
01:00 | 7805 | 6942.44 | 14747.44 | 14-09-2025
01:30 | 7667.5 | 6823.075 | 14490.575
02:00 | 7530 | 6703.71 | 14233.71
02:30 | 7335.8 | 6639.81 | 13975.61
03:00 | 7141.6 | 6575.91 | 13717.51
03:30 | 7020.15 | 6524.83 | 13544.98
04:00 | 6898.7 | 6473.75 | 13372.45
04:30 | 6821.1 | 6477.07 | 13298.17
05:00 | 6743.5 | 6480.39 | 13223.89
05:30 | 6584.75 | 6396.43 | 12981.18
06:00 | 6426 | 6312.47 | 12738.47
06:30 | 6338 | 6338.35 | 12676.35
07:00 | 6250 | 6364.23 | 12614.23
07:30 | 6189.84 | 6302.025 | 12491.865
08:00 | 6129.68 | 6239.82 | 12369.5
08:30 | 6228.605 | 6261.615 | 12490.22
09:00 | 6327.53 | 6283.41 | 12610.94
09:30 | 6239.9 | 6313.48 | 12553.38
10:00 | 6152.27 | 6343.55 | 12495.82
10:30 | 6131.58 | 6358.455 | 12490.035
11:00 | 6110.89 | 6373.36 | 12484.25
11:30 | 6340.35 | 6413.995 | 12754.345
12:00 | 6569.81 | 6454.63 | 13024.44
12:30 | 6619.135 | 6503.765 | 13122.9
13:00 | 6668.46 | 6552.9 | 13221.36
13:30 | 6512.195 | 6534.705 | 13046.9
14:00 | 6355.93 | 6516.51 | 12872.44
14:30 | 6478.635 | 6475.115 | 12953.75
15:00 | 6601.34 | 6433.72 | 13035.06
15:30 | 6549.39 | 6354.47 | 12903.86
16:00 | 6497.44 | 6275.22 | 12772.66
16:30 | 6495.98 | 6162.59 | 12658.57
17:00 | 6494.52 | 6049.96 | 12544.48
17:30 | 6608.76 | 6184.47 | 12793.23
18:00 | 6723 | 6318.98 | 13041.98
18:30 | 7195.1 | 6615 | 13810.1
19:00 | 7667.2 | 6911.02 | 14578.22
19:30 | 7434.2 | 6948.81 | 14383.01
20:00 | 7251.6 | 6959.8 | 14211.4
20:30 | 7218.3 | 7003.495 | 14221.795 |  | Executive Engineer
21:00 | 7185 | 7047.19 | 14232.19 |  | Network Operation Division
21:30 | 7121.15 | 6985.155 | 14106.305
22:00 | 7057.3 | 6923.12 | 13980.42
22:30 | 7063.4 | 6887.6 | 13951
23:00 | 7069.5 | 6852.08 | 13921.58

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 01:00 | 367 | 12:00 | Payra | 414 | 08:00 | 403 | 14:00
Ashuganj | 403 | 7:00 | 393 | 11:00 | Rahanpur | 401 | 02:00 | 388 | 18:30
Bhulta | 402 | 01:00 | 382 | 12:00 | Rampal | 402 | 08:00 | 390 | 19:00
Bibiana | 385 | 07:00 | 379 | 12:00
BIPTC | 403 | 17:00 | 394 | 01:00
Bogura | 392 | 01:00 | 376 | 19:00
Gopalganj | 394 | 07:00 | 384 | 12:00
Kaliakoir | 371 | 01:00 | 360 | 12:00
Madunaghat | 391 | 18:00 | 386 | 16:00
Meghnaghat | 381 | 06:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 01:00 | 216 | 12:00 | Keranigonj | 222 | 01:00 | 214 | 12:00
AKSML | 228 | 00:00 | 224 | 12:00 | Khulna(S) | 230 | 18:00 | 217 | 19:00
Aminbazar | 226 | 05:00 | 217 | 12:00 | Madunaghat | 232 | 17:00 | 227 | 11:00
Ashuganj | 235 | 07:00 | 226 | 11:00 | Madunaghat-400 | 231 | 06:00 | 228 | 12:00
Ashuganj-400 | 235 | 07:00 | 226 | 11:00 | Maniknagar | 219 | 18:00 | 212 | 12:00
Baghabari | 234 | 17:00 | 225 | 18:30 | Meghnaghat | 226 | 18:00 | 219 | 12:00
Barapukuria | 222 | 04:00 | 215 | 18:30 | Meghnaghat-400 | 223 | 18:00 | 216 | 12:00
Barapukuria-230 | 222 | 04:00 | 215 | 18:30 | Mirsorai | 227 | 00:00 | 222 | 12:00
Barishal | 227 | 04:00 | 220 | 22:00 | Rajshahi | 230 | 17:00 | 217 | 18:30
Bheramara | 234 | 17:00 | 222 | 03:00 | Rampal | 229 | 06:00 | 218 | 19:00
Bhulta | 229 | 02:00 | 212 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 01:00 | 223 | 12:00 | Rampura | 229 | 02:00 | 213 | 12:00
BIPTC | 236 | 17:00 | 222 | 18:30 | Shikalbaha | 229 | 05:00 | 224 | 15:00
Bogura | 234 | 00:00 | 224 | 18:30 | Shyampur | 222 | 18:00 | 213 | 12:00
Bogura-400 | 233 | 01:00 | 225 | 19:00 | Siddhirganj | 220 | 16:00 | 215 | 12:00
Borhanuddin | 232 | 04:00 | 227 | 18:30 | Sirajgonj | 239 | 17:00 | 234 | 12:00
BSRM | 228 | 07:00 | 222 | 12:00 | Sreepur | 228 | 01:00 | 223 | 12:00
Cumilla(N) | 223 | 18:00 | 217 | 11:00 | Tongi | 229 | 01:00 | 215 | 12:00
Faridpur | 224 | 09:00 | 216 | 19:00
Fenchuganj | 230 | 17:00 | 227 | 00:00
Ghorashal | 232 | 00:00 | 230 | 08:00
Ghorashal-230 | 230 | 01:00 | 215 | 12:00
Gopalganj | 225 | 08:00 | 218 | 22:00
GPH | 229 | 03:00 | 224 | 12:00
Haripur | 220 | 18:00 | 213 | 12:00
Hasnabad | 222 | 05:00 | 214 | 12:00
Hathazari | 229 | 07:00 | 224 | 12:00
Ishurdi | 235 | 17:00 | 225 | 03:00
Jhenaidah | 231 | 17:00 | 218 | 18:30
Kaliakoir | 234 | 01:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 00:00 | 125 | 12:00 | Lalmonirhat | 128 | 10:00 | 122 | 18:30
Agargaon | 136 | 06:00 | 129 | 12:00 | Madanganj | 130 | 18:00 | 123 | 12:00
Agrabad | 131 | 05:00 | 126 | 14:00 | Madaripur | 134 | 07:00 | 129 | 18:30
AKS | 129 | 04:00 | 126 | 15:00 | Madartek | 134 | 03:00 | 124 | 10:00
Aminbazar | 134 | 01:00 | 128 | 12:00 | Madunaghat | 133 | 06:00 | 129 | 17:00
Amnura | 136 | 01:00 | 125 | 12:00 | Magura | 136 | 16:00 | 124 | 00:00
Ashuganj | 141 | 18:00 | 138 | 12:00 | Mahasthangarh | 130 | 10:00 | 122 | 18:30
Bagerhat | 130 | 10:00 | 117 | 22:00 | Maijdee | 120 | 18:00 | 107 | 02:00
Bajitpur | 132 | 10:00 | 126 | 22:00 | Manikganj | 128 | 13:00 | 121 | 12:00
Bakulia | 132 | 18:00 | 128 | 12:00 | Maniknagar | 132 | 04:00 | 127 | 12:00
Banani | 134 | 02:00 | 123 | 12:00 | Matarbari | 125 | 14:00 | 109 | 00:00
Bangabhaban | 132 | 06:00 | 127 | 12:00 | Matuail | 129 | 18:30 | 124 | 12:00
Barapukuria | 135 | 12:00 | 125 | 18:30 | Millgate | 133 | 01:00 | 124 | 12:00
Barguna | 134 | 07:00 | 131 | 15:00 | Mirpur | 133 | 01:00 | 126 | 11:00
Barishal | 134 | 00:00 | 127 | 18:30 | Mirzapur | 131 | 10:00 | 123 | 12:00
Barishal-230 | 134 | 03:00 | 127 | 22:00 | Mithapukur | 130 | 10:00 | 121 | 18:30
Baroaulia | 131 | 04:00 | 129 | 00:00 | MI_Cement | 130 | 18:00 | 124 | 12:00
Baroirhat | 126 | 18:00 | 119 | 02:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 134 | 01:00 | 123 | 12:00 | Mogbazar | 135 | 01:00 | 124 | 12:00
BashundharaCement | 130 | 18:00 | 125 | 13:00 | Mongla | 130 | 08:00 | 119 | 19:00
Beanibazar | 128 | 06:00 | 124 | 00:00 | Motijheel | 132 | 06:00 | 127 | 12:00
Benapole | 129 | 09:00 | 118 | 22:00 | Muktagacha | 132 | 10:00 | 112 | 20:00
Bhaluka | 130 | 07:00 | 124 | 01:00 | Munshiganj | 130 | 18:00 | 124 | 11:00
Bhandaria | 133 | 04:00 | 117 | 22:00 | Muradnagar | 125 | 07:00 | 121 | 12:00
Bhangura | 133 | 18:00 | 127 | 18:30 | Mymensingh | 132 | 10:00 | 109 | 20:00
Bheramara | 136 | 17:00 | 128 | 03:00 | Naogaon | 128 | 17:00 | 119 | 18:30
Bheramara(GK) | 136 | 17:00 | 128 | 18:30 | Narail | 137 | 17:00 | 124 | 00:00
Bhulta | 123 | 18:00 | 119 | 09:00 | Narinda | 132 | 04:00 | 127 | 12:00
Bog-Sherpur | 131 | 01:00 | 124 | 18:30 | Narshingdi | 138 | 00:00 | 118 | 00:00
Bogura | 133 | 01:00 | 126 | 18:30 | Natore | 129 | 00:00 | 120 | 18:30
Bogura-230 | 133 | 01:00 | 125 | 18:30 | Nawabganj | 136 | 05:00 | 130 | 12:00
Brahmanbaria | 136 | 10:00 | 132 | 00:00 | Netrakona | 128 | 06:00 | 116 | 00:00
Cantonment | 135 | 01:00 | 129 | 12:00 | New | 133 | 00:00 | 125 | 12:00
Chandina | 128 | 07:00 | 124 | 12:00 | Niamatpur | 136 | 17:00 | 131 | 18:30
Chandpur | 133 | 01:00 | 126 | 12:00 | Noapara | 133 | 09:00 | 123 | 18:30
Chandraghona | 133 | 00:00 | 131 | 12:00 | Pabna | 134 | 17:00 | 127 | 03:00
Chapai | 135 | 00:00 | 131 | 18:30 | Palashbari | 128 | 10:00 | 118 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:00 | 124 | 12:00 | Panchagarh | 135 | 21:00 | 121 | 18:30
Chauddagram | 125 | 18:00 | 120 | 07:00 | Patiya | 131 | 06:00 | 126 | 12:00
Chhatak | 127 | 10:00 | 121 | 00:00 | Patuakhali | 134 | 05:00 | 131 | 15:00
Chowmuhani | 120 | 10:00 | 112 | 01:00 | Payra | 136 | 08:00 | 132 | 15:00
Chuadanga | 135 | 17:00 | 119 | 00:00 | PHP | 125 | 18:00 | 119 | 02:00
Coxsbazar | 120 | 11:00 | 110 | 18:30 | Postogola | 132 | 18:00 | 126 | 12:00
Cumilla(N) | 128 | 06:00 | 124 | 15:00 | Purbachal | 133 | 01:00 | 122 | 12:00
Cumilla(S) | 132 | 06:00 | 123 | 15:00 | Purbasadipur | 132 | 21:00 | 119 | 18:30
Daganbhuiyan | 121 | 07:00 | 113 | 02:00 | Rahanpur | 137 | 16:00 | 133 | 18:30
Daudkandi | 123 | 05:00 | 118 | 11:00 | Rahanpur-400 | 138 | 02:00 | 133 | 18:30
Dhaka | 134 | 01:00 | 122 | 12:00 | Rahim | 129 | 19:30 | 124 | 12:00
Dhamrai | 132 | 02:00 | 125 | 12:00 | Rajbari | 132 | 08:00 | 126 | 18:30
Dhanmondi | 134 | 02:00 | 122 | 12:00 | Rajendrapur | 139 | 01:00 | 125 | 18:30
Dohazari | 126 | 04:00 | 122 | 12:00 | Rajshahi | 132 | 02:00 | 123 | 12:00
Faridpur | 133 | 05:00 | 127 | 21:00 | Rajshahi-230 | 131 | 17:00 | 123 | 18:30
Fatullah | 132 | 18:00 | 126 | 12:00 | Ramganj | 123 | 17:00 | 112 | 01:00
Fenchuganj | 135 | 09:00 | 133 | 00:00 | Rampur | 131 | 06:00 | 126 | 14:00
Feni | 124 | 18:00 | 118 | 01:00 | Rampura | 134 | 02:00 | 122 | 12:00
Ghatail | 130 | 10:00 | 116 | 20:00 | Rangamati | 133 | 06:00 | 130 | 14:00
Ghorashal | 138 | 00:00 | 134 | 08:00 | Rangpur | 131 | 06:00 | 123 | 12:00
Goalpara | 135 | 08:00 | 125 | 18:30 | Ruppur | 136 | 16:00 | 129 | 18:30
Gollamari | 135 | 06:00 | 127 | 18:30 | Saidpur | 130 | 09:00 | 121 | 18:30
Gopalganj | 134 | 09:00 | 126 | 22:00 | Satkhira | 133 | 10:00 | 120 | 18:30
Gopalganj-400 | 135 | 05:00 | 130 | 19:00 | Satmasjid | 136 | 06:00 | 129 | 12:00
Gulshan | 133 | 05:00 | 123 | 12:00 | Savar | 134 | 01:00 | 126 | 11:00
Halishahar | 132 | 03:00 | 127 | 12:00 | SevenRings | 139 | 01:00 | 130 | 12:00
Haripur | 129 | 18:00 | 124 | 12:00 | ShahCement | 130 | 18:00 | 124 | 12:00
HaripurSBU | 129 | 18:30 | 124 | 11:00 | Shahjadpur | 137 | 04:00 | 130 | 22:00
Hasnabad | 132 | 18:00 | 127 | 11:00 | Shahjibazar | 136 | 09:00 | 131 | 23:00
Hathazari | 133 | 04:00 | 130 | 12:00 | Shahmirpur | 131 | 05:00 | 18 | 14:00
Ishurdi | 138 | 17:00 | 131 | 03:00 | Shariatpur | 133 | 08:00 | 126 | 19:00
Jaldhaka | 129 | 21:00 | 118 | 18:30 | Sherpur | 129 | 11:00 | 110 | 18:00
Jamalpur | 130 | 10:00 | 114 | 18:00 | Shikalbaha | 121 | 06:00 | 117 | 12:00
Jashore | 136 | 17:00 | 124 | 00:00 | Shikalbaha-230 | 132 | 01:00 | 129 | 14:00
Jhenaidah | 136 | 16:00 | 119 | 18:30 | Shitalakhya | 130 | 18:00 | 124 | 12:00
Jhenaidah-230 | 138 | 17:00 | 127 | 00:00 | Sholosohor | 133 | 08:00 | 130 | 11:00
Joydebpur | 139 | 20:00 | 125 | 12:00 | Shyampur | 132 | 21:00 | 126 | 12:00
Joypurhat | 126 | 07:00 | 118 | 18:30 | Shyampur-230 | 132 | 18:00 | 126 | 12:00
Juldah | 130 | 00:00 | 128 | 14:00 | Siddhirganj | 130 | 18:00 | 124 | 12:00
Kabirpur | 134 | 01:00 | 121 | 12:00 | Sirajganj | 130 | 02:00 | 124 | 18:30
Kachua | 132 | 04:00 | 127 | 15:00 | Sonargaon | 125 | 01:00 | 122 | 11:00
Kaliakoir | 135 | 01:00 | 128 | 12:00 | Sreemongol | 134 | 08:00 | 130 | 00:00
Kallyanpur | 133 | 18:00 | 128 | 11:00 | Sreepur | 133 | 06:00 | 130 | 12:00
Kalurghat | 133 | 06:00 | 130 | 12:00 | Srinagar | 139 | 18:00 | 130 | 12:00
Kamrangirchar | 136 | 03:00 | 130 | 12:00 | SSM | 134 | 03:00 | 14 | 05:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 13:00 | 119 | 00:00
Kasba | 124 | 05:00 | 120 | 12:00 | Sylhet | 129 | 18:00 | 126 | 00:00
Kazla | 131 | 05:00 | 127 | 12:00 | Sylhet-132 | 128 | 10:00 | 126 | 00:00
Keranigonj | 137 | 06:00 | 130 | 12:00 | Tangail | 130 | 10:00 | 119 | 20:00
Khagrachori | 132 | 03:00 | 129 | 12:00 | Taraganj | 131 | 10:00 | 121 | 18:30
Khulna | 134 | 09:00 | 124 | 18:30 | Thakurgaon | 134 | 21:00 | 120 | 12:00
Khulna(S) | 136 | 09:00 | 126 | 19:00 | TK | 133 | 02:00 | 131 | 16:00
Khulshi | 131 | 04:00 | 126 | 12:00 | Tongi | 134 | 01:00 | 127 | 12:00
Kishoreganj | 131 | 09:00 | 122 | 00:00 | Ullahpara | 132 | 16:00 | 126 | 18:00
Kodda | 138 | 01:00 | 123 | 08:00 | Ullon | 134 | 02:00 | 122 | 12:00
KSRM | 132 | 18:00 | 128 | 14:00 | Uttara | 133 | 02:00 | 126 | 12:00
Kulaura | 134 | 07:00 | 132 | 00:00 | UttaraNew | 132 | 01:00 | 125 | 11:00
Kurigram | 131 | 10:00 | 117 | 18:30 | Zigatola | 137 | 05:00 | 130 | 12:00
Kushtia | 132 | 17:00 | 123 | 18:30
Laksam | 130 | 07:00 | 126 | 12:00
Lakshmipur | 122 | 18:00 | 108 | 02:00
Lalbag | 137 | 07:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division