## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-28 | Monday
|  | Date (day): | 2019-01-28 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11371 | MW |  |  | (b) At Evening Peak Hour : |  | 12329 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-27 | 2019-01-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 136 | 137 | 137 | 137
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 330 | 330 | 330
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 365 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 103 | 270 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 340 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 12 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 160 | 155 | 210 | 210 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 170 | 170 | 170
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 91 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 45 | 47 | 47
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 84 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 54 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 30 | 30 | 30 | 30 |  | 78 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 25 | 50 | 50 |  | 30 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 15 | 73 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 1976 | 2532 | 4191 | 4391 | 656 | 357
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.8 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 74 | 78 | 108 | 108 |  | 122 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 150 | 150 |  | 75 | ST Under S/D
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 32 | 40 | 40
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 57 | 57 | 57
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 45 | 70 | 70 | 70 |  | 30 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 84 | 82 | 90 | 90 |  | 10 | Engine problem
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 27 | 35 | 35
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 36 | 93 | 93 | 93 |  | 15 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 516.8 | 724 | 828 | 808 | 360 | 442
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 145 | 150
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 192 | 207 | 221 | 221
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 260 | 260 |  | 100 | ST under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 298 | 342 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 36 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 5 | 55 | 55 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 45 | 45 | 45
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 72 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 20 | 10 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 18 | 100 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 98 | 124 | 98 | 117
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 16 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 22 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 16 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1239 | 1480 | 2012 | 2186 | 420 | 239
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 181 | 181 | 202 | 202 |  |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 87 | 87 | 90 | 90
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.7 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 80 | 196 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 371.7 | 486 | 416 | 514 | 0 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 61 | 60 | 61 | 61
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 101 | 103 | 105 | 105 |  | 225 | GT-2 & ST Under maint.
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 30 | 50 | 50
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under shut down
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 40 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 49 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 80 | 100 | 140
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 0 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 23 | 23 | 23 | 23 |  | 27 | Engine problem
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 305 | 306 | 260 | 260 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1227 | 1248 | 1366 | 1426 | 0 | 252
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 604 | 700 | 604 | 701
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 76 | 20 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 270 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 997 | 1317 | 1394 | 1639 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 112 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 19 | 20 | 26 |  | 7 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 30 | 30 | 30 | 30 |  | 164 | GT-2 & ST under maint.
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 82 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 158 | 243 | 255 | 291 | 0 | 171
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Gas shortage.
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 24 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 6 | 0 | 40 | 40
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage.
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 160 | 220 | 220
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 182 | 189 | 180 | 220
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 29 | 29 | 29 | 29
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 15 | 15 | 15 | 15
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 52 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 100 | 100
| Paramount Baghabari |  | HSD | IPP | 200 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 554 | 635 | 759 | 889 | 353 | 320
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 149 | 150 | 185 | 124 | 170
| Total |  |  |  |  | 17685 | 17142 | 7189.5 | 8814 | 11371 | 12329 | 1913 | 1951
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6881.9845 | 8437 | 10884.6298 | 11801.6534
A. |  | 2019-01-27 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 8814 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5642 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8814 | MW
3 | Day peak Generation : |  |  | 7189.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8437 | MW
4 | Evening peak Generation : |  |  | 8814 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 171.1796 | MKWHr | By Solar | 0.13968 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 129.7942 | MKWHr |  | By Oil: | 20.1592 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6637 | MKWHr |  | By Hydro: | 1.7662 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1913 | MW | Dhaka | 3031 | 3031 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1951 | MW | Chittagong | 930 | 930 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3864 | MW | Khulna | 997 | 997 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1114.46 | MMCFD |  |  | Rajshahi | 972 | 972 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 90699026.884 | ii) Oil : | Taka | 142432427.66 | Comilla | 715 | 715 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14141882 | Total | Taka | 247273336.544 | Mymensingh | 705 | 705 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6.366 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -620 | MW (E to W) at | 19:00 | hrs | Barisal | 164 | 164 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -620 | MW at | 19:00 | hrs | Rangpur | 609 | 609 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.0° C |  |  | Total | 8437 | 8437 |  | 0
B. |  | 2019-01-28 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 28.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12329 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7400 | MW
4 | Reserve(Generation end) |  |  |  | 3429 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 172.8498 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5614 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.1942 | MKWHr. | ii) HVDC Flow at Peak Time |  | 700 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4624 | MKWHr. | iii) Maximum HVDC Flow : |  | 700 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.59 |  | (b) Today: | 96.5 |  | (c) Rule Curve: |  | 97.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-27
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 218 | 0 | 0 | 300 | 0 | 20 | 350 | 307 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 0 | 80 | 0 | 220 | 287 | 184 | 8 | 100 | 36 | 10 | 5 | 7 | 85 | 0 | 0 | 19 | 11 | 0 | 22 | 86 | 171 | 0 | 22 | 0 | 30 | 61 | 53 | 50 | 100 | 95 | 0 | 10 | 49 | 78 | 0 | 23 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 84 | 0 | 0 | 270 |  | 307 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 52 | 28 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 95 | 0 | 178 | 0 | 0 | 0 | 0 |  | 4835 | 1442 | 6277 | 3822 | 307 | 1537 | 263 | 149 | 75 | 38 | 86 | 0 | 0 | 96.6
2:00 | 35 | 218 | 0 | 0 | 300 | 0 | 0 | 350 | 305 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 0 | 220 | 287 | 190 | 8 | 100 | 36 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 82 | 186 | 0 | 22 | 0 | 30 | 61 | 5 | 50 | 100 | 95 | 0 | 10 | 49 | 78 | 0 | 23 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 0 | 0 | 285 |  | 307 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 26 | 21 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 179 | 0 | 0 | 0 | 0 |  | 4564 | 1376 | 5940 | 3788 | 307 | 1338 | 175 | 149 | 75 | 26 | 82 | 0 | 0 | 96.6
3:00 | 35 | 218 | 0 | 0 | 300 | 0 | 0 | 348 | 307 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 0 | 220 | 294 | 193 | 8 | 100 | 36 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 80 | 186 | 0 | 22 | 0 | 30 | 61 | 5 | 5 | 100 | 99 | 0 | 10 | 5 | 78 | 0 | 7 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 305 |  | 311 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 179 | 0 | 0 | 0 | 0 |  | 4451 | 1321 | 5772 | 3778 | 311 | 1247 | 131 | 150 | 75 | 0 | 80 | 0 | 0 | 96.6
4:00 | 35 | 218 | 0 | 0 | 270 | 0 | 0 | 350 | 307 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 17 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 200 | 287 | 188 | 8 | 100 | 33 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 78 | 186 | 0 | 22 | 0 | 30 | 61 | 5 | 5 | 100 | 94 | 0 | 10 | 5 | 78 | 0 | 7 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 305 |  | 311 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 51 | 0 | 182 | 0 | 0 | 0 | 0 |  | 4339 | 1305 | 5644 | 3700 | 311 | 1208 | 123 | 149 | 75 | 0 | 78 | 0 | 0 | 96.59
5:00 | 35 | 219 | 0 | 0 | 270 | 0 | 0 | 348 | 309 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 25 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 80 | 0 | 200 | 287 | 185 | 8 | 99 | 33 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 82 | 201 | 0 | 22 | 0 | 30 | 61 | 5 | 5 | 100 | 98 | 0 | 10 | 5 | 79 | 0 | 7 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 304 |  | 311 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 30 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 50 | 0 | 180 | 0 | 0 | 0 | 0 |  | 4359 | 1283 | 5642 | 3717 | 311 | 1201 | 107 | 149 | 75 | 0 | 82 | 0 | 0 | 96.59
6:00 | 35 | 218 | 0 | 0 | 300 | 0 | 0 | 362 | 308 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 25 | 0 | 0 | 76 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 80 | 0 | 250 | 320 | 207 | 8 | 100 | 33 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 84 | 213 | 5 | 22 | 0 | 30 | 61 | 5 | 5 | 100 | 96 | 0 | 10 | 5 | 79 | 0 | 7 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 314 |  | 311 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 16 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 51 | 0 | 187 | 0 | 0 | 2 | 0 |  | 4638 | 1342 | 5980 | 3900 | 311 | 1292 | 167 | 150 | 76 | 0 | 84 | 0 | 0 | 96.59
7:00 | 35 | 218 | 0 | 0 | 330 | 0 | 0 | 358 | 330 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 160 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 2 | 0 | 76 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 3 | 22 | 37 | 0 | 80 | 0 | 260 | 287 | 185 | 8 | 95 | 31 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 8 | 0 | 22 | 86 | 216 | 16 | 22 | 0 | 30 | 61 | 20 | 13 | 130 | 86 | 0 | 10 | 47 | 78 | 0 | 23 | 0 | 260 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.1 | 77 | 8 | 0 | 91 |  | 603 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 43 | 0 | 22 | 15 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 184 | 0 | 0 | 70 | 0 |  | 4560.1 | 1861 | 6421.1 | 3603 | 603 | 1435 | 417 | 150 | 76 | 50 | 86 | 1.1 | 0 | 96.58
8:00 | 35 | 138 | 0 | 0 | 330 | 0 | 0 | 357 | 304 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 160 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 21 | 0 | 76 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 46 | 22 | 12 | 0 | 80 | 0 | 260 | 309 | 196 | 8 | 100 | 31 | 10 | 5 | 7 | 10 | 0 | 0 | 19 | 11 | 0 | 22 | 92 | 203 | 62 | 22 | 0.3 | 30 | 61 | 53 | 50 | 100 | 100 | 0 | 10 | 47 | 77 | 0 | 23 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 6.8 | 84 | 17 | 0 | 250 |  | 603 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 43 | 0 | 0 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 96 | 0 | 179 | 0 | 0 | 105 | 0 |  | 4819.1 | 1883 | 6702.1 | 3684 | 603 | 1392 | 649 | 149 | 76 | 50 | 92 | 7.1 | 0 | 96.58
9:00 | 35 | 138 | 0 | 0 | 330 | 0 | 0 | 350 | 116 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 160 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 33 | 17 | 30 | 0 | 74 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 50 | 22 | 2 | 0 | 80 | 0 | 260 | 320 | 205 | 8 | 100 | 30 | 9 | 5 | 7 | 50 | 0 | 0 | 19 | 11 | 0 | 22 | 100 | 185 | 83 | 22 | 0.6 | 30 | 61 | 53 | 50 | 100 | 106 | 0 | 40 | 47 | 80 | 0 | 23 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 12.2 | 84 | 17 | 0 | 318 |  | 604 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 20 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 50 | 0 | 42 | 28 | 22 | 15 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 188 | 0 | 0 | 105 | 0 |  | 4884.8 | 1956 | 6840.8 | 3778 | 604 | 1306 | 737 | 150 | 74 | 79 | 100 | 12.8 | 0 | 96.57
10:00 | 35 | 141 | 0 | 0 | 330 | 0 | 0 | 365 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 0 | 7 | 0 | 0 | 26 | 0 | 0 | 18 | 18 | 0 | 0 | 25 | 15 | 33 | 16 | 43 | 0 | 74 | 0 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 50 | 19 | 2 | 0 | 80 | 0 | 260 | 287 | 186 | 8 | 98 | 36 | 0 | 5 | 7 | 50 | 0 | 0 | 19 | 11 | 19 | 22 | 98 | 185 | 87 | 22 | 1.9 | 30 | 61 | 48 | 50 | 100 | 96 | 0 | 40 | 48 | 80 | 19 | 23 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 14 | 16.2 | 84 | 17 | 0 | 316 |  | 603 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 43 | 29 | 22 | 15 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 96 | 0 | 198 | 0 | 0 | 105 | 0 |  | 5085.1 | 1967 | 7052.1 | 3979 | 603 | 1239 | 838 | 149 | 74 | 54 | 98 | 18.1 | 0 | 96.57
11:00 | 35 | 136 | 0 | 0 | 330 | 0 | 0 | 345 | 91 | 0 | 0 | 400 | 0 | 0 | 0 | 20 | 120 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 31 | 0 | 4 | 54 | 18 | 0 | 0 | 25 | 25 | 33 | 16 | 43 | 0 | 74 | 0 | 130 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 50 | 22 | 2 | 0 | 80 | 0 | 260 | 283 | 187 | 8 | 100 | 36 | 0 | 5 | 30 | 20 | 0 | 0 | 21 | 11 | 25 | 22 | 100 | 183 | 87 | 22 | 2.1 | 30 | 61 | 50 | 50 | 100 | 96 | 0 | 20 | 48 | 80 | 19 | 23 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 14 | 18.5 | 84 | 17 | 0 | 309 |  | 604 | 0 | 300 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 35 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 96 | 0 | 178 | 0 | 0 | 53 | 0 |  | 5174.6 | 1841 | 7015.6 | 3931 | 604 | 1286 | 822 | 149 | 74 | 29 | 100 | 20.6 | 0 | 96.56
12:00 | 35 | 136 | 0 | 0 | 330 | 0 | 0 | 351 | 103 | 0 | 0 | 400 | 0 | 0 | 0 | 30 | 120 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 6 | 54 | 18 | 0 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 74 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 45 | 36 | 50 | 22 | 2 | 0 | 80 | 0 | 260 | 298 | 192 | 8 | 100 | 36 | 0 | 5 | 45 | 20 | 0 | 0 | 21 | 11 | 25 | 22 | 98 | 181 | 87 | 22 | 1.7 | 30 | 61 | 50 | 50 | 100 | 101 | 0 | 20 | 46 | 80 | 19 | 23 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 18.8 | 84 | 18 | 0 | 305 |  | 604 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 6 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 96 | 0 | 182 | 0 | 0 | 53 | 0 |  | 5330.5 | 1859 | 7189.5 | 4009 | 604 | 1331 | 868 | 150 | 74 | 35 | 98 | 20.5 | 0 | 96.56
13:00 | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 352 | 231 | 0 | 0 | 420 | 0 | 0 | 0 | 30 | 120 | 0 | 130 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 18 | 54 | 18 | 0 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 74 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 59 | 50 | 22 | 9 | 0 | 80 | 0 | 260 | 301 | 186 | 8 | 94 | 36 | 0 | 5 | 45 | 20 | 0 | 8 | 21 | 11 | 16 | 22 | 100 | 173 | 87 | 22 | 1.4 | 30 | 60 | 53 | 50 | 100 | 96 | 0 | 20 | 46 | 80 | 19 | 23 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 18 | 84 | 33 | 0 | 302 |  | 603 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 42 | 29 | 22 | 15 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 96 | 0 | 182 | 0 | 0 | 53 | 0 |  | 5489.4 | 1827 | 7316.4 | 3923 | 603 | 1479 | 940 | 149 | 74 | 29 | 100 | 19.4 | 0 | 96.55
14:00 | 35 | 137 | 0 | 0 | 300 | 0 | 0 | 315 | 231 | 0 | 0 | 360 | 0 | 0 | 0 | 30 | 120 | 0 | 73 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 18 | 54 | 18 | 0 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 74 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 59 | 50 | 22 | 3 | 0 | 80 | 0 | 260 | 287 | 185 | 8 | 102 | 36 | 0 | 5 | 45 | 10 | 0 | 8 | 21 | 11 | 16 | 22 | 102 | 173 | 87 | 22 | 1.3 | 30 | 60 | 11 | 10 | 100 | 95 | 0 | 10 | 47 | 80 | 19 | 23 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 15.5 | 84 | 34 | 0 | 285 |  | 604 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 42 | 29 | 18 | 15 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 159 | 0 | 96 | 0 | 160 | 0 | 0 | 53 | 0 |  | 5144.8 | 1803 | 6947.8 | 3736 | 604 | 1286 | 932 | 149 | 74 | 48 | 102 | 16.8 | 0 | 96.55
15:00 | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 300 | 261 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 120 | 0 | 119 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 18 | 54 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 83 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 56 | 50 | 22 | 2 | 0 | 80 | 0 | 260 | 305 | 185 | 8 | 100 | 36 | 0 | 5 | 45 | 10 | 0 | 8 | 21 | 11 | 16 | 22 | 104 | 173 | 87 | 22 | 1.2 | 30 | 60 | 11 | 10 | 100 | 96 | 0 | 10 | 20 | 78 | 19 | 23 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 12 | 84 | 34 | 0 | 304 |  | 604 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 42 | 29 | 16 | 15 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 153 | 0 | 80 | 0 | 152 | 0 | 0 | 53 | 0 |  | 5250.2 | 1769 | 7019.2 | 3816 | 604 | 1289 | 914 | 149 | 83 | 47 | 104 | 13.2 | 0 | 96.55
16:00 | 35 | 138 | 0 | 0 | 330 | 0 | 0 | 355 | 260 | 0 | 0 | 390 | 0 | 0 | 0 | 15 | 120 | 0 | 125 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 18 | 18 | 18 | 0 | 22 | 0 | 24 | 33 | 33 | 43 | 0 | 82 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 52 | 20 | 22 | 2 | 0 | 80 | 0 | 260 | 338 | 204 | 8 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 8 | 21 | 11 | 16 | 20 | 100 | 177 | 87 | 22 | 0.7 | 30 | 60 | 11 | 10 | 100 | 104 | 0 | 10 | 20 | 78 | 19 | 23 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 15 | 7 | 80 | 17 | 0 | 301 |  | 604 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 30 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 29 | 20 | 15 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 158 | 0 | 82 | 0 | 157 | 0 | 0 | 17 | 0 |  | 5216.7 | 1669 | 6885.7 | 3922 | 604 | 1307 | 659 | 149 | 82 | 55 | 100 | 7.7 | 0 | 96.54
17:00 | 35 | 138 | 0 | 0 | 380 | 0 | 0 | 360 | 311 | 0 | 0 | 430 | 0 | 3 | 3 | 15 | 120 | 0 | 125 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 18 | 18 | 18 | 0 | 22 | 0 | 24 | 33 | 33 | 43 | 0 | 82 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 58 | 19 | 22 | 11 | 0 | 80 | 0 | 260 | 305 | 185 | 8 | 100 | 33 | 5 | 5 | 45 | 10 | 0 | 8 | 21 | 11 | 16 | 16 | 100 | 182 | 87 | 22 | 0.1 | 30 | 60 | 11 | 10 | 100 | 95 | 0 | 10 | 20 | 80 | 19 | 23 | 10 | 290 | 24 | 11 | 0 | 5 | 0 | 0 | 60 | 0 | 15 | 1.4 | 82 | 17 | 0 | 308 |  | 604 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 2 | 35 | 16 | 30 | 14 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 12 | 8 | 0 | 8 | 29 | 20 | 15 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 156 | 0 | 82 | 0 | 156 | 0 | 0 | 17 | 0 |  | 5352.5 | 1715 | 7067.5 | 3923 | 604 | 1430 | 685 | 149 | 82 | 93 | 100 | 1.5 | 0 | 96.54
18:00 | 35 | 137 | 0 | 0 | 350 | 0 | 0 | 350 | 270 | 13 | 0 | 340 | 0 | 26 | 40 | 17 | 120 | 0 | 125 | 0 | 24 | 40 | 60 | 30 | 31 | 0 | 18 | 54 | 55 | 55 | 22 | 0 | 22 | 33 | 33 | 43 | 0 | 82 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 27 | 70 | 93 | 23 | 22 | 18 | 0 | 80 | 0 | 260 | 334 | 198 | 8 | 100 | 36 | 5 | 5 | 45 | 10 | 8 | 8 | 21 | 11 | 16 | 16 | 126 | 183 | 87 | 22 | 0 | 30 | 60 | 11 | 10 | 100 | 102 | 0 | 10 | 20 | 80 | 19 | 23 | 10 | 260 | 24 | 11 | 0 | 115 | 0 | 0 | 194 | 0 | 15 | 0 | 82 | 45 | 57 | 307 |  | 700 | 0 | 270 | 0 | 65 | 0 | 0 | 0 | 44 | 72 | 40 | 30 | 17 | 60 | 0 | 0 | 0 | 50 | 40 | 102 | 40 | 24 | 0 | 30 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 146 | 0 | 82 | 0 | 146 | 0 | 0 | 90 | 0 |  | 6047 | 2292 | 8339 | 3882 | 700 | 1281 | 1632 | 149 | 82 | 487 | 126 | 0 | 0 | 96.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 365 | 270 | 0 | 0 | 340 | 0 | 12 | 80 | 15 | 170 | 0 | 155 | 0 | 0 | 91 | 84 | 0 | 30 | 0 | 45 | 54 | 54 | 36 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 78 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 32 | 57 | 68 | 70 | 93 | 50 | 22 | 27 | 0 | 80 | 0 | 260 | 342 | 207 | 8 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 22 | 21 | 11 | 16 | 16 | 124 | 181 | 87 | 22 | 0 | 30 | 60 | 53 | 30 | 100 | 103 | 0 | 40 | 49 | 80 | 19 | 23 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 196 | 0 | 73 | 0 | 82 | 100 | 72 | 306 |  | 700 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 42 | 76 | 40 | 30 | 19 | 112 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 24 | 0 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 82 | 0 | 189 | 0 | 0 | 90 | 0 |  | 6470 | 2344 | 8814 | 4032 | 700 | 1463 | 1810 | 149 | 78 | 458 | 124 | 0 | 0 | 96.53
19:30 | 35 | 137 | 0 | 0 | 370 | 0 | 0 | 370 | 345 | 0 | 0 | 340 | 0 | 0 | 0 | 15 | 220 | 0 | 155 | 0 | 0 | 0 | 84 | 0 | 30 | 0 | 47 | 54 | 55 | 17 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 80 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 70 | 53 | 50 | 22 | 32 | 0 | 80 | 0 | 260 | 323 | 197 | 8 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 0 | 21 | 11 | 16 | 22 | 124 | 168 | 87 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 99 | 0 | 40 | 49 | 78 | 19 | 23 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 197 | 0 | 123 | 0 | 82 | 100 | 72 | 309 |  | 700 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 23 | 80 | 40 | 30 | 19 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 0 | 0 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 80 | 0 | 196 | 0 | 0 | 105 | 0 |  | 6353 | 2378 | 8731 | 4150 | 700 | 1596 | 1597 | 149 | 80 | 335 | 124 | 0 | 0 | 96.53
20:00 | 35 | 137 | 0 | 0 | 380 | 0 | 0 | 365 | 357 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 220 | 0 | 155 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 47 | 36 | 37 | 0 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 77 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 40 | 34 | 50 | 22 | 35 | 0 | 144 | 0 | 260 | 309 | 190 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 21 | 11 | 16 | 22 | 122 | 170 | 87 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 103 | 0 | 84 | 49 | 79 | 19 | 23 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 120 | 0 | 82 | 70 | 40 | 312 |  | 700 | 0 | 320 | 0 | 85 | 0 | 0 | 0 | 4 | 76 | 40 | 30 | 14 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 0 | 0 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 81 | 0 | 181 | 0 | 0 | 105 | 0 |  | 6412 | 2329 | 8741 | 4200 | 700 | 1811 | 1374 | 149 | 77 | 308 | 122 | 0 | 0 | 96.53
21:00 | 35 | 137 | 0 | 0 | 380 | 0 | 0 | 365 | 357 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 220 | 0 | 153 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 77 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 20 | 50 | 22 | 23 | 0 | 150 | 0 | 260 | 312 | 193 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 21 | 11 | 16 | 22 | 122 | 179 | 87 | 22 | 0 | 30 | 60 | 53 | 50 | 163 | 101 | 0 | 84 | 49 | 78 | 21 | 23 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 23 | 139 | 0 | 82 | 70 | 19 | 313 |  | 699 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 76 | 40 | 30 | 16 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 0 | 0 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 81 | 0 | 192 | 0 | 0 | 105 | 0 |  | 6303 | 2352 | 8655 | 4280 | 699 | 1854 | 1250 | 150 | 77 | 223 | 122 | 0 | 0 | 96.53
22:00 | 35 | 136 | 0 | 0 | 300 | 0 | 0 | 349 | 325 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 220 | 0 | 142 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 77 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 50 | 22 | 32 | 0 | 150 | 0 | 260 | 305 | 185 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 21 | 11 | 16 | 22 | 114 | 182 | 80 | 22 | 0 | 30 | 60 | 53 | 50 | 100 | 96 | 0 | 84 | 49 | 78 | 21 | 23 | 10 | 250 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 0 | 84 | 70 | 0 | 210 |  | 700 | 0 | 320 | 0 | 19 | 0 | 0 | 0 | 0 | 70 | 40 | 30 | 14 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 0 | 43 | 0 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 95 | 0 | 179 | 0 | 0 | 105 | 0 |  | 5689 | 2181 | 7870 | 3997 | 700 | 1720 | 1003 | 149 | 77 | 110 | 114 | 0 | 0 | 96.52
23:00 | 35 | 136 | 0 | 0 | 300 | 0 | 0 | 348 | 305 | 0 | 0 | 370 | 0 | 0 | 0 | 55 | 150 | 0 | 127 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 22 | 0 | 25 | 33 | 33 | 25 | 0 | 77 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 22 | 37 | 0 | 150 | 0 | 260 | 305 | 184 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 21 | 11 | 16 | 22 | 104 | 183 | 16 | 22 | 0 | 30 | 60 | 53 | 50 | 100 | 97 | 0 | 86 | 49 | 76 | 20 | 23 | 10 | 265 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 84 | 70 | 0 | 181 |  | 700 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 15 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 43 | 0 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 95 | 0 | 177 | 0 | 0 | 70 | 0 |  | 5302 | 1954 | 7256 | 3877 | 700 | 1643 | 706 | 149 | 77 | 0 | 104 | 0 | 0 | 96.52
24:00 | 35 | 136 | 0 | 0 | 300 | 0 | 0 | 350 | 306 | 0 | 0 | 340 | 0 | 0 | 0 | 40 | 150 | 0 | 127 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 77 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 22 | 35 | 0 | 150 | 0 | 260 | 305 | 185 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 21 | 11 | 24 | 22 | 96 | 184 | 16 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 98 | 0 | 86 | 49 | 79 | 20 | 23 | 10 | 285 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 84 | 70 | 0 | 181 |  | 406 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 14 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 15 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 181 | 0 | 95 | 0 | 180 | 0 | 0 | 44 | 0 |  | 5240 | 1611 | 6851 | 3914 | 406 | 1661 | 548 | 149 | 77 | 0 | 96 | 0 | 0 | 96.52
KWH | 720000 | 4203300 | 0 | 0 | 7729490 | 0 | 28224 | 8540160 | 6287000 | 11400 | 0 | 8980125 | 0 | 54720 | 151896 | 401007 | 3562492 | 0 | 3036000 | 0 | 43200 | 378576 | 217440 | 55865 | 231360 | 0 | 237696 | 531000 | 290861 | 88510 | 312804 | 375000 | 554580 | 777168 | 729500 | 646776 | 0 | 1766222 | 0 | 2700000 | 0 | 391860 | 0 | 0 | 0 | 0 | 0 | 806880 | 69632 | 105843 | 660240 | 552000 | 825600 | 506400 | 553920 | 0 | 2176900 | 50090 | 6066400 | 7334000 | 4638000 | 200727 | 2355570 | 790488 | 156960 | 120000 | 713404 | 802544 | 6184 | 81317 | 482400 | 233820 | 266900 | 502670 | 2462400 | 4328320 | 1376640 | 520956 | 11700 | 683000 | 1448040 | 751200 | 763000 | 3013920 | 2212000 | 0 | 798720 | 885960 | 1938990 | 284000 | 497040 | 151380 | 7245700 | 570352 | 236544 | 0 | 215780 | 0 | 3413 | 1732800 | 0 | 586080 | 127980 | 1608000 | 811200 | 205750 | 6762700 |  | 13194182 | 0 | 7261632 | 0 | 381120 | 0 | 0 | 0 | 84480 | 388736 | 873000 | 693000 | 326844 | 704640 | 0 | 0 | 0 | 53338 | 31729 | 690876 | 847020 | 350206 | 7480 | 977280 | 444777 | 479280 | 350280 | 205092 | 0 | 0 | 3663700 | 0 | 82000 | 0 | 0 | 4425745 | 0 | 2006119 | 0 | 4467309 | 0 | 0 | 863040 | 0 |  | 127326686 | 43852905 | 171179591 | 94681812 | 13194182 | 35112347 | 17976733 | 3663700 | 1766222 | 2182515 | 2462400 | 139680 | 0
Fuel Cost | 619200 | 3614838 | 0 | 0 | 4946873.6 | 0 | 26530.56 | 5209497.6 | 3835070 | 109554 | 0 | 6016683.75 | 0 | 343641.6 | 1014665.28 | 2450152.77 | 2315619.8 | 0 | 3369960 | 0 | 270000 | 2494815.84 | 2102644.8 | 355860.05 | 1385846.4 | 0 | 1585432.32 | 3786030 | 1817881.25 | 554957.7 | 234603 | 281250 | 0 | 0 | 0 | 6118500.96 | 0 | 0 | 0 | 2970000 | 0 | 3710914.2 | 0 | 0 | 0 | 0 | 0 | 7092475.2 | 749936.64 | 1029852.39 | 4086885.6 | 3565920 | 5399424 | 430440 | 0 | 0 | 1980979 | 45581.9 | 3761168 | 5060460 | 3246600 | 138501.63 | 2261347.2 | 529626.96 | 134985.6 | 110400 | 584991.28 | 762416.8 | 67034.56 | 603372.14 | 371448 | 175365 | 205513 | 377002.5 | 16842816 | 3246240 | 12651321.6 | 401136.12 | 0 | 710320 | 1505961.6 | 721152 | 686700 | 2350857.6 | 1548400 | 0 | 854630.4 | 974556 | 2210448.6 | 363520 | 462247.2 | 140783.4 | 4637248 | 427764 | 179773.44 | 0 | 1566562.8 | 0 | 58191.65 | 12389520 | 0 | 0 | 0 | 0 | 7576608 | 1921705 | 5883549 |  | 67290328.2 | 0 | 4865293.44 | 0 | 3159484.8 | 0 | 0 | 0 | 951244.8 | 4579310.08 | 6879240 | 478170 | 323575.56 | 5214336 | 0 | 0 | 0 | 610720.1 | 340134.88 | 6190248.96 | 7326723 | 3116833.4 | 79662 | 9694617.6 | 5235025.29 | 527208 | 329263.2 | 155254.644 | 0 | 0 | 14141882 | 0 | 2195140 | 0 | 0 | 3098021.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 184624763.29 | 146781717.454 | 331406480.744 | 67081225.904 | 67290328.2 | 23617800.98 | 118301473.16 | 14141882 | 0 | 24130954.5 | 16842816 | 0 | 0
Yesterday Day Peak | 35 | 136 | 0 | 0 | 330 | 0 | 0 | 351 | 103 | 0 | 0 | 400 | 0 | 0 | 0 | 30 | 120 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 6 | 54 | 18 | 0 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 74 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 45 | 36 | 50 | 22 | 2 | 0 | 80 | 0 | 260 | 298 | 192 | 8 | 100 | 36 | 0 | 5 | 45 | 20 | 0 | 0 | 21 | 11 | 25 | 22 | 98 | 181 | 87 | 22 | 1.7 | 30 | 61 | 50 | 50 | 100 | 101 | 0 | 20 | 46 | 80 | 19 | 23 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 18.8 | 84 | 18 | 0 | 305 |  | 604 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 6 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 96 | 0 | 182 | 0 | 0 | 53 | 0 |  | 7189.5 | DayPeak
Yesterday Evening Peak | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 365 | 270 | 0 | 0 | 340 | 0 | 12 | 80 | 15 | 170 | 0 | 155 | 0 | 0 | 91 | 84 | 0 | 30 | 0 | 45 | 54 | 54 | 36 | 22 | 0 | 25 | 33 | 33 | 43 | 0 | 78 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 32 | 57 | 68 | 70 | 93 | 50 | 22 | 27 | 0 | 80 | 0 | 260 | 342 | 207 | 8 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 22 | 21 | 11 | 16 | 16 | 124 | 181 | 87 | 22 | 0 | 30 | 60 | 53 | 30 | 100 | 103 | 0 | 40 | 49 | 80 | 19 | 23 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 196 | 0 | 73 | 0 | 82 | 100 | 72 | 306 |  | 700 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 42 | 76 | 40 | 30 | 19 | 112 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 24 | 0 | 43 | 29 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 82 | 0 | 189 | 0 | 0 | 90 | 0 |  | 8814 | EvPeak
Forecast for Evening | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 170 | 0 | 210 | 100 | 100 | 102 | 149 | 100 | 30 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 78 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 40 | 57 | 68 | 70 | 93 | 50 | 22 | 35 | 0 | 150 | 0 | 260 | 360 | 221 | 8 | 100 | 40 | 55 | 5 | 45 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 117 | 202 | 90 | 22 | 0 | 30 | 61 | 51 | 50 | 163 | 105 | 0 | 86 | 50 | 140 | 20 | 23 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 260 |  | 701 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 42 | 80 | 40 | 30 | 26 | 110 | 30 | 0 | 0 | 50 | 40 | 100 | 40 | 50 | 40 | 52 | 29 | 22 | 15 | 11 | 0 | 0 | 150 | 17 | 18 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 137 | 0 | 0 | 330 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 170 | 0 | 210 | 100 | 100 | 102 | 149 | 100 | 30 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 78 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 40 | 57 | 68 | 70 | 93 | 50 | 22 | 35 | 0 | 145 | 0 | 260 | 360 | 221 | 8 | 100 | 40 | 55 | 5 | 45 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 98 | 202 | 90 | 22 | 2 | 30 | 61 | 51 | 50 | 163 | 105 | 0 | 86 | 50 | 100 | 0 | 23 | 10 | 341 | 25 | 11 | 100 | 300 | 300 | 0 | 100 | 0 | 149 | 20 | 90 | 200 | 150 | 260 |  | 604 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 20 | 40 | 30 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 50 | 40 | 52 | 29 | 22 | 15 | 11 | 0 | 0 | 150 |  |  | 0 | 0 | 220 | 0 | 95 | 100 | 180 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 137 | 0 | 0 | 300 | 0 | 0 | 367 | 276 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 120 | 0 | 127 | 0 | 0 | 72 | 0 | 0 | 30 | 0 | 0 | 36 | 0 | 0 | 0 | 25 | 26 | 25 | 33 | 12 | 0 | 78 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 13 | 50 | 22 | 14 | 0 | 145 | 0 | 260 | 301 | 183 | 8 | 100 | 33 | 5 | 5 | 7 | 50 | 0 | 0 | 19 | 11 | 25 | 22 | 92 | 207 | 65 | 22 | 0.2 | 30 | 60 | 52 | 26 | 130 | 94 | 0 | 50 | 48 | 78 | 0 | 23 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 0 | 6.5 | 82 | 0 | 2 | 260 | 0 | 596 | 0 | 300 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 43 | 0 | 22 | 15 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 97 | 0 | 173 | 0 | 0 | 105 | 0 | 0
199
| Minimum Generation |  | 5642 | 5:00
| Highest Generation |  | 8814 | 19:00
| Day Peak Generation |  | 7189.5 | 12:00
| Evening Peak Generation |  | 8814 | 19:00
| HVDC Max Flow |  | 700 | 18:00
| HVDC EvPeak Flow |  | 700 | 19:00
| Load factor L.F |  | 80.92%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-28
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7189.5 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5614 | MW
Evening Peak Generation : |  | 8814 | MW Hour : | 19:00 | Available Max Generation : |  | 12329 | MW
E.P. Demand (at gen end) : |  | 8814 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8900 | MW
Maximum Generation : |  | 8814 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3429 | MW
Total Gen. (MKWH) : |  | 171.1796 | System Load Factor : | 80.92% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -620 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-28
Actual : | 96.5 | Ft.(MSL) , | Rule curve : | 97.8 | Ft.( MSL )
Gas Consumed : | Total = | 1114.46 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 90699026.884
|  | Coal : | 14141882 | Oil : | 142432427.66 | Total : | 247273336.544
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3182.0774 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1076.5299 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 963.5457 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 870.2935 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 786.6654 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 634.7971 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 362.0926 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 163.6323 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 489.5529 |  |  | 0 | 0%
Total | 0 |  | 8529.1867 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Sirajganj Unit-1,4
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Ashuganj #3 & 5
|  |  |  | 3) Ghorasal Unit-1,4,5 |  | 11) Raozan # 1,2
|  |  |  | 4) Tongi GT |  | 14) Bhola CCPP GT-2 & ST
|  |  |  | 5) Haripur GT-1,2 |  | 13) Shikalbaha 330 MW GT-1 & ST
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW,100 MW
8) Sikalbaha 150MW Peaking
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Aminbazar-Kaliakoir 230 kV was under shut down from 08:56 to 17:10 for A/M.
b) Chandpur-Ramganj 132 kV Ckt-2 was under shut down from 08:42 to 15:52 for A/M.
c) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 09:11 to 21:01 for D/W.
d) Mymensingh 132 kV Bus-2 was under shut down from 09:22 to 17:13 for C/M.
e) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 09:20 to 14:14 for C/M.
f) Mymensingh-Jamalpur 132 kV Ckt-1 was under shut down from 09:18 to 17:35 for C/M.
g) Bashundhara-Rampura 132 kV Ckt-2 was under shut down from 08:18 to 16:40 for A/M.
h) Ashuganj 132 kV Bus-2 was under shut down from 08:41 to 15:00 for C/M.
i) Haripur 360 MW CCPP was under shut down from 09:06 to 10:39 for maintenance work.
j) Natore 132/33 kV T2 transformer was under shut down from 10:03 to 11:31 for C/M. |  |  |  | About 6 MW Power interruption occurred under Natore S/S
k) Hasnabad-Brammongaon 132 Ckt was under shut down from 09:25 to 13:51 for A/M. |  |  |  | area from 10:03 to 11:31.
l) Hathazari-Baroihat 132 kV Ckt-1 tripped at 13:27 from Hathazari end showing dist.relay and was switched on
at 13:56.
m) Aminbazar 230/132 kV T1 transformer tripped at 14:57 from both ends showing WTA relay at 230 kV side &
OLA at 132 kV side and was switched on at 20:09.
n) Hasnabad 230 kV bus-2 was shut down at 07:12 (28/01/2019) for red hot maintenance.
o) Ghorasal-Tongi 230 kV Ckt-1 was shut down at 07:15 (28/01/2019) for A/M.
p) Ashuganj-Kishoreganj 132 kV Ckt-2 was shut down at 07:20 (28/01/2019) for D/W.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 720000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 137 | 4203300 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7729490
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 28224 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 8540160 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 11400 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 270 | 6287000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 340 | 8980125 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 12 | 54720 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 151896 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 401007 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 55865 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 312804
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 155 | 3036000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 43200 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 170 | 3562492 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 91 | 378576 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 45 | 237696
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 531000
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 84 | 217440 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 54 | 290861
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 88510 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 30 | 231360 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 929580 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 777168
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 729500
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 646776 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 215780 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 3413 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 73 | 586080 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2532 | 49981423
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2700000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 391860
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127980
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 825600
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 78 | 1766222 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 806880 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 57 | 69632 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 105843 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 660240 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 82 | 1608000 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 506400
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 553920
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 93 | 552000 | Low demand
| Chattogram area Total |  |  |  | 1681 | 724 | 10674577
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2176900 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 50090 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 207 | 4638000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6066400 | ST under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 342 | 7334000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 36 | 790488 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 156960 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 713404 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 72 | 205750 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 10 | 802544 | Line Over Load
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 6184 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2355570
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 100 | 811200 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 21 | 482400
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 233820
** | Tripura |  | Imported power | 0 | 160 | 124 | 2462400
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 16 | 266900 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 22 | 81317 | Low demand
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 16 | 502670
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1480 | 30457724
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 181 | 4328320 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 520956
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 87 | 1376640 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 11700
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 196 | 1732800
| Mymensingh Area Total |  |  |  | 522 | 486 | 7970416
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 683000 | GT-1 under maint.
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1448040
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3013920 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 103 | 2212000 | GT-2 under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 751200
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 30 | 763000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 236544
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 40 | 798720 | Line Over Load
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 885960
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 80 | 1938990 | Frequency control
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 284000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 23 | 497040 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 570352
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 310 | 7245700 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 306 | 6762700 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 151380
| Sylhet Area Total |  |  |  | 1549 | 1248 | 28242546
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 700 | 13194182
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 381120
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 42 | 84480
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 76 | 388736 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 270 | 7261632 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 873000
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 90 | 863040
| Khulna Area Total |  |  |  | 2209 | 1317 | 23046190
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 112 | 704640
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 19 | 326844 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 30 | 693000 | Under maint.
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 82 | 2006119 | Engine problem
| Barisal Area Total |  |  |  | 462 | 243 | 3730603
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 53338
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 31729 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 847020 | Engine problem
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 350206 | Engine problem
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 7480 | Under maint.
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4425745 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 189 | 4467309 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 29 | 444777
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 479280
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 15 | 350280
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 205092
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 977280 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 690876
| Paramount Baghabari |  | IPP | 200 MW | 0 | 0 | 0
| Rajshahi Area Total |  |  |  | 1546 | 635 | 13330412
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3663700
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 82000 | Reserve
| Rangpur Area Total |  |  |  | 484 | 149 | 3745700
| Total |  |  |  | 17142 | 8814 | 171179591
| Eastern Grid Total |  |  |  | 12441 | 6470 | 127326686
| Western Grid Total |  |  |  | 4701 | 2344 | 43852905
| National Grid Total |  |  |  | 17142 | 8814 | 171179591
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-27 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5695 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2742 | MW
i) Dhaka area |  |  | 3031 | MW | i) Khulna area |  |  | 997 | MW
ii) Chittagong area |  |  | 930 | MW | ii) Rajshahi area |  |  | 972 | MW
iii) Comilla area |  |  | 715 | MW | iii) Barisal area |  |  | 164 | MW
iv) Mymensingh area |  |  | 705 | MW | iv) Rangpur area |  |  | 609 | MW
v) Sylhet area |  |  | 314 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8437 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 86 | 2100 | Netrokona | 90 | 1930 | Goalpara | 26 | 1830
Munsiganj | 78 | 2000 | Jamalpur | 102 | 1830 | Central s/s | 57 | 1830
Sonargaon | 47 | 1830 | Sherpur | 84 | 1800 | Noapara | 74 | 1930
Shyampur | 150 | 1800 | Srimongal | 25 | 1800 | Jessore | 116 | 1830
Bhulta | 151 | 1900 | Shahjibazar | 86 | 2100 | Jhenida | 73 | 1830
Madanganj | 47 | 1900 | Fenchuganj | 27 | 1800 | Bottail | 94 | 1830
Shitalakhya | 91 | 1200 | Kulawara | 26 | 1800 | G.K Project | 32 | 1830
Rahim steel | 9 | 800 | Sylhet | 89 | 2200 | Faridpur | 120 | 1900
Matuail | 84 | 1000 | Chatak | 18 | 1800 | Madaripur | 91 | 2000
Ghorasal | 61 | 1900 | Sunamganj | 25 | 1830 | Gopalganj | 63 | 1900
Narsingdi | 102 | 100 | Biani Bazar | 32 | 1800 | Bagerhat | 64 | 1900
Haripur (SBU) | 94 | 1100 | Comilla (S) | 126 | 1800 | Mongla | 38 | 1000
Ullon | 59 | 1800 | Comilla(N) | 76 | 1830 | Satkhira | 68 | 2000
Hasnabad | 153 | 1800 | Chandpur | 73 | 1830 | Gallamari | 36 | 1300
Magbazar | 106 | 1500 | Feni | 91 | 1830 | Magura | 36 | 1830
Maniknagar | 92 | 1300 | Chowmuhani | 120 | 1900 | Chuadanga | 58 | 1830
Bangabhaban | 20 | 1300 | Ashuganj | 39 | 1900 | Barisal | 86 | 1930
Narinda | 72 | 1400 | Daudkandi | 92 | 1930 | Patuakhali | 70 | 2100
Dhanmondi | 74 | 1300 | B.Baria | 95 | 1930 | Bhandaria | 38 | 1930
Lalbag | 68 | 1300 | Ramganj | 21 | 1900 | Ishurdi | 40 | 1830
Madartek | 36 | 2000 | Madunaghat | 45 | 1830 | Ruppur Paromanobik | 1 | 100
Mirpur | 80 | 1830 | Hathazari | 68 | 1830 | Natore | 88 | 1930
Kalyanpur | 66 | 1800 | Khulshi | 138 | 1400 | Bogra | 194 | 1900
Gulshan | 92 | 1300 | Halishahar | 96 | 1800 | Noagaon | 117 | 1900
Uttara | 41 | 1400 | Baraulia | 157 | 1800 | Rajshahi | 102 | 2000
Uttara(New) | 6 | 1100 | Sikalbaha | 30 | 1830 | C.Nawabganj | 60 | 2000
Kamrangirchar | 61 | 1800 | Dohazari | 62 | 1800 | Amnura | 32 | 1830
Savar | 99 | 1830 | Cox'sbazar | 69 | 2000 | Pabna | 76 | 1900
Bhasantec | 102 | 1830 | Chandraghona | 20 | 1800 | Shahjadpur | 74 | 1830
Agargaon | 38 | 1800 | Kaptai | 4 | 1800 | Serajganj | 74 | 2000
Satmosjid | 65 | 1830 | A. Khaer Stl. | 0 | 0 | Niyamatpur | 91 | 1930
Tongi | 115 | 1800 | Bakulia | 75 | 1800 | Joypurhat | 40 | 1830
Kabirpur | 142 | 1100 | Julda | 21 | 1800 | Rangpur | 103 | 1830
Basundhara | 78 | 1600 | TK chemical | 3 | 1800 | Lalmonirhat | 85 | 1830
Manikganj | 62 | 1900 | Modern Steel | 15 | 200 | Saidpur | 100 | 1830
Joydevpur | 191 | 1800 | Shahmirpur | 22 | 1830 | Purbasadipur | 81 | 2000
New Tongi | 91 | 1830 | Khagrachhari | 16 | 1800 | Thakurgaon | 54 | 1830
Korda | 202 | 1800 | Matarbari | 20 | 1800 | Palashbari | 101 | 1830
Dhamrai | 38 | 1830 | Baroiar Hat | 20 | 1800 | Barapukuria | 53 | 1830
Tangail | 143 | 1900 | Rangamati | 8 | 1800 | Panchagar | 34 | 1800
Mymensing | 218 | 2100 | Abul Khair 230 | 161 | 200 | Joldhaka | 17 | 1830
Kishorganj | 86 | 1900 | BSRM | 108 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-27
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 406 | 5:00 | 396 | 9:00 | Kaliakoir | 394 | 5:00 | 382 | 12:00
Bheramara | 405 | 4:00 | 397 | 10:00 | Bhulta | 404 | 3:00 | 394 | 12:00
Ashuganj(N) | 404 | 1:00 | 396 | 20:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 235 | 1:00 | 232 | 9:00 | Hathazari | 232 | 19:00 | 210 | 9:00
Ishurdi | 237 | 1:00 | 226 | 8:00 | Megnaghat | 233 | 5:00 | 227 | 20:00
Ashuganj | 240 | 1:00 | 236 | 10:00 | Fenchuganj | 241 | 1:00 | 234 | 9:00
Serajganj | 232 | 4:00 | 220 | 19:00 | Siddhirganj | 234 | 5:00 | 226 | 16:00
Baghabari | 231 | 2:00 | 220 | 19:30 | Maniknagar | 231 | 1:00 | 225 | 15:00
Barapukuria | 228 | 4:00 | 217 | 13:00 | Old Airport | 230 | 4:00 | 219 | 16:00
Bogra | 231 | 3:00 | 208 | 19:30 | Barisal | 239 | 10:00 | 229 | 6:00
Khulna South | 238 | 22:00 | 222 | 7:00 | AKSML | 227 | 13:00 | 213 | 15:00
Rampura | 230 | 1:00 | 224 | 12:00 | BSRM | 228 | 14:00 | 217 | 9:00
Haripur | 230 | 1:00 | 223 | 15:00 | Bibiyana | 241 | 5:00 | 235 | 8:00
Hasnabad | 230 | 6:00 | 218 | 16:00 | Bhulta | 232 | 2:00 | 225 | 20:00
Aminbazar | 231 | 5:00 | 221 | 16:00 | Ashuganj (S) | 240 | 3:00 | 235 | 12:00
Tongi | 228 | 4:00 | 218 | 15:00 | Kaliakoir | 234 | 4:00 | 224 | 20:00
Comilla (N) | 239 | 1:00 | 236 | 8:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 200 | 132 | 1500 | Ramganj | 133 | 1400 | 130 | 1000
Munsiganj | 137 | 1800 | 131 | 900 | Madanhat | 136 | 1400 | 128 | 600
Megnaghat | 133 | 100 | 130 | 1100 | Hathazari | 135 | 1400 | 127 | 800
Shyampur | 133 | 700 | 127 | 2000 | Khulshi | 133 | 1400 | 124 | 800
Bhulta | 131 | 200 | 124 | 1500 | Halishahar | 135 | 1300 | 130 | 1100
Madanganj | 137 | 700 | 129 | 1300 | Baraulia | 135 | 1400 | 125 | 800
Shitalakhya | 138 | 300 | 129 | 1600 | Sikalbaha | 135 | 1400 | 125 | 300
Rahim steal | 136 | 1800 | 133 | 1000 | Dohazari | 135 | 1830 | 126 | 500
Matuail | 135 | 100 | 131 | 1600 | Cox'sbazar | 131 | 1400 | 119 | 600
Ghorasal | 140 | 100 | 138 | 1200 | Chandraghona | 135 | 1400 | 128 | 600
Narsinghdi | 134 | 1400 | 129 | 800 | Kaptai | 135 | 1300 | 130 | 700
Haripur (SBU) | 135 | 100 | 132 | 1400 | A. Khaer Stl. | 134 | 1400 | 121 | 1000
Ullon | 134 | 600 | 128 | 1600 | Bakulia | 133 | 1830 | 125 | 300
Hasnabad | 136 | 500 | 128 | 1600 | Julda | 135 | 1400 | 125 | 500
Magbazar | 132 | 500 | 127 | 1600 | TK Chemical | 138 | 1400 | 127 | 700
Maniknagar | 135 | 500 | 130 | 1600 | Modern Steel | 134 | 1830 | 126 | 600
Bangabhaban | 138 | 500 | 127 | 1600 | Shahmirpur | 135 | 1830 | 125 | 600
Narinda | 132 | 600 | 127 | 1700 | Khagrachhari | 135 | 1400 | 128 | 400
Dhanmondi | 135 | 500 | 130 | 1600 | Matarbari | 131 | 1400 | 120 | 600
Lalbag | 138 | 500 | 127 | 1600 | Baroiar Hat | 134 | 100 | 130 | 1100
Madartek | 132 | 600 | 127 | 1700 | Rangamati | 135 | 1400 | 126 | 900
Mirpur | 132 | 300 | 123 | 1600 | Goalpara | 137 | 100 | 127 | 700
Kalyanpur | 134 | 400 | 127 | 1700 | Central s/s | 137 | 1800 | 126 | 1300
Gulshan | 132 | 300 | 127 | 1200 | Noapara | 135 | 2200 | 122 | 1300
Uttara | 133 | 400 | 125 | 1100 | Jessore | 130 | 1500 | 118 | 800
Uttara(New) | 131 | 400 | 125 | 1200 | Jhenida | 131 | 1500 | 118 | 700
Kamrangirchar | 137 | 500 | 128 | 1600 | Bottail | 138 | 100 | 129 | 1300
Savar | 129 | 100 | 124 | 1000 | G.K.Project | 141 | 300 | 137 | 800
Bhasantec | 133 | 200 | 126 | 1200 | Faridpur | 133 | 200 | 125 | 2000
Agargaon | 134 | 600 | 127 | 1200 | Madaripur | 135 | 1600 | 127 | 2000
Satmosjid | 133 | 200 | 127 | 1200 | Gopalganj | 138 | 1700 | 127 | 700
Tongi | 135 | 400 | 128 | 1500 | Bagerhat | 136 | 2200 | 127 | 600
Kabirpur | 134 | 100 | 130 | 1900 | Mongla | 133 | 1000 | 122 | 1900
Basundhara | 130 | 300 | 124 | 1600 | Satkhira | 135 | 1000 | 126 | 1300
Manikganj | 139 | 100 | 135 | 1800 | Gallamari | 137 | 1500 | 127 | 1300
Joydevpur | 140 | 1900 | 135 | 900 | Magura | 135 | 100 | 121 | 1900
New Tongi | 132 | 100 | 127 | 1600 | Chuadanga | 134 | 300 | 119 | 830
Kodda | 137 | 1400 | 133 | 700 | Barisal | 137 | 1000 | 133 | 2100
Dhamrai | 134 | 200 | 129 | 1900 | Patuakhali | 135 | 2200 | 125 | 2000
Tangail | 135 | 100 | 128 | 700 | Bhandaria | 136 | 400 | 124 | 1300
Mymensing | 130 | 1500 | 120 | 700 | Ishurdi | 139 | 100 | 133 | 1900
Kishorganj | 133 | 100 | 126 | 700 | Ruppur Paromanobik | 140 | 100 | 135 | 2000
Netrokona | 129 | 300 | 120 | 700 | Natore | 136 | 200 | 127 | 800
Jamalpur | 137 | 1500 | 116 | 700 | Bogra | 132 | 1500 | 113 | 700
Sherpur | 135 | 1500 | 119 | 700 | Noagaon | 128 | 1500 | 110 | 700
Srimongal | 140 | 200 | 136 | 1830 | Rajshahi | 134 | 1800 | 126 | 1200
Shahjibazar | 138 | 100 | 135 | 700 | C.Nawabganj | 132 | 1800 | 123 | 1300
Fenchuganj | 138 | 100 | 135 | 900 | Amnura | 136 | 1800 | 126 | 1600
Khulawara | 137 | 100 | 135 | 1600 | Pabna | 134 | 100 | 126 | 2000
Sylhet | 135 | 100 | 134 | 1800 | Shahjadpur | 142 | 100 | 135 | 1830
Chatak | 136 | 100 | 134 | 1800 | Serajganj | 133 | 200 | 122 | 700
Sunamganj | 137 | 700 | 133 | 1800 | Niyamatpur | 120 | 1500 | 102 | 1800
Biani Bazar | 137 | 100 | 133 | 1800 | Joypurhat | 126 | 200 | 106 | 700
Cumilla(s) | 127 | 700 | 123 | 1800 | Rangpur | 124 | 400 | 107 | 1900
Cumilla(n) | 140 | 700 | 138 | 1100 | Lalmonirhat | 120 | 400 | 98 | 1900
Chandpur | 140 | 1500 | 138 | 800 | Saidpur | 125 | 500 | 111 | 1200
Feni | 135 | 1400 | 128 | 2000 | Purbasadipur | 126 | 500 | 105 | 1300
Chowmuhani | 133 | 1830 | 130 | 2100 | Thakurgaon | 120 | 300 | 95 | 1930
Ashuganj | 140 | 100 | 137 | 700 | Palashbari | 129 | 500 | 112 | 1900
Daudkandi | 137 | 700 | 133 | 1100 | Barapukuria | 128 | 1500 | 117 | 1300
B.Baria | 137 | 100 | 133 | 700 | Panchagar | 116 | 500 | 93 | 1900
[5 empty] | Joldhaka | 123 | 300 | 110 | 1000

## L-Curve
Date | 2019-01-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 620 | 5240 | 1611 | 6851 |  |  |  | QF-LDC-12
0:30 | 590 | 5037.5 | 1526.5 | 6564 | Date: | 2019-01-27
1:00 | 560 | 4835 | 1442 | 6277
1:30 | 555 | 4699.5 | 1409 | 6108.5
2:00 | 550 | 4564 | 1376 | 5940
2:30 | 545 | 4507.5 | 1348.5 | 5856 | [5 empty] | Gen. at Eve. Peak | 8814 | 8814 MW (19:00 )
3:00 | 540 | 4451 | 1321 | 5772 | [6 empty] | 19:00
3:30 | 540 | 4395 | 1313 | 5708 | [5 empty] | Gen. at Day Peak | 7189.5 | 7189.5 MW (12:00 )
4:00 | 540 | 4339 | 1305 | 5644 | [6 empty] | 12:00
4:30 | 550 | 4349 | 1294 | 5643 | [5 empty] | Highest Generation | 8814
5:00 | 560 | 4359 | 1283 | 5642 | [6 empty] | 19:00
5:30 | 585 | 4498.5 | 1312.5 | 5811
6:00 | 610 | 4638 | 1342 | 5980
6:30 | 505 | 4599.05 | 1601.5 | 6200.55
7:00 | 400 | 4560.1 | 1861 | 6421.1
7:30 | 430 | 4689.6 | 1872 | 6561.6
8:00 | 460 | 4819.1 | 1883 | 6702.1
8:30 | 365 | 4851.95 | 1919.5 | 6771.45
9:00 | 270 | 4884.8 | 1956 | 6840.8
9:30 | 265 | 4984.95 | 1961.5 | 6946.45
10:00 | 260 | 5085.1 | 1967 | 7052.1
10:30 | 285 | 5129.85 | 1904 | 7033.85
11:00 | 310 | 5174.6 | 1841 | 7015.6
11:30 | 325 | 5252.55 | 1850 | 7102.55
12:00 | 340 | 5330.5 | 1859 | 7189.5
12:30 | 410 | 5409.95 | 1843 | 7252.95
13:00 | 480 | 5489.4 | 1827 | 7316.4
13:30 | 445 | 5317.1 | 1815 | 7132.1
14:00 | 410 | 5144.8 | 1803 | 6947.8
14:30 | 375 | 5197.5 | 1786 | 6983.5
15:00 | 340 | 5250.2 | 1769 | 7019.2
15:30 | 340 | 5233.45 | 1719 | 6952.45
16:00 | 340 | 5216.7 | 1669 | 6885.7
16:30 | 370 | 5284.6 | 1692 | 6976.6
17:00 | 400 | 5352.5 | 1715 | 7067.5
17:30 | 420 | 5699.75 | 2003.5 | 7703.25
18:00 | 440 | 6047 | 2292 | 8339
18:30 | 530 | 6258.5 | 2318 | 8576.5
19:00 | 620 | 6470 | 2344 | 8814
19:30 | 610 | 6353 | 2378 | 8731
20:00 | 620 | 6412 | 2329 | 8741 |  |  |  | Executive Engineer
20:30 | 600 | 6357.5 | 2340.5 | 8698 |  |  |  | Network Operation Division
21:00 | 580 | 6303 | 2352 | 8655
21:30 | 530 | 5996 | 2266.5 | 8262.5
22:00 | 480 | 5689 | 2181 | 7870 |  |  |  |  | Page 6 of 7
22:30 | 460 | 5495.5 | 2067.5 | 7563
23:00 | 440 | 5302 | 1954 | 7256
23:30 | 530 | 5271 | 1782.5 | 7053.5
24:00 | 620 | 5240 | 1611 | 6851
8814 MW (19:00 )
7189.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-27 |  | Energy | 171179591
[10 empty] | 2019-01-27 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3914 | 406 | 1661 | 548 | 149 | 77 | 0 | 0 | 96
0:30 | 3868 | 356.5 | 1599 | 405.5 | 149 | 76 | 19 | 0 | 91 | Date: | 2019-01-27
1:00 | 3822 | 307 | 1537 | 263 | 149 | 75 | 38 | 0 | 86
1:30 | 3805 | 307 | 1437.5 | 219 | 149 | 75 | 32 | 0 | 84 | [7 empty] | Total Energy | 171.1796 | Total Energy Gen 171.180 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.180 MKWHr
2:00 | 3788 | 307 | 1338 | 175 | 149 | 75 | 26 | 0 | 82 | [7 empty] | Energy not Served | 0
2:30 | 3783 | 309 | 1292.5 | 153 | 149.5 | 75 | 13 | 0 | 81 | [7 empty] | Energy Requirement | 171.1796
3:00 | 3778 | 311 | 1247 | 131 | 150 | 75 | 0 | 0 | 80
3:30 | 3739 | 311 | 1227.5 | 127 | 149.5 | 75 | 0 | 0 | 79 | [6 empty] | Shortage
4:00 | 3700 | 311 | 1208 | 123 | 149 | 75 | 0 | 0 | 78
4:30 | 3708.5 | 311 | 1204.5 | 115 | 149 | 75 | 0 | 0 | 80
5:00 | 3717 | 311 | 1201 | 107 | 149 | 75 | 0 | 0 | 82
5:30 | 3808.5 | 311 | 1246.5 | 137 | 149.5 | 75.5 | 0 | 0 | 83
6:00 | 3900 | 311 | 1292 | 167 | 150 | 76 | 0 | 0 | 84
6:30 | 3751.5 | 457 | 1363.5 | 292 | 150 | 76 | 25 | 0 | 85 |  |  |  |  | Coal
7:00 | 3603 | 603 | 1435 | 417 | 150 | 76 | 50 | 0 | 86
7:30 | 3643.5 | 603 | 1413.5 | 533 | 149.5 | 76 | 50 | 0 | 89 |  |  |  | Oil |  |  |  | ,
8:00 | 3684 | 603 | 1392 | 649 | 149 | 76 | 50 | 0 | 92
8:30 | 3731 | 603.5 | 1349 | 693 | 149.5 | 75 | 64.5 | 0 | 96
9:00 | 3778 | 604 | 1306 | 737 | 150 | 74 | 79 | 0 | 100
9:30 | 3878.5 | 603.5 | 1272.5 | 787.5 | 149.5 | 74 | 66.5 | 0 | 99
10:00 | 3979 | 603 | 1239 | 838 | 149 | 74 | 54 | 0 | 98
10:30 | 3955 | 603.5 | 1262.5 | 830 | 149 | 74 | 41.5 | 0 | 99
11:00 | 3931 | 604 | 1286 | 822 | 149 | 74 | 29 | 0 | 100
11:30 | 3970 | 604 | 1308.5 | 845 | 149.5 | 74 | 32 | 0 | 99
12:00 | 4009 | 604 | 1331 | 868 | 150 | 74 | 35 | 0 | 98
12:30 | 3966 | 603.5 | 1405 | 904 | 149.5 | 74 | 32 | 0 | 99
13:00 | 3923 | 603 | 1479 | 940 | 149 | 74 | 29 | 0 | 100
13:30 | 3923 | 603 | 1479 | 940 | 149 | 74 | 29 | 0 | 100
14:00 | 3923 | 603 | 1479 | 940 | 149 | 74 | 29 | 0 | 100
14:30 | 3869.5 | 603.5 | 1384 | 927 | 149 | 78.5 | 38 | 0 | 102
15:00 | 3816 | 604 | 1289 | 914 | 149 | 83 | 47 | 0 | 104
15:30 | 3869 | 604 | 1298 | 786.5 | 149 | 82.5 | 51 | 0 | 102
16:00 | 3922 | 604 | 1307 | 659 | 149 | 82 | 55 | 0 | 100
16:30 | 3922.5 | 604 | 1368.5 | 672 | 149 | 82 | 74 | 0 | 100
17:00 | 3923 | 604 | 1430 | 685 | 149 | 82 | 93 | 0 | 100
17:30 | 3902.5 | 652 | 1355.5 | 1158.5 | 149 | 82 | 290 | 0 | 113
18:00 | 3882 | 700 | 1281 | 1632 | 149 | 82 | 487 | 0 | 126
18:30 | 3957 | 700 | 1372 | 1721 | 149 | 80 | 472.5 | 0 | 125
19:00 | 4032 | 700 | 1463 | 1810 | 149 | 78 | 458 | 0 | 124
19:30 | 4150 | 700 | 1596 | 1597 | 149 | 80 | 335 | 0 | 124
20:00 | 4200 | 700 | 1811 | 1374 | 149 | 77 | 308 | 0 | 122
20:30 | 4240 | 699.5 | 1832.5 | 1312 | 149.5 | 77 | 265.5 | 0 | 122
21:00 | 4280 | 699 | 1854 | 1250 | 150 | 77 | 223 | 0 | 122
21:30 | 4138.5 | 699.5 | 1787 | 1126.5 | 149.5 | 77 | 166.5 | 0 | 118
22:00 | 3997 | 700 | 1720 | 1003 | 149 | 77 | 110 | 0 | 114
22:30 | 3937 | 700 | 1681.5 | 854.5 | 149 | 77 | 55 | 0 | 109
23:00 | 3877 | 700 | 1643 | 706 | 149 | 77 | 0 | 0 | 104
23:30 | 3895.5 | 553 | 1652 | 627 | 149 | 77 | 0 | 0 | 100 | Max Temp. in Dhaka |  | 30.0° C
24:00 | 3914 | 406 | 1661 | 548 | 149 | 77 | 0 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 171.180 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.180 MKWHr
Note on W13: Author:

## Generation
2019-01-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 76 | 74 | 74 | 74 | 74 | 74 | 74 | 83 | 82 | 82 | 82 |  | 78 | 80 | 77 | 77 | 77 | 77 | 77 | 1766222
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 |  | 110 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2700000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [6 empty] | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 391860
| Teknaf Solartech 20MW | [6 empty] | 1.1 | 6.8 | 12.2 | 16.2 | 18.5 | 18.8 | 18 | 15.5 | 12 | 7 | 1.4 | 0 |  | 0 | [6 empty] | 127980
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 27 |  | 68 | 17 | 17 | 0 |  |  |  | 105843
12 | Hathazari peaking | [17 empty] | 37 |  | 57 | 0 | [5 empty] | 69632
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 6184
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 120 | 80 | 80 | 80 | 80 | 80 | 120 | 80 | 130 | 149 | 160 | 160 | 130 | 73 | 119 | 125 | 125 | 125 |  | 155 | 155 | 155 | 153 | 142 | 127 | 127 | 3036000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 120 | 120 | 120 | 160 | 160 | 160 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 170 | 220 | 220 | 220 | 220 | 150 | 150 | 3562492
18 | Summit Gazipur -2 | [15 empty] | 0 | 5 | 115 |  | 0 | [6 empty] | 215780
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 720000
21 | Ghorasal GT: Unit-3 | 218 | 218 | 218 | 218 | 219 | 218 | 218 | 138 | 138 | 141 | 136 | 136 | 137 | 137 | 137 | 138 | 138 | 137 |  | 137 | 137 | 137 | 137 | 136 | 136 | 136 | 4203300
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 270 | 270 | 300 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 330 | 330 | 380 | 350 |  | 330 | 370 | 380 | 380 | 300 | 300 | 300 | 7729490
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 144 | 150 | 150 | 150 | 150 | 2176900
30 | Ashuganj ST: Unit- 5 | 0 | [25 empty] | 50090
32 | Ashuganj Engines TSK | 36 | 36 | 36 | 33 | 33 | 33 | 31 | 31 | 30 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 33 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 790488
33 | Ashuganj CCPP 225 MW | 184 | 190 | 193 | 188 | 185 | 207 | 185 | 196 | 205 | 186 | 187 | 192 | 186 | 185 | 185 | 204 | 185 | 198 |  | 207 | 197 | 190 | 193 | 185 | 184 | 185 | 4638000
34 | Ashuganj CCPP(South) | 287 | 287 | 294 | 287 | 287 | 320 | 287 | 309 | 320 | 287 | 283 | 298 | 301 | 287 | 305 | 338 | 305 | 334 |  | 342 | 323 | 309 | 312 | 305 | 305 | 305 | 7334000
| Ashuganj CCPP(North) | 220 | 220 | 220 | 200 | 200 | 250 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6066400
35 | Ashuganj (Precision) 55MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 0 | 0 |  |  |  |  | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 156960
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 99 | 100 | 95 | 100 | 100 | 98 | 100 | 100 | 94 | 102 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2355570
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 350 | 350 | 348 | 350 | 348 | 362 | 358 | 357 | 350 | 365 | 345 | 351 | 352 | 315 | 300 | 355 | 360 | 350 |  | 365 | 370 | 365 | 365 | 349 | 348 | 350 | 8540160
40 | Meghnaghat CCPP 450MW | 360 | 330 | 330 | 300 | 300 | 380 | 380 | 350 | 350 | 400 | 400 | 400 | 420 | 360 | 360 | 390 | 430 | 340 |  | 340 | 340 | 450 | 450 | 450 | 370 | 340 | 8980125
41 | Haripur Power CCPP 360MW | 307 | 305 | 307 | 307 | 309 | 308 | 330 | 304 | 116 | 0 | 91 | 103 | 231 | 231 | 261 | 260 | 311 | 270 |  | 270 | 345 | 357 | 357 | 325 | 305 | 306 | 6287000
42 | Mymensingh RPCL 210MW | 171 | 186 | 186 | 186 | 201 | 213 | 216 | 203 | 185 | 185 | 183 | 181 | 173 | 173 | 173 | 177 | 182 | 183 |  | 181 | 168 | 170 | 179 | 182 | 183 | 184 | 4328320
43 | Haripur NEPC 110MW | [17 empty] | 13 |  | 0 | 0 | [5 empty] | 11400
44 | Fenchugonj CCPP-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 683000
45 | Fenchugonj CCPP-2 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1448040
46 | Shajibazar 330 MW | 95 | 95 | 99 | 94 | 98 | 96 | 86 | 100 | 106 | 96 | 96 | 101 | 96 | 95 | 96 | 104 | 95 | 102 |  | 103 | 99 | 103 | 101 | 96 | 97 | 98 | 2212000
47 | Shahjibazar GT: Unit- 8, 9
48 | Shahjibazar 86MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 |  | 40 | 40 | 84 | 84 | 84 | 86 | 86 | 798720
49 | Shahjibazar (EPL) 50MW | 49 | 49 | 5 | 5 | 5 | 5 | 47 | 47 | 47 | 48 | 48 | 46 | 46 | 47 | 20 | 20 | 20 | 20 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 885960
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 79 | 79 | 78 | 77 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 78 | 80 | 80 |  | 80 | 78 | 79 | 78 | 78 | 76 | 79 | 1938990
51 | Sylhet GT 20 MW | 0 | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 21 | 21 | 20 | 20 | 284000
52 | Sylhet (EPL) 50MW | 23 | 23 | 7 | 7 | 7 | 7 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 497040
53 | Sylhet (Desh) 10MW | 0 | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 151380
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236544
55 | Fenchugonj (Barakatullah) 51MW | 53 | 5 | 5 | 5 | 5 | 5 | 20 | 53 | 53 | 48 | 50 | 50 | 53 | 11 | 11 | 11 | 11 | 11 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 751200
56 | Shahjahanulla 25 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 570352
57 | Summit Bibiana- 2 | 270 | 270 | 280 | 290 | 280 | 290 | 260 | 280 | 300 | 300 | 280 | 300 | 290 | 270 | 290 | 270 | 290 | 260 |  | 310 | 315 | 290 | 310 | 250 | 265 | 285 | 7245700
58 | Southern 55MW | [17 empty] | 55 |  | 36 | 17 | 0 |  |  |  |  | 88510
59 | Sikalbaha (Energis) | 40 | 16 | 8 | 0 | 0 | 3 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 |  | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 806880
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 506400
61 | Narshingdi (Doreen) | 22 | 22 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 312804
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520956
63 | Tripura | 86 | 82 | 80 | 78 | 82 | 84 | 86 | 92 | 100 | 98 | 100 | 98 | 100 | 102 | 104 | 100 | 100 | 126 |  | 124 | 124 | 122 | 122 | 114 | 104 | 96 | 2462400
64 | Malancha, Ctg. EPZ (United) | 35 | 38 | 38 | 40 | 42 | 42 | 37 | 12 | 2 | 2 | 2 | 2 | 9 | 3 | 2 | 2 | 11 | 18 |  | 27 | 32 | 35 | 23 | 32 | 37 | 35 | 553920
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482400
66 | Feni, Mohipal (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 233820
67 | Jangalia (Summit) 33MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 19 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 266900
68 | Summit Cumilla 25MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 16 | 16 |  | 16 | 22 | 22 | 22 | 22 | 22 | 22 | 502670
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | 25 | 375000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 0 | 15 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 22 |  | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 554580
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 777168
72 | Summit Rupganj | 33 | 33 | 33 | 17 | 25 | 25 | 25 | 33 | 17 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 729500
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [17 empty] | 24 |  | 0 | [6 empty] | 43200
78 | Gazipur (RPCL) | [6 empty] | 2 | 21 | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 25 | 0 | 646776
79 | Kodda 149MW | [16 empty] | 0 | 60 |  | 84 | 84 | 80 | 16 | 0 |  |  | 217440
80 | Jamalpur 95MW | 0 |  |  |  | 0 | 5 | 16 | 62 | 83 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 80 | 16 | 16 | 1376640
81 | Lakdhanvi 52 MW | [11 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 |  | 22 | 0 | 0 |  |  |  |  | 81317
82 | Madanganj 102MW | [16 empty] | 3 | 40 |  | 80 | 0 | 0 |  |  |  |  | 151896
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 85 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 85 | 85 | 85 | 85 | 85 | 802544
85 | Keraniganj (Powerpac) 100MW | [16 empty] | 0 | 30 |  | 0 | [6 empty] | 55865
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [16 empty] | 3 | 26 |  | 12 | 0 | [5 empty] | 54720
88 | Ghorashal 78MW (MAX) | 20 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 28224
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [8 empty] | 15 | 15 | 15 | 45 | 60 | 60 | 60 | 60 | 60 | 70 |  | 70 | 70 | 40 | 40 | 40 | 0 |  | 660240
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 5 | 5 | 5 | 5 | 13 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 |  | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 763000
93 | Ashuganj (Midland) 51MW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 30 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 713404
94 | Gagnagar (Orion) | [9 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 40 |  | 91 | 0 | 0 | 7 | 102 | 74 | 7 | 378576
95 | Patenga 50MW | [6 empty] | 3 | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 19 | 23 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 825600
96 | Chattogram ECPV 108 MW | [11 empty] | 36 | 59 | 59 | 56 | 52 | 58 | 93 |  | 93 | 53 | 34 | 20 | 0 |  |  | 552000
97 | Katpotti 51 MW | [9 empty] | 0 | 4 | 6 | 18 | 18 | 18 | 18 | 18 | 18 |  | 45 | 47 | 47 | 0 |  |  |  | 237696
98 | Bosila 108MW | [9 empty] | 26 | 31 | 30 | 30 | 30 | 30 | 8 | 8 | 31 |  | 30 | 30 | 0 |  |  |  |  | 231360
99 | Madanganj-55 MW | [9 empty] | 0 | 20 | 30 | 30 | 30 | 15 | 15 | 15 | 17 |  | 15 | 15 | 0 | 0 | 55 | 55 | 40 | 401007
100 | Northern 55 MW | [8 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 55 |  | 54 | 55 | 37 | 0 |  |  |  | 290861
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 130 | 130 | 163 | 100 | 100 | 130 | 3013920
102 | Sarishabari (Solar) | [7 empty] | 0.3 | 0.6 | 1.9 | 2.1 | 1.7 | 1.4 | 1.3 | 1.2 | 0.7 | 0.1 | 0 |  | 0 | [6 empty] | 11700
103 | Banco Energy 54MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 18 | 54 | 54 | 54 | 54 | 54 | 18 | 18 | 54 |  | 54 | 54 | 36 | 18 | 18 | 18 | 18 | 531000
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [23 empty] | 0 |  |  | 3413
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 60 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 60 | 60 | 194 |  | 196 | 197 | 200 | 200 | 7 | 7 | 7 | 1732800
112 | Aggreko Aurahati 100MW | [22 empty] | 23 | 0
114 | Summit Gazipur-1 150MW | [9 empty] | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 73 | 123 | 120 | 139 | 32 | 0 |  | 586080
115 | Juldah 100 MW Unit-3 | 84 | 20 | 0 |  | 0 | 10 | 77 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 80 | 82 | 82 |  | 82 | 82 | 82 | 82 | 84 | 84 | 84 | 1608000
116 | Chandpur Desh 200MW | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 17 | 17 | 17 | 18 | 33 | 34 | 34 | 17 | 17 | 45 |  | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 811200
117 | Midland 150MW | [16 empty] | 0 | 57 |  | 72 | 72 | 40 | 19 | 0 |  |  | 205750
118 | Bibiyana-3 285MW | 270 | 285 | 305 | 305 | 304 | 314 | 91 | 250 | 318 | 316 | 309 | 305 | 302 | 285 | 304 | 301 | 308 | 307 |  | 306 | 309 | 312 | 313 | 210 | 181 | 181 | 6762700
120 | Eastern Zone Total | 4835 | 4564 | 4451 | 4339 | 4359 | 4638 | 4560.1 | 4819.1 | 4884.8 | 5085.1 | 5174.6 | 5330.5 | 5492.4 | 5144.8 | 5250.2 | 5216.7 | 5352.5 | 6047 |  | 6470 | 6353 | 6412 | 6303 | 5689 | 5302 | 5240 | 127326686
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [7 empty] | 16 | 16 | 16 | 4 | 0 |  |  |  |  | 8 | 65 |  | 99 | 99 | 85 | 49 | 19 | 0 |  | 381120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 2 | 44 |  | 42 | 23 | 4 | 0 |  |  |  | 84480
Khulna CCPP 225MW
129 | Labon Chora 105 MW |  |  |  |  | 0 | 2 | 70 | 105 | 105 | 105 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 90 |  | 90 | 105 | 105 | 105 | 105 | 70 | 44 | 863040
130
131
132
133
| Summit Barisal 110 MW | [10 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 60 |  | 112 | 110 | 110 | 110 | 110 | 64 | 64 | 704640
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 95 | 71 | 72 | 51 | 50 | 51 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 80 | 82 | 82 | 82 |  | 82 | 80 | 81 | 81 | 95 | 95 | 95 | 2006119
| Bhola CCPP 194MW | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 693000
140 | Bhola (Venture) 33MW | 14 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 13 | 15 | 16 | 16 | 16 | 14 | 13 | 11 | 14 | 17 |  | 19 | 19 | 14 | 16 | 14 | 15 | 14 | 326844
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 24 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 16 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 873000
143 | Gopalganj Peaking | [15 empty] | 8 | 35 | 72 |  | 76 | 80 | 76 | 76 | 70 | 0 |  | 388736
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 307 | 307 | 311 | 311 | 311 | 311 | 603 | 603 | 604 | 603 | 604 | 604 | 603 | 604 | 604 | 604 | 604 | 700 |  | 700 | 700 | 700 | 699 | 700 | 700 | 406 | 13194182
147 | Bheramara 360 MW | 280 | 250 | 230 | 230 | 230 | 230 | 260 | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 |  | 270 | 320 | 320 | 350 | 320 | 320 | 320 | 7261632
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 150 | 149 | 149 | 150 | 150 | 149 | 150 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 150 | 149 | 149 | 149 | 3663700
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 50 |  | 0 | 0 | 0 | 0 |  |  |  | 53338
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 178 | 180 | 180 | 183 | 180 | 187 | 185 | 179 | 188 | 191 | 178 | 198 | 186 | 159 | 153 | 158 | 156 | 146 |  | 160 | 165 | 172 | 192 | 179 | 178 | 181 | 4425745
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 178 | 179 | 179 | 182 | 180 | 187 | 184 | 179 | 188 | 198 | 178 | 182 | 182 | 160 | 152 | 157 | 156 | 146 |  | 189 | 196 | 181 | 192 | 179 | 177 | 180 | 4467309
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [16 empty] | 10 | 40 |  | 0 | 0 | 0 | 0 |  |  |  | 31729
162 | Bogra (GBB) | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 18 | 16 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 479280
163 | Bogra (EPL) | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 350280
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 8 | 0 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 205092
165 | Amnura 50MW | 40 | 40 | 24 | 24 | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 12 | 40 |  | 40 | 40 | 40 | 40 | 40 | 25 | 0 | 847020
166 | Katakhali (Northern) | [5 empty] | 16 | 50 | 50 | 50 | 50 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 24 | 0 | 0 | 0 |  |  |  | 350206
167 | Katakhali Peaking | [11 empty] | 6 | 0 | 0 | [12 empty] | 7480
168 | Santahar Peaking | 28 | 26 | 0 | 0 | 0 | 0 |  |  | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 0 |  |  | 444777
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 42 | 43 | 35 | 43 | 42 | 42 | 42 | 8 | 8 | 30 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 977280
170 | Chapainawabganj-100 MW | 10 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 51 | 25 | 0 | 0 | 0 | 0 |  |  |  | 102 |  | 102 | 102 | 102 | 102 | 40 | 0 |  | 690876
171 | Paramount Baghabari
172
173 | Rangpur GT
175 | Saidpur GT | [12 empty] | 0 | 19 | 18 | 18 | 17 | 18 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 82000
176
177
178
178 | Western Zone Total | 1442 | 1376 | 1321 | 1305 | 1283 | 1342 | 1861 | 1883 | 1956 | 1967 | 1841 | 1859 | 1827 | 1803 | 1769 | 1669 | 1715 | 2292 |  | 2344 | 2378 | 2329 | 2352 | 2181 | 1954 | 1611 | 43852905