## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: August 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-08-02 |  | 2025-07-01 |  | 2024-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16076.4 | 2025-08-11 | 16794 | 2025-07-23 | 14612 | 2024-08-31 | 16794 | 2025-07-23
|  |  | 19:30 Hr. |  | 21:00 Hr. |  | 19:30 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 9865.74 | 2025-08-08 | 9799.07 | 2025-07-25 | 9444 | 2024-08-03 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16076.4 | 2025-08-11 | 16794 | 2025-07-23 | 14612 | 2024-08-31 | 16794 | 2025-07-23
|  |  | 19:30 Hr. |  | 21:00 Hr. |  | 19:30 |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 14273.89 | 2025-08-12 | 14859 | 2025-07-23 | 13449 | 2024-08-15 | 14859 | 2025-07-23
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 16199.71 | 2025-08-11 | 17099.14 | 2025-07-23 | 15530 | 2024-08-15 | 17200 | 2024-04-29
|  |  | 19:30 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 15029.8061 |  | 14953.5771 |  | 13511.7742 |  | - | -
7 | Average Generation (MW) at Day Peak | 13104.8316 |  | 13322.5084 |  | 12004.0645 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 973 | 2025-08-29 | 976 | 2025-07-01 | 927 | 2024-08-07 | 973 | 2025-08-29
|  |  | 7:30 |  | 15:00 |  | 13:00 |  | 7:30
9 | Maximum Power Import from Tripura, India (MW) | 62 | 2025-08-18 | 64 | 2025-07-13 | 108 | 2024-08-14 | 194 | 12/06/19
|  |  | 13:00 |  | 20:00 |  | 16:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 197 | 2025-08-18 | 812 | 2025-07-21 | 1272 | 2024-08-15 | 4395 | 04/10/2022
|  |  | 20:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15945.99 | 2025-08-18 | 15152.08 | 2025-07-21 | 14198 | 45519 | 14965 | 2024-05-16
|  |  | 20:00 |  | 21:00 |  | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-08-01 | 0 | 2025-07-04 | 0 | 45506 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13620.22 | 2025-08-01 | 13879 | 2025-07-04 | 11816 | 2024-08-02 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 36 | 2025-08-28 | 190 | 2025-07-23 | 871 | 45518 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13864.61 | 2025-08-28 | 14859 | 2025-07-23 | 13188 | 45518 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-08-01 | 0 | 2025-07-04 | 0 | 45506 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11666.46 | 2025-08-01 | 12021 | 2025-07-04 | 10003 | 45506 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 13 |  | 24 |  | 26 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 1 |  | 4 |  | 25 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1209.5845 |  | 1285.2058 |  | 1275.7689 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 37.6999 |  | 42.7752 |  | 43.702 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1171.8847 |  | 1242.4306 |  | 1232.0669 |  | - | -
23 | Net Generation of IPP (MKWH) | 2717.094 |  | 3008.2106 |  | 3277.01 |  | - | -
23b | Net Generation by Generation Companies | 4555.8076 |  | 4093.7217 |  | 3001.2757
24 | Net Generation of REB (MKWH) | 48.2344 |  | 48.2102 |  | 76.5989 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 132.6744 |  | 135.6626 |  | 115.2578 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 8625.6951 |  | 8528.2357 |  | 7702.2094 |  | - | -
27 | Energy Generation by Gas (MKWH) | 4290.1188 |  | 4241.0786 |  | 3879.5447 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 12.0531 |  | 0.018 |  | 13.7151 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 935.2305 |  | 1124.286 |  | 1186.0914 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 162.1321 |  | 148.0037 |  | 155.7384 |  | - | -
31 | Energy Generation by Solar (MKWH) | 108.7313 |  | 99.5917 |  | 80.6135 |  | - | -
31b | Energy Generation by Wind (MKWH) | 10.2067 |  | 14.5906 |  | 14.3154 |  | - | -
32 | Energy Generation by Coal (MKWH) | 3144.9225 |  | 2943.4421 |  | 2415.8978 |  | - | -
33 | Enegry Import from India (MKWH) | 1458.9205 |  | 1545.2637 |  | 709.1439 |  | - | -
34 | Monthly Load Factor (%) | 84.6288 |  | 80.9643 |  | 82.4411 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: August 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16076.4 | 2025-08-11 | 19:30 Hr.
Generation Period
| Dhaka | MW | 5583.59
| Chattogram | MW | 1517.5
| Cumilla | MW | 1507.99
| Mymensingh | MW | 1221
| Sylhet | MW | 678
a) | Total supply in East zone | MW | 10508.08
| Khulna | MW | 1886.8
| Barisal | MW | 487
| Rajshahi | MW | 1586.4
| Rangpur | MW | 1011
b) | Total supply in West zone | MW | 4971.2
c) | Total supply in both zone ( a+b) | MW | 15479.28
Ref: | 27.21.0000.603.16.087.20.932 | Date: 15/09/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | -110 | 2025-08-20 | 22:00
| b) Ishurdi end | MW | 390 | 2025-08-07 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 998 | 2025-08-07 | 10:00
| b) Ishurdi end | MW | -48 | 2025-08-02 | 17:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0
| b) Ishurdi end | MKWH | 177.3593
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 170.843
| b) Ishurdi end | MKWH | 0
23 | Transmission loss of EWI/ NO-1 | % | 3.2
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 250 | 2025-08-20 | 21:00
| b)Serajganj end | MW | 740 | 2025-08-07 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2025-08-23 | 10:00
| b)Sirajganj end | MW | -106 | 2025-08-18 | 3:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 401.582
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 388.4315
30 | Transmission loss of EWI /NO-2 | % | 3.27%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2842 | 2025-08-24 | 13:00
|  | MW | 1824
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2822 | 2025-08-24 | 13:00
|  | MW | 1823
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 36792 | 2025-08-27 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 36670 | 2025-08-27
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 1026.009
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 1022.075
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.383%
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-08-27 14:12 | 2025-08-27 14:35 | 0.015972 | T | df/dt FBCPU | 44 | 16.8667 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-08-27 14:12 | 2025-08-27 14:22 | 0.0069444 | T | df/dt FBCPU | 51 | 8.5 | Power interruption
Tangail 132/33kV | Tr-3 | 2025-08-28 13:26 | 2025-08-28 13:42 | 0.011111 | T | 33kV feeder Fault RET 650 (Main-2 Protection) | 30 | 8 | Power interruption
Bajitpur 132/33kV | Tr-2(414T) | 2025-08-10 09:15 | 2025-08-11 14:28 | 1899-12-31 05:13 | T | Tripped | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-08-14 23:26 | 2025-08-15 00:30 | 0.044444 | T | Due to red hot maintenance at 33 KV tr-3 Bus section. | 45 | 48 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-08-06 19:22 | 2025-08-06 20:27 | 0.045139 | T | Tripped | 45 | 0 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-08-05 10:18 | 2025-08-05 12:36 | 0.095833 | T | GT-3, 33Kv LA change(R& Y) phage | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2025-08-06 15:13 | 2025-08-06 16:30 | 0.053472 | E/O | 33KV Isulator mantence | 30 | 38.5 | Power interruption
Tangail 132/33kV | Tr-1 | 2025-08-15 08:30 | 2025-08-15 10:28 | 0.081944 | E/O | 33 kv bus Maintenance | 60 | 118 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-08-15 08:31 | 2025-08-15 10:28 | 0.08125 | E/O | 33 bus maintenace | 60 | 117 | Power interruption
Tongi 230/132/33kV | T-02 | 2025-08-09 21:05 | 2025-08-09 23:22 | 0.095139 | E/O | Relay Setting work. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 17:58 |  | Unserved Energy: |  | 354.8667
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2025-08-08 07:17 | 2025-08-08 08:30 | 0.050694 | T | 33 KV incomer Breaker trip No signal | 0 | 0 | No interruption
Bhulta 132/33kV | GT1 | 2025-08-08 09:29 | 2025-08-08 12:50 | 0.13958 | T | 33 KV incomer breaker Trip No | 58 | 194.3 | Power interruption
Bhulta 132/33kV | GT2 | 2025-08-08 09:29 | 2025-08-08 20:21 | 0.45278 | T | 33 KV incomer breaker Trip No | 0 | 0 | No interruption
Bhulta 132/33kV | GT1 | 2025-08-08 15:30 | 2025-08-08 20:21 | 0.20208 | T | 33 KV incomer of GT-1 CB Trip No | 80 | 388 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-08-05 02:23 | 2025-08-05 06:38 | 0.17708 | T | 33kv outgoing-1 PBS Earth fault SIEMENS | 35 | 148.75 | Power interruption
Keranigonj 230/132/33kV | TR-2 | 2025-08-17 07:26 | 2025-08-17 07:50 | 0.016667 | T | Due to PBS 33kV feeder fault. 86.1 Trip Relay Operated | 36 | 14.4 | Power interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-08-30 20:32 | 2025-08-31 22:25 | 1899-12-31 01:53 | T | Unknown Micom P632 | 0 | 0 | No interruption
Mogbazar 132/33kV | GT-1 | 2025-08-12 11:32 | 2025-08-12 12:00 | 0.019444 | T | Object fall on 132kv BUS BUS BAR PROTECTION OPERATED | 50 | 23.3333 | Power interruption
Mogbazar 132/33kV | GT-2 | 2025-08-12 11:32 | 2025-08-12 12:03 | 0.021528 | T | Object fall on 132kv BUS BUSBAR PROTECTION OPERATED | 50 | 25.8333 | Power interruption
Mogbazar 132/33kV | GT-3 | 2025-08-12 11:32 | 2025-08-12 12:05 | 0.022917 | T | Object fall on 132kv BUS BUSBAR PROTECTION OPERATED | 45 | 24.75 | Power interruption
Shyampur 230/132kV | Bus-1 (132kV) | 2025-08-14 06:53 | 2025-08-14 18:25 | 0.48056 | T | busber protection | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-1 | 2025-08-14 06:53 | 2025-08-14 12:05 | 0.21667 | T | busber protection | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-08-18 09:10 | 2025-08-18 09:20 | 0.0069444 | T | Due to PBS Langolbandh Feeder Trip D/R Overcurrent Relay & E/F Relay | 53 | 8.8333 | Power interruption
Narshingdi 132/33kV | T-1 | 2025-08-20 19:02 | 2025-08-20 20:37 | 0.065972 | E/O | নরসিংদী ১৩২ কেভি গ্রিড উপকেন্দ্রের T-1 ট্রান্সফরমারের ৩৩ কেভি বাস এর Y-Phase T - Clamp Maintenance Work by PBS. | 55 | 87.0833 | Power interruption
Nawabganj 132/33kV | TR-1 | 2025-08-10 10:36 | 2025-08-10 11:22 | 0.066667 | E/O | Due to red hot maintenance on incomer-1 CB outgoing point. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 00:26 |  | Unserved Energy: |  | 915.2833
Chattogram Grid Circle :
Coxsbazar 132/33kV | 405T-T1 | 2025-08-31 20:24 | 2025-08-31 21:36 | 0.05 | T | Over current MCGG | 36 | 43.2 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-08-31 05:08 | 2025-08-31 05:45 | 0.025694 | T | Lohaghara PBS 33kv Feeder Fault. SIEMENS SIPROTEC (7SJ81) Relay. | 62 | 38.2333 | Power interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-08-09 16:33 | 2025-08-09 18:20 | 0.074306 | E/O | 33kv B phase connector maintainance | 0 | 0 | No interruption
Khulshi 132/33kV | 425T(BSRM) | 2025-08-25 15:47 | 2025-08-25 16:17 | 0.020833 | E/O | Breather change of 33/0.4 kV Auxiliary Transformer of T-3(BSRM). | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-08-17 08:52 | 2025-08-17 12:22 | 0.14583 | E/O | 33 KV Bus Maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-08-17 12:40 | 2025-08-17 16:57 | 0.17847 | E/O | 33 KV Bus Maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2025-08-07 11:24 | 2025-08-07 14:24 | 0.125 | E/O | Shutdown for BPDB Feeder Bus Isolator Replacement Works. | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2025-08-07 15:02 | 2025-08-07 19:27 | 0.18403 | E/O | Red Hot on Secondary Side of TR-02. | 0 | 0 | No interruption
|  |  | Total : | 0.80417 |  | Unserved Energy: |  | 81.4333
Cumilla Grid Circle :
Cumilla(S) 132/33kV | TR-1 | 2025-08-30 05:46 | 2025-08-30 06:00 | 0.0097222 | T | Chowddogram REB feeder Not trip REF615 | 20 | 4.6667 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-08-10 18:32 | 2025-08-10 18:58 | 0.018056 | T | Oil temperature Transformer -2 differential protection Relay | 6 | 2.6 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-08-03 04:16 | 2025-08-03 05:48 | 0.063889 | T | none lockout relay, OLTC Bucholz. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-08-04 12:33 | 2025-08-11 18:34 | 1900-01-06 06:01 | T | 33 KV CT Blast Over Current Earth Fault Relay, Lockout Relay, Siemens Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-04 12:33 | 2025-08-04 13:32 | 0.040972 | T | 33 KV CT Blast in B phase Over Current Earth Fault Relay, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-04 12:33 | 2025-08-04 13:29 | 0.038889 | T | 33 KV CT Blast in B Phase Over Current Earth Fault Relay, Diff Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-13 13:37 | 2025-08-13 13:51 | 0.0097222 | T | Bisic Feder O/C,E/F Relay O/C E/F Relay, Lockout 33KV & 132 KV Side | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-08-29 10:21 | 2025-08-29 21:40 | 0.47153 | T | 33 kv PT Blast of PDB 132 kv OCEF, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-29 10:21 | 2025-08-29 11:11 | 0.034722 | T | 33 kv PT Blast of PDB 132 kv OCEF, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-29 10:21 | 2025-08-29 11:40 | 0.054861 | T | 33 kv PT Blast of PDB 132 kv over current Relay | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-08-09 07:13 | 2025-08-09 18:16 | 0.46042 | E/O | To fix red hot in incomer -02 D/S | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-08-18 06:54 | 2025-08-18 09:53 | 0.12431 | E/O | 33kv bus coupler 2 DS RED HOT Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 402T | 2025-08-02 21:20 | 2025-08-02 22:48 | 0.061111 | E/O | Hotspot maintenance | 15 | 22 | Power interruption
Brahmanbaria 132/33kV | 403T | 2025-08-30 10:30 | 2025-08-30 15:05 | 0.19097 | E/O | Hotspot maintenance | 16 | 73.3333 | Power interruption
Chandpur 132/33kV | 412T (T-2) | 2025-08-10 17:01 | 2025-08-13 13:14 | 1900-01-01 20:13 | E/O | None | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2025-08-12 14:15 | 2025-08-12 16:25 | 0.090278 | E/O | Due to Maintenance work at 33 Kv VCB | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-3 | 2025-08-25 20:44 | 2025-08-25 21:45 | 0.042361 | E/O | 132/33 kv Transformer-3 Shutdown 33KV load side for PBS -3 | 28 | 28.4667 | Power interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-08-12 12:13 | 2025-08-12 13:28 | 0.052083 | E/O | 33kv bus S/D for pbs PT check. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 20:34 |  | Unserved Energy: |  | 131.0667
Khulna Grid Circle :
Barishal 132/33kV | T-1 (405T) | 2025-08-07 08:10 | 2025-08-07 08:26 | 0.011111 | T | Polaspur 33 kv feeder fault Lockout | 46 | 12.2667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-08-21 03:37 | 2025-08-21 03:47 | 0.0069444 | T | 33 kv wzpdco T4 feeder faulty trip Ins O/c,deff O/c | 38 | 6.3333 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-08-27 19:36 | 2025-08-27 19:48 | 0.0083333 | T | 33 kV T-4 Post insulator crack. Lockout. | 45 | 9 | Power interruption
Gollamari 132/33kV | Tr-1 | 2025-08-20 17:10 | 2025-08-20 17:29 | 0.013194 | T | Pbs sadar feeder 50/51 OC/EF | 68 | 21.5333 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-08-20 17:10 | 2025-08-20 17:30 | 0.013889 | T | Pbs sadar feeder 50/51 OC/EF | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-08-07 08:32 | 2025-08-07 08:55 | 0.015972 | T | Over current fault Lockout Relay | 12 | 4.6 | Power interruption
Noapara 132/33kV | T-1 | 2025-08-09 06:11 | 2025-08-09 06:25 | 0.0097222 | T | REB-2 (O/C ins: & E/F ins:) REB-4 (O/C ins: & E/F ins:) 33Kv feeder Fault. O/C | 15 | 3.5 | Power interruption
Noapara 132/33kV | T-2 | 2025-08-09 06:11 | 2025-08-09 06:25 | 0.0097222 | T | REB-2 (O/C ins: & E/F ins:) REB-4 (O/C ins: & E/F ins:) 33Kv feeder Fault. O/C | 15 | 3.5 | Power interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-08-05 21:23 | 2025-08-05 22:35 | 0.05 | E/O | 33 kv bus section 1&3 section DS red hot maintenance. | 18 | 21.6 | Power interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-08-05 21:24 | 2025-08-05 22:34 | 0.048611 | E/O | 33 kv bus section 1&3 section DS red hot maintenance. | 20 | 23.3333 | Power interruption
Barishal 230/132kV | ATR-2 | 2025-08-19 21:38 | 2025-08-19 22:42 | 0.044444 | E/O | Due to Red hot of Y-Phase of 230KV side. | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-08-02 15:29 | 2025-08-02 18:34 | 0.12847 | E/O | Bamna PBS 33 KV feeder Under Ground Cable Maintenance. | 10 | 30.8333 | Power interruption
Khulna (C) | TR-1 425T | 2025-08-04 06:02 | 2025-08-04 08:38 | 0.10833 | E/O | Redhot maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-08-31 06:50 | 2025-08-31 09:34 | 0.11389 | E/O | Hot Spot Maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-08-31 11:16 | 2025-08-31 13:12 | 0.080556 | E/O | Wz work purpose | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-08-01 08:51 | 2025-08-01 10:17 | 0.059722 | E/O | Hot spot maintenance | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-08-05 10:33 | 2025-08-05 12:52 | 0.096528 | E/O | To repair oil leakage | 0 | 0 | No interruption
|  |  | Total : | 0.81944 |  | Unserved Energy: |  | 136.5
HVDC Grid Circle :
BIPTC | 21T01 | 2025-08-27 06:46 | 2025-08-27 12:40 | 0.24583 | T | external protection trip Differential Relay | 348 | 2053.2 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-08-07 20:52 | 2025-08-07 22:09 | 0.053472 | E/O | Emergency Maintenance work | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-08-21 20:56 | 2025-08-21 21:47 | 0.035417 | E/O | 33kv Tr-2 Bus isolator B phase Red hot removing | 0 | 0 | No interruption
Bheramara 230/132kV | Transformer-1 | 2025-08-19 10:28 | 2025-08-19 13:27 | 0.12431 | E/O | Emergency Maintenance of DS1-20-89A | 0 | 0 | No interruption
Bheramara 230/132kV | Kushti | 2025-08-27 16:02 | 2025-08-27 18:46 | 0.11389 | E/O | Emergency Maintenance work | 0 | 0 | No interruption
BIPTC | Block-01, Trafo-02 | 2025-08-20 10:05 | 2025-08-20 12:44 | 0.11042 | E/O | Emergency Maintenance work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-08-10 13:07 | 2025-08-10 16:15 | 0.13056 | E/O | Oil leakage of 33kV CT. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-08-25 22:02 | 2025-09-06 16:01 | 1900-01-10 17:59 | E/O | DS 641s red hot | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-08-27 08:51 | 2025-08-27 11:07 | 0.094444 | E/O | Emergency Maintenance work | 35 | 79.3333 | Power interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-08-28 07:20 | 2025-08-28 09:03 | 0.071528 | E/O | 33kv Kaligong feeder LA Fault under 132kV T1 | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2025-08-31 07:16 | 2025-08-31 08:32 | 0.052778 | E/O | Emergency Maintenance work | 7 | 8.8667 | Power interruption
Kushtia 132/33kV | T2 | 2025-08-22 15:03 | 2025-08-22 18:42 | 0.15208 | E/O | Loop change inside CT and CB on the 33 kV side of T-2 Transformer | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramar | 2025-08-27 14:33 | 2025-08-27 15:53 | 0.055556 | E/O | Earthing Wire Connection | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Bheramar | 2025-08-27 16:01 | 2025-08-27 18:46 | 0.11458 | E/O | Emergency Maintenance work | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2025-08-14 11:25 | 2025-08-14 12:25 | 0.041667 | E/O | Emergency Maintenance work | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2025-08-23 19:48 | 2025-08-23 22:23 | 0.10764 | E/O | 33 kv CT R Phase hethot and flashing | 10 | 25.8333 | Power interruption
Pabna 132/33kV | T-3 | 2025-08-26 13:45 | 2025-08-26 15:12 | 0.060417 | E/O | Emergency Maintenance work | 20 | 29 | Power interruption
|  |  | Total : | 1900-01-12 07:32 |  | Unserved Energy: |  | 2196.2333
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-08-03 01:32 | 2025-08-03 04:00 | 0.10278 | T | Tr_4 trip due to conductor flashing between CT and lower contact of 33 KV CB at 33 KV NESCO Switching sub-station. 50/51 OC | 42 | 103.6 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2025-08-05 23:42 | 2025-08-06 00:06 | 0.016667 | T | Heavy raining & thundering. No relay operated. | 160 | 64 | Power interruption
Barapukuria 230/132/33kV | 230/132KV T-06, 723T | 2025-08-05 23:42 | 2025-08-06 00:06 | 0.016667 | T | Heavy raining & thundering. No relay Operated. | 200 | 80 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-08-04 05:36 | 2025-08-04 06:02 | 0.018056 | T | Bogura PBS-2 feeder fault under Ins.O/C & Ins.E/F. 50/51 trip | 20 | 8.6667 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-08-15 09:48 | 2025-08-15 10:20 | 0.022222 | T | Ins. O/C ,50/51 Trip Due to Bannani 33KV Feeder Fault. Ins. O/C ,50/51 Trip | 24 | 12.8 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-08-15 09:48 | 2025-08-15 10:20 | 0.022222 | T | Ins. O/C ,50/51 Trip Due to Bannani 33KV Feeder Fault. Ins. O/C ,50/51 Trip | 24.5 | 13.0667 | Power interruption
Bogura 132/33kV | Transformer-1 | 2025-08-23 17:08 | 2025-08-23 17:41 | 0.022917 | T | Shajahanpur PBS-1 feeder fault. SIPROTEC 7SJ81 | 37 | 20.35 | Power interruption
Bogura 230/132kV | T-01 | 2025-08-13 12:41 | 2025-08-13 13:05 | 0.016667 | T | Rain No Relay Operated | 0 | 0 | No interruption
Purbasadipur 132/33kV | Single Bus | 2025-08-05 23:43 | 2025-08-06 00:04 | 0.014583 | T | Grid fail (T2 & T3 transformer + Rangpur ckt trip in boropukuria 230kv grid substation). N/A | 200 | 70 | Power interruption
Saidpur 132/33kV | TR-4 (414T) | 2025-08-17 09:14 | 2025-08-17 09:26 | 0.0083333 | T | 33 kv Ghatabill feeder fault No | 18 | 3.6 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-08-03 09:42 | 2025-08-03 13:01 | 0.13819 | E/O | Conductor flashing between CT and lower contact of 33 KV circuit breaker at 33 KV NESCO Switching sub-station. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-08-23 06:08 | 2025-08-23 09:18 | 0.13194 | E/O | Red hot maintenance at 132 KV bushing of T-01 | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-08-05 13:10 | 2025-08-05 20:04 | 0.2875 | E/O | T-3 33kV CB & 33kV CT Loop Flashing. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-08-06 10:26 | 2025-08-06 10:40 | 0.0097222 | E/O | 33kV DS Operation | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) | 2025-08-09 06:20 | 2025-08-09 07:52 | 0.063889 | E/O | Red hot maintainanc | 29 | 44.4667 | Power interruption
Natore 132/33kV | TR-2 (415 T) | 2025-08-09 06:20 | 2025-08-09 07:53 | 0.064583 | E/O | Red hot maintainance | 0 | 0 | No interruption
Rahanpur 400/132kV | Bus Reactor 400 KV | 2025-08-26 15:26 | 2025-08-26 15:26 | 0 | E/O | WTI Temperature Rise | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2025-08-13 13:22 | 2025-08-13 14:40 | 0.054167 | E/O | 33kv Bus-2 S/D | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2025-08-11 22:22 | 2025-08-11 23:50 | 0.061111 | E/O | Red Hot has become visible at the R-Phase of the Raypur 33kV Feeder Raiser cable. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 01:44 |  | Unserved Energy: |  | 420.55
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-31 15:12 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-08-05 01:29 | 2025-08-05 02:48 | 0.054861 | T | Tripped | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-08-02 18:32 | 2025-08-02 18:50 | 0.0125 | T | Thundering | 30 | 9 | Power interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-08-02 18:32 | 2025-08-02 18:48 | 0.011111 | T | Thundering | 30 | 8 | Power interruption
Kaliakoir 400/230/132kV | Tangail-2 | 2025-08-07 13:08 | 2025-08-07 13:29 | 0.014583 | T | Tripped | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2025-08-17 08:31 | 2025-08-17 09:02 | 0.021528 | T | Tripped | 40 | 20.6667 | Power interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-08-17 08:31 | 2025-08-17 09:41 | 0.048611 | T | Tripped | 40 | 46.6667 | Power interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2025-08-18 02:30 | 2025-08-18 02:54 | 0.016667 | T | Tripped | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2025-08-18 12:08 | 2025-08-18 12:40 | 0.022222 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-08-14 17:24 | 2025-08-14 18:22 | 0.040278 | T | Tripped | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2025-08-21 06:23 | 2025-08-21 06:49 | 0.018056 | E/O | Ashuganj end busbar tree trimming. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-1 | 2025-08-13 14:50 | 2025-08-13 18:48 | 0.16528 | E/O | ROW Clearing. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Tongi 80 MW PS | 2025-08-12 16:04 | 2025-08-12 18:18 | 0.093056 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 0.51875 |  | Unserved Energy: |  | 84.3333
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-08-25 13:02 | 2025-08-25 16:20 | 0.1375 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-08-03 21:31 | 2025-08-04 08:24 | 0.45347 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-08-14 06:54 | 2025-08-14 07:12 | 0.0125 | T | Tripped | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2025-08-17 08:15 | 2025-08-17 11:29 | 0.13472 | T | Bad weather( rain & thundering) | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2025-08-23 11:17 | 2025-08-23 21:22 | 0.42014 | T | Heavy Rainfals,Bad Weather. | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 1 | 2025-08-12 11:32 | 2025-09-04 06:52 | 1900-01-21 19:20 | T | Object fall on 132kv BUS | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 2 | 2025-08-12 11:32 | 2025-08-12 11:32 | 0 | T | Object fall on 132kv BUS | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2025-08-24 15:01 | 2025-08-24 16:09 | 0.047222 | T | 132kv B phage current zero | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2025-08-25 12:15 | 2025-08-25 13:20 | 0.045139 | T | N/A | 0 | 0 | No interruption
Shitalakhya 132/33kV | 132 kV Digital Powerplant | 2025-08-30 11:20 | 2025-08-30 14:18 | 0.12361 | T | Tripping showing Relay "GR-B 3Ph (E/F)" | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-08-03 21:31 | 2025-08-06 17:18 | 1900-01-01 19:47 | T | Line Fault | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-08-14 06:53 | 2025-08-16 00:22 | 1899-12-31 17:29 | T | Relay Trip, R/Y/B ph pick up, Zone-2, SOTF, 4.3km | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-1(E06) | 2025-08-14 06:53 | 2025-08-14 11:05 | 0.175 | T | Tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-1 | 2025-08-03 22:03 | 2025-08-04 08:25 | 0.43194 | E/O | Haripur ckt-1 trip from Haripur side so for check line | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Shitalakhya 132 kv Ckt | 2025-08-09 20:17 | 2025-08-10 04:25 | 0.33889 | E/O | DS maintenance due to red hot | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Shitalakhya 132 kv Ckt | 2025-08-22 08:40 | 2025-08-22 16:39 | 0.33264 | E/O | Purpose of Haripur -Meghnaghat line S/D | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2025-08-24 15:02 | 2025-08-24 16:08 | 0.045833 | E/O | B-phase current zero occurred from Munshiganj ss side | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-08-09 03:20 | 2025-08-09 08:32 | 0.21667 | E/O | Haripur circuit over current | 0 | 0 | No interruption
|  |  | Total : | 1900-01-29 06:34 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2025-08-01 13:17 | 2025-08-01 15:00 | 0.071528 | T | 33 kv Incoming C.B flashing | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2025-08-03 17:12 | 2025-08-03 18:41 | 0.061806 | T | R and B phase fault, dist zone-01,z-com trip | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Old Madunaghat 230kV Ckt.-1 | 2025-08-07 12:15 | 2025-08-07 12:25 | 0.0069444 | T | None | 0 | 0 | No interruption
Baroirhat 132/33kV | Feni-1 | 2025-08-01 07:14 | 2025-08-01 11:39 | 0.18403 | E/O | Emergency maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Shahmirpur 2 | 2025-08-27 23:45 | 2025-08-28 01:13 | 0.061111 | E/O | Due to having continuous Flashing at LA counter Connection point of 132 KV julda-shahmirpur circuit-2 | 0 | 0 | No interruption
|  |  | Total : | 0.38542 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chowmuhani 132/33kV | Feni line-02 | 2025-08-31 13:14 | 2025-08-31 13:36 | 0.015278 | T | Distance Relay Trip A,B,C Distance Relay Trip 3PH Zone-2 Fault | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-08-31 14:13 | 2025-08-31 14:28 | 0.010417 | T | Distance Relay Tripped | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-08-18 04:38 | 2025-08-18 04:43 | 0.0034722 | T | Dif. E/F Trip | 0 | 0 | No interruption
Feni 132/33kV | Feni-Lanka HFO PS | 2025-08-09 11:15 | 2025-08-09 14:40 | 0.14236 | T | 1. Line differential protection operated 2. Distance protection operated 3. No MVOLT on line | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-2 | 2025-08-31 13:13 | 2025-08-31 13:36 | 0.015972 | T | Tripped | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-08-26 01:57 | 2025-08-26 02:21 | 0.016667 | T | Heavy rain | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-02 | 2025-08-26 01:57 | 2025-08-26 02:22 | 0.017361 | T | Heavy rain | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-08-26 01:57 | 2025-08-26 02:17 | 0.013889 | T | shahjibazar circuit-1 tripped showing A and B phase on distance relay | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2025-08-26 01:57 | 2025-08-26 02:17 | 0.013889 | T | shahjibazar circuit-2 tripped showing A and B phase on distance relay | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-08-18 04:38 | 2025-08-18 05:38 | 0.041667 | T | trip | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-08-18 08:59 | 2025-08-18 10:13 | 0.051389 | E/O | Red hot maintenance at Ashugonj end | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-08-26 08:19 | 2025-08-26 13:15 | 0.20556 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-08-26 08:19 | 2025-08-26 13:15 | 0.20556 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-08-27 15:10 | 2025-08-27 17:55 | 0.11458 | E/O | Distance Relay Failure Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-08-28 11:05 | 2025-08-28 15:47 | 0.19583 | E/O | Distance Relay Maintenance (Ramgonj Ckt-) | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-08-31 09:10 | 2025-08-31 23:48 | 0.60972 | E/O | Distance Relay Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-08-18 04:44 | 2025-08-18 05:36 | 0.036111 | E/O | After Shutdown | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 17:02 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-08-05 13:13 | 2025-08-05 17:40 | 0.18542 | T | Unknown | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-08-16 05:46 | 2025-08-16 05:58 | 0.0083333 | T | Unknown | 45 | 9 | Power interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-08-27 14:27 | 2025-08-27 18:28 | 0.16736 | E/O | Emergency maint.work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2025-08-13 07:04 | 2025-08-13 09:01 | 0.08125 | E/O | Due to Red hot maintenance for Noapara end. | 0 | 0 | No interruption
Payra 400kV | Line-1 (Amtoli) | 2025-08-07 20:28 | 2025-08-08 19:03 | 0.94097 | E/O | Due to the Red Hot in Payra Ckt-1 of Amtoli 400KV Switching station | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur - 2 | 2025-08-09 11:13 | 2025-08-09 12:43 | 0.0625 | E/O | Faridpur circuit-2 R-phase PT Red Hot maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 10:42 |  | Unserved Energy: |  | 9
HVDC Grid Circle :
BIPTC | Baharampur-4 | 2025-08-15 18:28 | 2025-08-16 10:54 | 0.68472 | T | Zone-01, R-phase tripped | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-08-25 12:57 | 2025-08-25 16:01 | 0.12778 | T | Tripped by CPRO4 Fault | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-08-25 23:00 | 2025-08-25 23:00 | 0 | T | Over current 50 CPRO4 Tripped | 0 | 0 | No interruption
BIPTC | 10CF16 | 2025-08-26 05:14 | 2025-08-27 14:52 | 1899-12-31 09:38 | T | C1 unbalance 60/61 instant L1 Tripped | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-08-31 06:14 | 2025-08-31 09:40 | 0.14306 | T | Tripped by lockout relay operated | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-08-02 16:39 | 2025-08-02 16:58 | 0.013194 | T | trip | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-08-25 13:01 | 2025-08-25 16:22 | 0.13958 | T | C-G Fault | 0 | 0 | No interruption
BIPTC | 20DF21 | 2025-08-10 17:02 | 2025-08-10 17:22 | 0.013889 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2025-08-15 22:12 | 2025-08-16 10:54 | 0.52917 | E/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-08-23 11:07 | 2025-08-27 17:59 | 1900-01-03 06:52 | E/O | Shutdown is taken for emergency maintenance work | 0 | 0 | No interruption
BIPTC | 10CF26 | 2025-08-31 08:35 | 2025-08-31 09:40 | 0.045139 | E/O | Shutdown is taken for emergency maintenance work | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2025-08-31 10:26 | 2025-08-31 20:10 | 0.40556 | E/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2025-08-24 11:39 | 2025-08-24 14:56 | 0.13681 | E/O | Emergency maint.work | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2025-08-24 11:39 | 2025-08-24 14:56 | 0.13681 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 01:31 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-08-05 23:42 | 2025-08-06 01:09 | 0.060417 | T | Heavy raining & thundering. | 83 | 120.35 | Power interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-08-09 00:59 | 2025-08-09 01:33 | 0.023611 | T | trip | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-08-09 00:59 | 2025-08-09 01:25 | 0.018056 | T | trip | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-08-26 13:34 | 2025-08-26 13:45 | 0.0076389 | T | trip | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Barapukuria-2 | 2025-08-05 23:43 | 2025-08-06 01:08 | 0.059028 | T | trip | 50 | 70.8333 | Power interruption
Rangpur 132/33kV | Rangpur-Barapukuria-1 | 2025-08-05 23:43 | 2025-08-05 23:58 | 0.010417 | T | trip | 50 | 12.5 | Power interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-01 | 2025-08-09 01:01 | 2025-08-09 01:37 | 0.025 | T | Over Current. | 165 | 99 | Power interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-08-09 01:01 | 2025-08-09 01:26 | 0.017361 | T | Over Load | 165 | 68.75 | Power interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-08-08 09:39 | 2025-08-08 12:16 | 0.10903 | E/O | Instruction by NLDC | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-08-23 14:26 | 2025-08-26 15:24 | 1900-01-02 00:58 | E/O | Emergency maint.work | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2025-08-14 11:04 | 2025-08-14 13:16 | 0.091667 | E/O | Redhot maintenance on R-ph DS connector. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 11:06 |  | Unserved Energy: |  | 371.4333
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-13 20:37 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 132kV Transformer-1 (405T1) | 2025-08-03 19:00 | 2025-08-03 21:35 | 2:35 | S/O | 132/33 kV Transformer-1 PRD Problem | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-02 | 2025-08-30 07:36 | 2025-08-30 13:09 | 5:33 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-08-30 14:27 | 2025-08-30 19:16 | 4:49 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus Coupler | 2025-08-02 13:09 | 2025-08-02 14:30 | 1:21 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-08-17 21:33 | 2025-08-17 22:30 | 0:57 | S/O | Red-hot Maintenance for PDB feeder. | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2025-08-17 21:34 | 2025-08-17 22:30 | 0:56 | S/O | Red-hot Maintenance for PDB feeder. | 10 | 9.3333 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2025-08-02 08:21 | 2025-08-02 11:27 | 3:06 | S/O | PBS work | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2025-08-19 06:51 | 2025-08-19 08:46 | 1:55 | S/O | Red-hot maintenance | 25 | 47.9167 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-08-26 06:19 | 2025-08-26 08:27 | 2:08 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-08-20 07:35 | 2025-08-20 08:47 | 1:12 | S/O | 33 kv jamuna feeder red hot. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2025-08-23 14:25 | 2025-08-23 15:36 | 1:11 | S/O | Red hot remove of 33kv Vabki feeder incooming D.S. | 12 | 14.2 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-08-07 08:35 | 2025-08-07 11:12 | 2:37 | S/O | Due to Red Hot Maintanence Work at 33 kV Ifad feeder. | 95 | 248.5833 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-08-12 06:41 | 2025-08-12 07:56 | 1:15 | S/O | 33KV mouchak feeder red hot maintenance | 25 | 31.25 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-08-12 21:05 | 2025-08-12 22:23 | 1:18 | S/O | 33 kv Ifad feeder bus DS redhot maintenance. | 80 | 104 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-08-17 18:07 | 2025-08-17 20:35 | 2:28 | S/O | Due to TR-3 ,33 kV Bus Red Hot maintenance | 40 | 98.6667 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-08-17 18:11 | 2025-08-17 20:33 | 2:22 | S/O | Due to TR-3, 33 kV Bus Red Hot maintenance | 90 | 213 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-08-31 18:09 | 2025-08-31 19:56 | 1:47 | S/O | Red Hot maintenance of TR-3 33 kV Bus section loop point | 20 | 35.6667 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-08-31 18:10 | 2025-08-31 19:55 | 1:45 | S/O | Red Hot maintenance of TR-3,33 kV Bus section loop point. | 50 | 87.5 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-08-26 09:26 | 2025-08-26 18:34 | 9:08 | S/O | IDRNPP project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-08-27 08:30 | 2025-08-27 18:34 | 10:04 | S/O | Project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-08-29 08:46 | 2025-08-29 18:50 | 10:04 | S/O | project work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-08-30 08:37 | 2025-08-30 19:44 | 11:07 | S/O | project work shutdown | 0 | 0 | No interruption
Kodda 132/33kV | Tr-5 (446T) | 2025-08-18 08:30 | 2025-08-18 12:51 | 4:21 | S/O | 33 KV BUS section 3 shutdown | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-08-06 07:01 | 2025-08-06 08:57 | 1:56 | S/O | OLTC CB change. | 15 | 29 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-08-09 06:15 | 2025-08-09 15:12 | 8:57 | S/O | Pbs 33kV bus working | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-08-12 12:21 | 2025-08-12 13:46 | 1:25 | S/O | 132kv ckt-2 পলিথিন অপসারণের জন্য | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-08-16 06:38 | 2025-08-16 17:44 | 11:06 | S/O | Pbs 33kV bus working | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-08-18 08:40 | 2025-08-18 10:21 | 1:41 | S/O | Maint.work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-08-30 10:50 | 2025-08-30 14:54 | 4:04 | S/O | For project punch points solve. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2025-08-18 06:10 | 2025-08-18 08:54 | 2:44 | S/O | High temperature maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-08-20 06:33 | 2025-08-20 09:06 | 2:33 | S/O | Due to High temperature mitigate work of 33kV Batirkal Feeder Bus-T(R-Ph) | 0 | 0 | No interruption
New Tongi | T2(413T) | 2025-08-01 10:34 | 2025-08-02 16:17 | 29:43 | S/O | DESCO AIS to GIS work. | 0 | 0 | No interruption
New Tongi | T1(403T) | 2025-08-03 11:35 | 2025-08-03 17:39 | 6:04 | S/O | For DESCO Project work | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-08-16 08:46 | 2025-08-16 14:20 | 5:34 | S/O | loop change of T-1 and T-2 Transformer. | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-08-16 09:01 | 2025-08-16 11:58 | 2:57 | S/O | loop change of T-2 Transformer. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-08-16 12:18 | 2025-08-16 14:09 | 1:51 | S/O | Loop change | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-08-17 15:30 | 2025-08-17 15:49 | 0:19 | S/O | OLTC Sample collection. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-08-17 15:32 | 2025-08-17 15:50 | 0:18 | S/O | OLTC Sample collection. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-08-29 06:44 | 2025-08-29 07:19 | 0:35 | S/O | Project work | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-08-14 09:22 | 2025-08-14 10:15 | 0:53 | S/O | Project work of PDB | 10 | 8.8333 | Power interruption
Tangail 132/33kV | Tr-1 | 2025-08-23 16:44 | 2025-08-23 17:38 | 0:54 | S/O | Red hot at 33KV Bus DS of 33KV Betka feeder. | 40 | 36 | Power interruption
Tongi 230/132/33kV | T-02 | 2025-08-09 16:18 | 2025-08-09 19:28 | 3:10 | S/O | Protection works | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 02:43 |  | Unserved Energy: |  | 963.95
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2025-08-08 21:02 | 2025-08-14 08:28 | 131:26 | S/O | 33 KV Bus at PBS Area Maintenance | 80 | 10514.6667 | Power interruption
Bhulta 132/33kV | GT2 | 2025-08-10 14:05 | 2025-08-10 14:05 | 0:00 | S/O | 33 KV Bus fault, which is connected GT-1. Which is controlling by PBS. | 50 | 0 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-08-13 12:29 | 2025-08-13 15:03 | 2:34 | S/O | To change the neutral PI of Transformer-02 for Project-01( Energypac). | 75 | 192.5 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-08-16 11:12 | 2025-08-16 14:48 | 3:36 | S/O | 33 kv CT, PT junction point tightening. | 55 | 198 | Power interruption
Haripur 230/132kV | Auto TR-1 | 2025-08-26 16:44 | 2025-08-26 17:42 | 0:58 | S/O | Maintenance Work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-08-03 09:35 | 2025-08-04 10:20 | 24:45 | S/O | Pbs maintainence | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-08-03 10:46 | 2025-08-03 19:45 | 8:59 | S/O | Rev.bus DS alignment correction | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2025-08-12 11:42 | 2025-08-12 17:01 | 5:19 | S/O | 33kv main bus D/S Maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2025-08-12 11:44 | 2025-08-12 17:02 | 5:18 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-2 | 2025-08-01 06:16 | 2025-08-01 11:15 | 4:59 | S/O | Red Hot Maintenance Work at R-phase | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-08-26 06:54 | 2025-08-26 10:43 | 3:49 | S/O | Due to maintenance of PBS 33kV feeders. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-2 | 2025-08-26 06:58 | 2025-08-26 10:49 | 3:51 | S/O | Due to maintenance of PBS 33kV feeders. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2025-08-29 06:22 | 2025-08-29 09:43 | 3:21 | S/O | GT-1 Bushing maintenance due to red hot. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-08-29 13:03 | 2025-08-30 20:31 | 31:28 | S/O | 33 kv Maniknagar Control room GIS work | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) | 2025-08-19 05:39 | 2025-08-19 07:49 | 2:10 | S/O | Maintenance Work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-08-01 06:19 | 2025-08-01 10:11 | 3:52 | S/O | Red hot problem. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -02 | 2025-08-27 06:52 | 2025-08-27 09:25 | 2:33 | S/O | Project work | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-08-12 09:23 | 2025-08-12 17:54 | 8:31 | S/O | Maintenance Work | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2025-08-12 16:15 | 2025-08-12 17:53 | 1:38 | S/O | Due to PBS Tr-4 33kV Y-phase Bus Isolator Change. | 0 | 0 | No interruption
Narshingdi 132/33kV | Bhu | 2025-08-14 15:27 | 2025-08-14 16:57 | 1:30 | S/O | A shutdown has been taken at 400kV Bhulta GSS for Bus DS Hotspot Maintenance of the 400kV Bhulta -Narsingdi Line. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2025-08-20 22:30 | 2025-08-21 01:08 | 2:38 | S/O | Maintenance work | 40 | 105.3333 | Power interruption
Rampura 230/132kV | NLDC Trafo | 2025-08-13 08:25 | 2025-08-14 17:48 | 33:23 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 04 | 2025-08-14 06:54 | 2025-08-14 10:40 | 3:46 | S/O | 33kv nldc feeder ct and cb change. | 0 | 0 | No interruption
Rampura 230/132kV | 132 kV Busbar-1 | 2025-08-22 06:40 | 2025-08-22 12:06 | 5:26 | S/O | Bus city (B phase) change in Basundhara ckt-1 side | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 | 2025-08-26 05:51 | 2025-08-26 08:31 | 2:40 | S/O | 132kV breaker loop maintenance | 0 | 0 | No interruption
Rampura 230/132kV | 132 kV Busbar-2 | 2025-08-26 05:54 | 2025-08-26 08:33 | 2:39 | S/O | Bus DS Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV | Bus-1 (132kV) | 2025-08-15 07:11 | 2025-08-15 09:25 | 2:14 | S/O | IR test of CB at E07-132kV Shyampur -01 | 0 | 0 | No interruption
Shyampur 230/132kV | Bus-1 (132kV) | 2025-08-25 11:23 | 2025-08-25 15:13 | 3:50 | S/O | CB Timing Test | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-08-02 08:16 | 2025-08-02 11:11 | 2:55 | S/O | Replacement of multifunctional meter | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2025-08-02 11:25 | 2025-08-02 13:23 | 1:58 | S/O | Replacement of multifunctional meter. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2025-08-11 10:25 | 2025-08-11 12:20 | 1:55 | S/O | PBS maintenance work at their bus coupler. Work done by PBS. | 55 | 105.4167 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-08-11 10:35 | 2025-08-11 12:50 | 2:15 | S/O | PBS maintenance work at their bus coupler. Work done by PBS. | 45 | 101.25 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2025-08-26 09:17 | 2025-08-26 11:01 | 1:44 | S/O | MIEZ feeder red hot maintenance under 33 KV T1 Bus section1 | 60 | 104 | Power interruption
Srinagar 132/33kV | Tr-01 | 2025-08-10 09:06 | 2025-08-10 11:00 | 1:54 | S/O | Red Hot Maintenance at 33 kv Bus-1 side by PBS. | 17 | 32.3 | Power interruption
Srinagar 132/33kV | Tr-02 | 2025-08-17 16:11 | 2025-08-17 17:47 | 1:36 | S/O | Red hot maintenance by Pbs. | 17.5 | 28 | Power interruption
Srinagar 132/33kV | 33 kV bus | 2025-08-17 16:15 | 2025-08-17 17:42 | 1:27 | S/O | Red hot maintenance by Pbs. | 0 | 0 | Power interruption
|  |  | Total : | 1900-01-12 10:57 |  | Unserved Energy: |  | 11381.4667
Chattogram Grid Circle :
Bakulia 132/33kV | T-3 (422T) | 2025-08-11 06:02 | 2025-08-11 07:15 | 1:13 | S/O | Emergency Hot Spot Maintenance of T-03 Secondary Side R-Phase Bushing. | 6 | 7.3 | Power interruption
Baroaulia 132/33kV | T-1(405T) | 2025-08-15 07:01 | 2025-08-15 09:50 | 2:49 | S/O | TR-01 Redhot Maintenance. | 10 | 28.1667 | Power interruption
Baroaulia 132/33kV | T-1(405T) | 2025-08-22 07:16 | 2025-08-22 08:28 | 1:12 | S/O | Redhot maintenance. | 15 | 18 | Power interruption
Baroirhat 132/33kV | TR-2, 416T | 2025-08-20 08:15 | 2025-08-20 12:05 | 3:50 | S/O | PBS maintenance work | 20 | 76.6667 | Power interruption
Coxsbazar 132/33kV | Main Bus | 2025-08-01 05:50 | 2025-08-01 13:00 | 7:10 | S/O | Patiya Grid substation Commission. | 95 | 680.8333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-08-15 00:44 | 2025-08-15 01:50 | 1:06 | S/O | Bandarban feeder CB loop maintenance work | 63 | 69.3 | Power interruption
Hathazari 230/132/33kV | T-01 | 2025-08-05 04:40 | 2025-08-05 15:50 | 11:10 | S/O | Y-phase red hot maintenance | 20 | 223.3333 | Power interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-01 | 2025-08-28 09:40 | 2025-08-28 17:30 | 7:50 | S/O | G2G CCCE Progect work | 0 | 0 | No interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-02 | 2025-08-29 09:30 | 2025-08-29 18:20 | 8:50 | S/O | G2G project by CCCE | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-08-27 10:06 | 2025-08-27 13:12 | 3:06 | S/O | for checking oil leakage of CT | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-3(725T) | 2025-08-02 10:20 | 2025-08-02 14:09 | 3:49 | S/O | SCADA Integration by CNTIC project | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-1(705T) | 2025-08-02 14:37 | 2025-08-02 16:54 | 2:17 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 06:22 |  |  |  | 1103.6
Cumilla Grid Circle :
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-08-11 08:54 | 2025-08-11 18:02 | 9:08 | S/O | Oil leakage & red hot maintenance work | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-08-23 08:45 | 2025-08-23 11:44 | 2:59 | S/O | 33 KV Incomer -01 Red hot Extinguish | 20 | 59.6667 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2025-08-10 15:05 | 2025-08-10 16:56 | 1:51 | S/O | For set up Digital energy meter and multifunction meter | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-08-13 10:22 | 2025-08-13 11:54 | 1:32 | S/O | New multifuntionong meter is being installed. | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2025-08-13 12:04 | 2025-08-13 13:14 | 1:10 | S/O | New multifuntionong meter is being installed. | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-08-13 13:14 | 2025-08-13 13:14 | 0:00 | S/O | 33 kv load side open | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-05 | 2025-08-02 08:55 | 2025-08-02 08:55 | 0:00 | S/O | 33kv Underground to Over head line replaced. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-08-02 08:55 | 2025-08-03 01:14 | 16:19 | S/O | maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-08-10 22:59 | 2025-08-11 00:24 | 1:25 | S/O | maintenance | 60 | 85 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2025-08-15 07:06 | 2025-08-15 15:13 | 8:07 | S/O | Bus Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-2 | 2025-08-15 07:50 | 2025-08-15 15:12 | 7:22 | S/O | Bus-1 DS maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2025-08-16 04:50 | 2025-08-16 10:31 | 5:41 | S/O | DS Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-01 | 2025-08-16 04:52 | 2025-08-16 10:15 | 5:23 | S/O | maintenance | 0 | 0 | No interruption
Feni 132/33kV | Bus-2 | 2025-08-01 07:07 | 2025-08-01 11:10 | 4:03 | S/O | For Red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-08-10 15:35 | 2025-08-10 16:30 | 0:55 | S/O | 33/11 kV PDB Feeder 33/11 kV T-1 Transformer DS to Bus LA Loop (Y-Phase) flashing & Cutup. | 16 | 14.6667 | Power interruption
Kasba 132/33kV | TR-1 | 2025-08-01 09:37 | 2025-08-01 10:31 | 0:54 | S/O | Shutdown taken by PBS for red hot maintenace | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2025-08-01 11:00 | 2025-08-01 11:52 | 0:52 | S/O | Kasba-2 feeder Isolator Jumper red hot maintenance by PBS. | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 | 2025-08-13 09:47 | 2025-08-13 12:37 | 2:50 | S/O | Oil temperature meter maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-08-15 07:59 | 2025-08-15 10:06 | 2:07 | S/O | Pbs feeder Red hot maintenance | 22 | 46.5667 | Power interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-08-27 19:47 | 2025-08-27 21:04 | 1:17 | S/O | maintenance | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-08-29 21:52 | 2025-08-29 23:02 | 1:10 | S/O | Red hot | 10 | 0 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2025-08-13 07:36 | 2025-08-13 08:11 | 0:35 | S/O | LT bushing red hot point maintenance | 20 | 11.6667 | Power interruption
Ramganj 132/33kV | Transformer -02 | 2025-08-14 06:54 | 2025-08-14 07:47 | 0:53 | S/O | LT Bushing red hot point maintenance | 20 | 17.6667 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-01 17:45 | 2025-08-01 18:10 | 0:25 | S/O | S/D taken By PDB | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-08-02 16:30 | 2025-08-02 19:08 | 2:38 | S/O | maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-02 16:35 | 2025-08-03 13:03 | 20:28 | S/O | maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-08-03 13:27 | 2025-08-03 21:15 | 7:48 | S/O | For CT checking | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-04 07:15 | 2025-08-04 09:45 | 2:30 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-04 07:23 | 2025-08-04 09:49 | 2:26 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-13 19:53 | 2025-08-13 22:00 | 2:07 | S/O | 33 kv Bus Red hot maitenance work by PBS. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-13 20:01 | 2025-08-13 22:01 | 2:00 | S/O | 33 kv Bus Red hot maitenance work by PBS. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-08-23 07:40 | 2025-08-23 09:38 | 1:58 | S/O | Shutdown taken by PBS. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-08-23 07:47 | 2025-08-23 09:42 | 1:55 | S/O | Shutdown taken by PBS. | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-08-09 07:44 | 2025-08-09 09:18 | 1:34 | S/O | T1 Transformer S/D due to PDB division 01 maintenance work . | 35 | 54.8333 | Power interruption
Sylhet 132/33kV | T2 | 2025-08-15 08:00 | 2025-08-15 09:09 | 1:09 | S/O | PDB Division 05 feeder maintenance work. | 10 | 11.5 | Power interruption
|  |  | Total : | 1900-01-04 03:31 |  |  |  | 301.5667
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-08-01 07:11 | 2025-08-01 11:36 | 4:25 | S/O | Condutor loop (B Phase) Replace of CT to CB | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-08-01 12:24 | 2025-08-01 12:49 | 0:25 | S/O | Same as LT | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-2 (413 T) | 2025-08-22 07:11 | 2025-08-22 09:28 | 2:17 | S/O | Maintenance work | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2025-08-02 22:03 | 2025-08-02 22:52 | 0:49 | S/O | To remove red hot problem of Jhalokathi 33kV feeder (WZPDCL). | 40 | 32.6667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-08-04 06:08 | 2025-08-04 07:51 | 1:43 | S/O | High temperature remedy work | 13 | 22.3167 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-08-21 15:08 | 2025-08-21 16:16 | 1:08 | S/O | 33 kV T4 post insulator change. | 15 | 17 | Power interruption | 14:29
Barishal 132/33kV | T-2 (415T) | 2025-08-28 16:06 | 2025-08-28 16:39 | 0:33 | S/O | 33kv T4 feeder post insulator repair. | 15 | 8.25 | Power interruption
Barishal 230/132kV | T-4 | 2025-08-09 07:55 | 2025-08-09 10:03 | 2:08 | S/O | 33kv Korapur feeder bus ds maintenance | 10 | 21.3333 | Power interruption
Barishal 230/132kV | ATR-1 | 2025-08-12 16:12 | 2025-08-12 17:36 | 1:24 | S/O | oil leakage repair of auxiliary transformer (LT Y- phase) | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2025-08-23 08:35 | 2025-08-23 10:45 | 2:10 | S/O | Redhot maintenance from pbs | 34 | 73.6667 | Power interruption
Barishal 230/132kV | T-5 | 2025-08-24 16:30 | 2025-08-24 17:52 | 1:22 | S/O | 33kv busbar section C DS Redhot maintenance by Barishal PBS -1 | 34 | 46.4667 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-08-04 10:16 | 2025-08-04 12:07 | 1:51 | S/O | To cheak and rectify the 33 kv CSE insulation & transformer oil leakage | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-08-04 12:23 | 2025-08-04 13:21 | 0:58 | S/O | Project work | 0 | 0 | No interruption
Borhanuddin 230/33kV | Tr-Load | 2025-08-30 07:17 | 2025-08-30 10:04 | 2:47 | S/O | Due to high temperature at 33kv bus. | 76 | 211.5333 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-08-09 07:32 | 2025-08-09 09:18 | 1:46 | S/O | Hot Spot Maintenance | 50 | 88.3333 | Power interruption
Faridpur 132/33kV | Transformer-3 | 2025-08-23 11:07 | 2025-08-23 14:10 | 3:03 | S/O | Red hot maintenance | 8 | 24.4 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-08-23 11:08 | 2025-08-23 15:55 | 4:47 | S/O | 33 kv bus section maintenance | 42 | 200.9 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-08-30 07:07 | 2025-08-30 09:49 | 2:42 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-08-25 08:03 | 2025-08-25 10:15 | 2:12 | S/O | Red hot maintenance (BPBS-2) | 30 | 66 | Power interruption
Gopalganj 132/33kV | T2 | 2025-08-31 07:15 | 2025-08-31 10:34 | 3:19 | S/O | Auxiliary 2 finger adjustment. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-08-16 08:17 | 2025-08-16 16:33 | 8:16 | S/O | Shutdown taken by Khulna PBS due to replace bus raiser and loop conductor. | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-08-21 07:30 | 2025-08-21 11:48 | 4:18 | S/O | Maintenance work of string cutting of t1 LT Bushing y phase. | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2025-08-22 09:45 | 2025-08-22 12:51 | 3:06 | S/O | Due to Hot Spot Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-08-23 09:40 | 2025-08-23 13:51 | 4:11 | S/O | Section DS and Faulty insulator Repair | 0 | 0 | No interruption
Madaripur 132/33kV | T3-426T | 2025-08-23 09:40 | 2025-08-23 16:15 | 6:35 | S/O | Section DS and Faulty insulator Repair | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-08-11 08:14 | 2025-08-11 11:05 | 2:51 | S/O | Maintenance work | 18 | 51.3 | Power interruption
Noapara 132/33kV | T-2 | 2025-08-13 15:43 | 2025-08-13 16:50 | 1:07 | S/O | REB-1 Feeder red hot maintenance of Y-Phase source side. | 15 | 16.75 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2025-08-07 09:37 | 2025-08-07 14:26 | 4:49 | S/O | High Temperature Maintenance. | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2025-08-28 07:05 | 2025-08-28 09:36 | 2:31 | S/O | High temperature maintenace. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-08-02 10:51 | 2025-08-02 16:37 | 5:46 | S/O | oil leakaOltcge observation | 0 | 0 | No interruption
Shariatpur 132/33kV | T2-416T | 2025-08-06 06:06 | 2025-08-06 09:07 | 3:01 | S/O | Pbs Maintanance Work. | 26 | 78.4333 | Power interruption
Shariatpur 132/33kV | T1-406T | 2025-08-20 09:18 | 2025-08-20 13:03 | 3:45 | S/O | Maintenance Work by PBS | 27 | 101.25 | Power interruption
|  |  | Total : | 1900-01-02 20:05 |  | Unserved Energy : |  | 1060.6
HVDC Grid Circle
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-08-08 07:23 | 2025-08-08 12:19 | 4:56 | S/O | Red hot Maintenance work. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-08-02 08:43 | 2025-08-02 15:23 | 6:40 | S/O | Maintanance Work. | 25 | 166.6667 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-08-10 06:53 | 2025-08-10 09:08 | 2:15 | S/O | Maintanance Work. | 16 | 36 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-08-11 16:42 | 2025-08-11 23:04 | 6:22 | S/O | Maintanance Work. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-08-11 23:19 | 2025-08-13 16:38 | 41:19 | S/O | New 132/33 kv x-former T-3 load shifting T-1 to T-3 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-08-12 16:33 | 2025-08-12 16:47 | 0:14 | S/O | Energy audit's meter inspection. | 36 | 8.4 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-08-13 16:31 | 2025-08-13 18:03 | 1:32 | S/O | Maintanance Work. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bus-1 | 2025-08-26 10:53 | 2025-08-26 12:46 | 1:53 | S/O | 641 DS red hot maintenance. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2025-08-26 10:52 | 2025-08-26 12:46 | 1:54 | S/O | for 132 KV bus Shutdown | 0 | 0 | No interruption
Jashore 132/33kV | T-2 | 2025-08-30 07:06 | 2025-08-30 11:06 | 4:00 | S/O | PBS work on 33 KV T2 Bus | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2025-08-04 06:35 | 2025-08-04 07:54 | 1:19 | S/O | Red hot maintenance by Wzpdcl | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2025-08-20 07:02 | 2025-08-20 09:28 | 2:26 | S/O | Housing feeder red hot maintenance | 18 | 43.8 | Power interruption
Magura 132/33kV | T-3 (425T) | 2025-08-15 08:55 | 2025-08-15 10:44 | 1:49 | S/O | 33kV Bus DS red hot maintenance of PBS | 20 | 36.3333 | Power interruption
|  |  | Total : | 1900-01-02 04:39 |  | Unserved Energy : |  | 291.2
Bogura Grid Circle:
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-08-29 06:35 | 2025-08-29 09:06 | 2:31 | S/O | LT bushing red hot maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2025-08-02 07:32 | 2025-08-02 11:55 | 4:23 | S/O | T-1 33kv PT change work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2025-08-29 08:55 | 2025-08-29 12:48 | 3:53 | S/O | leakage radiator replacement work. | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-08-06 10:42 | 2025-08-06 14:18 | 3:36 | S/O | Fire fighting system testing | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-08-07 09:40 | 2025-08-07 11:05 | 1:25 | S/O | water spray system testing | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-08-07 11:15 | 2025-08-07 14:24 | 3:09 | S/O | Fire fighting water spray testing | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-08-26 10:32 | 2025-08-26 17:36 | 7:04 | S/O | Temperature meter change | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2025-08-30 07:01 | 2025-08-30 13:32 | 6:31 | S/O | OPGW works | 23 | 149.8833 | Power interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2025-08-30 07:01 | 2025-08-30 13:32 | 6:31 | S/O | OPGW | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-08-16 08:41 | 2025-08-16 10:53 | 2:12 | S/O | 33 kv bus section-4 DS redhot problem. | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-08-27 11:06 | 2025-08-27 18:57 | 7:51 | S/O | DS QB-02 (132 KV ATR-02 Side) Magnatic contact change | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2025-08-14 08:25 | 2025-08-14 10:05 | 1:40 | S/O | 33KV BUS-2 S/D | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2025-08-26 10:10 | 2025-08-26 17:47 | 7:37 | S/O | QF- GMD-39 and as the instruction of ALDC Bogura (499264) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 10:23 |  | Unserved Energy : |  | 149.8833
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 898:40 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-08-25 10:42 | 2025-08-25 10:42 | 0:00 | S/O | EEGBPS প্রজেক্টের ২৩০ কেভি আমিনবাজার -কালিয়াকৈর সার্কিট -০২ এর LILO অংশে stringing কাজের জন্য। | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-08-11 11:14 | 2025-08-11 17:35 | 6:21 | S/O | NLDC Signal list End to End test | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-08-14 11:50 | 2025-08-14 17:12 | 5:22 | S/O | Development work | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-08-25 11:36 | 2025-08-25 19:23 | 7:47 | S/O | Nldc signal list end to end test | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2025-08-09 11:58 | 2025-08-09 16:26 | 4:28 | S/O | As per the instruction of NLDC, Mymensingh Circuit 2 has been Shutdown. | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-08-12 12:21 | 2025-08-12 13:17 | 0:56 | S/O | 132kv ckt-2 পলিথিন অপসারণের জন্য | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-08-18 08:40 | 2025-08-18 10:21 | 1:41 | S/O | 0 | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-08-23 06:22 | 2025-08-23 09:54 | 3:32 | S/O | Red hot maintenance CT & LA clump | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-2 | 2025-08-09 11:55 | 2025-08-09 16:26 | 4:31 | S/O | 0 | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2025-08-11 10:51 | 2025-08-11 16:17 | 5:26 | S/O | Kaliakair end really test. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-08-09 07:46 | 2025-08-09 16:03 | 8:17 | S/O | Shutdown taken for spmd works | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2025-08-25 15:42 | 2025-08-25 18:31 | 2:49 | S/O | Protection work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-08-27 09:55 | 2025-08-27 11:57 | 2:02 | S/O | 0 | 40 | 81.3333 | Power interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-08-31 15:24 | 2025-08-31 16:34 | 1:10 | S/O | Emergency Right of Way checking | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 06:22 |  | Unserved Energy: |  | 81.3333
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Hasnabad | 2025-08-23 07:17 | 2025-08-23 20:51 | 13:34 | S/O | for working purpose | 0 | 0 | No interruption
Gulshan 132/33kV | Rampura-2 | 2025-08-01 07:18 | 2025-08-03 06:28 | 47:10 | S/O | IVT Replacement Work Gulshan End. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-08-23 07:18 | 2025-08-23 20:20 | 13:02 | S/O | 76 no tower erection work. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-08-23 07:19 | 2025-08-23 20:20 | 13:01 | S/O | 76 no tower erection work. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2025-08-29 14:46 | 2025-08-29 16:30 | 1:44 | S/O | Hotspot Maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-2 | 2025-08-29 16:45 | 2025-08-29 19:06 | 2:21 | S/O | Hotspot Maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-08-01 07:15 | 2025-08-01 10:45 | 3:30 | S/O | Shutdown for maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-08-21 08:21 | 2025-08-21 12:25 | 4:04 | S/O | 400 kV Aminbazar-2 ckt shutdown to change Mid DS Finger | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Madunaghat 400KV Ckt-1 | 2025-08-30 07:54 | 2025-09-05 11:53 | 147:59 | S/O | Meghnaghat-Madunaghat line will be LILO at Karerhat Substation. | 0 | 0 | No interruption
Narshingdi 132/33kV | Haripur | 2025-08-14 15:26 | 2025-08-14 16:57 | 1:31 | S/O | A shutdown has been taken at 400kV Bhulta GSS for Bus DS Hotspot Maintenance of the 400kV Bhulta -Narsingdi Line. | 0 | 0 | No interruption
Rampura 230/132kV | Gulshan Ckt-02 | 2025-08-01 07:10 | 2025-08-02 20:59 | 37:49 | S/O | GIS IVT change in Gulshan SS | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2025-08-07 09:37 | 2025-08-11 09:36 | 95:59 | S/O | 0 | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-02 | 2025-08-22 06:40 | 2025-08-22 12:06 | 5:26 | S/O | Bus city (B phase) change in Basundhara ckt-1 side | 0 | 0 | No interruption
Shitalakhya 132/33kV | 132 kV Hasnabad | 2025-08-23 07:14 | 2025-08-23 20:57 | 13:43 | S/O | Increasing for Tower height | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2025-08-01 07:14 | 2025-08-01 10:46 | 3:32 | S/O | Red Hot maintenance at Meghnaghat 400KV End. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-08-25 11:12 | 2025-08-25 15:40 | 4:28 | S/O | CB Timing Test | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2025-08-07 12:30 | 2025-08-07 14:03 | 1:33 | S/O | Oil leakage check in Unit Transformer | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2025-08-27 11:18 | 2025-08-27 17:19 | 6:01 | S/O | OLTC oil change. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-16 08:27 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroaulia 132/33kV | Kulshi | 2025-08-11 07:07 | 2025-08-11 10:14 | 3:07 | S/O | Khulshi circuit loop change | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2025-08-14 05:51 | 2025-08-14 08:58 | 3:07 | S/O | Redhot maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-08-05 13:09 | 2025-08-05 14:55 | 1:46 | S/O | Low SF6 gas pressure maintenance work at Dohazari-Coxsbazar # 02 GCB. Shift the protection of Dohazari-Coxsbazar # 02 to Bus Coupler bay. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-08-01 07:01 | 2025-08-01 11:31 | 4:30 | S/O | Chittagong Waterlogging Removal Project of Chattogram City by the Bangladesh Army. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-08-01 07:18 | 2025-08-01 11:34 | 4:16 | S/O | Chittagong Waterlogging Removal Project of Chattogram City by the Bangladesh Army. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-08-02 06:04 | 2025-08-02 15:38 | 9:34 | S/O | For the Chattogram waterlogging mitigation project by the Bangladesh Army. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-08-02 06:10 | 2025-08-02 15:16 | 9:06 | S/O | For the Chattogram waterlogging mitigation project by the Bangladesh Army. | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Old Madunaghat 230kV Ckt.-2 | 2025-08-07 10:10 | 2025-08-07 17:05 | 6:55 | S/O | S/D is taken by Madunaghat230 KV S/S | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-1 | 2025-08-30 07:34 | 2025-09-04 21:48 | 134:14 | S/O | Project work | 0 | 0 | No interruption
Shikalbaha 230/132kV | Dohazari ckt-1 | 2025-08-01 06:14 | 2025-08-01 12:23 | 6:09 | S/O | Maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV | Dohazari Ckt-2 | 2025-08-01 06:14 | 2025-08-01 14:20 | 8:06 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 22:50 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-08-15 04:47 | 2025-08-15 06:23 | 1:36 | S/O | Maintenance work in Sylhet -02 line due to temperature rise | 66 | 105.6 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-08-15 04:47 | 2025-08-15 06:24 | 1:37 | S/O | Maintenance work in Sylhet -02 line due to temperature rise | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2025-08-10 07:06 | 2025-08-10 08:40 | 1:34 | S/O | Project work at Kachua grid S /s. | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2025-08-11 09:45 | 2025-08-11 13:20 | 3:35 | S/O | Set up digital energy meter and multifunction meter | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-08-11 13:30 | 2025-08-11 16:15 | 2:45 | S/O | Set up digital energy meter and multifunction meter | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2025-08-12 09:40 | 2025-08-12 11:50 | 2:10 | S/O | Multifunction meter & Energy meter installing work. | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-2 | 2025-08-12 12:02 | 2025-08-12 13:45 | 1:43 | S/O | Multifunction meter & Energy meter installing work. | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-1 | 2025-08-02 07:21 | 2025-08-03 18:57 | 35:36 | S/O | Feni - 1 gone under shutdown for there schedule maintenance. | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-2 | 2025-08-04 06:27 | 2025-08-04 16:47 | 10:20 | S/O | Feni - 2 gone under shutdown for their scheduled maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-08-01 07:00 | 2025-08-01 11:48 | 4:48 | S/O | 132 KV Bus Shutdown Feni End Sub Station | 20 | 96 | Power interruption
Cumilla(S) 132/33kV | Cumilla North-1 | 2025-08-09 06:03 | 2025-08-09 07:32 | 1:29 | S/O | 0 | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2025-08-09 07:41 | 2025-08-09 08:28 | 0:47 | S/O | 0 | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-08-15 04:53 | 2025-08-15 15:47 | 10:54 | S/O | Red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-2 | 2025-08-01 07:00 | 2025-08-01 11:46 | 4:46 | S/O | For red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-08-01 07:05 | 2025-08-01 11:50 | 4:45 | S/O | For red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | Barayerhat Ckt | 2025-08-01 07:06 | 2025-08-01 11:40 | 4:34 | S/O | For red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2025-08-01 07:07 | 2025-08-01 11:36 | 4:29 | S/O | For red hot maintenance | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-1 | 2025-08-02 07:02 | 2025-08-03 18:58 | 35:56 | S/O | Chauddagram ckt -1 S/D taken by EEGBPS Project for Feni 230 kV LILO Stringing Work | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-2 | 2025-08-04 06:35 | 2025-08-04 16:48 | 10:13 | S/O | Ptoject work of 230 kv feni s/s | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-08-18 08:23 | 2025-08-18 08:36 | 0:13 | S/O | For Detect Gas Leakage of Circuit Breaker and Load Shift to transfer bus. | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-08-18 08:23 | 2025-08-18 08:36 | 0:13 | S/O | S/D taken for GCB Gas leakage finding; Load Share by Bus-Coupler | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-1 | 2025-08-10 08:40 | 2025-08-10 09:39 | 0:59 | S/O | 0 | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-08-27 15:21 | 2025-08-27 18:00 | 2:39 | S/O | project work | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-08-28 11:06 | 2025-08-28 15:47 | 4:41 | S/O | Project Work | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-08-15 04:47 | 2025-08-15 06:21 | 1:34 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-08-15 04:48 | 2025-08-15 06:22 | 1:34 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-08-21 05:55 | 2025-08-21 08:04 | 2:09 | S/O | sylhet - chattak ckt-02 tower loop maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 13:39 |  | Unserved Energy: |  | 201.6
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-08-11 08:32 | 2025-08-11 16:05 | 7:33 | S/O | Shutdown taken due to soil test work of boundary wall under the line. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2025-08-12 08:14 | 2025-08-12 16:40 | 8:26 | S/O | Due to Soil Test work | 0 | 0 | No interruption
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2025-08-15 06:50 | 2025-08-15 08:34 | 1:44 | S/O | Barishal 132kv Grid Sub - Station project work | 16 | 27.7333 | Power interruption
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2025-08-31 07:26 | 2025-08-31 08:45 | 1:19 | S/O | High Temperature Maintenance. | 10 | 13.1667 | Power interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2025-08-28 10:34 | 2025-08-28 14:56 | 4:22 | S/O | Hot spot maintenance at Gopalgonj 400kV SS end. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-08-01 08:58 | 2025-08-01 17:44 | 8:46 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-08-02 09:42 | 2025-08-02 18:45 | 9:03 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-08-03 09:52 | 2025-08-03 20:58 | 11:06 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2025-08-28 10:34 | 2025-08-28 15:57 | 5:23 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-02 | 2025-08-27 14:25 | 2025-08-27 18:29 | 4:04 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-08-11 08:30 | 2025-08-11 16:05 | 7:35 | S/O | Soil test of bagerhat ss as per request of bagerhat Ss. | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-08-28 15:16 | 2025-08-28 17:32 | 2:16 | S/O | Breaker maintenance at bagerhat end. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2025-08-13 07:03 | 2025-08-13 09:02 | 1:59 | S/O | Maintenance Working purpose. | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2025-08-07 14:38 | 2025-08-07 16:29 | 1:51 | S/O | Maintenance work at Payra end. | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-08-15 06:52 | 2025-08-15 08:33 | 1:41 | S/O | Barishal-Patuakhali 132KV Line Barishal End Project Work. | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-08-31 07:26 | 2025-08-31 08:45 | 1:19 | S/O | Due to rea hot maintenance at barguna Grid. | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2025-08-07 14:39 | 2025-08-07 16:28 | 1:49 | S/O | High Temperature Maintenance. | 0 | 0 | No interruption
Payra 400kV | Line-1 (Amtoli) | 2025-08-09 08:04 | 2025-08-09 08:04 | 0:00 | S/O | Completion of CSD Testing Activitis at Amtoli 400kV Switching Station | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 08:16 |  | Unserved Energy: |  | 40.9
HVDC Grid Circle :
BIPTC | 10CF15 | 2025-08-07 15:20 | 2025-08-07 15:39 | 0:19 | S/O | Tripped by C1 unbalance 60/61 stage-1 L1 trip. | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-08-30 13:02 | 2025-09-01 15:50 | 50:48 | S/O | For Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 51:07 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-08-01 09:11 | 2025-08-01 13:18 | 4:07 | S/O | Due to Maintenance work at Saidpur Substation end. | 0 | 0 | No interruption
Bogura 132/33kV | Natore-1 | 2025-08-25 09:01 | 2025-08-25 13:28 | 4:27 | S/O | Line PT (y-phase) oil leakage maintenance work. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2025-08-06 10:09 | 2025-08-06 19:53 | 9:44 | S/O | FM-1 Relay change | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2025-08-07 09:27 | 2025-08-07 16:55 | 7:28 | S/O | Relay changing work | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2025-08-19 10:58 | 2025-08-19 12:37 | 1:39 | S/O | Line CB Gas Pressure Maintenance work | 0 | 0 | No interruption
Kurigram 132/33kV | Rangpur-Kurigram Ckt-01 | 2025-08-30 07:09 | 2025-08-30 13:05 | 5:56 | S/O | OPGW maintenance work by TRTU | 62 | 367.8667 | Power interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2025-08-30 07:01 | 2025-08-30 14:25 | 7:24 | S/O | OPGW works. | 46 | 340.4 | Power interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-08-08 08:17 | 2025-08-08 17:20 | 9:03 | S/O | Re conductoring purpose. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-08-09 07:27 | 2025-08-09 17:06 | 9:39 | S/O | Reconducting | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-08-22 06:34 | 2025-08-22 10:32 | 3:58 | S/O | Due to OPGW armoring | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-08-08 08:17 | 2025-08-08 17:20 | 9:03 | S/O | Project work S/D | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-08-09 07:40 | 2025-08-09 17:04 | 9:24 | S/O | For Maintenance Work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-08-09 07:40 | 2025-08-09 17:04 | 9:24 | S/O | For Maintenance Work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-08-09 07:40 | 2025-08-09 17:04 | 9:24 | S/O | For Maintenance Work | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-08-22 06:33 | 2025-08-22 10:33 | 4:00 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2025-08-15 06:09 | 2025-08-15 14:08 | 7:59 | S/O | Gantry erection work from EEGBPS project | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2025-08-06 10:09 | 2025-08-06 19:54 | 9:45 | S/O | Work At Bogura Side | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2025-08-07 09:28 | 2025-08-07 16:56 | 7:28 | S/O | Bogura End Relay work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-08-30 07:03 | 2025-08-30 14:20 | 7:17 | S/O | OPGW changing work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2025-08-30 07:10 | 2025-08-30 13:05 | 5:55 | S/O | OPGW changing work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-08-01 09:01 | 2025-08-01 13:14 | 4:13 | S/O | Braker replacement work. | 7 | 29.5167 | Power interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-01 | 2025-08-15 06:11 | 2025-08-15 14:08 | 7:57 | S/O | For Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 11:14 |  | Unserved Energy: |  | 737.7833
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-02-14 01:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2025
| Area | Previous Month (July' 2025) |  |  |  | Current Month (August '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 28 | 9 | 48 | 85 | 16 | 7 | 56 | 79
2 | Dhaka (South) Grid Circle. | 26 | 9 | 38 | 73 | 26 | 7 | 54 | 87
3 | Chattogram Grid Circle. | 9 | 8 | 28 | 45 | 5 | 8 | 23 | 36
4 | Cumilla Grid Circle. | 39 | 22 | 58 | 119 | 20 | 15 | 62 | 97
5 | Khulna Grid Circle. | 36 | 16 | 38 | 90 | 10 | 13 | 50 | 73
6 | HVDC Grid Circle | 20 | 11 | 20 | 51 | 8 | 23 | 15 | 46
7 | Bogura Grid Circle. | 26 | 26 | 94 | 146 | 18 | 12 | 35 | 65
8 | Others
9 | Total | 184 | 101 | 324 | 609 | 103 | 85 | 295 | 483
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August 2025
| Area | Previous Month (July' 2025) |  |  |  | Current Month (August '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 624.97 | 255.2 | 3277 | 4157.17 | 165.7 | 273.5 | 1045.28 | 1484.48
2 | Dhaka (South) Grid Circle. | 385.9 | 187.33 | 553.2 | 1126.43 | 828.2 | 87.08 | 11381.47 | 12296.75
3 | Chattogram Grid Circle. | 205.8 | 44.8 | 332.65 | 583.25 | 81.43 | - | 1103.6 | 1185.03
4 | Cumilla Grid Circle. | 349.43 | 675.41 | 1238.12 | 2262.96 | 7.27 | 123.8 | 503.17 | 634.24
5 | Khulna Grid Circle. | 299.38 | 70.79 | 1110.27 | 1480.44 | 69.73 | 75.77 | 1101.5 | 1247
6 | HVDC Grid Circle | 170.99 | 47.33 | 607.18 | 825.5 | 2053.2 | 143.03 | 291.2 | 2487.43
7 | Bogura Grid Circle. | 402.8 | 464.65 | 1078.71 | 1946.16 | 747.51 | 44.47 | 887.66 | 1679.64
8 | Others
9 | Total | 2439.27 | 1745.51 | 8197.13 | 12381.91 | 3953.04 | 747.65 | 16313.88 | 21014.57
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 7 | 13 | 20 | 3 | 3 | 14 | 1318.82
2 | Dhaka (South) | 5031.6 | 9 | 9 | 18 | 3 | 2 | 13 | 12296.75
3 | Chattogram | 2042 | 2 | 7 | 9 |  | 1 | 8 | 1185.03
4 | Khulna | 2434 | 10 | 16 | 26 | 7 | 2 | 17 | 1197.1
5 | HVDC | 5954.3 | 5 | 5 | 10 | 1 |  | 9 | 2487.43
6 | Bogura | 3145.6 | 10 | 1 | 11 | 5 | 3 | 3 | 570.43
7 | Cumilla | 2981 | 5 | 8 | 13 | 2 | 3 | 8 | 432.63
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 19488.19
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.98%
4 | Khulna | 99.96%
5 | HVDC | 99.92%
6 | Bogura | 99.95%
7 | Cumilla | 99.97% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 1 | 5 | 2 | 1 | 2 | 165.67
2 | Dhaka (South) | 990.29 | - | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | 1 | 2 | 3 | 1 | - | 2 | 49.9
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 5 | 3 | 8 | 2 | 1 | 5 | 1109.22
7 | Cumilla | 1648.16 | - | - | 2 | 2 | - | - | 2 | 201.6
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1526.39
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 100%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.98%
7 | Cumilla | 100% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-08-01 | 9 | - | 7 | 14 hr 09 min | - | - | - | - | 1 | 00:21 | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Sreepur 230/132/33kV | 1 | 0.015972 | 16.8667
Sreepur 230/132/33kV | 1 | 0.0069444 | 8.5
Tangail 132/33kV | 1 | 0.011111 | 8
Kabirpur 132/33kV | 1 | 0.044444 | 48
Tangail 132/33kV | 1 | 0.053472 | 38.5
Tangail 132/33kV | 1 | 0.081944 | 118
Tangail 132/33kV | 1 | 0.08125 | 117
Dhamrai 132/33kV | 1 | 0.0125 | 9
Dhamrai 132/33kV | 1 | 0.011111 | 8
Manikganj 132/33kV | 1 | 0.021528 | 20.6667
Manikganj 132/33kV | 1 | 0.048611 | 46.6667
Bajitpur 132/33kV | 1 | 0:56 | 9.3333
Dhamrai 132/33kV | 1 | 1:55 | 47.9167
Jamalpur 132/33kV | 1 | 1:11 | 14.2
Kabirpur 132/33kV | 7 | 13:32 | 818.67
Manikganj 132/33kV | 1 | 1:56 | 29
Tangail 132/33kV | 1 | 0:53 | 8.8333
Tangail 132/33kV | 1 | 0:54 | 36
Tongi 230/132/33kV | 1 | 2:02 | 81.3333
Bhulta 132/33kV | 2 | 0.34167 | 582.3
Ghorashal 230kV | 1 | 0.17708 | 148.75
Keranigonj 230/132/33kV | 1 | 0.016667 | 14.4
Mogbazar 132/33kV | 3 | 0.063889 | 73.92
Sonargaon 132/33kV | 1 | 0.0069444 | 8.8333
Narshingdi 132/33kV | 1 | 0.065972 | 87.0833
Bhulta 132/33kV | 1 | 131:26 | 10514.6667
Ghorashal 230kV | 2 | 6:10 | 192.5
Ghorashal 230kV | 1 | 3:36 | 198
Narshingdi 132/33kV | 1 | 2:38 | 105.3333
Sonargaon 132/33kV | 3 | 5:54 | 310.67
Srinagar 132/33kV | 2 | 3:30 | 60.3
Coxsbazar 132/33kV | 1 | 0.05 | 43.2
Dohazari 132/33kV | 1 | 0.025694 | 38.2333
Bakulia 132/33kV | 1 | 0.050694 | 7.3
Baroaulia 132/33kV | 2 | 0.16736 | 46.17
Baroirhat 132/33kV | 1 | 0.15972 | 76.6667
Coxsbazar 132/33kV | 1 | 0.29861 | 680.8333
Dohazari 132/33kV | 1 | 0.045833 | 69.3
Hathazari 230/132/33kV | 1 | 0.46528 | 223.3333
Cumilla(S) 132/33kV | 1 | 0.0097222 | 4.6667
Kulaura 132/33kV | 1 | 0.018056 | 2.6
Brahmanbaria 132/33kV | 2 | 0.25208 | 95.33
Daudkandi 132/33kV | 1 | 0.042361 | 28.4667
Beanibazar 132/33kV | 1 | 0.12431 | 59.6667
Cumilla(N) 230/132/33kV | 1 | 1:25 | 85
Feni 132/33kV | 1 | 0:55 | 14.6667
Kulaura 132/33kV | 1 | 2:07 | 46.5667
Ramganj 132/33kV | 2 | 1:28 | 29.33
Sylhet 132/33kV | 2 | 2:43 | 66.33
Beanibazar 132/33kV | 1 | 0.066667 | 105.6
Chowmuhani 132/33kV | 1 | 0.2 | 96
Barishal 132/33kV | 3 | 0.026389 | 27.6
Gollamari 132/33kV | 1 | 0.013194 | 21.5333
Mongla 132/33kV | 1 | 0.015972 | 4.6
Noapara 132/33kV | 2 | 0.019444 | 7
Bagerhat 132/33kV | 2 | 0.098611 | 44.93
Bhandaria 132/33kV | 1 | 0.12847 | 30.8333
Barishal 132/33kV | 5 | 0.18403 | 89.23
Barishal 230/132kV | 3 | 5:40 | 141.47
Borhanuddin 230/33kV | 1 | 2:47 | 211.5333
Faridpur 132/33kV | 3 | 9:36 | 313.63
Gopalganj 132/33kV | 1 | 2:12 | 66
Noapara 132/33kV | 2 | 3:58 | 68.05
Shariatpur 132/33kV | 2 | 6:46 | 179.68
Barguna 132/33kV | 2 | 0.12708 | 40.9
BIPTC | 1 | 0.24583 | 2053.2
Jhenaidah 132/33kV | 2 | 0.14722 | 88.2
Pabna 132/33kV | 2 | 0.16806 | 54.83
Ishurdi 132/33kV | 3 | 9:09 | 211.07
Kushtia 132/33kV | 1 | 2:26 | 43.8
Magura 132/33kV | 1 | 1:49 | 36.3333
Barapukuria 230/132/33kV | 3 | 0.13611 | 247.6
Bogura 132/33kV | 4 | 0.085417 | 54.88
Purbasadipur 132/33kV | 1 | 0.014583 | 70
Saidpur 132/33kV | 1 | 0.0083333 | 3.6
Natore 132/33kV | 1 | 0.063889 | 44.4667
Barapukuria 230/132/33kV | 1 | 0.060417 | 120.35
Rangpur 132/33kV | 2 | 0.069444 | 83.33
Saidpur 132/33kV | 2 | 0.042361 | 167.75
Lalmonirhat 132/33kV | 1 | 6:31 | 149.8833
Kurigram 132/33kV | 1 | 5:56 | 367.8667
Lalmonirhat 132/33kV | 1 | 7:24 | 340.4
Saidpur 132/33kV | 1 | 4:13 | 29.5167
| 126 | 366:15 | 21014.57
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 23 | 2025-08-04 06:00
2 | AKSML | 173.3 | 2025-08-01 09:00
3 | Aftabnagar | 56 | 2025-08-03 13:00
4 | Agargaon | 143 | 2025-08-12 13:00
5 | Agrabad | 98 | 2025-08-18 15:00
6 | Amnura | 37 | 2025-08-11 19:30
7 | Ashuganj | 109 | 2025-08-12 00:00
8 | BSRM | 206 | 2025-08-07 17:00
9 | Bagerhat | 94 | 2025-08-11 23:00
10 | Bajitpur | 97 | 2025-08-11 21:00
11 | Bakulia | 103 | 2025-08-20 18:30
12 | Banani | 96.2 | 2025-08-03 13:00
13 | Bangabhaban | 25 | 2025-08-31 10:00
14 | Barapukuria | 82 | 2025-08-16 21:00
15 | Barguna | 24 | 2025-08-02 22:00
16 | Barishal | 122 | 2025-08-12 23:00
17 | Barishal-230 | 118 | 2025-08-02 23:00
18 | Baroaulia | 73 | 2025-08-13 11:00
19 | Baroirhat | 75 | 2025-08-04 19:00
20 | Bashundhara | 219 | 2025-08-18 16:00
21 | BashundharaCement | 15 | 2025-08-02 19:30
22 | Beanibazar | 90 | 2025-08-17 21:00
23 | Benapole | 70 | 2025-08-02 21:00
24 | Bhaluka | 164 | 2025-08-17 20:00
25 | Bhandaria | 68 | 2025-08-10 22:00
26 | Bhangura | 44 | 2025-08-17 22:00
27 | Bheramara(GK) | 73 | 2025-08-16 19:00
28 | Bhulta | 267 | 2025-08-03 00:00
29 | Bog-Sherpur | 82 | 2025-08-19 00:00
30 | Bogura | 181 | 2025-08-26 19:30
31 | Borhanuddin | 95 | 2025-08-03 19:00
32 | Brahmanbaria | 146 | 2025-08-17 23:00
33 | Cantonment | 152 | 2025-08-12 14:00
34 | Chandina | 36.82 | 2025-08-02 22:00
35 | Chandpur | 87 | 2025-08-12 00:00
36 | Chandraghona | 39 | 2025-08-14 19:00
37 | Chapai | 78 | 2025-08-18 23:00
38 | Charsaidpur | 46 | 2025-08-15 11:00
39 | Chauddagram | 78 | 2025-08-31 22:00
40 | Chhatak | 46 | 2025-08-14 21:00
41 | Chowmuhani | 202 | 2025-08-18 21:00
42 | Chuadanga | 134 | 2025-08-16 19:00
43 | Coxsbazar | 139 | 2025-08-12 23:00
44 | Cumilla(N) | 157 | 2025-08-28 00:00
45 | Cumilla(S) | 168 | 2025-08-11 19:30
46 | Daganbhuiyan | 0 | 2025-08-01 00:00
47 | Daudkandi | 160 | 2025-08-02 21:00
48 | Dhaka | 112 | 2025-08-31 11:00
49 | Dhamrai | 138 | 2025-08-28 18:30
50 | Dhanmondi | 157 | 2025-08-11 14:00
51 | Dohazari | 122 | 2025-08-11 19:30
52 | Faridpur | 183 | 2025-08-12 21:00
53 | Fatullah | 112 | 2025-08-27 16:00
54 | Fenchuganj | 56 | 2025-08-30 19:30
55 | Feni | 128 | 2025-08-16 21:00
56 | GPH | 92 | 2025-08-01 01:00
57 | Ghatail | 92 | 2025-08-11 19:00
58 | Ghorashal | 16 | 2025-08-12 20:00
59 | Ghorashal-230 | 113 | 2025-08-11 22:00
60 | Goalpara | 42 | 2025-08-12 23:00
61 | Gollamari | 102 | 2025-08-12 13:00
62 | Gopalganj | 117 | 2025-08-12 22:00
63 | Gulshan | 140 | 2025-08-18 13:00
64 | Halishahar | 76 | 2025-08-26 09:00
65 | HaripurSBU | 175 | 2025-08-30 16:00
66 | Hasnabad | 115 | 2025-08-26 13:00
67 | Hathazari | 96 | 2025-08-02 05:00
68 | Ishurdi | 91 | 2025-08-18 19:30
69 | Jaldhaka | 96 | 2025-08-12 19:00
70 | Jamalpur | 150 | 2025-08-11 22:00
71 | Jashore | 152 | 2025-08-13 19:00
72 | Jhenaidah | 142 | 2025-08-31 19:00
73 | Joydebpur | 167 | 2025-08-18 19:00
74 | Joypurhat | 70 | 2025-08-17 21:00
75 | Juldah | 19.5 | 2025-08-28 16:00
76 | KSRM | 55 | 2025-08-01 06:00
77 | Kabirpur | 267 | 2025-08-26 15:00
78 | Kachua | 102 | 2025-08-31 22:00
79 | Kallyanpur | 114 | 2025-08-03 21:00
80 | Kalurghat | 68 | 2025-08-03 10:00
81 | Kamrangirchar | 81 | 2025-08-18 16:00
82 | Kaptai | N/A | N/A
83 | Kasba | 39 | 2025-08-16 22:00
84 | Kazla | 116 | 2025-08-16 13:00
85 | Keranigonj | 108 | 2025-08-12 17:00
86 | Khagrachori | 38 | 2025-08-25 19:00
87 | Khulna | 78 | 2025-08-11 19:30
88 | Khulshi | 199 | 2025-08-26 19:30
89 | Kishoreganj | 148 | 2025-08-17 19:30
90 | Kodda | 324 | 2025-08-28 18:30
91 | Kulaura | 64 | 2025-08-26 18:30
92 | Kurigram | 80 | 2025-08-17 19:30
93 | Kushtia | 170 | 2025-08-26 19:00
94 | Laksam | 44 | 2025-08-20 10:00
95 | Lakshmipur | 35 | 2025-08-30 14:00
96 | Lalbag | 65 | 2025-08-19 13:00
97 | Lalmonirhat | 74 | 2025-08-19 19:00
98 | MI_Cement | 17.8 | 2025-08-30 13:00
99 | Madanganj | 45 | 2025-08-09 12:00
100 | Madaripur | 129 | 2025-08-11 22:00
101 | Madartek | 104 | 2025-08-13 00:00
102 | Madunaghat | 61 | 2025-08-26 14:00
103 | Magura | 72 | 2025-08-12 19:00
104 | Mahasthangarh | 102 | 2025-08-18 00:00
105 | Maijdee | 41 | 2025-08-27 18:30
106 | Manikganj | 140 | 2025-08-12 22:00
107 | Maniknagar | 90 | 2025-08-11 13:00
108 | Matarbari | 132 | 2025-08-27 12:00
109 | Matuail | 74 | 2025-08-18 15:00
110 | Millgate | 139 | 2025-08-02 15:00
111 | Mirpur | 147 | 2025-08-26 15:00
112 | Mirsorai | 12 | 2025-08-02 10:00
113 | Mirzapur | 55 | 2025-08-16 21:00
114 | Mithapukur | 80 | 2025-08-17 19:00
115 | Modern | N/A | N/A
116 | Mogbazar | 167.9 | 2025-08-11 16:00
117 | Mongla | 53 | 2025-08-12 13:00
118 | Motijheel | 49 | 2025-08-12 13:00
119 | Muktagacha | 41 | 2025-08-11 19:00
120 | Munshiganj | 125 | 2025-08-12 23:00
121 | Muradnagar | 46 | 2025-08-18 21:00
122 | Mymensingh | 224 | 2025-08-26 19:00
123 | Naogaon | 146 | 2025-08-17 23:00
124 | Narail | 65 | 2025-08-31 19:00
125 | Narinda | 91 | 2025-08-12 13:00
126 | Narshingdi | 197 | 2025-08-13 02:00
127 | Natore | 159 | 2025-08-16 23:00
128 | Nawabganj | 90.8 | 2025-08-16 21:00
129 | Netrakona | 151 | 2025-08-18 19:00
130 | New | 79.4 | 2025-08-26 15:00
131 | Niamatpur | 84 | 2025-08-17 22:00
132 | Noapara | 50 | 2025-08-13 00:00
133 | PHP | 9 | 2025-08-03 18:00
134 | Pabna | 138 | 2025-08-16 19:30
135 | Palashbari | 130 | 2025-08-27 19:00
136 | Panchagarh | 69 | 2025-08-25 19:30
137 | Patiya | 70 | 2025-08-22 08:00
138 | Patuakhali | 76 | 2025-08-12 22:00
139 | Payra | 48 | 2025-08-23 17:00
140 | Postogola | 60 | 2025-08-11 23:00
141 | Purbachal | 24 | 2025-08-16 23:00
142 | Purbasadipur | 140 | 2025-08-12 22:00
143 | Rahanpur | 46 | 2025-08-11 22:00
144 | Rahim | 48 | 2025-08-07 17:00
145 | Rajbari | 91 | 2025-08-26 19:30
146 | Rajendrapur | 145 | 2025-08-16 21:00
147 | Rajshahi | 144 | 2025-08-16 22:00
148 | Rajshahi-230 | 116 | 2025-08-26 21:00
149 | Ramganj | 122 | 2025-08-25 22:00
150 | Rampur | 45 | 2025-08-30 22:00
151 | Rangamati | 24 | 2025-08-03 20:00
152 | Rangpur | 164 | 2025-08-19 19:00
153 | Ruppur | 11.4 | 2025-08-12 02:00
154 | SSM | 16 | 2025-08-25 02:00
155 | Saidpur | 118 | 2025-08-26 19:00
156 | Satkhira | 143 | 2025-08-11 22:00
157 | Satmasjid | 106 | 2025-08-11 18:30
158 | Savar | 247 | 2025-08-27 12:00
159 | SevenRings | 22.65 | 2025-08-21 18:00
160 | ShahCement | 37 | 2025-08-31 00:00
161 | Shahjadpur | 100 | 2025-08-26 20:00
162 | Shahjibazar | 144 | 2025-08-17 22:00
163 | Shahmirpur | 69 | 2025-08-20 18:30
164 | Shariatpur | 99 | 2025-08-12 22:00
165 | Sherpur | 174 | 2025-08-16 22:00
166 | Shikalbaha | 17 | 2025-08-01 18:00
167 | Shitalakhya | 93.2 | 2025-08-11 16:00
168 | Sholosohor | 50 | 2025-08-30 12:00
169 | Shyampur | 180 | 2025-08-24 09:00
170 | Siddhirganj | 125 | 2025-08-11 12:00
171 | Sirajganj | 126 | 2025-08-27 19:30
172 | Sonargaon | 149 | 2025-08-17 19:00
173 | Sreemongol | 93 | 2025-08-02 19:00
174 | Sreepur | 111 | 2025-08-07 15:00
175 | Srinagar | 53.99 | 2025-08-12 22:00
176 | Sunamganj | 67 | 2025-08-18 21:00
177 | Sylhet | 60 | 2025-08-31 18:30
178 | Sylhet-132 | 156 | 2025-08-17 18:30
179 | TK | 39 | 2025-08-12 19:30
180 | Tangail | 212 | 2025-08-11 22:00
181 | Taraganj | 26 | 2025-08-10 19:30
182 | Thakurgaon | 122 | 2025-08-12 22:00
183 | Tongi | 124 | 2025-08-12 11:00
184 | Ullahpara | 46 | 2025-08-28 19:00
185 | Ullon | 64 | 2025-08-12 23:00
186 | Uttara | 97 | 2025-08-26 18:30
187 | UttaraNew | 68 | 2025-08-26 23:00
188 | Zigatola | 76 | 2025-08-11 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: August 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5808.52 | 2025-08-27 | 16:00
Chattogram | 1630.5 | 2025-08-12 | 14:00
Cumilla | 1536.73 | 2025-08-12 | 23:00
Mymensingh | 1302 | 2025-08-17 | 0:00
Sylhet | 722 | 2025-08-17 | 21:00
Khulna | 1944 | 2025-08-12 | 19:30
Barishal | 514 | 2025-08-12 | 23:00
Rajshahi | 1661 | 2025-08-26 | 21:00
Rangpur | 1090 | 2025-08-27 | 19:30
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 394 | 2025-08-08 09:00 | 333 | 2025-08-16 15:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 412 | 2025-08-06 04:00 | 366 | 2025-08-18 15:00
4 | Bibiana | 400 | 393 | 2025-08-15 08:00 | 375 | 2025-08-25 16:00
5 | BIPTC | 400 | 409 | 2025-08-01 04:00 | 384 | 2025-08-15 23:00
6 | Bogura | 400 | 394 | 2025-08-15 10:00 | 357 | 2025-08-06 20:00
7 | Gopalganj | 400 | 407 | 2025-08-08 09:00 | 384 | 2025-08-26 22:00
8 | Kaliakoir | 400 | 387 | 2025-08-09 02:00 | 282 | 2025-08-09 04:00
9 | Madunaghat | 400 | 398 | 2025-08-08 10:00 | 398 | 2025-08-19 13:00
10 | Meghnaghat | 400 | 396 | 2025-08-05 07:00 | 380 | 2025-08-14 23:00
11 | Payra | 400 | 421 | 2025-08-08 16:00 | 405 | 2025-08-30 21:00
12 | Rahanpur | 400 | 407 | 2025-08-08 09:00 | 378 | 2025-08-16 22:00
13 | Rampal | 400 | 412 | 2025-08-08 16:00 | 390 | 2025-08-16 14:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 230 | 2025-08-05 06:00 | 213 | 2025-08-18 15:00
2 | AKSML | 230 | 235 | 2025-08-01 07:00 | 221 | 2025-08-01 22:00
3 | Aminbazar | 230 | 254 | 2025-08-20 08:00 | 214 | 2025-08-18 14:00
4 | Ashuganj | 230 | 239 | 2025-08-06 06:00 | 216 | 2025-08-18 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2025-08-01 10:00 | 224 | 2025-08-12 01:00
7 | Barapukuria | 230 | 232 | 2025-08-06 00:00 | 210 | 2025-08-28 05:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 233 | 2025-08-08 17:00 | 218 | 2025-08-11 23:00
10 | Bheramara | 230 | 250 | 2025-08-24 06:00 | 221 | 2025-08-06 19:30
11 | Bhulta | 230 | 238 | 2025-08-06 04:00 | 203 | 2025-08-18 14:00
12 | Bibiana | 230 | 232 | 2025-08-08 07:00 | 220 | 2025-08-02 00:00
13 | BIPTC | 230 | 238 | 2025-08-29 08:00 | 221 | 2025-08-02 19:00
14 | Bogura | 230 | 244 | 2025-08-22 08:00 | 223 | 2025-08-02 21:00
15 | Bogura-400 | 230 | 244 | 2025-08-15 10:00 | 223 | 2025-08-06 20:00
16 | Borhanuddin | 230 | 239 | 2025-08-01 09:00 | 224 | 2025-08-10 22:00
17 | BSRM | 230 | 232 | 2025-08-05 16:00 | 217 | 2025-08-01 23:00
18 | Cumilla(N) | 230 | 228 | 2025-08-05 16:00 | 213 | 2025-08-18 15:00
19 | Faridpur | 230 | 235 | 2025-08-01 18:30 | 215 | 2025-08-16 21:00
20 | Fenchuganj | 230 | 234 | 2025-08-09 08:00 | 220 | 2025-08-02 23:00
21 | Ghorashal | 230 | 235 | 2025-08-02 04:00 | 220 | 2025-08-04 18:00
22 | Ghorashal-230 | 230 | 235 | 2025-08-06 05:00 | 207 | 2025-08-18 15:00
23 | Gopalganj | 230 | 232 | 2025-08-08 09:00 | 217 | 2025-08-14 20:00
24 | GPH | 230 | 233 | 2025-08-08 09:00 | 201 | 2025-08-09 09:00
25 | Haripur | 230 | 228 | 2025-08-08 18:00 | 212 | 2025-08-02 13:00
26 | Hasnabad | 230 | 228 | 2025-08-08 08:00 | 211 | 2025-08-18 14:00
27 | Hathazari | 230 | 232 | 2025-08-22 18:00 | 218 | 2025-08-11 12:00
28 | Ishurdi | 230 | 238 | 2025-08-29 08:00 | 224 | 2025-08-07 21:00
29 | Jhenaidah | 230 | 234 | 2025-08-04 06:00 | 213 | 2025-08-16 19:00
30 | Kaliakoir | 230 | 237 | 2025-08-05 02:00 | 219 | 2025-08-18 14:00
31 | Keranigonj | 230 | 228 | 2025-08-05 06:00 | 210 | 2025-08-18 15:00
32 | Khulna(S) | 230 | 236 | 2025-08-04 06:00 | 217 | 2025-08-13 01:00
33 | Madunaghat | 230 | 236 | 2025-08-08 09:00 | 225 | 2025-08-21 19:30
34 | Madunaghat-400 | 230 | 236 | 2025-08-01 08:00 | 225 | 2025-08-10 14:00
35 | Maniknagar | 230 | 231 | 2025-08-14 13:00 | 210 | 2025-08-02 13:00
36 | Meghnaghat | 230 | 233 | 2025-08-05 08:00 | 219 | 2025-08-02 13:00
37 | Meghnaghat-400 | 230 | 230 | 2025-08-08 09:00 | 215 | 2025-08-02 12:00
38 | Mirsorai | 230 | 232 | 2025-08-05 16:00 | 217 | 2025-08-01 23:00
39 | Rajshahi | 230 | 234 | 2025-08-03 07:00 | 218 | 2025-08-02 23:00
40 | Rampal | 230 | 236 | 2025-08-08 09:00 | 218 | 2025-08-06 21:00
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 237 | 2025-08-06 04:00 | 199 | 2025-08-18 15:00
43 | Shikalbaha | 230 | 233 | 2025-08-01 08:00 | 221 | 2025-08-02 23:00
44 | Shyampur | 230 | 230 | 2025-08-29 17:00 | 211 | 2025-08-18 15:00
45 | Siddhirganj | 230 | 247 | 2025-08-09 14:00 | 213 | 2025-08-18 12:00
46 | Sirajgonj | 230 | 245 | 2025-08-31 22:00 | 233 | 2025-08-18 12:00
47 | Sreepur | 230 | 233 | 2025-08-05 15:00 | 218 | 2025-08-10 15:00
48 | Tongi | 230 | 233 | 2025-08-05 07:00 | 211 | 2025-08-31 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2025-08-07 04:00 | 141 | 45876.2083
2 | Agargaon | 132 | 136 | 2025-08-05 07:00 | 122 | 18/8/2025 15:00
3 | Agrabad | 132 | 136 | 2025-08-01 08:00 | 124 | 2025-08-10 15:00
4 | AKS | 132 | 132 | 2025-08-01 08:00 | 123 | 2025-08-11 15:00
5 | Aminbazar | 132 | 138 | 2025-08-27 20:00 | 124 | 2025-08-17 14:00
6 | Amnura | 132 | 138 | 2025-08-05 06:00 | 125 | 2025-08-02 22:00
7 | Ashuganj | 132 | 145 | 2025-08-05 15:00 | 132 | 2025-08-18 15:00
8 | Bagerhat | 132 | 139 | 2025-08-08 17:00 | 118 | 2025-08-12 14:00
9 | Bajitpur | 132 | 138 | 2025-08-13 23:00 | 121 | 2025-08-25 22:00
10 | Bakulia | 132 | 137 | 2025-08-01 08:00 | 125 | 2025-08-11 15:00
11 | Banani | 132 | 140 | 2025-08-07 04:00 | 122 | 2025-08-06 11:00
12 | Bangabhaban | 132 | 137 | 2025-08-08 08:00 | 124 | 2025-08-18 13:00
13 | Barapukuria | 132 | 140 | 2025-08-01 09:00 | 124 | 2025-08-26 19:00
14 | Barguna | 132 | 137 | 2025-08-08 09:00 | 129 | 2025-08-03 22:00
0 | Barishal | 132 | 136 | 2025-08-22 10:00 | 125 | 2025-08-10 19:00
16 | Barishal-230 | 132 | 137 | 2025-08-08 08:00 | 126 | 2025-08-03 23:00
17 | Baroaulia | 132 | 134 | 2025-08-01 08:00 | 125 | 2025-08-11 12:00
18 | Baroirhat | 132 | 132 | 2025-08-01 08:00 | 114 | 2025-08-01 23:00
19 | Bashundhara | 132 | 138 | 2025-08-05 06:00 | 120 | 2025-08-18 15:00
20 | BashundharaCement | 132 | 133 | 2025-08-08 18:00 | 122 | 2025-08-26 12:00
21 | Beanibazar | 132 | 132 | 2025-08-05 07:00 | 118 | 2025-08-01 23:00
22 | Benapole | 132 | 138 | 2025-08-08 09:00 | 118 | 2025-08-310 23:00
23 | Bhaluka | 132 | 133 | 2025-08-01 07:00 | 120 | 2025-08-18 15:00
24 | Bhandaria | 132 | 134 | 2025-08-01 17:00 | 115 | 2025-08-10 22:00
25 | Bhangura | 132 | 137 | 2025-08-06 01:00 | 126 | 2025-08-16 19:30
26 | Bheramara | 132 | 138 | 2025-08-01 06:00 | 130 | 2025-08-20 21:00
27 | Bheramara(GK) | 132 | 138 | 2025-08-01 08:00 | 131 | 2025-08-02 23:00
28 | Bhulta | 132 | 128 | 2025-08-08 13:00 | 117 | 2025-08-04 02:00
29 | Bog-Sherpur | 132 | 140 | 2025-08-08 09:00 | 123 | 2025-08-16 22:00
30 | Bogura | 132 | 143 | 2025-08-08 09:00 | 125 | 2025-08-15 23:00
31 | Bogura-230 | 132 | 143 | 2025-08-08 09:00 | 125 | 2025-08-16 22:00
32 | Brahmanbaria | 132 | 141 | 2025-08-05 15:00 | 126 | 2025-08-18 15:00
33 | Cantonment | 132 | 136 | 2025-08-09 04:00 | 122 | 2025-08-18 15:00
34 | Chandina | 132 | 131 | 2025-08-05 16:00 | 120 | 2025-08-16 23:00
35 | Chandpur | 132 | 134 | 2025-08-27 18:00 | 115 | 2025-08-15 13:00
36 | Chandraghona | 132 | 134 | 2025-08-01 07:00 | 120 | 2025-08-10 15:00
37 | Chapai | 132 | 137 | 2025-08-01 10:00 | 125 | 2025-08-02 23:00
39 | Charsaidpur | 132 | 134 | 2025-08-08 18:00 | 122 | 2025-08-02 13:00
40 | Chauddagram | 132 | 127 | 2025-08-27 18:00 | 112 | 2025-08-27 07:00
41 | Chhatak | 132 | 134 | 2025-08-03 15:00 | 113 | 2025-08-26 13:00
42 | Chowmuhani | 132 | 125 | 2025-08-04 08:00 | 125 | 2025-08-04 08:00
43 | Chuadanga | 132 | 137 | 2025-08-21 09:00 | 116 | 2025-08-16 19:00
44 | Coxsbazar | 132 | 125 | 2025-08-08 09:00 | 107 | 2025-08-12 12:00
45 | Cumilla(N) | 132 | 131 | 2025-08-08 05:00 | 120 | 2025-08-01 23:00
46 | Cumilla(S) | 132 | 133 | 2025-08-02 05:00 | 118 | 2025-08-01 23:00
47 | Daganbhuiyan | 132 | 126 | 2025-08-27 18:00 | 110 | 2025-08-01 22:00
48 | Daudkandi | 132 | 129 | 2025-08-05 16:00 | 113 | 2025-08-18 15:00
49 | Dhaka | 132 | 140 | 2025-08-03 05:00 | 122 | 2025-08-18 15:00
50 | Dhamrai | 132 | 137 | 2025-08-05 07:00 | 123 | 2025-08-10 15:00
51 | Dhanmondi | 132 | 141 | 2025-08-07 06:00 | 119 | 2025-08-18 15:00
52 | Dohazari | 132 | 132 | 2025-08-23 19:30 | 119 | 45872
53 | Faridpur | 132 | 138 | 2025-08-08 16:00 | 126 | 2025-08-26 22:00
54 | Fatullah | 132 | 135 | 2025-08-08 18:30 | 123 | 2025-08-26 12:00
55 | Fenchuganj | 132 | 139 | 2025-08-09 08:00 | 128 | 2025-08-03 00:00
56 | Feni | 132 | 126 | 2025-08-01 08:00 | 113 | 2025-08-02 01:00
57 | Ghatail | 132 | 136 | 2025-08-05 01:00 | 118 | 2025-08-26 18:30
58 | Ghorashal | 132 | 139 | 2025-08-06 06:00 | 126 | 2025-08-18 11:00
59 | Goalpara | 132 | 142 | 2025-08-08 10:00 | 125 | 2025-08-26 19:00
60 | Gollamari | 132 | 142 | 2025-08-08 09:00 | 127 | 2025-08-06 21:00
61 | Gopalganj | 132 | 139 | 2025-08-08 09:00 | 125 | 2025-08-26 22:00
62 | Gopalganj-400 | 132 | 139 | 2025-08-04 06:00 | 129 | 2025-08-26 22:00
63 | Gulshan | 132 | 140 | 2025-08-07 05:00 | 120 | 2025-08-18 15:00
64 | Halishahar | 132 | 137 | 2025-08-01 08:00 | 124 | 2025-08-31 16:00
65 | Haripur | 132 | 133 | 2025-08-08 09:00 | 122 | 2025-08-02 13:00
66 | HaripurSBU | 132 | 133 | 2025-08-08 09:00 | 113 | 2025-08-31 01:00
67 | Hasnabad | 132 | 138 | 2025-08-15 02:00 | 125 | 2025-08-02 12:00
68 | Hathazari | 132 | 135 | 2025-08-01 08:00 | 126 | 2025-08-17 15:00
69 | Ishurdi | 132 | 139 | 2025-08-01 09:00 | 130 | 2025-08-13 01:00
70 | Jaldhaka | 132 | 136 | 2025-08-17 10:00 | 128 | 2025-08-12 11:00
71 | Jamalpur | 132 | 140 | 2025-08-03 09:00 | 118 | 2025-08-05 11:00
72 | Jashore | 132 | 139 | 2025-08-06 06:00 | 115 | 2025-08-16 19:30
73 | Jhenaidah | 132 | 139 | 2025-08-08 08:00 | 121 | 2025-08-31 22:00
74 | Jhenaidah-230 | 132 | 140 | 2025-08-04 06:00 | 122 | 2025-08-16 19:30
75 | Joydebpur | 132 | 142 | 2025-08-08 06:00 | 118 | 2025-08-18 15:00
76 | Joypurhat | 132 | 136 | 2025-08-08 09:00 | 113 | 2025-08-17 01:00
77 | Juldah | 132 | 136 | 2025-08-01 08:00 | 125 | 2025-08-18 15:00
78 | Kabirpur | 132 | 137 | 2025-08-05 07:00 | 118 | 2025-08-20 15:00
79 | Kachua | 132 | 132 | 2025-08-27 18:00 | 115 | 2025-08-13 22:00
80 | Kaliakoir | 132 | 138 | 2025-08-05 02:00 | 125 | 2025-08-25 08:00
81 | Kallyanpur | 132 | 137 | 2025-08-16 02:00 | 125 | 2025-08-13 14:00
82 | Kalurghat | 132 | 134 | 2025-08-01 07:00 | 126 | 2025-08-10 15:00
83 | Kamrangirchar | 132 | 138 | 2025-08-08 09:00 | 125 | 2025-08-02 13:00
84 | Kaptai | 132 | N/A | N/A | N/A | N/A
85 | Kasba | 132 | 129 | 2025-08-05 16:00 | 115 | 2025-08-16 22:00
86 | Kazla | 132 | 137 | 2025-08-08 09:00 | 124 | 2025-08-18 13:00
87 | Keranigonj | 132 | 137 | 2025-08-04 05:00 | 125 | 2025-08-02 13:00
88 | Khagrachori | 132 | 133 | 2025-08-01 08:00 | 125 | 2025-08-17 16:00
89 | Khulna | 132 | 142 | 2025-08-08 09:00 | 124 | 2025-08-16 19:00
90 | Khulna(S) | 132 | 143 | 2025-08-08 09:00 | 127 | 2025-08-06 21:00
91 | Khulshi | 132 | 134 | 2025-08-01 08:00 | 123 | 2025-08-17 15:00
92 | Kishoreganj | 132 | 132 | 2025-08-04 05:00 | 116 | 2025-08-17 00:00
93 | Kodda | 132 | 137 | 2025-08-08 07:00 | 117 | 2025-08-18 15:00
94 | KSRM | 132 | 135 | 2025-08-01 08:00 | 125 | 2025-08-11 15:00
95 | Kulaura | 132 | 138 | 2025-08-03 15:00 | 127 | 2025-08-01 23:00
96 | Kurigram | 132 | 134 | 2025-08-13 18:30 | 114 | 2025-08-26 19:00
97 | Kushtia | 132 | 138 | 2025-08-12 12:00 | 123 | 2025-08-27 15:00
98 | Laksam | 132 | 137 | 2025-08-05 07:00 | 123 | 2025-08-10 15:00
99 | Lakshmipur | 132 | 126 | 2025-08-27 18:00 | 108 | 2025-08-01 23:00
100 | Lalbag | 132 | 138 | 2025-08-08 09:00 | 124 | 2025-08-18 15:00
101 | Lalmonirhat | 132 | 134 | 2025-08-01 09:00 | 115 | 2025-08-26 19:00
102 | Madanganj | 132 | 133 | 2025-08-08 18:00 | 122 | 2025-08-26 12:00
103 | Madaripur | 132 | 138 | 2025-08-08 17:00 | 127 | 2025-08-16 23:00
104 | Madartek | 132 | 140 | 2025-08-07 06:00 | 120 | 2025-08-10 02:00
105 | Madunaghat | 132 | 134 | 2025-08-01 07:00 | 126 | 2025-08-10 15:00
106 | Magura | 132 | 138 | 2025-08-04 06:00 | 119 | 2025-08-16 19:00
107 | Mahasthangarh | 132 | 142 | 2025-08-08 09:00 | 120 | 2025-08-16 22:00
108 | Maijdee | 132 | 125 | 2025-08-27 18:00 | 106 | 2025-08-15 21:00
109 | Manikganj | 132 | 135 | 2025-08-05 06:00 | 116 | 2025-08-18 15:00
110 | Maniknagar | 132 | 137 | 2025-08-08 08:00 | 124 | 2025-08-18 13:00
111 | Matarbari | 132 | 130 | 2025-08-01 14:00 | 106 | 2025-08-15 20:00
112 | Matuail | 132 | 142 | 2025-08-14 02:00 | 126 | 2025-08-01 23:00
113 | Millgate | 132 | 138 | 2025-08-05 07:00 | 119 | 2025-08-18 15:00
114 | Mirpur | 132 | 134 | 2025-08-05 06:00 | 123 | 2025-08-24 23:00
115 | Mirzapur | 132 | 133 | 2025-08-05 01:00 | 122 | 2025-08-18 15:00
116 | Mithapukur | 132 | 135 | 2025-08-06 06:00 | 105 | 2025-08-17
117 | MI_Cement | 132 | 133 | 2025-08-05 06:00 | 122 | 2025-08-02 13:00
118 | Modern | 132 | N/A | N/A | N/A | N/A
119 | Mogbazar | 132 | 141 | 2025-08-15 06:00 | 121 | 2025-08-06 12:00
120 | Mongla | 132 | 139 | 2025-08-08 09:00 | 119 | 2025-08-12 13:00
121 | Motijheel | 132 | 137 | 2025-08-08 08:00 | 124 | 2025-08-18 13:00
122 | Muktagacha | 132 | 137 | 2025-08-08 04:00 | 122 | 2025-08-22 19:30
123 | Munshiganj | 132 | 133 | 2025-08-08 17:00 | 121 | 2025-08-26 12:00
124 | Muradnagar | 132 | 130 | 2025-08-05 16:00 | 116 | 2025-08-16 22:00
125 | Mymensingh | 132 | 139 | 2025-08-08 06:00 | 123 | 45874.5
126 | Naogaon | 132 | 137 | 2025-08-08 08:00 | 116 | 2025-08-17 01:00
127 | Narail | 132 | 138 | 2025-08-04 05:00 | 115 | 2025-08-16 19:00
128 | Narinda | 132 | 0 | 2025-08-01 00:00 | N/A | N/A
129 | Narshingdi | 132 | 140 | 2025-08-08 06:00 | 118 | 2025-08-03 00:00
130 | Natore | 132 | 137 | 2025-08-08 17:00 | 125 | 2025-08-12 00:00
131 | Nawabganj | 132 | 138 | 2025-08-08 18:00 | 124 | 2025-08-18 15:00
132 | Netrakona | 132 | 129 | 2025-08-05 02:00 | 108 | 2025-08-18 18:30
133 | New | 132 | 139 | 2025-08-05 06:00 | 119 | 2025-08-18 15:00
134 | Niamatpur | 132 | 139 | 2025-08-08 09:00 | 127 | 2025-08-16 19:30
135 | Noapara | 132 | 140 | 2025-08-08 09:00 | 123 | 2025-08-16 19:00
136 | Pabna | 132 | 137 | 2025-08-08 15:00 | 126 | 2025-08-16 19:30
137 | Palashbari | 132 | 134 | 2025-08-08 08:00 | 104 | 2025-08-17 00:00
139 | Panchagarh | 132 | 142 | 2025-08-19 18:30 | 118 | 2025-08-06 07:00
140 | Patiya | 132 | 134 | 2025-08-08 09:00 | 104 | 2025-08-13 19:00
141 | Patuakhali | 132 | 138 | 2025-08-31 22:00 | 130 | 2025-08-03 00:00
142 | Payra | 132 | 138 | 2025-08-08 07:00 | 132 | 2025-08-24 12:00
143 | PHP | 132 | 130 | 2025-08-01 10:00 | 112 | 2025-08-01 23:00
144 | Postogola | 132 | 137 | 2025-08-25 06:00 | 124 | 2025-08-18 15:00
145 | Purbachal | 132 | 140 | 2025-08-04 03:00 | 120 | 2025-08-18 15:00
146 | Purbasadipur | 132 | 137 | 2025-08-19 18:30 | 115 | 2025-08-17 20:00
147 | Rahanpur | 132 | 140 | 2025-08-08 09:00 | 128 | 2025-08-16 22:00
148 | Rahanpur-400 | 132 | 140 | 2025-08-06 18:00 | 130 | 2025-08-16 20:00
149 | Rahim | 132 | 132 | 2025-08-04 06:00 | 123 | 2025-08-02 13:00
150 | Rajbari | 132 | 137 | 2025-08-08 17:00 | 123 | 2025-08-26 22:00
151 | Rajendrapur | 132 | 136 | 2025-08-28 19:30 | 120 | 2025-08-04 14:00
152 | Rajshahi | 132 | 136 | 2025-08-08 17:00 | 120 | 2025-08-17 20:00
153 | Rajshahi-230 | 132 | 135 | 2025-08-08 06:00 | 121 | 2025-08-23 19:00
154 | Ramganj | 132 | 128 | 2025-08-27 18:00 | 109 | 2025-08-01 23:00
155 | Rampur | 132 | 135 | 2025-08-01 08:00 | 124 | 2025-08-11 12:00
156 | Rampura | 132 | 140 | 2025-08-04 04:00 | 120 | 2025-08-18 15:00
157 | Rangamati | 132 | 133 | 2025-08-01 07:00 | 126 | 2025-08-18 15:00
158 | Rangpur | 132 | 144 | 2025-08-06 00:00 | 121 | 2025-08-25 21:00
159 | Ruppur | 132 | 139 | 2025-08-08 17:00 | 130 | 2025-08-14 20:00
160 | Saidpur | 132 | 137 | 2025-08-17 10:00 | 119 | 2025-08-02 21:00
161 | Satkhira | 132 | 139 | 2025-08-08 09:00 | 119 | 2025-08-17 23:00
162 | Satmasjid | 132 | 139 | 2025-08-06 03:00 | 121 | 2025-08-18 15:00
163 | Savar | 132 | 134 | 2025-08-01 19:00 | 120 | 2025-08-12 14:00
164 | SevenRings | 132 | 140 | 2025-08-06 04:00 | 123 | 2025-08-18 15:00
165 | ShahCement | 132 | 134 | 2025-08-08 18:00 | 122 | 2025-08-02 13:00
166 | Shahjadpur | 132 | 139 | 2025-08-01 08:00 | 130 | 2025-08-16 21:00
167 | Shahjibazar | 132 | 141 | 2025-08-05 16:00 | 123 | 2025-08-21 23:00
168 | Shahmirpur | 132 | 139 | 2025-08-17 23:00 | 125 | 2025-08-11 15:00
169 | Shariatpur | 132 | 137 | 2025-08-08 16:00 | 124 | 2025-08-12 23:00
170 | Sherpur | 132 | 139 | 2025-08-03 09:00 | 121 | 2025-08-06 06:00
171 | Shikalbaha | 132 | 127 | 2025-08-01 08:00 | 125 | 2025-08-10 10:00
172 | Shikalbaha-230 | 132 | 138 | 2025-08-01 08:00 | 125 | 2025-08-10 10:00
173 | Shitalakhya | 132 | 133 | 2025-08-05 06:00 | 122 | 2025-08-02 13:00
174 | Sholosohor | 132 | 134 | 2025-08-08 09:00 | 126 | 2025-08-10 15:00
175 | Shyampur | 132 | 134 | 2025-08-08 17:00 | 123 | 2025-08-28 10:00
176 | Shyampur-230 | 132 | 134 | 2025-08-01 18:30 | 123 | 2025-08-02 13:00
177 | Siddhirganj | 132 | 134 | 2025-08-08 17:00 | 123 | 2025-08-02 15:00
178 | Sirajganj | 132 | 137 | 2025-08-01 10:00 | 121 | 2025-08-25 22:00
179 | Sonargaon | 132 | 132 | 2025-08-08 18:00 | 120 | 2025-08-02 15:00
180 | Sreemongol | 132 | 138 | 2025-08-05 15:00 | 125 | 2025-08-02 22:00
181 | Sreepur | 132 | 136 | 2025-08-05 15:00 | 124 | 2025-08-09 23:00
182 | Srinagar | 132 | 138 | 2025-08-08 08:00 | 125 | 2025-08-02 14:00
183 | SSM | 132 | 139 | 2025-08-01 08:00 | 129 | 2025-08-10 13:00
184 | Sunamganj | 132 | 132 | 2025-08-03 15:00 | 111 | 2025-08-01 23:00
185 | Sylhet | 132 | 134 | 2025-08-09 08:00 | 119 | 2025-08-01 23:00
186 | Sylhet-132 | 132 | 135 | 2025-08-03 15:00 | 120 | 2025-08-01 23:00
187 | Tangail | 132 | 135 | 2025-08-05 01:00 | 118 | 2025-08-26 18:30
188 | Taraganj | 132 | 135 | 2025-08-13 19:00 | 119 | 2025-08-02 22:00
189 | Thakurgaon | 132 | 141 | 2025-08-19 18:30 | 117 | 2025-08-05 13:00
190 | TK | 132 | 133 | 2025-08-07 19:00 | 126 | 2025-08-10 15:00
191 | Tongi | 132 | 140 | 2025-08-05 07:00 | 124 | 2025-08-14 15:00
192 | Ullahpara | 132 | 138 | 2025-08-01 10:00 | 125 | 2025-08-16 22:00
193 | Ullon | 132 | 140 | 2025-08-04 04:00 | 120 | 2025-08-18 15:00
194 | Uttara | 132 | 135 | 2025-08-06 05:00 | 122 | 2025-08-18 15:00
195 | UttaraNew | 132 | 138 | 2025-08-14 17:00 | 122 | 2025-08-02 12:00
196 | Zigatola | 132 | 146 | 2025-08-16 11:00 | 125 | 2025-08-18 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: August 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 25-08-2025 | 09:00 | 415 | 185 | 87.3784
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 25-08-2025 | 09:00 | 415 | 185 | 87.3784
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 25-08-2025 | 09:00 | 415 | 185 | 87.3784
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-08-2025 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 03-08-2025 | 13:00 | 209 | 93 | 43.9918
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 03-08-2025 | 13:00 | 209 | 93 | 43.9918
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 11-08-2025 | 20:00 | 240 | 67 | 47.9186
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 11-08-2025 | 20:00 | 232 | 59 | 46.0355
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 07-08-2025 | 12:00 | 428 | 127 | 59.526
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 07-08-2025 | 12:00 | 428 | 127 | 59.526
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 07-08-2025 | 10:00 | 427 | 120 | 59.1389
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 11-08-2025 | 22:00 | 175 | 67 | 57.6576
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 11-08-2025 | 22:00 | 175 | 67 | 57.6576
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 11-08-2025 | 22:00 | 175 | 67 | 57.6576
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 11-08-2025 | 23:00 | 277 | 30 | 37.1493
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 19-08-2025 | 14:00 | 322 | 199 | 72.7942
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 19-08-2025 | 16:00 | 322 | 192 | 72.0956
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 03-08-2025 | 18:00 | 300 | 58 | 94.017
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 03-08-2025 | 18:00 | 300 | 58 | 94.017
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 07-08-2025 | 01:00 | 428 | 157 | 60.7849
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 07-08-2025 | 01:00 | 428 | 157 | 60.7849
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 07-08-2025 | 01:00 | 428 | 157 | 60.7849
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 01-08-2025 | 23:00 | 445 | 147 | 62.4868
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 01-08-2025 | 23:00 | 444 | 146 | 62.3185
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 |  |  |  |  | 0
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 20-08-2025 | 21:00 | 414 | 61 | 80.475
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 20-08-2025 | 21:00 | 410 | 61 | 79.714
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 28-08-2025 | 08:00 | 74 | 16 | 23.2954
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 07-08-2025 | 13:00 | 76 | 17 | 23.9625
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 27-08-2025 | 14:00 | 167 | 53 | 33.6939
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 11-08-2025 | 22:00 | 117 | 26 | 23.0489
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 12-08-2025 | 13:00 | 201 | 84 | 72.6154
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 12-08-2025 | 13:00 | 201 | 84 | 72.6154
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 30-08-2025 | 08:00 | 186 | 35 | 84.1175
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 30-08-2025 | 15:00 | 180 | 46 | 82.571
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 30-08-2025 | 08:00 | 186 | 35 | 84.1175
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 29-08-2025 | 21:00 | 227 | 120 | 85.5888
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 08-08-2025 | 05:00 | 216 | 26 | 72.5197
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 27-08-2025 | 00:00 | 171 | 60 | 60.407
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 26-08-2025 | 18:30 | 131 | 33 | 60.0411
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 10-08-2025 | 19:00 | 221 | 38 | 99.6636
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 17-08-2025 | 21:00 | 212 | 73 | 99.6517
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 17-08-2025 | 20:00 | 275 | 71 | 94.6725
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 19-08-2025 | 22:00 | 207 | 63 | 72.1249
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 12-08-2025 | 17:00 | 194 | 46 | 66.4597
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 20-08-2025 | 19:30 | 117 | 15 | 52.4256
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 20-08-2025 | 19:30 | 117 | 15 | 52.4256
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 26-08-2025 | 01:00 | 175 | 42 | 79.9864
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 26-08-2025 | 01:00 | 175 | 42 | 79.9864
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 26-08-2025 | 01:00 | 234 | 60 | 80.5233
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 26-08-2025 | 01:00 | 234 | 60 | 80.5233
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 12-08-2025 | 22:00 | 171 | 70 | 82.1213
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 12-08-2025 | 22:00 | 169 | 68 | 80.9633
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 12-08-2025 | 22:00 | 181 | 72 | 86.5755
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 16-08-2025 | 06:00 | 212 | 126 | 82.2057
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 07-08-2025 | 21:00 | 239 | 98 | 86.1039
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 06-08-2025 | 21:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 06-08-2025 | 21:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 29-08-2025 | 15:00 | 129 | 71 | 65.4436
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 06-08-2025 | 10:00 | 121 | 68 | 61.6882
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 06-08-2025 | 10:00 | 115 | 74 | 60.7785
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 17-08-2025 | 16:00 | 77 | 44 | 39.4155
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 17-08-2025 | 16:00 | 77 | 44 | 39.4155
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 17-08-2025 | 16:00 | 77 | 44 | 39.4155
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 02-08-2025 | 19:30 | 96 | 55 | 73.7594
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-08-2025 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 02-08-2025 | 19:30 | 96 | 55 | 73.7594
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 02-08-2025 | 19:30 | 96 | 55 | 73.7594
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 20-08-2025 | 21:00 | 110 | 39 | 51.8707
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 20-08-2025 | 21:00 | 110 | 39 | 51.8707
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 20-08-2025 | 19:00 | 108 | 36 | 50.5964
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 16-08-2025 | 19:30 | 212 | 77 | 75.1835
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 16-08-2025 | 19:30 | 212 | 77 | 75.1835
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 31-08-2025 | 06:00 | 279 | 41 | 93.9988
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 16-08-2025 | 19:00 | 207 | 67 | 72.5243
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 16-08-2025 | 19:00 | 207 | 67 | 72.5243
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-08-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 17-08-2025 | 00:00 | 156 | 60 | 74.2847
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 17-08-2025 | 00:00 | 156 | 60 | 74.2847
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 17-08-2025 | 00:00 | 202 | 71 | 71.3715
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 02-08-2025 | 18:30 | 121 | 21 | 40.9363
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 02-08-2025 | 16:00 | 114 | 24 | 38.833
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 02-08-2025 | 18:30 | 121 | 21 | 40.9363
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 22-08-2025 | 07:00 | 183 | 57 | 63.8905
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 23-08-2025 | 03:00 | 220 | 96 | 80.0111
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 17-08-2025 | 05:00 | 108 | 28 | 37.1902
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 17-08-2025 | 05:00 | 108 | 28 | 37.1902
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-08-2025 | 04:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 16-08-2025 | 21:00 | 1 | 0 | 0.33333
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 14-08-2025 | 10:00 | 363 | 38 | 81.1075
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 14-08-2025 | 10:00 | 363 | 38 | 81.1075
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 18-08-2025 | 16:00 | 288 | 66 | 65.6591
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 02-08-2025 | 12:00 | 220 | 107 | 81.5469
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 02-08-2025 | 12:00 | 220 | 107 | 81.5469
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 30-08-2025 | 16:00 | 159 | 66 | 57.3847
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 30-08-2025 | 16:00 | 159 | 66 | 57.3847
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 17-08-2025 | 12:00 | 215 | 98 | 78.7605
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 06-08-2025 | 09:00 | 124 | 3 | 41.3454
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 11-08-2025 | 19:00 | 250 | 91 | 88.6823
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 11-08-2025 | 19:00 | 250 | 91 | 88.6823
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 09-08-2025 | 18:00 | 210 | 22 | 93.8441
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 16-08-2025 | 18:30 | 188 | 40 | 85.4259
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 09-08-2025 | 18:00 | 192 | 35 | 86.7396
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: August 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: August 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-08-01 | 13620.22 | 13620.22 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-01 | 11666.46 | 11666.46 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-02 | 15156.2 | 15156.2 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-02 | 13004.82 | 13004.82 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-03 | 15065.51 | 15065.51 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-03 | 13601.24 | 13601.24 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-04 | 15107.95 | 15107.95 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-04 | 13182.89 | 13182.89 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-05 | 13303.05 | 13303.05 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-05 | 11508.45 | 11508.45 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-06 | 14817.97 | 14880.67 | 60 | 19:30 Hr. | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 35 | - | 2025-08-06 | 13201.79 | 13201.79 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-07 | 14752 | 14782 | 29 | 19:30 Hr. | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | - | 2025-08-07 | 13527.41 | 13527.41 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-08 | 12825 | 12825 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-08 | 11154.53 | 11154.53 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-09 | 14688.56 | 14750.22 | 59 | 19:30 Hr. | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | - | 2025-08-09 | 12274.85 | 12274.85 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-10 | 15608.83 | 15670.83 | 59 | 19:30 Hr. | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 44 | - | 2025-08-10 | 13712.73 | 13712.73 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-08-11 | 16076.4 | 16199.71 | 118 | 19:30 Hr. | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 43 | - | 2025-08-11 | 13833.5 | 13833.5 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-12 | 15957.1 | 16011.1 | 52 | 21:00 Hr. | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 47 | - | 2025-08-12 | 14273.89 | 14273.89 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-13 | 14980.18 | 14980.18 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-13 | 13396.18 | 13396.18 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-14 | 15163.03 | 15163.03 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-14 | 13450.25 | 13450.25 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-15 | 14692.43 | 14692.43 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-15 | 12362.08 | 12362.08 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-16 | 15951.16 | 16046.16 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-16 | 13239.6 | 13239.6 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-17 | 15869.27 | 16031.27 | 155 | 21:00 Hr. | 10 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 55 | - | 2025-08-17 | 13946.14 | 13946.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-18 | 15945.99 | 16151.86 | 197 | 20:00 Hr. | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 90 | - | 2025-08-18 | 14011 | 14011 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-19 | 15448.06 | 15501.36 | 51 | 20:00 Hr. | 45 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-19 | 13600.46 | 13600.46 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-20 | 15100.67 | 15100.67 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-20 | 13217.94 | 13217.94 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-21 | 14587.2 | 14616.46 | 28 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | - | 2025-08-21 | 13263.58 | 13263.58 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-22 | 13502.5 | 13502.5 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-22 | 11424.63 | 11424.63 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-23 | 14280.17 | 14280.17 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-23 | 11741.39 | 11741.39 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-24 | 14966.06 | 14966.06 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-24 | 12931.36 | 12931.36 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-25 | 15672.2 | 15749.53 | 74 | 20:00 Hr | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-25 | 13445.14 | 13445.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-26 | 16054.39 | 16131.39 | 74 | 19:30 Hr. | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-26 | 14206.37 | 14206.37 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-27 | 15878.29 | 15878.29 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-27 | 14200.84 | 14200.84 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-28 | 15506.45 | 15506.45 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-08-28 | 13864.61 | 13902.61 | 36 | 12:00 Hr. | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | -
2025-08-29 | 14139.55 | 14139.55 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-08-29 | 12221.54 | 12221.54 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-30 | 15432.34 | 15432.34 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-08-30 | 12576.66 | 12576.66 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-08-31 | 15775.26 | 15825.42 | 48 | 21:00 Hr. | 7 | 0 | 11 | 30 | 0 | 0 | 0 | 0 | 0 |  | 2025-08-31 | 14207.45 | 14207.45 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: August 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16076.4 | 2025-08-11 | 19:30 Hr.
2 | Maximum Day Peak Genaration | MW | 14273.89 | 2025-08-12 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 16199.71 | 2025-08-11 | 19:30 Hr.
4 | Minimum Generation | MW | 9865.74 | 2025-08-08 | 05:00 Hr
5 | Average of the daily evening peak Genaration | MW | 15029.8061 | - | -
6 | Average of the daily day peak Genaration | MW | 13104.8316 | - | -
7 | Maximum load shed (Evening Peak) | MW | 197 | 2025-08-18 | 20:00 Hr.
8 | Minimum load shed | MW | 0 | 2025-08-01 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 13 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 31.8667 | - | -
11 | Total Generation | MkWh | 10122.3155 | - | -
12 | Total Generation by BPDB | MkWh | 1209.5845 | % of total Gen. | 11.95%
13 | Total Generation by IPP | MkWh | 2717.094 | '' | 26.84%
14 | A) Total Generation by Generation Companies | MkWh | 4555.8076 | '' | 45.01%
| B) Total Generation by REB | MkWh | 48.2344 | " | 0.4765%
| C) Total Generation by RENTAL | MkWh | 132.6744 | " | 1.311%
| D) Total Imported from India (BIPTC) | MkWh | 643.7724 | " | 6.36%
| E) Total Imported from Tripura, India (A.C) | MkWh | 29.4278 | " | 0.2907%
| F) Total Imported from Nepal | MkWh | 27.556 | " | 0.2722%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 758.1643 | " | 7.49%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4290.1188 | % of total Gen. | 42.38%
| B) Oil | MkWh | 947.2836 | '' | 9.358%
| C) Hydro | MkWh | 162.1321 | '' | 1.602%
| D) Solar | MkWh | 108.7313 | '' | 1.074%
| E) Coal | MkWh | 3144.9225 | '' | 31.07%
| F) BIPTC (Import from India) | MkWh | 643.7724 | '' | 6.36%
| G) A.C (Import from Tripura, India) | MkWh | 29.4278 | '' | 0.2907%
| H) Total Imported from Nepal | MkWh | 27.556 | '' | 0.2722%
| I) Adani (Import from India) | MkWh | 758.1643 | '' | 7.49%
| J) Wind | MkWh | 10.2067 | '' | 0.1008%
16 | Maximun of the daily total Generation . | MkWh | 363.0276 | 2025-08-18
17 | Monthly Load factor | % | 84.6288 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 61394.0404 | - | -
| A) Gas | M.Taka | 15396.8042 | - | -
| B) Coal | M.Taka | 18793.6642 | - | -
| C) HFO | M.Taka | 17546.0822 | - | -
| D) HSD | M.Taka | 34.4148 | - | -
| E) Hydro | M.Taka | 16.2188 | - | -
| F) Solar | M.Taka | 1648.1095 | - | -
| G) Total Import | M.Taka | 7810.1012 | - | -
| H) Wind | M.Taka | 148.6454 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2518.7733 | 2025-08-18
| A) Gas | M.Taka | 525.0203 | 2025-08-17
| B) Coal | M.Taka | 670.5722 | 2025-08-27
| C) HFO | M.Taka | 1033.2087 | 2025-08-18
| D) HSD | M.Taka | 33.1127 | 2025-08-27 | -
| E) Hydro | M.Taka | 0.5346 | 2025-08-20 | -
| F) Solar | M.Taka | 79.5822 | 2025-08-16 | -
| G) Total Import | M.Taka | 293.447 | 2025-08-28
| H) Wind | M.Taka | 12.4099 | 2025-08-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.0652
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.2384
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/08/2025 | 06:00
b) | Actual | FT (MSL) | 107.88 | 31/08/2025 | 06:00
22 | Peak Genaration of August 2024 | MW | 14612 | 2024-08-31 | 21:00
23 | Peak Demand of August 2024 | MW | 15530 | 2024-08-15 | 21:00
24 | Maximum peak Generation recorded upto 31/08/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/08/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/08/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [26 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable |  |  | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable |  |  |  | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | 305 | Capable | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [34 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable |  |  |  | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | 412 | Capable | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | [9 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable | [27 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [24 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable |  | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | 194 | Capable | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable |  |  | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable | [12 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
26 | b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
27 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
28 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
29 | Bibiyana South 400 MW CCPP | BPDB | 400 | Capable | [32 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
| Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244 | Capable | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150 | Capable |  | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105 | Capable
40 | Gazipur 100 MW PP | IPP | 105 | Capable
41 | United Payra Power Ltd. | IPP | 150 | Capable
42 | Madhumati 100 MW PP | IPP | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149 | Capable
48 | Feni Lanka Power | IPP | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55 | Capable
52 | Zodiac 54 MW | IPP | 54 | Capable
53 | Anlima Energy Ltd | IPP | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 | Capable | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 | Capable | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | 1234 | Capable | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | 307 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Payra 1320 MW Unit-2 | BCPCL | 622 | Capable | [16 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
| Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
Total Installed capacity |  |  |  |  | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: August 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ |  | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | [5 empty] | √ | √ |  |  |  | √ | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 |  |  | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ |  | √ | √ | √ | √ | [5 empty] | √ | √ |  |  |  |  | √
5 | Meghnaghat CCPP(Summit) | IPP | 305 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360
7 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | 410
9 | Haripur 412 MW CCPP | EGCB | 412 | [8 empty] | √ |  |  |  |  | √ |  | √ | √ |  | √ |  |  |  |  | √ |  |  |  | √ | √ | √ | √
10 | Fenchugonj CCPP Phase-1 | BPDB | 97
11 | Chandpur 150 MW CCPP | BPDB | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210
13 | Shikalbaha 225 MW CCPP | BPDB | 225
14 | Shikalbaha Peaking GT | BPDB | 150
15 | Shahjibazar 330 MW CCPP | BPDB | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | 104
18 | Bhola 225 MW CCPP | BPDB | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √ | [5 empty] | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | 231
24 | RPCL 210 MW CCPP | IPP | 210
25 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
27 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | 220 | [28 empty] | √
33 | Haripur 360MW CCPP(HPL) | IPP | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150 |  |  |  |  | √ | [13 empty] | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
36 | Anwara 300 MW PP (United) | IPP | 300
37 | Chandpur 200MW (Desh energy) | IPP | 200 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105
40 | Gazipur 100 MW PP | IPP | 105
41 | United Payra Power Ltd. | IPP | 150
42 | Madhumati 100 MW PP | IPP | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105
44 | Karnaphuli Power Ltd. | IPP | 110
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300
46 | Madanganj-55 MW PP(Summit) | IPP | 55
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149
48 | Feni Lanka Power | IPP | 114 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | 110
50 | Manikganj 162 MW (MPGL) | IPP | 162 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55
52 | Zodiac 54 MW | IPP | 54
53 | Anlima Energy Ltd | IPP | 116
54 | Thakurgaon 115 MW (EPV) | IPP | 115
55 | Confidence Unit-2 Bogura | IPP | 113
56 | Confidence Unit-1 Bogura | IPP | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | 54 | [13 empty] | √ | [5 empty] | √ | [7 empty] | √ | √ | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55
59 | Kodda 150 MW (BR Power) | IPP | 149
60 | Chandpur 115 MW (Doreen) | IPP | 115 | [12 empty] | √ | [8 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
61 | Kanchan Purbachal Power Ltd | IPP | 55
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 |  |  |  | √ |  | √ | [7 empty] | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 |  |  |  | √ |  |  |  |  | √ |  |  |  |  | √ |  |  |  |  | √ |  |  |  |  | √ |  |  |  | √ | √
64 | Rampal 1320 MW (BIFPCL) | BIFPCL | 1234 |  |  |  | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | 307 | [8 empty] | √ |  |  |  |  | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ |  |  |  | √
| Unique Meghnaghat Power Limited (UMPL) | IPP | 584 | [7 empty] | √ | [8 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| Meghnaghat CCPP(Summit)-2 | IPP | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| United Payra Power Ltd. | IPP | 150 | [24 empty] | √ | √ | √ |  | √ | √ | √
| Bibiyana South 400 MW | BPDB | 383
| Ashuganj 420 MW CCPP(East) | APSCL | 400
| Ashuganj 55 MW PP (Precision) | QRPP | 55
| Bagura 113 MW PP (Confidence)-2 | IPP | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP | 115
| Chandpur 150 MW CCPP | BPDB | 163
| Khulna 225 MW CCPP | NWPGCL | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
| Shajibazar 100 MW PP | BPDB | 100
| Payra 1320 MW Unit-1 | BCPCL | 622