## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-09-2025 | during | 18-09-2025 | during | 18-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 351 | 335 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 340 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 293 | 295 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 50 | 0 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 11 | 43 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 74 | 124 | 133 | 133 | 117 | 117 | FGMO
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 44 | 55 | 55 | 55 | 40 | 40 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 24 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 80 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 91 | 113 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 87.5 | 87.5 | 51 | 70 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 148 | 144 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 7 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 320 | 584 | 584 | 528 | 528 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2319 | 2525 | 5800.54 | 5820.54 | 3621.5 | 3678.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 195 | 195 | 195 | 195 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 31 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 54 | 56 | 70 | 56 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.88 | 0 | 1.34 | 0 | 1.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 28 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1120 | 1130 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 265 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1877.88 | 2149 | 3110.2 | 3118.86 | 2839.7 | 2848.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 181 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 410 | 0 | 393 | 393 | 393 | 393
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 37 | 55 | 55 | 10 | 10 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 81 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 100 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 35 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 7 | 123 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 44 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 91 | 115 | 115 | 92 | 92 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1530 | 1657 | 2822.56 | 2772.56 | 2506.06 | 2465.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-09-2025 | during | 18-09-2025 | during | 18-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 22 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.78 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 18 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 125.78 | 143 | 356.7 | 320.5 | 151.7 | 115.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 58 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 167 | 167 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 5 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 301 | 348 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1053 | 1164 | 1278 | 1278 | 1185 | 1185
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 881 | 882 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 5 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63.04 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 946 | 1096 | 1234.2 | 1234.2 | 1204 | 1204
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1933.04 | 2016 | 3640.2 | 3552.2 | 3005 | 2917
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 304 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1080 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 241 | 268 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1969 | 1987 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 45.9 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 196 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 158 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 158 | 220 | 220 | 195 | 195 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 7 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.76 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 818 | 1449.45 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 6.13 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 89 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1921.79 | 2541.45 | 3181.52 | 3014.87 | 3123.64 | 2956.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 42 | 43 | 45 | 45 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 165 | 160 | 160 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 2.6 | 0 | 2.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 112 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 111 | 0 | 123.05 | 0 | 123.05 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 501.1 | 433 | 602.65 | 453 | 597.65 | 448
System Total |  |  |  |  | 28823.2 | 27829.875 | 13230.59 | 14615.45 | 22954.37 | 22491.53 | 19112.25 | 18695.41
Forecast Scenario (18-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13890 |  | 0 |  | 13890
|  |  |  | 1:00 | 13380 |  | 0 |  | 13380
|  |  |  | 2:00 | 12990 |  | 0 |  | 12990
|  |  |  | 3:00 | 12650 |  | 0 |  | 12650
|  |  |  | 4:00 | 12450 |  | 0 |  | 12450
|  |  |  | 5:00 | 12300 |  | 0 |  | 12300
|  |  |  | 6:00 | 11950 |  | 0 |  | 11950
|  |  |  | 7:00 | 12100 |  | 0 |  | 12100
|  |  |  | 8:00 | 12260 |  | 0 |  | 12260
|  |  |  | 9:00 | 12520 |  | 0 |  | 12520
|  |  |  | 10:00 | 12730 |  | 0 |  | 12730
|  |  |  | 11:00 | 13030 |  | 0 |  | 13030
|  |  |  | 12:00 | 13530 |  | 0 |  | 13530
|  |  |  | 13:00 | 13650 |  | 0 |  | 13650
|  |  |  | 14:00 | 13360 |  | 0 |  | 13360
|  |  |  | 15:00 | 13390 |  | 0 |  | 13390
|  |  |  | 16:00 | 13260 |  | 0 |  | 13260
|  |  |  | 17:00 | 12960 |  | 0 |  | 12960
|  |  |  | 18:00 | 13430 |  | 0 |  | 13430
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14960 |  | 0 |  | 14960
|  |  |  | 19:30 | 15000 |  | 0 |  | 15000
|  |  |  | 20:00 | 14900 |  | 0 |  | 14900
|  |  |  | 21:00 | 14750 |  | 0 |  | 14750
|  |  |  | 22:00 | 14540 |  | 0 |  | 14540
|  |  |  | 23:00 | 14500 |  | 0 |  | 14500
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13530.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.48 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:07 hrs on 18-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-09-2025 | [28 empty] | Date: | 17-09-2025 | [28 empty] | Date: | 17-09-2025 | [28 empty] | Date: | 17-09-2025 | [28 empty] | Date: | 17-09-2025 | [14 empty] | Date: | 17-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 15.1 | 17 | 96 | 90 | 15 | 0 | 17 | 101 | 0 | 300 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 36 | 265 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 1112 | 0 | 51 | 20 | 0 | 275 | 300 | 300 | 5 | 217 | 5 | 91 | 90 | 15 | 0 | 19 | 114 | 44 | 0 | 0 | 37 | 305 | 0 | 308 | 0 | 58 | 137 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 0 | 0 | 0 | 18 | 6891.1 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1131 | 0 | 1416.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 170 | 0 | 170 | 0 | 414 | 0 | 0 | 166 | 42 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 115 | 220 | 0 | 304 | 1090 | 0 | 6658.97 | 13550.07 | 108.4
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 69 | 90 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 36 | 265 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1082 | 0 | 51 | 0 | 0 | 285 | 300 | 300 | 5 | 189 | 5 | 90 | 90 | 14 | 0 | 19 | 114 | 44 | 0 | 0 | 37 | 310 | 0 | 316 | 0 | 58 | 137 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 0 | 0 | 0 | 18 | 6587 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 1356.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 170 | 0 | 170 | 0 | 414 | 0 | 0 | 165 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 115 | 220 | 0 | 305 | 1090 | 0 | 6464.48 | 13051.48 | 108.4
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 36 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 35 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 36 | 265 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1102 | 0 | 51 | 0 | 0 | 285 | 300 | 300 | 5 | 200 | 5 | 91 | 90 | 15 | 0 | 19 | 114 | 42 | 0 | 0 | 37 | 310 | 0 | 330 | 0 | 0 | 144 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 0 | 0 | 0 | 18 | 6513 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1042 | 0 | 1210.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 171 | 0 | 170 | 0 | 414 | 0 | 0 | 162 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 115 | 220 | 0 | 305 | 1000 | 0 | 6155.57 | 12668.57 | 108.4
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 36 | 265 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 0 | 285 | 300 | 300 | 5 | 197 | 5 | 90 | 90 | 16 | 0 | 19 | 70 | 40 | 0 | 0 | 37 | 310 | 0 | 321 | 0 | 0 | 146 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 0 | 78 | 9 | 0 | 0 | 0 | 14 | 6341 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 1117.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 174 | 0 | 170 | 0 | 414 | 0 | 0 | 162 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 115 | 220 | 0 | 305 | 990 | 0 | 6014.43 | 12355.43 | 108.4
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 23.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 36 | 266 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 968 | 0 | 51 | 0 | 0 | 285 | 300 | 300 | 5 | 193 | 5 | 90 | 90 | 0 | 0 | 19 | 34 | 40 | 0 | 0 | 37 | 310 | 0 | 315 | 0 | 0 | 142 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 0 | 78 | 9 | 0 | 0 | 0 | 18 | 6229.5 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 1044.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 176 | 0 | 176 | 0 | 414 | 0 | 0 | 163 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 115 | 220 | 0 | 305 | 990 | 0 | 5922.31 | 12151.81 | 108.4
05:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 37 | 266 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 914 | 0 | 51 | 0 | 0 | 300 | 300 | 300 | 5 | 198 | 5 | 58 | 90 | 0 | 0 | 19 | 34 | 40 | 0 | 0 | 37 | 315 | 0 | 336 | 0 | 0 | 147 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 0 | 78 | 9 | 0 | 0 | 0 | 13 | 6168.5 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 882 | 0 | 1015.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 179 | 0 | 182 | 0 | 414 | 0 | 0 | 163 | 44 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 181 | 115 | 220 | 0 | 305 | 902 | 0 | 5840.38 | 12008.88 | 108.4
06:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 334 | 0 | 0 | 1 | 35 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0.12 | 222 | 0 | 31 | 266 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 866 | 0 | 51 | 0 | 0 | 300 | 300 | 300 | 5 | 198 | 5 | 31 | 90 | 0 | 0 | 8 | 34 | 38 | 0 | 1 | 0 | 305 | 0 | 337 | 0 | 0 | 141 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 0 | 0 | 0 | 12 | 6008.62 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 824 | 0 | 914.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 0 | 0 | 0 | 194 | 0 | 179 | 0 | 186 | 0 | 414 | 0 | 0 | 164 | 44 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0.01 | 0 | 178 | 115 | 220 | 0 | 304 | 820 | 0 | 5646.98 | 11655.6 | 108.4
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 333 | 0 | 0 | 6 | 35 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 26 | 265 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 906 | 2 | 51 | 0 | 0 | 335 | 300 | 300 | 5 | 202 | 5 | 32 | 90 | 0 | 0 | 19 | 34 | 34 | 0 | 14 | 0 | 310 | 0 | 335 | 0 | 0 | 147 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 0 | 0 | 0.43 | 12 | 6125.43 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 805 | 0 | 916.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.29 | 16 | 0 | 0 | 6.05 | 196 | 0 | 180 | 0 | 188 | 0 | 414 | 0 | 0.47 | 163 | 44 | 0 | 1 | 0 | 0 | 170 | 0 | 0.1 | 4 | 0.15 | 0 | 182 | 115 | 220 | 0 | 305 | 804 | 0 | 5677.68 | 11803.11 | 108.4
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 33 | 45 | 0 | 0 | 6 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 333 | 0 | 0 | 7 | 35 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 222 | 0 | 9 | 265 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 900 | 4 | 51 | 0 | 0 | 335 | 300 | 300 | 5 | 190 | 5 | 30 | 90 | 0 | 0 | 19 | 34 | 32 | 0 | 40 | 0 | 310 | 0 | 308 | 0 | 0 | 141 | 6 | 0 | 82 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 0 | 1 | 2.67 | 12 | 6100.76 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 824 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.15 | 58 | 0 | 0 | 7.45 | 196 | 0 | 181 | 0 | 185 | 0 | 414 | 0 | 0.93 | 160 | 44 | 0 | 2 | 0 | 0 | 170 | 0 | 0.5 | 15 | 0.19 | 0 | 175 | 115 | 220 | 0 | 306 | 870 | 0 | 5859.22 | 11959.98 | 108.4
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 33 | 45 | 0 | 0 | 17 | 0 | 0 | 300 | 308 | 0 | 0 | 0 | 330 | 0 | 0 | 20 | 35 | 24.5 | 22 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.14 | 222 | 0 | 3 | 265 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 920 | 9 | 51 | 0 | 0 | 335 | 300 | 300 | 5 | 204 | 5 | 16 | 90 | 0 | 0 | 19 | 16 | 34 | 0 | 58 | 0 | 315 | 0 | 346 | 0 | 0 | 144 | 6 | 0 | 82 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 0 | 1 | 6.56 | 12 | 6257.2 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 850 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.22 | 85 | 0 | 0 | 9.05 | 195 | 0 | 180 | 0 | 182 | 0 | 414 | 0 | 1.39 | 160 | 44 | 0 | 4 | 0 | 0 | 168 | 0 | 1.2 | 38 | 0.97 | 0 | 181 | 115 | 220 | 0 | 306 | 894 | 0 | 5967.83 | 12225.03 | 108.4
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 52 | 45 | 0 | 0 | 20 | 30 | 0 | 300 | 301 | 0 | 0 | 0 | 325 | 0 | 0 | 32 | 35 | 24.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.91 | 220 | 0 | 3 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1060 | 14 | 51 | 0 | 0 | 371 | 300 | 300 | 5 | 204 | 5 | 17 | 90 | 0 | 0 | 19 | 15 | 36 | 0 | 68 | 0 | 315 | 0 | 339 | 0 | 0 | 156 | 6 | 0 | 0 | 30 | 0 | 18 | 167 | 0 | 77 | 9 | 0 | 1 | 11.13 | 12 | 6399.54 | 880 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 94.33 | 860 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4 | 55 | 0 | 0 | 30.72 | 196 | 0 | 179 | 0 | 180 | 0 | 414 | 0 | 2.55 | 166 | 44 | 0 | 10 | 0 | 0 | 168 | 0 | 3.4 | 77 | 0.71 | 0 | 180 | 115 | 220 | 0 | 304 | 919 | 0 | 6030.11 | 12429.65 | 108.4
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 83 | 45 | 0 | 0 | 35 | 33 | 0 | 300 | 305 | 0 | 0 | 0 | 323 | 0 | 0 | 16 | 35 | 23 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 220 | 0 | 4 | 265 | 0 | 0 | 17 | 0 | 0 | 216 | 0 | 0 | 0 | 1175 | 16 | 51 | 0 | 0 | 410 | 300 | 280 | 5 | 205 | 5 | 16 | 90 | 0 | 0 | 19 | 15 | 38 | 0 | 58 | 0 | 310 | 0 | 345 | 0 | 0 | 156 | 6 | 0 | 0 | 30 | 0 | 18 | 167 | 0 | 77 | 9 | 0 | 1 | 18.22 | 12 | 6585.82 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 89.57 | 842 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.22 | 88 | 0 | 0 | 38.36 | 196 | 0 | 177 | 0 | 178 | 0 | 414 | 0 | 2.15 | 168 | 43 | 0 | 6 | 0 | 0 | 168 | 0 | 3.4 | 77 | 0.59 | 0 | 180 | 115 | 220 | 0 | 303 | 1036 | 0 | 6148.29 | 12734.11 | 108.4
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 11 | 7 | 91 | 74 | 80 | 0 | 44 | 148 | 0 | 350 | 293 | 0 | 0 | 30 | 325 | 0 | 0 | 29 | 35 | 24 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 219 | 0 | 6 | 265 | 0 | 0 | 30 | 0 | 0 | 218 | 0 | 0 | 0 | 1120 | 17 | 51 | 10 | 0 | 410 | 320 | 280 | 5 | 181 | 5 | 17 | 90 | 7 | 0 | 7 | 44 | 38 | 0 | 65 | 0 | 315 | 0 | 301 | 0 | 0 | 157 | 5 | 0 | 60 | 30 | 0 | 18 | 167 | 0 | 77 | 9 | 10 | 2 | 15.78 | 12 | 6905.66 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 63.04 | 946 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.9 | 89 | 0 | 0 | 6.13 | 197 | 0 | 175 | 0 | 175 | 0 | 414 | 0 | 1.76 | 166 | 42 | 0 | 10 | 0 | 0 | 167 | 0 | 5.1 | 111 | 0 | 0 | 241 | 115 | 220 | 0 | 303 | 1090 | 0 | 6324.93 | 13230.59 | 108.4
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 44.8 | 17 | 143 | 62 | 145 | 8 | 55 | 154 | 0 | 350 | 287 | 0 | 0 | 55 | 327 | 0 | 0 | 24 | 108 | 24 | 0 | 0 | 350 | 0 | 0 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 2.75 | 219 | 0 | 15 | 265 | 0 | 0 | 50 | 1 | 0 | 217 | 0 | 0 | 0 | 1141 | 18 | 51 | 70 | 6 | 0 | 341 | 330 | 8 | 192 | 12 | 16 | 90 | 29 | 0 | 7 | 40 | 42 | 0 | 73 | 2 | 300 | 0 | 305 | 0 | 0 | 140 | 5 | 0 | 78 | 30 | 0 | 18 | 167 | 15 | 76 | 9 | 10 | 0 | 45.16 | 12 | 7068.71 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 59.56 | 1026 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.64 | 20 | 0 | 0 | 8.44 | 196 | 0 | 175 | 0 | 173 | 0 | 414 | 0 | 0.87 | 168 | 43 | 0 | 14 | 0 | 0 | 126 | 0 | 5.2 | 113 | 0.34 | 0 | 246 | 115 | 220 | 0 | 303 | 1090 | 0 | 6281.05 | 13349.76 | 108.4
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 41 | 17 | 138 | 74 | 145 | 0 | 55 | 150 | 0 | 300 | 301 | 0 | 0 | 17 | 250 | 0 | 0 | 9 | 70 | 24.5 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 3.13 | 220 | 0 | 10 | 265 | 0 | 0 | 50 | 8 | 0 | 216 | 0 | 0 | 0 | 1100 | 17 | 51 | 70 | 8 | 0 | 344 | 330 | 31 | 196 | 33 | 17 | 90 | 29 | 0 | 7 | 40 | 44 | 0 | 64 | 17 | 300 | 0 | 332 | 0 | 0 | 137 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 77 | 9 | 10 | 0 | 8.04 | 12 | 6834.67 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 23.62 | 1020 | 0 | 816.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.59 | 30 | 0 | 0 | 12.66 | 195 | 0 | 150 | 0 | 150 | 0 | 414 | 0 | 1.17 | 168 | 43 | 0 | 14 | 0 | 0 | 125 | 0 | 2.2 | 134 | 0.17 | 0 | 248 | 115 | 220 | 0 | 304 | 1086 | 0 | 6225.81 | 13060.48 | 108.4
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 31 | 17 | 113 | 74 | 30 | 0 | 55 | 155 | 0 | 300 | 298 | 0 | 0 | 17 | 327 | 0 | 0 | 14 | 70 | 24 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 1 | 220 | 0 | 5 | 265 | 0 | 0 | 50 | 11 | 0 | 217 | 0 | 0 | 0 | 1091 | 13 | 51 | 55 | 41 | 0 | 350 | 330 | 37 | 194 | 34 | 16 | 90 | 32 | 0 | 7 | 46 | 42 | 0 | 53 | 14 | 315 | 0 | 316 | 0 | 0 | 145 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 77 | 9 | 11 | 0 | 23.12 | 12 | 6828.12 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 31.99 | 1041 | 0 | 919.25 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 26.63 | 0 | 0 | 0 | 8.09 | 196 | 0 | 150 | 0 | 151 | 0 | 414 | 0 | 0.68 | 164 | 42 | 0 | 15 | 0 | 0 | 84 | 0 | 3 | 93 | 0.11 | 0 | 246 | 115 | 220 | 0 | 305 | 1097 | 0 | 6263.75 | 13091.87 | 108.4
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 31.4 | 17 | 85 | 74 | 15 | 0 | 55 | 126 | 0 | 340 | 299 | 0 | 0 | 0 | 328 | 0 | 0 | 8 | 52 | 24 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0.92 | 220 | 0 | 8 | 268 | 0 | 0 | 50 | 6 | 0 | 218 | 0 | 0 | 0 | 1103 | 8 | 51 | 20 | 45 | 0 | 351 | 330 | 24 | 198 | 37 | 16 | 70 | 33 | 0 | 7 | 48 | 40 | 0 | 33 | 9 | 310 | 0 | 336 | 0 | 40 | 154 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 77 | 9 | 11 | 1 | 7.34 | 12 | 6751.66 | 881 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1040 | 0 | 921.49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 9.49 | 0 | 0 | 0 | 11.12 | 196 | 0 | 157 | 0 | 153 | 0 | 414 | 0 | 0.96 | 166 | 43 | 0 | 17 | 0 | 0 | 84 | 0 | 3.1 | 54 | 0.05 | 0 | 248 | 115 | 220 | 0 | 304 | 1095 | 0 | 6208.21 | 12959.87 | 108.4
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 31 | 17 | 80 | 74 | 15 | 0 | 55 | 119 | 0 | 340 | 298 | 0 | 0 | 0 | 330 | 0 | 0 | 4 | 52 | 23 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0.52 | 220 | 0 | 16 | 265 | 0 | 0 | 50 | 17 | 0 | 217 | 0 | 0 | 0 | 1103 | 2 | 51 | 20 | 71 | 0 | 348 | 330 | 18 | 195 | 37 | 17 | 70 | 32 | 0 | 7 | 46 | 38 | 0 | 11 | 14 | 310 | 0 | 336 | 0 | 40 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 77 | 9 | 11 | 0 | 1.45 | 12 | 6734.97 | 882 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 997 | 0 | 907.47 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 4.44 | 2 | 0 | 0 | 0.66 | 195 | 0 | 158 | 0 | 157 | 0 | 414 | 0 | 0.07 | 162 | 43 | 0 | 1 | 0 | 0 | 0 | 0 | 0.8 | 10 | 0.04 | 0 | 247 | 115 | 220 | 0 | 302 | 1050 | 0 | 5928.48 | 12663.45 | 108.39
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 31 | 19 | 80 | 105 | 15 | 7 | 55 | 140 | 0 | 340 | 292 | 0 | 0 | 17 | 309 | 0 | 0 | 0 | 90 | 23 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 0 | 36 | 22 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 265 | 0 | 0 | 50 | 17 | 0 | 216 | 0 | 0 | 0 | 1084 | 0 | 51 | 28 | 81 | 0 | 344 | 325 | 26 | 186 | 37 | 18 | 40 | 32 | 0 | 7 | 46 | 46 | 2 | 0 | 21 | 305 | 0 | 310 | 0 | 58 | 153 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 11 | 0 | 0 | 12 | 6772 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 943 | 0 | 1268.37 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 0 | 5 | 0 | 0 | 196 | 0 | 158 | 0 | 157 | 0 | 350 | 0 | 0 | 166 | 43 | 90 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 302 | 995 | 0 | 6316.37 | 13088.37 | 108.39
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 49 | 35 | 103 | 124 | 95 | 15 | 55 | 153 | 0 | 340 | 298 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 108 | 24 | 5 | 0 | 320 | 0 | 0 | 50 | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 220 | 25 | 20 | 265 | 0 | 0 | 50 | 17 | 30 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 81 | 0 | 356 | 330 | 37 | 195 | 37 | 76 | 34 | 95 | 0 | 12 | 102 | 46 | 27 | 0 | 23 | 315 | 0 | 382 | 0 | 58 | 159 | 6 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 11 | 0 | 0 | 18 | 7650 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 1460.01 | 0 | 0 | 0 | 25 | 28 | 0 | 51 | 24 | 0 | 0 | 0 | 7 | 0 | 0 | 196 | 0 | 158 | 0 | 158 | 0 | 414 | 0 | 0 | 166 | 43 | 110 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 304 | 1080 | 0 | 6939.01 | 14589.01 | 108.39
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 43 | 35 | 113 | 124 | 95 | 0 | 55 | 144 | 0 | 340 | 295 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 108 | 24 | 14 | 0 | 320 | 0 | 0 | 50 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 28 | 18 | 265 | 0 | 0 | 50 | 17 | 31 | 220 | 0 | 0 | 0 | 1130 | 0 | 51 | 100 | 81 | 0 | 356 | 330 | 37 | 186 | 38 | 91 | 35 | 123 | 9 | 19 | 98 | 46 | 34 | 0 | 23 | 300 | 0 | 348 | 0 | 58 | 151 | 8 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 77 | 9 | 22 | 0 | 0 | 18 | 7638 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 1449.45 | 0 | 0 | 0 | 35 | 35 | 0 | 51 | 38 | 0 | 0 | 0 | 7 | 0 | 0 | 196 | 0 | 158 | 0 | 158 | 0 | 414 | 0 | 0 | 165 | 43 | 112 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 304 | 1080 | 0 | 6977.45 | 14615.45
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 44.6 | 35 | 113 | 124 | 15 | 0 | 55 | 145 | 0 | 340 | 295 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 320 | 0 | 0 | 50 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 30 | 21 | 265 | 0 | 0 | 50 | 17 | 32 | 220 | 0 | 0 | 0 | 1140 | 0 | 51 | 100 | 81 | 0 | 356 | 330 | 34 | 192 | 38 | 91 | 30 | 123 | 0 | 19 | 100 | 48 | 34 | 0 | 23 | 300 | 0 | 361 | 0 | 58 | 151 | 8 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 76 | 9 | 22 | 0 | 0 | 18 | 7616.6 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1079 | 0 | 1459.63 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 38 | 0 | 0 | 0 | 7 | 0 | 0 | 196 | 0 | 158 | 0 | 158 | 0 | 414 | 0 | 0 | 163 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 304 | 1085 | 0 | 6912.63 | 14529.23 | 108.39
21:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 44 | 35 | 104 | 108 | 0 | 0 | 55 | 108 | 0 | 340 | 302 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 320 | 0 | 0 | 38 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 30 | 31 | 265 | 0 | 0 | 50 | 8 | 30 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 60 | 81 | 0 | 355 | 330 | 36 | 197 | 37 | 90 | 70 | 127 | 2 | 19 | 100 | 48 | 34 | 0 | 23 | 310 | 0 | 383 | 0 | 58 | 153 | 8 | 0 | 85 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 22 | 0 | 0 | 18 | 7580 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1441.1 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 162 | 0 | 162 | 0 | 414 | 0 | 0 | 165 | 42 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 304 | 1092 | 0 | 6878.1 | 14458.1 | 108.39
22:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 31.6 | 35 | 80 | 76 | 0 | 0 | 40 | 90 | 0 | 340 | 301 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 320 | 0 | 0 | 19 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 32 | 34 | 265 | 0 | 0 | 40 | 8 | 31 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 10 | 35 | 0 | 355 | 330 | 38 | 213 | 35 | 51 | 90 | 120 | 0 | 19 | 102 | 48 | 34 | 0 | 23 | 310 | 0 | 386 | 0 | 58 | 159 | 8 | 0 | 85 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 22 | 0 | 0 | 18 | 7348.6 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 163 | 0 | 164 | 0 | 414 | 0 | 0 | 165 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 304 | 1095 | 0 | 6891 | 14239.6 | 108.39
23:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 32.6 | 17 | 72 | 60 | 0 | 0 | 35 | 87 | 0 | 340 | 308 | 0 | 0 | 17 | 328 | 0 | 0 | 0 | 108 | 25 | 22 | 0 | 350 | 0 | 0 | 18 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 32 | 35 | 265 | 0 | 0 | 40 | 8 | 33 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 10 | 35 | 0 | 350 | 330 | 38 | 204 | 34 | 55 | 90 | 117 | 0 | 19 | 114 | 50 | 8 | 0 | 23 | 315 | 0 | 390 | 0 | 58 | 160 | 8 | 0 | 85 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 21 | 0 | 0 | 18 | 7305.6 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 166 | 0 | 172 | 0 | 414 | 0 | 0 | 165 | 43 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 302 | 1095 | 0 | 6843 | 14148.6 | 108.38
Total KWH | 0 | 1490880 | 506880 | 0 | 0 | 0 | 0 | 0 | 8334000 | 0 | 0 | 475200 | 299880 | 1739808 | 1471200 | 660644 | 47250 | 752053 | 1709280 | 0 | 7926500 | 7154589 | 0 | 0 | 309214 | 7881058 | 0 | 0 | 153748 | 1543200 | 559800 | 304200 | 0 | 8766363.64 | 0 | 0 | 394560 | 0 | 1440 | 883838 | 306144 | 0 | 0 | 0 | 22316 | 5327658 | 189855 | 493440 | 6370909.09 | 0 | 0 | 649440 | 134139.6 | 197382 | 5008047 | 0 | 0 | 0 | 25625452 | 113670 | 1258760 | 662400 | 602182 | 4027800 | 8161700 | 7594000 | 431520 | 4830000 | 461952 | 1172160 | 1902710 | 952800 | 9240 | 349990 | 1541280 | 984960 | 164362 | 531509 | 416768 | 7555000 | 0 | 8512000 | 0 | 524520 | 3592390 | 166032 | 0 | 1799040 | 716448 | 0 | 438000 | 4431970 | 209520 | 1854000 | 220800 | 172800 | 6950 | 147030 | 358800 | 164565431.33 | 21336000 | 0 | 0 | 0 | 90112 | 912000 | 0 | 0 | 0 | 0 | 0 | 498240 | 23614500 | 0 | 25673818 | 0 | 0 | 0 | 51744 | 58752 | 0 | 365104 | 54206 | 0 | 280488 | 395410 | 17649 | 0 | 136504 | 4771455 | 0 | 4272873 | 0 | 4348655 | 0 | 9996218 | 0 | 13500 | 4039000 | 973527 | 694618 | 90265 | 652819 | 0 | 1671232.5 | 0 | 28378.56 | 745920 | 3366 | 0 | 5455000 | 2761000 | 5463730 | 0 | 7322904 | 25024000 | 0 | 151812988.06 | 316378419.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13230.59 | MW | 12:00 Hr. | Energy Generated |  |  | 316.3784 |  | MKWHr.
| Day Peak Demand |  |  | 13230.59 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.3 |  | MKWHr.
| Evening Peak Generation |  |  | 14615.45 | MW | 19:30 Hr. | Energy Demand |  |  | 316.6784 |  | MKWHr.
| Evening Peak Demand |  |  | 14700.1 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.3 |  | °C
| Minimum Generation of the Day |  |  | 11655.6 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1010.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 14615.45 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.7903 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.9265 | 0 | 11.0055 | 0 | 0 | 0.15375 | 0 | 0 | 52.0857 | Gas | 135.5707 | Gas | 484716518.5088
| Chattogram Zone |  |  | 5.5015 | 31.9964 | 2.7554 | 0 | 5.3277 | 0.13599 | 0 | 0.00144 | 45.7183 | Coal | 98.4253 | Coal | 586387898.4968
| Cumilla Zone |  |  | 29.6206 | 0 | 4.919 | 0 | 0 | 0.53151 | 0.98496 | 0 | 36.0561 | HFO | 23.308 | HFO | 429885633.148
| Mymensingh Zone |  |  | 0.1728 | 0 | 2.6431 | 0 | 0 | 0.15398 | 0 | 0 | 2.9699 | HSD | 1.6712 | HSD | 0
| Sylhet Zone |  |  | 27.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7354 | Hydro | 5.3277 | Hydro | 532765.8
| Khulna Zone |  |  | 0 | 23.6145 | 0.090112 | 0 | 0 | 0.49824 | 22.248 | 0 | 46.4509 | Solar | 3.1673 | Solar | 45982368.6976
| Barishal Zone |  |  | 8.2247 | 37.8019 | 0 | 0 | 0 | 0.003366 | 0 | 0 | 46.03 | Import | 48.9068 | Import | 284411941.94
| Rajshahi Zone |  |  | 23.3892 | 0 | 0.54746 | 0 | 0 | 0.8259 | 25.6738 | 0 | 50.4364 | Wind | 0.00144 | Wind | 21225.6
| Rangpur Zone |  |  | 0 | 5.0125 | 1.3474 | 1.6712 | 0 | 0.86456 | 0 | 0 | 8.8958
| Total |  |  | 135.5707 | 98.4253 | 23.308 | 1.6712 | 5.3277 | 3.1673 | 48.9068 | 0.00144 | 316.3784
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 484716518.5088 |  | Hydro | 532765.8
|  |  |  | Coal | 586387898.4968 |  | Solar | 45982368.6976
|  |  |  | HFO | 429885633.148 |  | Import | 284411941.94
|  |  |  | HSD | 0 |  | Wind | 21225.6
[5 empty] | Total: | 183,19,38,352 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.336 | Peak Hr Flow | 882.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33460453.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.6738 | Peak Hr Flow | 1449.45 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2386 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.98496 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2774 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.9948 | Peak Hr Flow | 2377.45 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5266
|  |  |  | Chattogram |  | 0 |  | 1402
|  |  |  | Cumilla |  | 0 |  | 1380
|  |  |  | Mymensingh |  | 81 |  | 1062
|  |  |  | Sylhet |  | 0 |  | 589
|  |  |  | Khulna |  | 0 |  | 1691
|  |  |  | Barishal |  | 0 |  | 410
|  |  |  | Rajshahi |  | 0 |  | 1331
|  |  |  | Rangpur |  | 0 |  | 908
|  |  |  | Total |  | 81 |  | 14039
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:23 | 10:48 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Forced S/D Due to Emergency maintanance Works at
907 DS Loap Repairing.
| 09:23 | 10:48 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Forced S/D Due to Emergency maintanance Works at
907 DS Loap Repairing.
| 09:25 | 10:55 | Bogura 230/132kV S/S T-03 HT Tripped showing BZT. OLTC, Lock Out Relay relays.
| 09:25 | 10:55 | Bogura 230/132kV S/S T-03 LT Tripped showing No Relay relays.
| 09:42 | 11:33 | Shahjibazar 132/33kV S/S SPCL 86 MW Scheduled S/D Due to Hotspot maintenance by 86 MW
| 09:45 | 10:55 | Bogura 230/132kV S/S T-03 HT Forced S/D Due to Emergency Maintenance
| 09:45 | 10:55 | Bogura 230/132kV S/S T-03 LT Forced S/D Due to Emergency Maintenance
| 09:47 | 14:24 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to DFDR Commissioning at Bhulta
400 KV SS.
| 09:50 | 17:42 | BIPTC S/S Baharampur-2 Scheduled S/D Due to Shutdown is taken for Isolator maintenance
|  | 09:58 | Feni 132/33kV S/S T-2(415T) HT is restored.
|  | 10:35 | Hathazari 230/132/33kV S/S T-01 LT is restored.
|  | 10:35 | Hathazari 230/132/33kV S/S T-01 HT is restored.
| 10:54 | 13:42 | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Auxiliary 2 Y and B jumper | [7 empty] | 6.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 12:11 | 12:38 | Ashuganj-Kishoreganj 132kV Ckt-1 Forced S/D from Kishoreganj 132/33kV end Due to Tree
trimming
| 13:20 | 15:42 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to Red Hot | [7 empty] | 30.0MW load
interrup.
| 13:20 | 15:33 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to Red Hot
|  | 15:00 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 16:17 |  | Bogura-Kaliakoir 400kV ckt-1 tripped showing distance relay. The line was charged from
Bogura end up to Jamuna bridge.
| 16:17 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Tripped showing Distance relay, Bay
protection relay 86.1 @ 86.2 relays.
| 16:26 | 16:50 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Tripped from Thakurgaon 132/33kV end showing | [7 empty] | 58.0MW load
|  |  | Distance: QUADRAMHO, SHPM 101, GEC, U.K relays Due to Zone-1 and from Purbasadipur | [7 empty] | interrup.
|  |  | 132/33kV end showing Distance Auto Reclose relays Due to None | [7 empty] | Thakurgaon 132/33kV
end
| 16:27 | 16:55 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Tripped from Purbasadipur 132/33kV end showing
Distance relays Due to None
| 16:30 | 17:28 | Saidpur 132/33kV S/S 150 MW Cable Line Tripped showing 85/21;85/67; k861; k862. relays
Due to 85/21;85/67; k861; k862.
| 16:32 | 18:25 | Patiya 132/33kV S/S TRAFO-01 HT Project Work S/D Due to PBS project work
| 16:32 | 18:27 | Patiya 132/33kV S/S TRAFO-01 LT Project Work S/D Due to PBS project work
| 16:41 | 21:10 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Tripped showing on load tap changer trip relays.
| 16:41 | 21:11 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Tripped showing on load tap changer trip relays.
| 17:01 | 19:36 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 17:01 | 19:36 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 19:15 | 19:37 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing Line Distance Protn.
Optd relays.
| 19:15 | 19:36 | Fatullah-Madanganj 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 21 trip
zone-1 trip B phase relays Due to tripprd
| 19:15 | 19:41 | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing 50N/51N Trip
P-127 relays.
| 19:16 | 19:23 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing DEF, AIDED.
relays Due to Unknown.
| 19:30 |  | Evening Peak Generation 14615 MW.
| 23:23 | 06:42 | Bibiana 400/230kV S/S ICT-02 HT Tripped showing RTE670,Main 2 relays Due to PRD Trip.
| 05:02 | 05:18 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Panchagarh 132/33kV end showing MICOM P442
relays Due to Fault and from Thakurgaon 132/33kV end showing Micom P442 relays Due to
Zone 1 (14.59km)
| 05:22 | 05:58 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Thakurgaon 132/33kV end showing Micom
P442 Siprotec F21 (Panchagarh Ckt-2 Relay panel Zone-1 & Zone-2) relays Due to Zone 1
(22.12km) Breaker trip 905B & 920B
| 05:52 |  | Siddhirganj 335 MW CCPP ST was shutdown due to scheduled maintenance work
| 06:03 |  | Siddhirganj 335 MW CCPP GT was shutdown due to scheduled maintenance work
| 06:21 | 07:49 | Bakulia 132/33kV S/S T-3 (422T) LT Scheduled S/D Due to Hot spot maintenance.
| 06:22 | 07:48 | Bakulia 132/33kV S/S T-3 (422T) HT Scheduled S/D Due to Hot spot maintenance.
| 06:26 |  | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Forced S/D Due to Red hot maintenance
work at Baraulia s/s end.
| 06:32 |  | Baroaulia-Khulshi 132 kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to High
temperature maintenance at 132kv khulshi bay
| 06:34 | 06:50 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing CB1 A/R
Fail & B relays.
| 07:00 |  | Minimum Generation is 11900 MW
| 07:11 |  | Siddhirganj 2x120 MW GT-1 was sync.
| 07:14 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to 33kv CT Maintenance
| 07:14 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to 33kv CT Maintenance
| 07:30 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to 33kv T1A, DS red hot
maintainence of B-phase.
| 07:32 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kv T1A, DS red hot | [7 empty] | 35.0MW load
|  |  | maintainence of B-phase. | [7 empty] | interrup.
| 07:38 |  | Siddhirganj 230/132kV S/S 335MW EGCB 2 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 335 | 8334000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7926500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 7154589 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 47250 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7881058 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 43 | 475200 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 124 | 1471200 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 752053 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 309214 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 559800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 304200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 506880 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 660644 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 1739808 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1490880 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1709280 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 153748 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 299880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 8766363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1543200 | -
Dhaka Area Total |  |  |  |  | 6657.724 | 2525 | 52085747.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 134139.6 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 113670 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 649440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5327658 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5008047 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 31 | 197382 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 306144 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 883838 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 493440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 394560 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22316 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 28 | 189855 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1130 | 25625452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 1440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6370909.09 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2149 | 45718290.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 186 | 4830000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8161700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7594000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 4027800 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 461952 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 37 | 431520 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 81 | 602182 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1258760 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 662400 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 416768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 1902710 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 123 | 952800 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 46 | 984960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 164362 | FGMO
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 349990 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1541280 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 9240 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 1172160 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 531509 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1657 | 36056093
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 172800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 220800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1854000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 147030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 358800 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 209520 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 143 | 2969900
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 524520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3592390 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716448 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1799040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 167 | 4431970 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 438000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 166032 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7555000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8512000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1164 | 27735400
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 882 | 21336000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 90112 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 498240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1096 | 23614500 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2016 | 46450852
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7322904 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2761000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 25024000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5463730 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | FGMO
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5455000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3366 | -
Barishal Area Total |  |  |  |  | 2236 | 1987 | 46030000
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 280488 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 54206 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4771455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 158 | 4272873 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 158 | 4348655 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9996218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 7 | 17649 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 365104 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 58752 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 51744 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449.45 | 25673818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 136504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 395410 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2541.45 | 50436376
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 1671232.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 43 | 973527 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4039000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 652819 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28378.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 112 | 694618 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 90265 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 745920 | -
Rangpur Area Total |  |  |  |  | 950 | 433 | 8895760.06
Eastern Grid Total |  |  |  |  | 17385.715 | 7638 | 164565431.33
Western Grid Total |  |  |  |  | 10444.16 | 6977.45 | 151812988.06
National Grid Total |  |  |  |  | 27829.875 | 14615.45 | 316378419.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-09-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9617.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4339.6 | MW
i) Dhaka area |  |  | 5266.06 |  | MW | i) Khulna area |  |  |  | 1691 | MW
ii) Chattogram area |  |  | 1401.6 |  | MW | ii) Barishal area |  |  |  | 410 | MW
iii) Cumilla area |  |  | 1379.78 |  | MW | iii) Rajshahi area |  |  |  | 1330.6 | MW
iv) Mymensingh area |  |  | 981 |  | MW | iv) Rangpur area |  |  |  | 908 | MW
v) Sylhet area |  |  | 589 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13957.04 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 18:30 | 133 | PHP | 8 | 00:00
2 | AKSML | 130.1 | 01:00 | 68 | Ishurdi | 72 | 12:00 | 134 | Pabna | 119 | 19:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 76 | 18:30 | 135 | Palashbari | 106 | 18:30
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 105 | 21:00 | 136 | Panchagarh | 51 | 19:00
5 | Agrabad | 96 | 15:00 | 71 | Jashore | 136 | 19:30 | 137 | Patiya | 0 | 00:00
6 | Amnura | 27 | 22:00 | 72 | Jhenaidah | 121 | 19:00 | 138 | Patuakhali | 68.5 | 22:00
7 | Ashuganj | 84 | 01:00 | 73 | Joydebpur | 167 | 12:00 | 139 | Payra | 36 | 23:00
8 | BSRM | 149 | 02:00 | 74 | Joypurhat | 54 | 19:00 | 140 | Postogola | 64 | 14:00
9 | Bagerhat | 80 | 19:00 | 75 | Juldah | 16.5 | 13:00 | 141 | Purbachal | 21 | 19:30
10 | Bajitpur | 87 | 00:00 | 76 | KSRM | 20 | 02:00 | 142 | Purbasadipur | 113 | 19:00
11 | Bakulia | 95 | 18:30 | 77 | Kabirpur | 262 | 11:00 | 143 | Rahanpur | 36 | 21:00
12 | Banani | 53.6 | 13:00 | 78 | Kachua | 86 | 19:00 | 144 | Rahim | 38 | 01:00
13 | Bangabhaban | 24 | 11:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajbari | 83 | 20:00
14 | Barapukuria | 61 | 19:00 | 80 | Kalurghat | 40 | 15:00 | 146 | Rajendrapur | 126 | 19:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 81 | 13:00 | 147 | Rajshahi | 90 | 21:00
16 | Barishal | 112 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 92 | 13:00
17 | Barishal-230 | 94 | 20:00 | 83 | Kasba | 36 | 20:00 | 149 | Ramganj | 108 | 19:00
18 | Baroaulia | 71 | 11:00 | 84 | Kazla | 103 | 12:00 | 150 | Rampur | 41 | 23:00
19 | Baroirhat | 62 | 19:00 | 85 | Keranigonj | 89 | 19:00 | 151 | Rangamati | 21 | 18:30
20 | Bashundhara | 189 | 13:00 | 86 | Khagrachori | 30 | 19:00 | 152 | Rangpur | 139 | 19:00
21 | BashundharaCement | 8 | 08:00 | 87 | Khulna | 65 | 13:00 | 153 | Ruppur | 7.6 | 09:00
22 | Beanibazar | 74 | 18:30 | 88 | Khulshi | 190 | 16:00 | 154 | SSM | 17 | 02:00
23 | Benapole | 66 | 18:30 | 89 | Kishoreganj | 122 | 19:30 | 155 | Saidpur | 100 | 18:30
24 | Bhaluka | 127 | 20:00 | 90 | Kodda | 313 | 18:30 | 156 | Satkhira | 122 | 22:00
25 | Bhandaria | 53 | 23:00 | 91 | Kulaura | 48 | 19:30 | 157 | Satmasjid | 106 | 13:00
26 | Bhangura | 31 | 20:00 | 92 | Kurigram | 64 | 18:30 | 158 | Savar | 233 | 12:00
27 | Bheramara(GK) | 57 | 19:30 | 93 | Kushtia | 142 | 18:30 | 159 | SevenRings | 11.56 | 00:00
28 | Bhulta | 212 | 22:00 | 94 | Laksam | 33 | 23:00 | 160 | ShahCement | 30 | 18:00
29 | Bog-Sherpur | 64 | 18:30 | 95 | Lakshmipur | 34 | 19:00 | 161 | Shahjadpur | 84 | 19:30
30 | Bogura | 145 | 23:00 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 122 | 22:00
31 | Borhanuddin | 89 | 00:00 | 97 | Lalmonirhat | 58 | 19:30 | 163 | Shahmirpur | 61 | 00:00
32 | Brahmanbaria | 137 | 21:00 | 98 | MI_Cement | 12.3 | 23:00 | 164 | Shariatpur | 85 | 22:00
33 | Cantonment | 142 | 13:00 | 99 | Madanganj | 34 | 00:00 | 165 | Sherpur | 110 | 21:00
34 | Chandina | 18.03 | 18:30 | 100 | Madaripur | 111 | 23:00 | 166 | Shikalbaha | 14 | 11:00
35 | Chandpur | 82 | 21:00 | 101 | Madartek | 88 | 22:00 | 167 | Shitalakhya | 76 | 12:00
36 | Chandraghona | 36 | 18:30 | 102 | Madunaghat | 56 | 18:30 | 168 | Sholosohor | 47 | 18:30
37 | Chapai | 65 | 21:00 | 103 | Magura | 64 | 19:00 | 169 | Shyampur | 162 | 00:00
38 | Charsaidpur | 35 | 11:00 | 104 | Mahasthangarh | 68 | 18:30 | 170 | Siddhirganj | 125 | 12:00
39 | Chauddagram | 66 | 21:00 | 105 | Maijdee | 15 | 22:00 | 171 | Sirajganj | 102 | 20:00
40 | Chhatak | 35 | 00:00 | 106 | Manikganj | 126 | 18:30 | 172 | Sonargaon | 132 | 15:00
41 | Chowmuhani | 182 | 19:30 | 107 | Maniknagar | 62 | 12:00 | 173 | Sreemongol | 76 | 23:00
42 | Chuadanga | 103 | 19:30 | 108 | Matarbari | 51 | 19:00 | 174 | Sreepur | 105 | 18:30
43 | Coxsbazar | 134 | 20:00 | 109 | Matuail | 71 | 16:00 | 175 | Srinagar | 47.74 | 22:00
44 | Cumilla(N) | 132 | 22:00 | 110 | Millgate | 113 | 12:00 | 176 | Sunamganj | 58 | 21:00
45 | Cumilla(S) | 151 | 14:00 | 111 | Mirpur | 124.5 | 12:00 | 177 | Sylhet | 47 | 19:00
46 | Daganbhuiyan | 0 | 10:00 | 112 | Mirsorai | 11 | 16:00 | 178 | Sylhet-132 | 113 | 19:00
47 | Daudkandi | 146 | 22:00 | 113 | Mirzapur | 35 | 00:00 | 179 | TK | 36 | 23:00
48 | Dhaka | 92 | 13:00 | 114 | Mithapukur | 62 | 18:30 | 180 | Tangail | 160 | 18:00
49 | Dhamrai | 128 | 13:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 18 | 18:30
50 | Dhanmondi | 145 | 13:00 | 116 | Mogbazar | 98.5 | 13:00 | 182 | Thakurgaon | 90 | 19:00
51 | Dohazari | 108 | 00:00 | 117 | Mongla | 32 | 12:00 | 183 | Tongi | 128 | 11:00
52 | Faridpur | 171 | 19:30 | 118 | Motijheel | 45 | 12:00 | 184 | Ullahpara | 34 | 20:00
53 | Fatullah | 100 | 12:00 | 119 | Muktagacha | 33 | 18:30 | 185 | Ullon | 52 | 20:00
54 | Fenchuganj | 39 | 18:00 | 120 | Munshiganj | 117 | 23:00 | 186 | Uttara | 80 | 13:00
55 | Feni | 125 | 18:30 | 121 | Muradnagar | 42 | 21:00 | 187 | UttaraNew | 58 | 14:00
56 | GPH | 7 | 01:00 | 122 | Mymensingh | 189 | 20:00 | 188 | Zigatola | 74 | 13:00
57 | Ghatail | 74 | 19:00 | 123 | Naogaon | 111 | 21:00
58 | Ghorashal | 20 | 18:30 | 124 | Narail | 60 | 19:00
59 | Ghorashal-230 | 90 | 00:00 | 125 | Narinda | 76 | 13:00
60 | Goalpara | 33 | 13:00 | 126 | Narshingdi | 174 | 20:00
61 | Gollamari | 96 | 19:00 | 127 | Natore | 129 | 18:30
62 | Gopalganj | 107 | 22:00 | 128 | Nawabganj | 48.8 | 22:00
63 | Gulshan | 124 | 13:00 | 129 | Netrakona | 134 | 18:30
64 | Halishahar | 72 | 15:00 | 130 | New | 68 | 15:00
65 | HaripurSBU | 165 | 12:00 | 131 | Niamatpur | 65 | 22:00
66 | Hasnabad | 90 | 14:00 | 132 | Noapara | 45 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13550.07 | 39 |  | 13590.83
1:00 | 13051.48 | 28 |  | 13080.74
2:00 | 12668.57 | 26 |  | 12695.74
3:00 | 12355.43 | 0 |  | 12355.43
4:00 | 12151.81 | 0 |  | 12151.81
5:00 | 12008.88 | 0 |  | 12008.88
6:00 | 11655.6 | 0 |  | 11655.6
7:00 | 11803.11 | 0 |  | 11803.11
8:00 | 11959.98 | 0 |  | 11959.98
9:00 | 12225.03 | 0 |  | 12225.03
10:00 | 12429.65 | 0 |  | 12429.65
11:00 | 12734.11 | 0 |  | 12734.11
12:00 | 13230.59 | 0 |  | 13230.59
13:00 | 13349.76 | 0 |  | 13349.76
14:00 | 13060.48 | 0 |  | 13060.48
15:00 | 13091.87 | 0 |  | 13091.87
16:00 | 12959.87 | 0 |  | 12959.87
17:00 | 12663.45 | 0 |  | 12663.45
18:00 | 13088.37 | 40 |  | 13130.17
19:00 | 14589.01 | 77 |  | 14669.48
19:30 | 14615.45 | 81 |  | 14700.1
20:00 | 14529.23 | 69 |  | 14601.34
21:00 | 14458.1 | 0 |  | 14458.1
22:00 | 14239.6 | 0 |  | 14239.6
23:00 | 14148.6 | 21 |  | 14170.6
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6891.1 | 6658.97 | 13550.07 | DAILY GENERATION CURVE
00:30 | 6739.05 | 6561.725 | 13300.775
01:00 | 6587 | 6464.48 | 13051.48 | 17-09-2025
01:30 | 6550 | 6310.025 | 12860.025
02:00 | 6513 | 6155.57 | 12668.57
02:30 | 6427 | 6085 | 12512
03:00 | 6341 | 6014.43 | 12355.43
03:30 | 6285.25 | 5968.37 | 12253.62
04:00 | 6229.5 | 5922.31 | 12151.81
04:30 | 6199 | 5881.345 | 12080.345
05:00 | 6168.5 | 5840.38 | 12008.88
05:30 | 6088.56 | 5743.68 | 11832.24
06:00 | 6008.62 | 5646.98 | 11655.6
06:30 | 6067.025 | 5662.33 | 11729.355
07:00 | 6125.43 | 5677.68 | 11803.11
07:30 | 6113.095 | 5768.45 | 11881.545
08:00 | 6100.76 | 5859.22 | 11959.98
08:30 | 6178.98 | 5913.525 | 12092.505
09:00 | 6257.2 | 5967.83 | 12225.03
09:30 | 6328.37 | 5998.97 | 12327.34
10:00 | 6399.54 | 6030.11 | 12429.65
10:30 | 6492.68 | 6089.2 | 12581.88
11:00 | 6585.82 | 6148.29 | 12734.11
11:30 | 6745.74 | 6236.61 | 12982.35
12:00 | 6905.66 | 6324.93 | 13230.59
12:30 | 6987.185 | 6302.99 | 13290.175
13:00 | 7068.71 | 6281.05 | 13349.76
13:30 | 6951.69 | 6253.43 | 13205.12
14:00 | 6834.67 | 6225.81 | 13060.48
14:30 | 6831.395 | 6244.78 | 13076.175
15:00 | 6828.12 | 6263.75 | 13091.87
15:30 | 6789.89 | 6235.98 | 13025.87
16:00 | 6751.66 | 6208.21 | 12959.87
16:30 | 6743.315 | 6068.345 | 12811.66
17:00 | 6734.97 | 5928.48 | 12663.45
17:30 | 6753.485 | 6122.425 | 12875.91
18:00 | 6772 | 6316.37 | 13088.37
18:30 | 7211 | 6627.69 | 13838.69
19:00 | 7650 | 6939.01 | 14589.01
19:30 | 7638 | 6977.45 | 14615.45
20:00 | 7616.6 | 6912.63 | 14529.23
20:30 | 7598.3 | 6895.365 | 14493.665 |  | Executive Engineer
21:00 | 7580 | 6878.1 | 14458.1 |  | Network Operation Division
21:30 | 7464.3 | 6884.55 | 14348.85
22:00 | 7348.6 | 6891 | 14239.6
22:30 | 7327.1 | 6867 | 14194.1
23:00 | 7305.6 | 6843 | 14148.6

## En-Curve
QF-LDC-12
Date | 17-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3703 | 1899 | 881 | 38 | 44 | 1416.97 | 221 | 4343 | 0 | 311 | 693.1 | 0 | 0 | 0 | 39 | DAILY ENERGY CURVE
00:30 | 3691.5 | 1903 | 881.5 | 38 | 44 | 1386.725 | 221 | 4295.5 | 0 | 297.5 | 542.05 | 0 | 0 | 0 | 33.5 | 17-09-2025
01:00 | 3680 | 1907 | 882 | 38 | 44 | 1356.48 | 221 | 4248 | 0 | 284 | 391 | 0 | 0 | 0 | 28
01:30 | 3671 | 1912 | 882 | 38 | 43 | 1283.525 | 221 | 4175.5 | 0 | 258.5 | 375.5 | 0 | 0 | 0 | 27 | Energy Generated | 316.3784 |  | MKWHr
02:00 | 3662 | 1917 | 882 | 38 | 42 | 1210.57 | 221 | 4103 | 0 | 233 | 360 | 0 | 0 | 0 | 26 | Energy not Served | 0.3 |  | MKWHr
02:30 | 3661 | 1918 | 881.5 | 38 | 41 | 1164 | 220.5 | 4027 | 0 | 225.5 | 335.5 | 0 | 0 | 0 | 13 | Total Energy Requirement | 316.6784 |  | MKWHr
03:00 | 3660 | 1919 | 881 | 38 | 40 | 1117.43 | 220 | 3951 | 0 | 218 | 311 | 0 | 0 | 0 | 0
03:30 | 3654.5 | 1915.25 | 881 | 38 | 40 | 1080.87 | 221 | 3922.5 | 0 | 213.5 | 287 | 0 | 0 | 0 | 0
04:00 | 3649 | 1911.5 | 881 | 38 | 40 | 1044.31 | 222 | 3894 | 0 | 209 | 263 | 0 | 0 | 0 | 0
04:30 | 3679 | 1916 | 881 | 38 | 40 | 1029.845 | 222 | 3775.5 | 0 | 201.5 | 237.5 | 60 | 0 | 0 | 0
05:00 | 3709 | 1920.5 | 881 | 38 | 40 | 1015.38 | 222 | 3657 | 0 | 194 | 212 | 120 | 0 | 0 | 0
05:30 | 3705 | 1904.5 | 881.5 | 38 | 39 | 965.105 | 222 | 3561.5 | 1.135 | 175.5 | 196.5 | 142.5 | 0 | 0 | 0
06:00 | 3701 | 1888.5 | 882 | 38 | 38 | 914.83 | 222 | 3466 | 2.27 | 157 | 181 | 165 | 0 | 0 | 0
06:30 | 3726.5 | 1900.75 | 881.5 | 38 | 36 | 915.725 | 222 | 3470 | 37.88 | 147.5 | 186 | 167.5 | 0 | 0 | 0
07:00 | 3752 | 1913 | 881 | 38 | 34 | 916.62 | 222 | 3474 | 73.49 | 138 | 191 | 170 | 0 | 0 | 0
07:30 | 3730 | 1896 | 881 | 38 | 33 | 916.31 | 222 | 3509 | 144.235 | 145.5 | 196.5 | 170 | 0 | 0 | 0
08:00 | 3708 | 1879 | 881 | 38 | 32 | 916 | 222 | 3544 | 214.98 | 153 | 202 | 170 | 0 | 0 | 0
08:30 | 3736 | 1901.75 | 881 | 38 | 33 | 919.5 | 222 | 3582 | 261.755 | 157.5 | 191 | 169 | 0 | 0 | 0
09:00 | 3764 | 1924.5 | 881 | 38 | 34 | 923 | 222 | 3620 | 308.53 | 162 | 180 | 168 | 0 | 0 | 0
09:30 | 3784 | 1862.5 | 880.5 | 38 | 35 | 891.5 | 221 | 3709 | 369.84 | 162 | 206 | 168 | 0 | 0 | 0
10:00 | 3804 | 1800.5 | 880 | 38 | 36 | 860 | 220 | 3798 | 431.15 | 162 | 232 | 168 | 0 | 0 | 0
10:30 | 3805.5 | 1807.25 | 880.5 | 38 | 37 | 844.5 | 220 | 3905 | 449.63 | 162 | 264.5 | 168 | 0 | 0 | 0
11:00 | 3807 | 1814 | 881 | 38 | 38 | 829 | 220 | 4012 | 468.11 | 162 | 297 | 168 | 0 | 0 | 0
11:30 | 3794.5 | 1828.5 | 881 | 38 | 38 | 823.5 | 219.5 | 4092.5 | 465.85 | 176.5 | 457 | 167.5 | 0 | 0 | 0
12:00 | 3782 | 1843 | 881 | 38 | 38 | 818 | 219 | 4173 | 463.59 | 191 | 617 | 167 | 0 | 0 | 0
12:30 | 3610.5 | 1842 | 881.5 | 38 | 40 | 817.5 | 219 | 4227.5 | 435.275 | 239 | 793.4 | 146.5 | 0 | 0 | 0
13:00 | 3439 | 1841 | 882 | 38 | 42 | 817 | 219 | 4282 | 406.96 | 287 | 969.8 | 126 | 0 | 0 | 0
13:30 | 3397.5 | 1820.25 | 882 | 38 | 43 | 816.7 | 219.5 | 4258 | 377.27 | 281.5 | 945.9 | 125.5 | 0 | 0 | 0
14:00 | 3356 | 1799.5 | 882 | 38 | 44 | 816.4 | 220 | 4234 | 347.58 | 276 | 922 | 125 | 0 | 0 | 0
14:30 | 3407 | 1826.25 | 882 | 38 | 43 | 867.825 | 220 | 4242.5 | 315.1 | 282.5 | 847.5 | 104.5 | 0 | 0 | 0
15:00 | 3458 | 1853 | 882 | 38 | 42 | 919.25 | 220 | 4251 | 282.62 | 289 | 773 | 84 | 0 | 0 | 0
15:30 | 3495.5 | 1872.5 | 881.5 | 38 | 41 | 920.37 | 220 | 4259 | 226.3 | 277.5 | 710.2 | 84 | 0 | 0 | 0
16:00 | 3533 | 1892 | 881 | 38 | 40 | 921.49 | 220 | 4267 | 169.98 | 266 | 647.4 | 84 | 0 | 0 | 0
16:30 | 3533.5 | 1906.5 | 881.5 | 38 | 39 | 914.48 | 220 | 4218 | 104.48 | 268.5 | 645.7 | 42 | 0 | 0 | 0
17:00 | 3534 | 1921 | 882 | 38 | 38 | 907.47 | 220 | 4169 | 38.98 | 271 | 644 | 0 | 0 | 0 | 0
17:30 | 3448 | 1920 | 882 | 38 | 42 | 1087.92 | 220 | 4119 | 19.49 | 353.5 | 746 | 0 | 0 | 0 | 20
18:00 | 3362 | 1919 | 882 | 38 | 46 | 1268.37 | 220 | 4069 | 0 | 436 | 848 | 0 | 0 | 0 | 40
18:30 | 3466 | 1945.5 | 882 | 38 | 46 | 1364.19 | 220 | 4214.5 | 0 | 496 | 1166.5 | 0 | 0 | 0 | 58.5
19:00 | 3570 | 1972 | 882 | 38 | 46 | 1460.01 | 220 | 4360 | 0 | 556 | 1485 | 0 | 0 | 0 | 77
19:30 | 3516 | 1962 | 882 | 38 | 46 | 1449.45 | 220 | 4351 | 0 | 584 | 1567 | 0 | 0 | 0 | 81
20:00 | 3539 | 1971 | 882 | 38 | 48 | 1459.63 | 220 | 4353 | 0 | 601 | 1417.6 | 0 | 0 | 0 | 69
20:30 | 3579 | 1987 | 882 | 38 | 48 | 1450.365 | 220 | 4368.5 | 0 | 562 | 1358.8 | 0 | 0 | 0 | 34.5
21:00 | 3619 | 2003 | 882 | 38 | 48 | 1441.1 | 220 | 4384 | 0 | 523 | 1300 | 0 | 0 | 0 | 0
21:30 | 3643.5 | 1985 | 882 | 38 | 48 | 1441.55 | 220 | 4388.5 | 0 | 507 | 1195.3 | 0 | 0 | 0 | 0
22:00 | 3668 | 1967 | 882 | 38 | 48 | 1442 | 220 | 4393 | 0 | 491 | 1090.6 | 0 | 0 | 0 | 0
22:30 | 3668 | 1989 | 882 | 38 | 49 | 1443.5 | 220 | 4396 | 0 | 474.5 | 1034.1 | 0 | 0 | 0 | 10.5
23:00 | 3668 | 2011 | 882 | 38 | 50 | 1445 | 220 | 4399 | 0 | 458 | 977.6 | 0 | 0 | 0 | 21
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 06:00 | 369 | 11:00 | Payra | 413 | 07:00 | 407 | 23:00
Ashuganj | 411 | 7:00 | 388 | 16:00 | Rahanpur | 408 | 06:00 | 390 | 23:00
Bhulta | 406 | 07:00 | 383 | 16:00 | Rampal | 407 | 06:00 | 394 | 00:00
Bibiana | 388 | 06:00 | 380 | 11:00
BIPTC | 405 | 06:00 | 397 | 10:00
Bogura | 400 | 09:00 | 374 | 23:00
Gopalganj | 399 | 06:00 | 387 | 23:00
Kaliakoir | 376 | 06:00 | 362 | 11:00
Madunaghat | 392 | 06:00 | 385 | 12:00
Meghnaghat | 385 | 06:00 | 376 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 06:00 | 218 | 11:00 | Kaliakoir | 234 | 06:00 | 225 | 11:00
AKSML | 232 | 05:00 | 224 | 10:00 | Keranigonj | 225 | 06:00 | 217 | 11:00
Aminbazar | 228 | 05:00 | 220 | 11:00 | Khulna(S) | 233 | 06:00 | 220 | 23:00
Ashuganj | 234 | 07:00 | 226 | 00:00 | Madunaghat | 231 | 06:00 | 225 | 11:00
Ashuganj-400 | 234 | 7:00 | 225 | 16:00 | Madunaghat-400 | 232 | 06:00 | 227 | 12:00
Baghabari | 234 | 06:00 | 224 | 20:00 | Maniknagar | 220 | 04:00 | 213 | 11:00
Barapukuria | 225 | 08:00 | 217 | 23:00 | Meghnaghat | 228 | 03:00 | 221 | 13:00
Barapukuria-230 | 225 | 8:00 | 216 | 22:00 | Meghnaghat-400 | 225 | 06:00 | 218 | 11:00
Barishal | 229 | 06:00 | 221 | 23:00 | Mirsorai | 228 | 05:00 | 223 | 00:00
Bheramara | 235 | 05:00 | 222 | 19:00 | Rajshahi | 232 | 06:00 | 217 | 09:00
Bhulta | 233 | 06:00 | 213 | 11:00 | Rampal | 234 | 09:00 | 221 | 23:00
Bibiana | 230 | 07:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 05:00 | 221 | 23:00 | Rampura | 232 | 07:00 | 217 | 13:00
Bogura | 238 | 06:00 | 223 | 23:00 | Shikalbaha | 230 | 06:00 | 223 | 11:00
Bogura-400 | 238 | 09:00 | 224 | 23:00 | Shyampur | 224 | 06:00 | 216 | 11:00
Borhanuddin | 233 | 06:00 | 227 | 23:00 | Siddhirganj | 222 | 05:00 | 216 | 11:00
BSRM | 228 | 07:00 | 223 | 00:00 | Sirajgonj | 241 | 06:00 | 233 | 23:00
Cumilla(N) | 224 | 06:00 | 218 | 11:00 | Sreepur | 230 | 07:00 | 222 | 00:00
Faridpur | 226 | 06:00 | 218 | 21:00 | Tongi | 228 | 06:00 | 217 | 11:00
Fenchuganj | 231 | 06:00 | 226 | 11:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 230 | 06:00 | 219 | 16:00
Gopalganj | 227 | 06:00 | 219 | 23:00
GPH | 230 | 08:00 | 225 | 10:00
Haripur | 221 | 04:00 | 215 | 11:00
Hasnabad | 222 | 04:00 | 217 | 11:00
Hathazari | 228 | 04:00 | 222 | 11:00
Ishurdi | 238 | 05:00 | 223 | 19:00
Jhenaidah | 233 | 06:00 | 218 | 21:00
Kachua | 217 | 07:00 | 211 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 126 | 11:00 | Lalmonirhat | 131 | 06:00 | 122 | 19:30
Agargaon | 137 | 04:00 | 131 | 11:00 | Madanganj | 129 | 03:00 | 125 | 11:00
Agrabad | 130 | 05:00 | 125 | 11:00 | Madaripur | 135 | 05:00 | 130 | 22:00
AKS | 129 | 05:00 | 124 | 04:00 | Madartek | 135 | 06:00 | 124 | 13:00
Aminbazar | 135 | 05:00 | 129 | 11:00 | Madunaghat | 133 | 20:00 | 130 | 11:00
Amnura | 138 | 10:00 | 124 | 00:00 | Magura | 135 | 05:00 | 124 | 23:00
Ashuganj | 142 | 05:00 | 137 | 11:00 | Mahasthangarh | 133 | 06:00 | 123 | 23:00
Bagerhat | 135 | 06:00 | 122 | 21:00 | Maijdee | 115 | 06:00 | 110 | 15:00
Bajitpur | 132 | 14:00 | 126 | 19:00 | Manikganj | 128 | 07:00 | 120 | 18:30
Bakulia | 131 | 05:00 | 128 | 00:00 | Maniknagar | 134 | 06:00 | 127 | 12:00
Banani | 136 | 06:00 | 125 | 13:00 | Matarbari | 119 | 05:00 | 109 | 23:00
Bangabhaban | 134 | 06:00 | 127 | 13:00 | Matuail | 129 | 05:00 | 125 | 11:00
Barapukuria | 137 | 06:00 | 129 | 01:00 | Millgate | 134 | 05:00 | 126 | 11:00
Barguna | 134 | 07:00 | 130 | 01:00 | Mirpur | 133 | 04:00 | 127 | 11:00
Barishal | 134 | 05:00 | 128 | 23:00 | Mirzapur | 130 | 04:00 | 126 | 00:00
Barishal-230 | 135 | 07:00 | 129 | 21:00 | Mithapukur | 132 | 06:00 | 124 | 23:00
Baroaulia | 133 | 05:00 | 127 | 16:00 | MI_Cement | 130.7 | 05:00 | 125 | 11:00
Baroirhat | 124 | 04:00 | 118 | 11:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 06:00 | 125 | 13:00 | Mogbazar | 137 | 04:00 | 126 | 13:00
BashundharaCement | 129 | 03:00 | 125 | 11:00 | Mongla | 134 | 07:00 | 124 | 18:30
Beanibazar | 128 | 05:00 | 125 | 00:00 | Motijheel | 134 | 06:00 | 127 | 13:00
Benapole | 134 | 06:00 | 121 | 22:00 | Muktagacha | 126 | 13:00 | 117 | 00:00
Bhaluka | 132 | 13:00 | 124 | 00:00 | Munshiganj | 129 | 05:00 | 124 | 11:00
Bhandaria | 130 | 07:00 | 120 | 23:00 | Muradnagar | 125 | 07:00 | 120 | 10:00
Bhangura | 134 | 05:00 | 127 | 18:30 | Mymensingh | 126 | 13:00 | 115 | 00:00
Bheramara | 136 | 05:00 | 127 | 18:30 | Naogaon | 129 | 06:00 | 119 | 21:00
Bheramara(GK) | 136 | 05:00 | 127 | 18:30 | Narail | 135 | 05:00 | 122 | 21:00
Bhulta | 122 | 17:00 | 115 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 134 | 06:00 | 124 | 21:00 | Narshingdi | 137 | 13:00 | 115 | 12:00
Bogura | 134 | 06:00 | 126 | 21:00 | Natore | 130 | 15:00 | 120 | 21:00
Bogura-230 | 135 | 06:00 | 125 | 23:00 | Nawabganj | 138 | 06:00 | 132 | 11:00
Brahmanbaria | 137 | 07:00 | 130 | 11:00 | Netrakona | 126 | 13:00 | 114 | 18:30
Cantonment | 137 | 03:00 | 130 | 11:00 | New | 157 | 16:00 | 128 | 11:00
Chandina | 128 | 06:00 | 124 | 11:00 | Niamatpur | 139 | 10:00 | 131 | 22:00
Chandpur | 127 | 19:00 | 120 | 11:00 | Noapara | 137 | 08:00 | 125 | 23:00
Chandraghona | 133 | 03:00 | 130 | 11:00 | Pabna | 135 | 05:00 | 125 | 19:00
Chapai | 138 | 09:00 | 131 | 00:00 | Palashbari | 130 | 06:00 | 121 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 06:00 | 125 | 12:00 | Panchagarh | 135 | 06:00 | 120 | 17:00
Chauddagram | 123 | 06:00 | 118 | 15:00 | Patiya | 131 | 06:00 | 126 | 11:00
Chhatak | 128 | 06:00 | 122 | 22:00 | Patuakhali | 135 | 07:00 | 131 | 00:00
Chowmuhani | 116 | 06:00 | 111 | 11:00 | Payra | 135 | 05:00 | 133 | 00:00
Chuadanga | 134 | 06:00 | 122 | 21:00 | PHP | 122 | 02:00 | 117 | 15:00
Coxsbazar | 119 | 07:00 | 110 | 21:00 | Postogola | 132 | 04:00 | 127 | 11:00
Cumilla(N) | 128 | 06:00 | 124 | 11:00 | Purbachal | 136 | 06:00 | 125 | 13:00
Cumilla(S) | 132 | 02:00 | 121 | 11:00 | Purbasadipur | 131 | 05:00 | 122 | 17:00
Daganbhuiyan | 116 | 13:00 | 113 | 15:00 | Rahanpur | 140 | 05:00 | 137 | 03:00
Daudkandi | 123 | 06:00 | 117 | 10:00 | Rahanpur-400 | 140 | 06:00 | 134 | 00:00
Dhaka | 135 | 03:00 | 126 | 12:00 | Rahim | 130 | 06:00 | 126 | 11:00
Dhamrai | 133 | 04:00 | 127 | 11:00 | Rajbari | 134 | 06:00 | 127 | 21:00
Dhanmondi | 136.5 | 06:00 | 126 | 16:00 | Rajendrapur | 136 | 13:00 | 125 | 00:00
Dohazari | 127 | 06:00 | 121 | 11:00 | Rajshahi | 131 | 04:00 | 122 | 23:00
Faridpur | 135 | 09:00 | 129 | 22:00 | Rajshahi-230 | 132 | 06:00 | 123 | 23:00
Fatullah | 133 | 06:00 | 127 | 11:00 | Ramganj | 119 | 03:00 | 115 | 11:00
Fenchuganj | 137 | 18:00 | 133 | 10:00 | Rampur | 131 | 04:00 | 125 | 11:00
Feni | 121 | 19:30 | 116 | 10:00 | Rampura | 136 | 06:00 | 125 | 13:00
Ghatail | 127 | 14:00 | 118 | 18:30 | Rangamati | 133 | 07:00 | 129 | 11:00
Ghorashal | 137 | 06:00 | 133 | 11:00 | Rangpur | 131 | 09:00 | 126 | 01:00
Goalpara | 139 | 09:00 | 128 | 23:00 | Ruppur | 137 | 05:00 | 128 | 19:00
Gollamari | 139 | 06:00 | 129 | 23:00 | Saidpur | 133 | 06:00 | 128 | 19:30
Gopalganj | 137 | 08:00 | 128 | 22:00 | Satkhira | 136 | 06:00 | 124 | 21:00
Gopalganj-400 | 137 | 06:00 | 132 | 00:00 | Satmasjid | 138 | 06:00 | 131 | 11:00
Gulshan | 136 | 05:00 | 126 | 13:00 | Savar | 133 | 13:00 | 127 | 09:00
Halishahar | 132 | 06:00 | 127 | 10:00 | SevenRings | 137 | 06:00 | 133 | 10:00
Haripur | 129 | 04:00 | 126 | 11:00 | ShahCement | 131 | 06:00 | 125 | 12:00
HaripurSBU | 129 | 05:00 | 126 | 11:00 | Shahjadpur | 137 | 03:00 | 131 | 18:00
Hasnabad | 132 | 04:00 | 128 | 10:00 | Shahjibazar | 136 | 06:00 | 129 | 11:00
Hathazari | 134 | 04:00 | 130 | 11:00 | Shahmirpur | 131 | 06:00 | 127 | 11:00
Ishurdi | 139 | 08:00 | 129 | 18:30 | Shariatpur | 135 | 06:00 | 128 | 22:00
Jaldhaka | 132 | 06:00 | 123 | 01:00 | Sherpur | 125 | 13:00 | 112 | 00:00
Jamalpur | 126 | 09:00 | 115 | 00:00 | Shikalbaha | 121 | 05:00 | 117 | 11:00
Jashore | 137 | 08:00 | 123 | 23:00 | Shikalbaha-230 | 134 | 06:00 | 129 | 11:00
Jhenaidah | 138 | 07:00 | 117 | 21:00 | Shitalakhya | 130.7 | 06:00 | 125 | 11:00
Jhenaidah-230 | 139 | 05:00 | 128 | 19:00 | Sholosohor | 133 | 03:00 | 130 | 14:00
Joydebpur | 136 | 19:30 | 127 | 09:00 | Shyampur | 133 | 19:00 | 130 | 00:00
Joypurhat | 128 | 06:00 | 117 | 23:00 | Shyampur-230 | 133 | 06:00 | 128 | 10:00
Juldah | 130 | 02:00 | 128 | 11:00 | Siddhirganj | 130 | 04:00 | 126 | 11:00
Kabirpur | 134 | 19:30 | 122 | 16:00 | Sirajganj | 132 | 06:00 | 124 | 19:30
Kachua | 128 | 07:00 | 124 | 14:00 | Sonargaon | 128 | 04:00 | 124 | 11:00
Kaliakoir | 135 | 19:30 | 129 | 14:00 | Sreemongol | 135 | 07:00 | 128 | 11:00
Kallyanpur | 134 | 15:00 | 127 | 11:00 | Sreepur | 134 | 14:00 | 128 | 00:00
Kalurghat | 133 | 04:00 | 129 | 11:00 | Srinagar | 138 | 05:00 | 131 | 11:00
Kamrangirchar | 138 | 06:00 | 132 | 11:00 | SSM | 132 | 00:00 | 131 | 18:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 11:00 | 120 | 01:00
Kasba | 124 | 06:00 | 119 | 11:00 | Sylhet | 130 | 07:00 | 126 | 23:00
Kazla | 133 | 05:00 | 127 | 12:00 | Sylhet-132 | 129 | 07:00 | 127 | 00:00
Keranigonj | 139 | 06:00 | 133 | 11:00 | Tangail | 127 | 14:00 | 120 | 18:30
Khagrachori | 132 | 06:00 | 129 | 11:00 | Taraganj | 131 | 10:00 | 125 | 17:00
Khulna | 138 | 09:00 | 127 | 22:00 | Thakurgaon | 134 | 18:00 | 120 | 17:00
Khulna(S) | 140 | 06:00 | 129 | 23:00 | TK | 133 | 05:00 | 130 | 00:00
Khulshi | 130 | 05:00 | 125 | 11:00 | Tongi | 136 | 06:00 | 128 | 11:00
Kishoreganj | 131 | 14:00 | 123 | 18:30 | Ullahpara | 134 | 05:00 | 126 | 19:00
Kodda | 135 | 13:00 | 125 | 11:00 | Ullon | 136 | 06:00 | 124 | 13:00
KSRM | 132 | 06:00 | 127 | 11:00 | Uttara | 132 | 03:00 | 127 | 11:00
Kulaura | 134 | 05:00 | 131 | 23:00 | UttaraNew | 133 | 04:00 | 128 | 14:00
Kurigram | 131 | 06:00 | 123 | 01:00 | Zigatola | 139 | 06:00 | 132 | 11:00
Kushtia | 133 | 05:00 | 121 | 18:30
Laksam | 127 | 19:30 | 124 | 00:00
Lakshmipur | 117 | 07:00 | 108 | 22:00
Lalbag | 137 | 04:00 | 132 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division