## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-09-2025 | during | 19-09-2025 | during | 19-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 367 | 337 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 309 | 296 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 95 | 99 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 7 | 0 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 29.8 | 43.7 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 122 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 48 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 25 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 81 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 87 | 87.5 | 87.5 | 51 | 87 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 141 | 140 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 465 | 400 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2335.8 | 2748.7 | 5465.54 | 5442.54 | 3590.75 | 3621.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 202 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 195 | 200 | 195 | 200 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 10 | 59 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 70 | 70 | 70 | 70 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 29 | 35 | 42 | 35 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 93 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.92 | 0 | 2.88 | 0 | 2.88 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 1 | 64 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1165 | 1125 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 265 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1935.92 | 2279 | 3314.6 | 3305.72 | 2914.24 | 2905.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 270 | 270 | 270 | 270 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 37 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 36 | 55 | 55 | 38 | 38 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 108 | 195 | 195 | 81 | 81 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 105 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 34 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 94 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 68 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 67 | 91 | 115 | 115 | 92 | 92 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 76 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1459 | 1703 | 2709.56 | 2649.56 | 2307.06 | 2256.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-09-2025 | during | 19-09-2025 | during | 19-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 0 | 157.5 | 157.5 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 76 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 4.48 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 114.48 | 102 | 357.4 | 320.5 | 175.4 | 138.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 143 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 4 | 7 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 357 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1228 | 1168 | 1268 | 1268 | 1223 | 1223
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 881 | 882 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1117 | 1152 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2136 | 2072 | 3617.2 | 3552.2 | 2446.2 | 2381.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 350 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1095 | 1225 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 273 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.74 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1903.74 | 2183 | 2162 | 2161 | 2082 | 2081
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 25.66 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 195 | 196 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 176 | 165 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 166 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 7 | 18 | 18 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 62 | 0 | 0 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.72 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 921.42 | 1440 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 3.37 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 67 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1978.17 | 2553 | 3073.47 | 2918.87 | 3096.09 | 2941.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 43 | 45 | 45 | 45 | 45 | 45 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 170 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 24 | 0 | 44.95 | 0 | 44.95 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 413.9 | 436 | 527.95 | 453 | 527.95 | 453
System Total |  |  |  |  | 28823.2 | 27829.875 | 13505.01 | 15244.7 | 22495.72 | 22071.39 | 18362.69 | 18001.36
Forecast Scenario (19-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14900 |  | 0 |  | 14900
|  |  |  | 1:00 | 14490 |  | 0 |  | 14490
|  |  |  | 2:00 | 14180 |  | 0 |  | 14180
|  |  |  | 3:00 | 13640 |  | 0 |  | 13640
|  |  |  | 4:00 | 13290 |  | 0 |  | 13290
|  |  |  | 5:00 | 13090 |  | 0 |  | 13090
|  |  |  | 6:00 | 12340 |  | 0 |  | 12340
|  |  |  | 7:00 | 11980 |  | 0 |  | 11980
|  |  |  | 8:00 | 11920 |  | 0 |  | 11920
|  |  |  | 9:00 | 11660 |  | 0 |  | 11660
|  |  |  | 10:00 | 11580 |  | 0 |  | 11580
|  |  |  | 11:00 | 11930 |  | 0 |  | 11930
|  |  |  | 12:00 | 12350 |  | 0 |  | 12350
|  |  |  | 13:00 | 13100 |  | 0 |  | 13100
|  |  |  | 14:00 | 12480 |  | 0 |  | 12480
|  |  |  | 15:00 | 12570 |  | 0 |  | 12570
|  |  |  | 16:00 | 12270 |  | 0 |  | 12270
|  |  |  | 17:00 | 11920 |  | 0 |  | 11920
|  |  |  | 18:00 | 11800 |  | 0 |  | 11800
|  |  |  | 18:30 | 12900 |  | 0 |  | 12900
|  |  |  | 19:00 | 14030 |  | 0 |  | 14030
|  |  |  | 19:30 | 14380 |  | 0 |  | 14380
|  |  |  | 20:00 | 14460 |  | 0 |  | 14460
|  |  |  | 21:00 | 14800 |  | 0 |  | 14800
|  |  |  | 22:00 | 14840 |  | 0 |  | 14840
|  |  |  | 23:00 | 14890 |  | 0 |  | 14890
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 12350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 314.51 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:47 hrs on 19-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-09-2025 | [28 empty] | Date: | 18-09-2025 | [28 empty] | Date: | 18-09-2025 | [28 empty] | Date: | 18-09-2025 | [28 empty] | Date: | 18-09-2025 | [14 empty] | Date: | 18-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 31.6 | 17 | 62 | 60 | 0 | 0 | 30 | 86 | 0 | 340 | 295 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 25 | 21 | 0 | 320 | 0 | 0 | 17 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 0 | 220 | 33 | 36 | 265 | 0 | 0 | 40 | 8 | 31 | 220 | 0 | 0 | 0 | 1125 | 0 | 51 | 10 | 35 | 0 | 355 | 330 | 38 | 192 | 34 | 65 | 90 | 100 | 0 | 19 | 114 | 48 | 8 | 0 | 23 | 310 | 0 | 373 | 0 | 58 | 156 | 8 | 0 | 84 | 30 | 0 | 18 | 167 | 17 | 78 | 9 | 21 | 0 | 0 | 18 | 7153.6 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 169 | 0 | 174 | 0 | 414 | 0 | 0 | 166 | 43 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 303 | 1195 | 0 | 6909 | 14062.6 | 108.37
01:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 60 | 30 | 0 | 0 | 0 | 52 | 0 | 340 | 307 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 90 | 25 | 21 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 0 | 219 | 32 | 35 | 265 | 0 | 0 | 40 | 0 | 29 | 219 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 35 | 0 | 353 | 330 | 38 | 199 | 37 | 62 | 90 | 100 | 0 | 19 | 114 | 46 | 0 | 0 | 23 | 305 | 0 | 385 | 0 | 58 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 78 | 9 | 23 | 0 | 0 | 18 | 6917 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 1309.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 170 | 0 | 174 | 0 | 414 | 0 | 0 | 163 | 43 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 115 | 220 | 0 | 304 | 1230 | 0 | 6675.71 | 13592.71 | 108.36
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 340 | 292 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 219 | 27 | 35 | 265 | 0 | 0 | 40 | 0 | 31 | 219 | 0 | 0 | 0 | 1115 | 0 | 51 | 0 | 35 | 0 | 355 | 330 | 38 | 189 | 37 | 62 | 90 | 100 | 0 | 19 | 114 | 44 | 0 | 0 | 23 | 305 | 0 | 359 | 0 | 58 | 152 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 23 | 0 | 0 | 18 | 6697 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 1214.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 174 | 0 | 174 | 0 | 414 | 0 | 0 | 164 | 43 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 304 | 1230 | 0 | 6529.54 | 13226.54 | 108.34
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 49 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 298 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 35 | 265 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 1085 | 0 | 51 | 0 | 35 | 0 | 355 | 330 | 38 | 199 | 37 | 63 | 90 | 85 | 0 | 19 | 114 | 44 | 0 | 0 | 23 | 300 | 0 | 386 | 0 | 58 | 153 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 23 | 0 | 0 | 12 | 6588 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 1110.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 175 | 0 | 174 | 0 | 414 | 0 | 0 | 166 | 43 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 220 | 0 | 304 | 1120 | 0 | 6248.41 | 12836.41 | 108.32
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 310 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 35 | 265 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 35 | 0 | 353 | 330 | 38 | 204 | 37 | 66 | 90 | 85 | 0 | 19 | 98 | 42 | 0 | 0 | 23 | 310 | 0 | 396 | 0 | 58 | 155 | 6 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 23 | 0 | 0 | 12 | 6536 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 919 | 0 | 1044.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 176 | 0 | 176 | 0 | 414 | 0 | 0 | 164 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 303 | 1110 | 0 | 5972.3 | 12508.3 | 108.3
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 304 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 37 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 35 | 0 | 354 | 330 | 38 | 199 | 37 | 71 | 90 | 85 | 0 | 19 | 98 | 42 | 0 | 0 | 23 | 320 | 0 | 408 | 0 | 58 | 161 | 6 | 0 | 85 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 23 | 0 | 0 | 12 | 6559 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 908 | 0 | 1012.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 176 | 0 | 186 | 0 | 414 | 0 | 0 | 163 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 297 | 1110 | 0 | 5931.56 | 12490.56 | 108.28
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 34 | 28 | 0 | 0 | 0 | 0 | 0 | 340 | 295 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.08 | 220 | 0 | 38 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 995 | 1 | 51 | 0 | 35 | 0 | 355 | 330 | 38 | 192 | 37 | 67 | 90 | 85 | 0 | 19 | 70 | 40 | 0 | 3 | 0 | 305 | 0 | 366 | 0 | 58 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 23 | 0 | 0 | 12 | 6031.08 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 923 | 0 | 1007.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 196 | 0 | 176 | 0 | 189 | 0 | 414 | 0 | 0.01 | 164 | 44 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0.01 | 0 | 168 | 115 | 220 | 0 | 296 | 1110 | 0 | 6090.93 | 12122.01 | 108.26
07:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 0 | 0 | 340 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 70 | 25 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 220 | 0 | 38 | 265 | 0 | 0 | 10 | 0 | 0 | 220 | 0 | 0 | 0 | 910 | 5 | 51 | 0 | 35 | 0 | 351 | 330 | 38 | 204 | 37 | 65 | 90 | 85 | 8 | 7 | 70 | 38 | 0 | 18 | 0 | 305 | 0 | 400 | 0 | 58 | 156 | 0 | 0 | 85 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 22 | 0 | 1.71 | 12 | 6072.21 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 972 | 0 | 911.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 8 | 0 | 0 | 0.82 | 196 | 0 | 176 | 0 | 192 | 0 | 414 | 0 | 0.01 | 163 | 44 | 0 | 0 | 0 | 0 | 176 | 0 | 0.5 | 7 | 0.07 | 0 | 174 | 115 | 220 | 0 | 296 | 1000 | 0 | 6007.02 | 12079.23 | 108.24
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 68 | 45 | 0 | 0 | 2 | 0 | 0 | 400 | 306 | 0 | 0 | 0 | 0 | 39 | 0 | 11 | 52 | 26 | 22 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 222 | 0 | 11 | 265 | 0 | 0 | 34 | 0 | 0 | 220 | 0 | 0 | 0 | 900 | 10 | 51 | 0 | 35 | 0 | 351 | 330 | 36 | 199 | 37 | 66 | 90 | 68 | 8 | 7 | 37 | 36 | 0 | 34 | 0 | 310 | 0 | 396 | 0 | 58 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 22 | 1 | 5.8 | 12 | 6248.62 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 950 | 0 | 910.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 21 | 0 | 0 | 3.38 | 196 | 0 | 181 | 0 | 187 | 0 | 414 | 0 | 0.48 | 163 | 43 | 0 | 2 | 0 | 0 | 177 | 0 | 1 | 7 | 0.37 | 0 | 171 | 115 | 220 | 0 | 296 | 990 | 0 | 6022.83 | 12271.45 | 108.25
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 4.5 | 0 | 70 | 45 | 30 | 0 | 26 | 15 | 0 | 400 | 296 | 0 | 0 | 0 | 0 | 97 | 0 | 18 | 52 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 222 | 0 | 5 | 265 | 0 | 0 | 39 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 13 | 51 | 5 | 35 | 0 | 351 | 330 | 35 | 193 | 36 | 67 | 90 | 68 | 9 | 7 | 34 | 32 | 0 | 46 | 0 | 310 | 0 | 370 | 0 | 58 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 22 | 1 | 8.19 | 12 | 6461.61 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 945 | 0 | 909.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.54 | 59 | 0 | 0 | 13.45 | 195 | 0 | 184 | 0 | 185 | 0 | 414 | 0 | 0.97 | 165 | 44 | 0 | 2 | 0 | 0 | 176 | 0 | 1.5 | 6 | 0.23 | 0 | 168 | 115 | 220 | 0 | 297 | 1050 | 0 | 6151.25 | 12612.86 | 108.26
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15.4 | 0 | 70 | 45 | 30 | 0 | 36 | 50 | 0 | 400 | 300 | 0 | 0 | 0 | 0 | 96 | 0 | 20 | 52 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 222 | 0 | 6 | 265 | 0 | 0 | 46 | 0 | 0 | 219 | 0 | 0 | 0 | 1071 | 17 | 43 | 10 | 35 | 0 | 349 | 330 | 35 | 195 | 37 | 65 | 90 | 68 | 8 | 7 | 34 | 36 | 0 | 67 | 1 | 310 | 0 | 386 | 0 | 58 | 156 | 0 | 0 | 63 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 18 | 1 | 29.24 | 12 | 6614.15 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 930 | 0 | 907.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.27 | 45 | 0 | 0 | 17.83 | 196 | 0 | 182 | 0 | 183 | 0 | 414 | 0 | 2.29 | 168 | 43 | 0 | 9 | 0 | 0 | 167 | 0 | 5.9 | 3 | 0.65 | 0 | 169 | 115 | 220 | 0 | 297 | 1090 | 0 | 6201.27 | 12815.42 | 108.26
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15.4 | 6 | 70 | 45 | 30 | 0 | 53 | 105 | 0 | 400 | 304 | 0 | 0 | 0 | 0 | 96 | 0 | 36 | 52 | 19 | 22 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 222 | 0 | 2 | 265 | 0 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 0 | 1092 | 18 | 43 | 10 | 35 | 0 | 347 | 330 | 37 | 200 | 37 | 64 | 90 | 68 | 0 | 7 | 34 | 36 | 0 | 74 | 22 | 315 | 0 | 386 | 0 | 58 | 156 | 4 | 0 | 70 | 30 | 0 | 18 | 166 | 0 | 77 | 9 | 10 | 1 | 2.72 | 12 | 6763.98 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 955 | 0 | 922.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.06 | 65 | 0 | 0 | 8.61 | 196 | 0 | 179 | 0 | 179 | 0 | 414 | 0 | 1.68 | 168 | 43 | 0 | 9 | 0 | 0 | 174 | 0 | 4.7 | 18 | 0.7 | 0 | 170 | 115 | 220 | 0 | 300 | 1090 | 0 | 6300.79 | 13064.77 | 108.27
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 29.8 | 17 | 81 | 45 | 95 | 0 | 55 | 141 | 0 | 400 | 309 | 0 | 0 | 48 | 0 | 95 | 0 | 15 | 52 | 24 | 22 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 202 | 1 | 6 | 265 | 0 | 0 | 50 | 0 | 10 | 215 | 0 | 0 | 0 | 1165 | 18 | 43 | 18 | 35 | 0 | 343 | 330 | 36 | 203 | 37 | 67 | 90 | 68 | 0 | 16 | 34 | 42 | 0 | 76 | 21 | 315 | 0 | 389 | 0 | 58 | 163 | 4 | 0 | 85 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 10 | 1 | 4.48 | 12 | 7073.2 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 1117 | 0 | 921.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.66 | 67 | 0 | 0 | 3.37 | 195 | 0 | 176 | 0 | 175 | 0 | 414 | 0 | 0.72 | 166 | 43 | 0 | 6 | 0 | 0 | 172 | 0 | 2.9 | 24 | 0.74 | 0 | 172 | 115 | 220 | 0 | 301 | 1095 | 0 | 6431.81 | 13505.01 | 108.27
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 49.2 | 17 | 147 | 45 | 95 | 0 | 55 | 157 | 0 | 400 | 292 | 0 | 0 | 55 | 0 | 95 | 0 | 22 | 52 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.7 | 221 | 15 | 13 | 265 | 0 | 0 | 46 | 0 | 32 | 215 | 0 | 0 | 0 | 1130 | 19 | 43 | 73 | 35 | 0 | 354 | 330 | 36 | 188 | 37 | 70 | 90 | 68 | 0 | 19 | 34 | 42 | 0 | 70 | 27 | 320 | 0 | 355 | 0 | 58 | 161 | 4 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 10 | 1 | 0.8 | 12 | 7202.7 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95 | 1160 | 0 | 1002.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.46 | 30 | 0 | 0 | 11.84 | 197 | 0 | 175 | 0 | 174 | 0 | 414 | 0 | 0.51 | 168 | 43 | 0 | 14 | 0 | 0 | 171 | 0 | 4 | 78 | 0.37 | 0 | 253 | 115 | 220 | 0 | 302 | 1095 | 0 | 6681.4 | 13884.1 | 108.27
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 44.5 | 17 | 149 | 45 | 95 | 0 | 55 | 148 | 0 | 400 | 298 | 0 | 0 | 55 | 0 | 35 | 0 | 12 | 35 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.15 | 221 | 14 | 7 | 265 | 0 | 0 | 50 | 0 | 29 | 215 | 0 | 0 | 0 | 1146 | 17 | 43 | 80 | 35 | 0 | 349 | 330 | 37 | 192 | 37 | 64 | 90 | 68 | 0 | 19 | 34 | 44 | 0 | 61 | 27 | 300 | 0 | 363 | 0 | 58 | 141 | 4 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 10 | 0 | 2.93 | 12 | 7042.58 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 1172 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.74 | 52 | 0 | 0 | 16 | 196 | 0 | 174 | 0 | 173 | 0 | 414 | 0 | 1.2 | 167 | 43 | 0 | 18 | 0 | 0 | 172 | 0 | 5.9 | 106 | 0.66 | 0 | 273 | 115 | 220 | 0 | 302 | 1085 | 0 | 6768.5 | 13811.08 | 108.27
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 48.6 | 17 | 149 | 45 | 95 | 0 | 55 | 153 | 0 | 420 | 300 | 0 | 0 | 55 | 0 | 98 | 0 | 9 | 35 | 24 | 22 | 0 | 455 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.5 | 220 | 15 | 5 | 265 | 0 | 0 | 50 | 1 | 32 | 215 | 0 | 0 | 0 | 1160 | 15 | 43 | 80 | 35 | 0 | 347 | 330 | 37 | 197 | 37 | 67 | 90 | 68 | 0 | 19 | 70 | 46 | 0 | 47 | 27 | 310 | 0 | 384 | 0 | 58 | 154 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 9 | 1 | 4.01 | 12 | 7248.11 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 1179 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.19 | 48 | 0 | 0 | 14.92 | 198 | 0 | 168 | 0 | 170 | 0 | 414 | 0 | 1.21 | 166 | 43 | 0 | 14 | 0 | 0 | 129 | 0 | 5.2 | 72 | 0 | 0 | 275 | 115 | 220 | 0 | 303 | 1100 | 0 | 6644.52 | 13892.63 | 108.26
16:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 46.2 | 30 | 141 | 45 | 95 | 0 | 55 | 146 | 0 | 420 | 309 | 0 | 0 | 55 | 0 | 97 | 0 | 6 | 35 | 23 | 22 | 0 | 460 | 0 | 0 | 50 | 0 | 6 | 65 | 0 | 0 | 0 | 0 | 2.03 | 221 | 14 | 5 | 265 | 0 | 0 | 50 | 15 | 31 | 215 | 0 | 0 | 0 | 1117 | 5 | 43 | 80 | 35 | 0 | 339 | 330 | 36 | 205 | 37 | 68 | 40 | 68 | 0 | 19 | 70 | 42 | 0 | 29 | 27 | 310 | 0 | 391 | 0 | 58 | 154 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 16 | 78 | 9 | 10 | 0 | 4.58 | 12 | 7278.81 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1156 | 0 | 961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.04 | 40 | 0 | 0 | 10.76 | 197 | 0 | 166 | 0 | 167 | 0 | 350 | 0 | 0.84 | 166 | 43 | 0 | 5 | 0 | 0 | 129 | 0 | 0.5 | 37 | 0 | 0 | 229 | 115 | 220 | 0 | 304 | 1060 | 0 | 6309.14 | 13587.95 | 108.26
17:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 49.8 | 35 | 97 | 65 | 95 | 0 | 55 | 157 | 0 | 420 | 299 | 0 | 0 | 55 | 0 | 97 | 0 | 3 | 35 | 23 | 22 | 0 | 450 | 0 | 0 | 50 | 0 | 4 | 64 | 0 | 0 | 0 | 0 | 0.33 | 222 | 16 | 15 | 265 | 0 | 0 | 50 | 17 | 30 | 216 | 0 | 0 | 0 | 1092 | 1 | 51 | 80 | 35 | 0 | 343 | 330 | 36 | 195 | 37 | 68 | 0 | 68 | 0 | 19 | 70 | 30 | 0 | 7 | 27 | 320 | 0 | 369 | 0 | 58 | 158 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 78 | 9 | 10 | 0 | 2.57 | 12 | 7178.7 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 1112 | 0 | 954 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 2.45 | 15 | 0 | 0 | 4.36 | 198 | 0 | 166 | 0 | 167 | 0 | 414 | 0 | 0.37 | 168 | 45 | 0 | 2 | 0 | 0 | 86 | 0 | 0.1 | 16 | 0.04 | 0 | 226 | 115 | 220 | 0 | 302 | 1050 | 0 | 6200.32 | 13379.02 | 108.26
18:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 46.6 | 35 | 101 | 0 | 195 | 0 | 55 | 146 | 0 | 300 | 310 | 0 | 0 | 55 | 0 | 36 | 0 | 0 | 35 | 23.5 | 22 | 0 | 340 | 0 | 0 | 55 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 222 | 32 | 12 | 265 | 0 | 0 | 50 | 17 | 31 | 205 | 0 | 0 | 0 | 1095 | 0 | 51 | 88 | 35 | 0 | 300 | 280 | 36 | 198 | 37 | 70 | 40 | 69 | 0 | 19 | 114 | 50 | 8 | 0 | 27 | 305 | 0 | 359 | 0 | 58 | 153 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 6729.1 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 1100 | 0 | 15 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 155 | 0 | 166 | 0 | 165 | 0 | 300 | 0 | 0 | 168 | 45 | 75 | 0 | 58 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 222 | 100 | 180 | 0 | 304 | 1056 | 0 | 6189 | 12918.1 | 108.26
19:00 | 0 | 2 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 49.4 | 17 | 122 | 25 | 293 | 17 | 55 | 155 | 0 | 420 | 298 | 0 | 0 | 55 | 0 | 98 | 0 | 0 | 35 | 24 | 22 | 0 | 400 | 0 | 0 | 79 | 0 | 0 | 66 | 32 | 0 | 0 | 0 | 0 | 222 | 48 | 20 | 265 | 0 | 0 | 50 | 17 | 56 | 215 | 0 | 0 | 0 | 1129 | 0 | 51 | 90 | 88 | 0 | 352 | 330 | 36 | 189 | 37 | 83 | 94 | 68 | 0 | 19 | 114 | 46 | 25 | 0 | 28 | 310 | 0 | 357 | 0 | 58 | 158 | 5 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 2 | 5 | 0 | 0 | 0 | 0 | 7511.4 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 1449 | 0 | 48 | 0 | 35 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 180 | 0 | 166 | 0 | 167 | 0 | 414 | 0 | 0 | 170 | 45 | 110 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 350 | 1185 | 0 | 7186 | 14697.4 | 108.25
19:30 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 44 | 17 | 132 | 85 | 293 | 55 | 55 | 140 | 0 | 420 | 291 | 0 | 0 | 55 | 0 | 98 | 0 | 0 | 125 | 25 | 22 | 0 | 400 | 0 | 0 | 85 | 0 | 0 | 66 | 70 | 0 | 0 | 0 | 0 | 221 | 60 | 25 | 265 | 0 | 0 | 50 | 17 | 57 | 218 | 0 | 0 | 0 | 1120 | 0 | 51 | 108 | 107 | 0 | 354 | 330 | 36 | 184 | 37 | 91 | 94 | 68 | 0 | 19 | 114 | 46 | 25 | 0 | 28 | 300 | 0 | 349 | 0 | 58 | 148 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 64 | 9 | 0 | 0 | 0 | 6 | 7837 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 1443 | 0 | 48 | 0 | 50 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 196 | 0 | 165 | 0 | 166 | 0 | 414 | 0 | 0 | 170 | 45 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 115 | 220 | 0 | 350 | 1210 | 0 | 7295 | 15132
20:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 43.7 | 17 | 132 | 122 | 293 | 55 | 55 | 140 | 0 | 420 | 296 | 0 | 0 | 55 | 0 | 99 | 0 | 0 | 125 | 25 | 22 | 0 | 400 | 0 | 0 | 93 | 0 | 0 | 66 | 70 | 0 | 0 | 0 | 0 | 222 | 64 | 29 | 265 | 0 | 0 | 50 | 17 | 59 | 219 | 0 | 0 | 0 | 1125 | 0 | 51 | 105 | 108 | 0 | 353 | 330 | 36 | 190 | 37 | 91 | 94 | 68 | 0 | 19 | 114 | 48 | 25 | 0 | 34 | 305 | 0 | 357 | 0 | 58 | 143 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 76 | 9 | 0 | 0 | 0 | 0 | 8000.7 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 1440 | 0 | 47 | 0 | 50 | 70 | 0 | 62 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 196 | 0 | 165 | 0 | 166 | 0 | 350 | 0 | 0 | 170 | 45 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 350 | 1225 | 0 | 7244 | 15244.7 | 108.25
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 44.5 | 17 | 138 | 123 | 160 | 0 | 55 | 141 | 0 | 450 | 296 | 0 | 0 | 55 | 0 | 98 | 0 | 0 | 108 | 25.5 | 22 | 0 | 425 | 0 | 0 | 93 | 0 | 0 | 66 | 45 | 0 | 0 | 0 | 0 | 221 | 64 | 31 | 265 | 0 | 0 | 50 | 12 | 60 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 113 | 128 | 0 | 354 | 330 | 36 | 192 | 37 | 82 | 94 | 68 | 0 | 19 | 114 | 46 | 8 | 0 | 36 | 305 | 0 | 360 | 0 | 58 | 143 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 17 | 78 | 9 | 0 | 0 | 0 | 0 | 7874 | 882 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 0 | 1442.27 | 0 | 22 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 167 | 0 | 166 | 0 | 414 | 0 | 0 | 170 | 45 | 115 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 304 | 1225 | 0 | 7098.27 | 14972.27 | 108.25
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 45 | 17 | 149 | 116 | 45 | 0 | 55 | 142 | 0 | 450 | 296 | 0 | 0 | 17 | 0 | 98 | 0 | 0 | 108 | 25.5 | 22 | 0 | 440 | 0 | 0 | 74 | 0 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 221 | 48 | 31 | 265 | 0 | 0 | 50 | 17 | 50 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 90 | 137 | 0 | 354 | 330 | 37 | 192 | 34 | 70 | 95 | 68 | 0 | 19 | 114 | 48 | 8 | 0 | 36 | 305 | 0 | 362 | 0 | 58 | 151 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 7638.5 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 1447.85 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 168 | 0 | 168 | 0 | 414 | 0 | 0 | 170 | 45 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 305 | 1230 | 0 | 7034.85 | 14673.35 | 108.25
23:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 44.4 | 17 | 130 | 90 | 15 | 0 | 35 | 108 | 0 | 450 | 298 | 0 | 0 | 17 | 0 | 98 | 0 | 0 | 108 | 25.8 | 22 | 0 | 450 | 0 | 0 | 70 | 0 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 221 | 49 | 35 | 265 | 0 | 0 | 50 | 17 | 44 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 30 | 80 | 0 | 352 | 330 | 37 | 176 | 37 | 70 | 95 | 68 | 0 | 19 | 114 | 52 | 8 | 0 | 36 | 300 | 0 | 396 | 0 | 58 | 150 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 7434.2 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 1462.18 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 168 | 0 | 169 | 0 | 414 | 0 | 0 | 170 | 45 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 303 | 1232 | 0 | 7030.18 | 14464.38 | 108.25
Total KWH | 0 | 1220160 | 497760 | 0 | 0 | 0 | 0 | 0 | 8690400 | 0 | 0 | 651240 | 293040 | 2261088 | 1242240 | 1675822 | 108199 | 804893 | 2105280 | 0 | 9219000 | 7293760 | 0 | 0 | 583238 | 1848364 | 1562000 | 0 | 148091 | 1622400 | 563400 | 513000 | 0 | 9729090.91 | 0 | 0 | 638400 | 0 | 19200 | 945596 | 240912 | 0 | 0 | 0 | 27242 | 5308833 | 564543 | 518400 | 6363636.36 | 0 | 0 | 973920 | 151506 | 623927 | 5218876 | 0 | 0 | 0 | 26225452 | 124335 | 1188020 | 1068872 | 1237818 | 0 | 8739800 | 7950000 | 885600 | 4762000 | 891288 | 1665600 | 1980250 | 1862880 | 39480 | 378600 | 1944840 | 1018560 | 105062 | 528582 | 525040 | 7538500 | 0 | 9427000 | 0 | 1340040 | 3709063 | 123984 | 0 | 1990080 | 719712 | 0 | 440000 | 4425340 | 144000 | 1765200 | 199200 | 288000 | 5250 | 71590 | 238560 | 169775055.27 | 21335272 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 622800 | 25781800 | 0 | 27021091 | 0 | 125330 | 0 | 88224 | 154560 | 0 | 328960 | 0 | 0 | 272691 | 507408 | 25274 | 0 | 117000 | 4945445 | 0 | 4382145 | 0 | 4273818 | 0 | 9842327 | 0 | 9600 | 4058000 | 1003636 | 775191 | 93494 | 574464 | 0 | 1910947.5 | 0 | 31240.32 | 375840 | 4516 | 0 | 5323000 | 2754000 | 5428200 | 0 | 7351992 | 27761454.55 | 0 | 158191720.37 | 327966775.64

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13505.01 | MW | 12:00 Hr. | Energy Generated |  |  | 327.9668 |  | MKWHr.
| Day Peak Demand |  |  | 13505.01 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.762 |  | MKWHr.
| Evening Peak Generation |  |  | 15244.7 | MW | 20:00 Hr. | Energy Demand |  |  | 328.7288 |  | MKWHr.
| Evening Peak Demand |  |  | 15400.7 | MW | 20:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 12079.23 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 983.47 |  | MMCFD
| Maximum Generation of the Day |  |  | 15244.7 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.015 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.419 | 0 | 13.0654 | 0 | 0 | 0.14809 | 0 | 0 | 52.6325 | Gas | 134.7973 | Gas | 488142682.9347
| Chattogram Zone |  |  | 5.7373 | 32.5891 | 4.1388 | 0 | 5.3088 | 0.15158 | 0 | 0.0192 | 47.9448 | Coal | 103.869 | Coal | 620248680.1507
| Cumilla Zone |  |  | 28.0134 | 0 | 7.2118 | 0 | 0 | 0.52858 | 1.0186 | 0 | 36.7723 | HFO | 28.8349 | HFO | 528750748.86
| Mymensingh Zone |  |  | 0.288 | 0 | 2.347 | 0 | 0 | 0.07684 | 0 | 0 | 2.7118 | HSD | 1.9109 | HSD | 0
| Sylhet Zone |  |  | 29.7137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.7137 | Hydro | 5.3088 | Hydro | 530883.3
| Khulna Zone |  |  | 0 | 25.7818 | 0 | 0 | 0 | 0.6228 | 22.2473 | 0 | 48.6519 | Solar | 2.9397 | Solar | 41254342.5472
| Barishal Zone |  |  | 8.1822 | 40.4364 | 0 | 0 | 0 | 0.004516 | 0 | 0 | 48.6232 | Import | 50.2869 | Import | 293516669.75
| Rajshahi Zone |  |  | 23.4437 | 0 | 0.72235 | 0 | 0 | 0.9067 | 27.0211 | 0 | 52.0939 | Wind | 0.0192 | Wind | 283008
| Rangpur Zone |  |  | 0 | 5.0616 | 1.3497 | 1.9109 | 0 | 0.50057 | 0 | 0 | 8.8228
| Total |  |  | 134.7973 | 103.869 | 28.8349 | 1.9109 | 5.3088 | 2.9397 | 50.2869 | 0.0192 | 327.9668
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 488142682.9347 |  | Hydro | 530883.3
|  |  |  | Coal | 620248680.1507 |  | Solar | 41254342.5472
|  |  |  | HFO | 528750748.86 |  | Import | 293516669.75
|  |  |  | HSD | 0 |  | Wind | 283008
[5 empty] | Total: | 197,27,27,015 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3353 | Peak Hr Flow | 882.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51604369.56 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.0211 | Peak Hr Flow | 1440.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2290 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0186 | Peak Hr Flow | 48.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2754 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.3749 | Peak Hr Flow | 2370.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5393
|  |  |  | Chattogram |  | 0 |  | 1436
|  |  |  | Cumilla |  | 20 |  | 1485
|  |  |  | Mymensingh |  | 119 |  | 1121
|  |  |  | Sylhet |  | 0 |  | 594
|  |  |  | Khulna |  | 0 |  | 1852
|  |  |  | Barishal |  | 0 |  | 464
|  |  |  | Rajshahi |  | 0 |  | 1478
|  |  |  | Rangpur |  | 0 |  | 900
|  |  |  | Total |  | 149 |  | 14723
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 09:54 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to WZ red hot maintenance. | [7 empty] | 20.0MW load
interrup.
| 08:11 | 09:53 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to WZ red hot maintenance. | [7 empty] | 20.0MW load
interrup.
| 08:19 | 09:06 | Cumilla(S) 132/33kV S/S Cumilla North-2 Scheduled S/D Due to Emergency maintenance work.
| 08:44 | 10:10 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing CB1 A/R
Fail & B relays.
|  | 09:11 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
|  | 09:12 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
|  | 09:47 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
| 09:48 | 12:34 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Forced S/D Due to Red Hot (Ashuganj end)
|  | 09:50 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT is restored.
|  | 09:50 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT is restored.
|  | 09:53 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 is restored.
| 10:59 | 13:05 | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to due to 33kv busbar clamp &connector | [7 empty] | 12.5MW load
|  |  | measuring | [7 empty] | interrup.
| 10:59 | 13:05 | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to due to 33kv busbar clamp &connector
measuring
| 12:00 |  | Day peak Generation: 13499 MW.
| 12:05 | 00:57 | Bajitpur 132/33kV S/S Tr-1(404T) HT Scheduled S/D Due to Redhot maintenance
| 12:05 | 00:57 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D Due to Redhot Maintenance
| 14:27 | 15:40 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to T-2 is in shutdown for | [7 empty] | 34.0MW load
|  |  | maintenance (Red Hot) at PBS end. | [7 empty] | interrup.
|  | 15:07 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
| 15:16 | 17:30 | Bhaluka 132/33kV S/S Capacitor Bank- 01 Forced S/D Due to For pbs feeder no 16
| 15:17 | 17:25 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Forced S/D Due to For pbs feeder no 16 | [7 empty] | 25.0MW load
interrup.
| 15:17 | 17:26 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Forced S/D Due to For pbs feeder no 16 | [7 empty] | 25.0MW load
interrup.
| 16:21 | 17:58 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to OTI metre replacement
| 16:22 | 17:56 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to OTI metre replacement
| 16:22 | 17:56 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to OTI metre replacement
| 17:36 | 17:42 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 44.0MW load
interrup.
| 17:49 | 18:15 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Tripped showing RET 670 relays Due to | [7 empty] | 250.0MW load
|  |  | Directional Overcurrent | [7 empty] | interrup.
| 17:49 | 18:12 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Tripped showing RET 670 relays Due to | [7 empty] | 250.0MW load
|  |  | Directional Overcurrent | [7 empty] | interrup.
| 17:49 | 18:27 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 LT Tripped showing RET 670 relays Due to | [7 empty] | 250.0MW load
|  |  | Mechanical Protection trip | [7 empty] | interrup.
| 17:49 | 18:26 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 HT Tripped showing RET 670 relays Due to | [7 empty] | 250.0MW load
|  |  | Mechanical Protection trip | [7 empty] | interrup.
| 17:50 | 18:32 | Mymensingh RPCL-Tangail 132kV Ckt-2 Tripped from Ghatail 132/33kV end showing | [7 empty] | 60.0MW load
|  |  | REL650,REL670 relays Due to Due to 400/132 KV X-former tripped at Kaliakair Grid SS. | [7 empty] | interrup. Ghatail
132/33kV end
| 17:50 | 18:23 | Mymensingh RPCL-Tangail 132kV Ckt-1 Tripped from Ghatail 132/33kV end showing | [7 empty] | 60.0MW load
|  |  | REL650,REL670 relays Due to Due to 400/132 KV X-former tripped at Kaliakair Grid SS. | [7 empty] | interrup. Ghatail
132/33kV end
| 20:00 |  | Evening peak Generation is 15244 MW
|  | 20:30 | Siddhirganj 230/132kV S/S 335MW EGCB 2 is restored.
| 21:38 | 22:34 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D Due to 33KV Section Isolator Red | [7 empty] | 25.0MW load
|  |  | Hot Removed. | [7 empty] | interrup.
| 21:38 | 22:34 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to 33KV Section Isolator Red | [7 empty] | 25.0MW load
|  |  | Hot Removed. | [7 empty] | interrup.
| 21:59 | 22:19 | Bheramara P/S-Kustia 132 kV Ckt-1 Tripped from Kushtia 132/33kV end showing Z1 Fault
ABC C Phase 2.2 kilometer relays Due to Earth Fault and from Bheramara 230/132kV end
showing 86B relays Due to Distance, Overcorrect
| 22:46 | 23:10 | Baghabari-Ishurdi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing ABB relays.
| 23:16 | 01:18 | Pabna- Shahjadpur 132kV Ckt-1 Tripped from Pabna 132/33kV end showing GEN TRIP,Z1Trip,AR
Successful, VT fuse fail . relays. and from Shahjadpur 132/33kV end showing Distance
relay relays Due to Thundering
| 23:25 | 23:29 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 53.0MW load
interrup.
| 23:25 | 01:04 | Baghabari-Shahjadpur 132 kV Ckt-2 Tripped from Shahjadpur 132/33kV end showing Trip
circuit supervision relay relays Due to Thundering
| 23:25 | 00:39 | Baghabari-Ullahpara 132 kV Ckt-1 Tripped from Ullahpara 132/33kV end showing REL 650, REL
670 relays Due to Baghabari ckt Trip at Baghabari End But BKR Close on Ullapara Grid.
| 23:25 | 23:29 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 38.0MW load
interrup.
| 06:10 |  | Ashuganj South 360 MW CCPP ST was shutdown due to offline wash and maintenance work.
|  | 06:28 | Bhulta-Narsingdi 132 kV Ckt-1 is restored.
| 06:45 |  | Bhulta-Haripur 132 kV Ckt-1 Project Work S/D from Bhulta 132/33kV end Due to DFDR | [7 empty] | 60.0MW load
|  |  | Installation | [7 empty] | interrup. Bhulta
132/33kV end
| 06:47 |  | Meghnaghat 400/230kV S/S ATR - 2 LT Scheduled S/D Due to ATR 2 shutdown by siemens for
project work
| 06:47 |  | Meghnaghat 400/230kV S/S ATR - 2 HT Scheduled S/D Due to ATR 2 shutdown by siemens for
project work
| 06:49 |  | Ashuganj South 360 MW CCPP GT was shutdown due to offline wash and maintenance work.
| 06:49 |  | Ashuganj 450 MW CCPP(South) Shutdown
| 06:55 |  | Dhamrai-Kaliakoir 132 kV Ckt-1 Project Work S/D from Dhamrai 132/33kV end Due to Project
work and from Kaliakoir 400/230/132kV end Due to scheduled Shutdown Dhamrai s/s end
project works
| 07:00 |  | Minimum Generation: 11873 MW.
| 07:11 |  | Dhamrai 132/33kV S/S Transformer-1 LT Project Work S/D Due to Project work | [7 empty] | 50.0MW load
interrup.
| 07:11 |  | Dhamrai 132/33kV S/S Transformer-1 HT Project Work S/D Due to Project work | [7 empty] | 50.0MW load
interrup.
| 07:51 |  | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to Internal maintenance of EGCB
end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 337 | 8690400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9219000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 7293760 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 108199 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 1562000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1848364 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 43.7 | 651240 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 1242240 | FGMO
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 804893 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 583238 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 563400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 513000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 497760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 1675822 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2261088 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1220160 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 2105280 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 148091 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 293040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9729090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1622400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2748.7 | 52632465.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 151506 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 124335 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 973920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5308833 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5218876 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 59 | 623927 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 240912 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 945596 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 518400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 638400 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 64 | 564543 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1125 | 26225452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 19200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6363636.36 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2279 | 47944778.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4762000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8739800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7950000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 891288 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 36 | 885600 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 108 | 1237818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1188020 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 105 | 1068872 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 525040 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 1980250 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 1862880 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1018560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 105062 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 378600 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1944840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 39480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 1665600 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 528582 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1703 | 36772292
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 288000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 199200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 76 | 1765200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 71590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 238560 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 144000 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 102 | 2711800
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1340040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3709063 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719712 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1990080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4425340 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 440000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 123984 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7538500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 357 | 9427000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1168 | 29713719
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 882 | 21335272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 622800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1152 | 25781800 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2072 | 48651872
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 350 | 7351992 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2754000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1225 | 27761454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5428200 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 5323000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4516 | -
Barishal Area Total |  |  |  |  | 2236 | 2183 | 48623162.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 272691 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 125330 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4945445 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 165 | 4382145 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 166 | 4273818 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 9842327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 7 | 25274 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 62 | 328960 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 154560 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 88224 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1440 | 27021091 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 117000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 507408 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2553 | 52093873
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 1910947.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1003636 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4058000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 574464 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31240.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 775191 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93494 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 375840 | -
Rangpur Area Total |  |  |  |  | 950 | 436 | 8822812.82
Eastern Grid Total |  |  |  |  | 17385.715 | 8000.7 | 169775055.27
Western Grid Total |  |  |  |  | 10444.16 | 7244 | 158191720.37
National Grid Total |  |  |  |  | 27829.875 | 15244.7 | 327966775.64
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-09-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9879.01 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4693.9 | MW
i) Dhaka area |  |  | 5382.57 |  | MW | i) Khulna area |  |  |  | 1852 | MW
ii) Chattogram area |  |  | 1435.77 |  | MW | ii) Barishal area |  |  |  | 463.5 | MW
iii) Cumilla area |  |  | 1464.67 |  | MW | iii) Rajshahi area |  |  |  | 1478.4 | MW
iv) Mymensingh area |  |  | 1002 |  | MW | iv) Rangpur area |  |  |  | 900 | MW
v) Sylhet area |  |  | 594 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14572.91 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 19:00 | 133 | PHP | 9 | 13:00
2 | AKSML | 126 | 11:00 | 68 | Ishurdi | 83 | 19:00 | 134 | Pabna | 129 | 19:00
3 | Aftabnagar | 40 | 20:00 | 69 | Jaldhaka | 76 | 18:30 | 135 | Palashbari | 102 | 18:30
4 | Agargaon | 134 | 13:00 | 70 | Jamalpur | 101 | 00:00 | 136 | Panchagarh | 56 | 19:30
5 | Agrabad | 102 | 16:00 | 71 | Jashore | 148 | 18:30 | 137 | Patiya | 12 | 11:00
6 | Amnura | 29 | 20:00 | 72 | Jhenaidah | 139 | 19:00 | 138 | Patuakhali | 71.5 | 22:00
7 | Ashuganj | 91 | 00:00 | 73 | Joydebpur | 165 | 15:00 | 139 | Payra | 38 | 23:00
8 | BSRM | 150 | 22:00 | 74 | Joypurhat | 55 | 19:00 | 140 | Postogola | 66 | 13:00
9 | Bagerhat | 86 | 18:30 | 75 | Juldah | 19 | 11:00 | 141 | Purbachal | 21 | 12:00
10 | Bajitpur | 81 | 22:00 | 76 | KSRM | 23 | 16:00 | 142 | Purbasadipur | 114 | 18:30
11 | Bakulia | 95 | 19:00 | 77 | Kabirpur | 261 | 19:30 | 143 | Rahanpur | 39 | 22:00
12 | Banani | 52 | 13:00 | 78 | Kachua | 96 | 21:00 | 144 | Rahim | 30 | 13:00
13 | Bangabhaban | 24 | 10:00 | 79 | Kallyanpur | 105 | 23:00 | 145 | Rajbari | 86 | 18:30
14 | Barapukuria | 64 | 20:00 | 80 | Kalurghat | 42 | 15:00 | 146 | Rajendrapur | 130 | 19:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 81 | 16:00 | 147 | Rajshahi | 98 | 19:30
16 | Barishal | 115 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 96 | 13:00
17 | Barishal-230 | 96 | 18:30 | 83 | Kasba | 37 | 20:00 | 149 | Ramganj | 108 | 00:00
18 | Baroaulia | 72 | 13:00 | 84 | Kazla | 102 | 16:00 | 150 | Rampur | 42 | 23:00
19 | Baroirhat | 66 | 18:30 | 85 | Keranigonj | 90 | 18:30 | 151 | Rangamati | 18 | 19:30
20 | Bashundhara | 203 | 13:00 | 86 | Khagrachori | 34 | 18:30 | 152 | Rangpur | 137 | 19:00
21 | BashundharaCement | 11 | 13:00 | 87 | Khulna | 69 | 13:00 | 153 | Ruppur | 7.6 | 16:00
22 | Beanibazar | 70 | 00:00 | 88 | Khulshi | 191 | 17:00 | 154 | SSM | 10 | 00:00
23 | Benapole | 68 | 18:30 | 89 | Kishoreganj | 124 | 21:00 | 155 | Saidpur | 105 | 18:30
24 | Bhaluka | 142 | 18:00 | 90 | Kodda | 303 | 19:30 | 156 | Satkhira | 131 | 21:00
25 | Bhandaria | 54 | 23:00 | 91 | Kulaura | 47 | 18:30 | 157 | Satmasjid | 103 | 11:00
26 | Bhangura | 39 | 19:00 | 92 | Kurigram | 60 | 19:00 | 158 | Savar | 229 | 18:30
27 | Bheramara(GK) | 71 | 20:00 | 93 | Kushtia | 166 | 19:30 | 159 | SevenRings | 2.65 | 15:00
28 | Bhulta | 217 | 10:00 | 94 | Laksam | 35 | 22:00 | 160 | ShahCement | 28 | 21:00
29 | Bog-Sherpur | 68 | 18:30 | 95 | Lakshmipur | 35 | 21:00 | 161 | Shahjadpur | 87 | 19:30
30 | Bogura | 169 | 19:30 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 125 | 19:30
31 | Borhanuddin | 94 | 20:00 | 97 | Lalmonirhat | 58 | 19:30 | 163 | Shahmirpur | 59 | 00:00
32 | Brahmanbaria | 134 | 19:00 | 98 | MI_Cement | 16 | 16:00 | 164 | Shariatpur | 91 | 22:00
33 | Cantonment | 144 | 13:00 | 99 | Madanganj | 30 | 00:00 | 165 | Sherpur | 102 | 00:00
34 | Chandina | 19.21 | 11:00 | 100 | Madaripur | 117 | 23:00 | 166 | Shikalbaha | 17 | 22:00
35 | Chandpur | 86 | 21:00 | 101 | Madartek | 92 | 20:00 | 167 | Shitalakhya | 83.6 | 16:00
36 | Chandraghona | 38 | 18:30 | 102 | Madunaghat | 59 | 18:30 | 168 | Sholosohor | 48 | 18:30
37 | Chapai | 70 | 21:00 | 103 | Magura | 70 | 19:00 | 169 | Shyampur | 154 | 10:00
38 | Charsaidpur | 36 | 02:00 | 104 | Mahasthangarh | 70 | 20:00 | 170 | Siddhirganj | 124 | 15:00
39 | Chauddagram | 71 | 22:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sirajganj | 102 | 18:30
40 | Chhatak | 36 | 22:00 | 106 | Manikganj | 130 | 18:30 | 172 | Sonargaon | 124 | 00:00
41 | Chowmuhani | 176 | 00:00 | 107 | Maniknagar | 64 | 13:00 | 173 | Sreemongol | 80 | 21:00
42 | Chuadanga | 124 | 19:00 | 108 | Matarbari | 54 | 22:00 | 174 | Sreepur | 105 | 12:00
43 | Coxsbazar | 143 | 18:30 | 109 | Matuail | 76 | 15:00 | 175 | Srinagar | 48.33 | 21:00
44 | Cumilla(N) | 141 | 23:00 | 110 | Millgate | 127 | 12:00 | 176 | Sunamganj | 58 | 00:00
45 | Cumilla(S) | 151 | 18:00 | 111 | Mirpur | 126 | 13:00 | 177 | Sylhet | 46 | 00:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Mirsorai | 11 | 18:30 | 178 | Sylhet-132 | 114 | 19:00
47 | Daudkandi | 151 | 19:30 | 113 | Mirzapur | 36 | 12:00 | 179 | TK | 31 | 00:00
48 | DhakaUniversity | 102 | 13:00 | 114 | Mithapukur | 62 | 18:30 | 180 | Tangail | 156 | 16:00
49 | Dhamrai | 124 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 19 | 19:00
50 | Dhanmondi | 141 | 13:00 | 116 | Mogbazar | 104 | 14:00 | 182 | Thakurgaon | 104 | 19:00
51 | Dohazari | 112 | 19:00 | 117 | Mongla | 38 | 15:00 | 183 | Tongi | 141 | 12:00
52 | Faridpur | 171 | 18:30 | 118 | Motijheel | 46 | 13:00 | 184 | Ullahpara | 38 | 18:30
53 | Fatullah | 116 | 10:00 | 119 | Muktagacha | 31 | 20:00 | 185 | Ullon | 53 | 21:00
54 | Fenchuganj | 38 | 00:00 | 120 | Munshiganj | 117 | 22:00 | 186 | Uttara | 83 | 13:00
55 | Feni | 128 | 20:00 | 121 | Muradnagar | 43 | 21:00 | 187 | UttaraNew | 59 | 23:00
56 | GPH | 2 | 00:00 | 122 | Mymensingh | 181 | 21:00 | 188 | Zigatola | 74 | 14:00
57 | Ghatail | 68 | 07:00 | 123 | Naogaon | 119 | 19:00
58 | Ghorashal | 20 | 11:00 | 124 | Narail | 61 | 22:00
59 | Ghorashal-230 | 95 | 22:00 | 125 | Narinda | 72 | 13:00
60 | Goalpara | 39 | 13:00 | 126 | Narshingdi | 180 | 22:00
61 | Gollamari | 102 | 19:00 | 127 | Natore | 145 | 19:00
62 | Gopalganj | 111 | 19:00 | 128 | Nawabganj | 49.4 | 22:00
63 | Gulshan | 124 | 12:00 | 129 | Netrakona | 131 | 20:00
64 | Halishahar | 75 | 15:00 | 130 | New | 50 | 12:00
65 | HaripurSBU | 155 | 09:00 | 131 | Niamatpur | 71 | 21:00
66 | Hasnabad | 96 | 20:00 | 132 | Noapara | 48 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14062.6 | 22 |  | 14085.59
1:00 | 13592.71 | 0 |  | 13592.71
2:00 | 13226.54 | 0 |  | 13226.54
3:00 | 12836.41 | 0 |  | 12836.41
4:00 | 12508.3 | 0 |  | 12508.3
5:00 | 12490.56 | 0 |  | 12490.56
6:00 | 12122.01 | 0 |  | 12122.01
7:00 | 12079.23 | 0 |  | 12079.23
8:00 | 12271.45 | 0 |  | 12271.45
9:00 | 12612.86 | 0 |  | 12612.86
10:00 | 12815.42 | 0 |  | 12815.42
11:00 | 13064.77 | 0 |  | 13064.77
12:00 | 13505.01 | 0 |  | 13505.01
13:00 | 13884.1 | 0 |  | 13884.1
14:00 | 13811.08 | 0 |  | 13811.08
15:00 | 13892.63 | 25 |  | 13918.76
16:00 | 13587.95 | 0 |  | 13587.95
17:00 | 13379.02 | 0 |  | 13379.02
18:00 | 12918.1 | 0 |  | 12918.1
19:00 | 14697.4 | 194 |  | 14900.4
19:30 | 15132 | 175 |  | 15315
20:00 | 15244.7 | 149 |  | 15400.7
21:00 | 14972.27 | 138 |  | 15116.27
22:00 | 14673.35 | 122 |  | 14800.84
23:00 | 14464.38 | 112 |  | 14581.42
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7153.6 | 6909 | 14062.6 | DAILY GENERATION CURVE
00:30 | 7035.3 | 6792.355 | 13827.655
01:00 | 6917 | 6675.71 | 13592.71 | 18-09-2025
01:30 | 6807 | 6602.625 | 13409.625
02:00 | 6697 | 6529.54 | 13226.54
02:30 | 6642.5 | 6388.975 | 13031.475
03:00 | 6588 | 6248.41 | 12836.41
03:30 | 6562 | 6110.355 | 12672.355
04:00 | 6536 | 5972.3 | 12508.3
04:30 | 6547.5 | 5951.93 | 12499.43
05:00 | 6559 | 5931.56 | 12490.56
05:30 | 6295.04 | 6011.245 | 12306.285
06:00 | 6031.08 | 6090.93 | 12122.01
06:30 | 6051.645 | 6048.975 | 12100.62
07:00 | 6072.21 | 6007.02 | 12079.23
07:30 | 6160.415 | 6014.925 | 12175.34
08:00 | 6248.62 | 6022.83 | 12271.45
08:30 | 6355.115 | 6087.04 | 12442.155
09:00 | 6461.61 | 6151.25 | 12612.86
09:30 | 6537.88 | 6176.26 | 12714.14
10:00 | 6614.15 | 6201.27 | 12815.42
10:30 | 6689.065 | 6251.03 | 12940.095
11:00 | 6763.98 | 6300.79 | 13064.77
11:30 | 6918.59 | 6366.3 | 13284.89
12:00 | 7073.2 | 6431.81 | 13505.01
12:30 | 7137.95 | 6556.605 | 13694.555
13:00 | 7202.7 | 6681.4 | 13884.1
13:30 | 7122.64 | 6724.95 | 13847.59
14:00 | 7042.58 | 6768.5 | 13811.08
14:30 | 7145.345 | 6706.51 | 13851.855
15:00 | 7248.11 | 6644.52 | 13892.63
15:30 | 7263.46 | 6476.83 | 13740.29
16:00 | 7278.81 | 6309.14 | 13587.95
16:30 | 7228.755 | 6254.73 | 13483.485
17:00 | 7178.7 | 6200.32 | 13379.02
17:30 | 6953.9 | 6194.66 | 13148.56
18:00 | 6729.1 | 6189 | 12918.1
18:30 | 7120.25 | 6687.5 | 13807.75
19:00 | 7511.4 | 7186 | 14697.4
19:30 | 7837 | 7295 | 15132
20:00 | 8000.7 | 7244 | 15244.7
20:30 | 7937.35 | 7171.135 | 15108.485 |  | Executive Engineer
21:00 | 7874 | 7098.27 | 14972.27 |  | Network Operation Division
21:30 | 7756.25 | 7066.56 | 14822.81
22:00 | 7638.5 | 7034.85 | 14673.35
22:30 | 7536.35 | 7032.515 | 14568.865
23:00 | 7434.2 | 7030.18 | 14464.38

## En-Curve
QF-LDC-12
Date | 18-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3652 | 1958 | 882 | 38 | 48 | 1448 | 220 | 4503 | 0 | 399 | 914.6 | 0 | 0 | 0 | 22 | DAILY ENERGY CURVE
00:30 | 3655 | 1964.5 | 882 | 38 | 47 | 1378.855 | 219.5 | 4500.5 | 0 | 345 | 797.3 | 0 | 0 | 0 | 11 | 18-09-2025
01:00 | 3658 | 1971 | 882 | 38 | 46 | 1309.71 | 219 | 4498 | 0 | 291 | 680 | 0 | 0 | 0 | 0
01:30 | 3642 | 1957 | 882 | 38 | 45 | 1262.125 | 219 | 4455.5 | 0 | 265 | 644 | 0 | 0 | 0 | 0 | Energy Generated | 327.9668 |  | MKWHr
02:00 | 3626 | 1943 | 882 | 38 | 44 | 1214.54 | 219 | 4413 | 0 | 239 | 608 | 0 | 0 | 0 | 0 | Energy not Served | 0.762 |  | MKWHr
02:30 | 3648 | 1944 | 882 | 38 | 44 | 1162.475 | 219.5 | 4309 | 0 | 231.5 | 553 | 0 | 0 | 0 | 0 | Total Energy Requirement | 328.7288 |  | MKWHr
03:00 | 3670 | 1945 | 882 | 38 | 44 | 1110.41 | 220 | 4205 | 0 | 224 | 498 | 0 | 0 | 0 | 0
03:30 | 3680 | 1969.5 | 882 | 38 | 43 | 1077.355 | 220 | 4093 | 0 | 220 | 449.5 | 0 | 0 | 0 | 0
04:00 | 3690 | 1994 | 882 | 38 | 42 | 1044.3 | 220 | 3981 | 0 | 216 | 401 | 0 | 0 | 0 | 0
04:30 | 3707 | 2000.5 | 881.5 | 38 | 42 | 1028.43 | 220 | 3972 | 0 | 216 | 394 | 0 | 0 | 0 | 0
05:00 | 3724 | 2007 | 881 | 38 | 42 | 1012.56 | 220 | 3963 | 0 | 216 | 387 | 0 | 0 | 0 | 0
05:30 | 3541.5 | 1977 | 881.5 | 38 | 41 | 1010.15 | 220 | 3964 | 2.635 | 186 | 371 | 73.5 | 0 | 0 | 0
06:00 | 3359 | 1947 | 882 | 38 | 40 | 1007.74 | 220 | 3965 | 5.27 | 156 | 355 | 147 | 0 | 0 | 0
06:30 | 3367 | 1973.5 | 882 | 38 | 39 | 959.585 | 220 | 3894.5 | 37.035 | 165 | 363.5 | 161.5 | 0 | 0 | 0
07:00 | 3375 | 2000 | 882 | 38 | 38 | 911.43 | 220 | 3824 | 68.8 | 174 | 372 | 176 | 0 | 0 | 0
07:30 | 3393.5 | 2062.5 | 881.5 | 38 | 37 | 910.915 | 221 | 3801 | 111.425 | 165 | 377 | 176.5 | 0 | 0 | 0
08:00 | 3412 | 2125 | 881 | 38 | 36 | 910.4 | 222 | 3778 | 154.05 | 156 | 382 | 177 | 0 | 0 | 0
08:30 | 3423 | 2110 | 881.5 | 38 | 34 | 909.98 | 222 | 3856 | 203.425 | 164 | 423.75 | 176.5 | 0 | 0 | 0
09:00 | 3434 | 2095 | 882 | 38 | 32 | 909.56 | 222 | 3934 | 252.8 | 172 | 465.5 | 176 | 0 | 0 | 0
09:30 | 3438 | 2071 | 881.5 | 38 | 34 | 908.445 | 222 | 3983.5 | 295.745 | 172.5 | 497.95 | 171.5 | 0 | 0 | 0
10:00 | 3442 | 2047 | 881 | 38 | 36 | 907.33 | 222 | 4033 | 338.69 | 173 | 530.4 | 167 | 0 | 0 | 0
10:30 | 3436 | 2068 | 881 | 38 | 36 | 914.685 | 222 | 4058 | 365.51 | 183.5 | 566.9 | 170.5 | 0 | 0 | 0
11:00 | 3430 | 2089 | 881 | 38 | 36 | 922.04 | 222 | 4083 | 392.33 | 194 | 603.4 | 174 | 0 | 0 | 0
11:30 | 3428 | 2116 | 881 | 38 | 39 | 921.73 | 212 | 4203.5 | 370.56 | 193.5 | 708.6 | 173 | 0 | 0 | 0
12:00 | 3426 | 2143 | 881 | 38 | 42 | 921.42 | 202 | 4324 | 348.79 | 193 | 813.8 | 172 | 0 | 0 | 0
12:30 | 3407 | 2133 | 881.5 | 38 | 42 | 961.82 | 211.5 | 4370 | 368.735 | 196 | 913 | 171.5 | 0 | 0.5 | 0
13:00 | 3388 | 2123 | 882 | 38 | 42 | 1002.22 | 221 | 4416 | 388.68 | 199 | 1012.2 | 171 | 0 | 1 | 0
13:30 | 3339 | 2103.5 | 881.5 | 38 | 43 | 1014.61 | 221 | 4434.5 | 400.63 | 190.5 | 1006.85 | 171.5 | 0 | 3 | 0
14:00 | 3290 | 2084 | 881 | 38 | 44 | 1027 | 221 | 4453 | 412.58 | 182 | 1001.5 | 172 | 0 | 5 | 0
14:30 | 3341 | 2108.5 | 881.5 | 38 | 45 | 1021 | 220.5 | 4472 | 360.305 | 182 | 1028.05 | 150.5 | 0 | 3.5 | 12.5
15:00 | 3392 | 2133 | 882 | 38 | 46 | 1015 | 220 | 4491 | 308.03 | 182 | 1054.6 | 129 | 0 | 2 | 25
15:30 | 3333.5 | 2139 | 882 | 38 | 44 | 988 | 220.5 | 4415.5 | 240.39 | 214.5 | 1091.9 | 129 | 0 | 4 | 12.5
16:00 | 3275 | 2145 | 882 | 38 | 42 | 961 | 221 | 4340 | 172.75 | 247 | 1129.2 | 129 | 0 | 6 | 0
16:30 | 3287.5 | 2151 | 881.5 | 38 | 36 | 957.5 | 221.5 | 4300 | 118.485 | 260.5 | 1119 | 107.5 | 0 | 5 | 0
17:00 | 3300 | 2157 | 881 | 38 | 30 | 954 | 222 | 4260 | 64.22 | 274 | 1108.8 | 86 | 0 | 4 | 0
17:30 | 3124.5 | 2016.25 | 881 | 38 | 40 | 1027 | 222 | 4252 | 32.11 | 236.5 | 1213.2 | 64 | 0 | 2 | 0
18:00 | 2949 | 1875.5 | 881 | 38 | 50 | 1100 | 222 | 4244 | 0 | 199 | 1317.6 | 42 | 0 | 0 | 0
18:30 | 3137.5 | 2015.25 | 881.5 | 38 | 48 | 1274.5 | 222 | 4407 | 0 | 259.5 | 1503.5 | 21 | 0 | 0 | 97
19:00 | 3326 | 2155 | 882 | 38 | 46 | 1449 | 222 | 4570 | 0 | 320 | 1689.4 | 0 | 0 | 0 | 194
19:30 | 3320 | 2155 | 882 | 38 | 46 | 1443 | 221 | 4578 | 0 | 546 | 1903 | 0 | 0 | 0 | 175
20:00 | 3280 | 2165 | 882 | 38 | 48 | 1440 | 222 | 4605 | 0 | 645 | 1919.7 | 0 | 0 | 0 | 149
20:30 | 3320 | 2203.75 | 882 | 38 | 47 | 1441.135 | 221.5 | 4605.5 | 0 | 610 | 1739.6 | 0 | 0 | 0 | 143.5
21:00 | 3360 | 2242.5 | 882 | 38 | 46 | 1442.27 | 221 | 4606 | 0 | 575 | 1559.5 | 0 | 0 | 0 | 138
21:30 | 3362 | 2259 | 881.5 | 38 | 47 | 1445.06 | 221 | 4615 | 0 | 549.5 | 1404.75 | 0 | 0 | 0 | 130
22:00 | 3364 | 2275.5 | 881 | 38 | 48 | 1447.85 | 221 | 4624 | 0 | 524 | 1250 | 0 | 0 | 0 | 122
22:30 | 3373.5 | 2252.15 | 881 | 38 | 50 | 1455.015 | 221 | 4629.5 | 0 | 505 | 1163.7 | 0 | 0 | 0 | 117
23:00 | 3383 | 2228.8 | 881 | 38 | 52 | 1462.18 | 221 | 4635 | 0 | 486 | 1077.4 | 0 | 0 | 0 | 112
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 05:00 | 369 | 11:00 | Payra | 412 | 06:00 | 407 | 19:30
Ashuganj | 406 | 6:00 | 380 | 12:00 | Rahanpur | 407 | 07:00 | 391 | 00:00
Bhulta | 403 | 06:00 | 374 | 11:00 | Rampal | 404 | 06:00 | 392 | 00:00
Bibiana | 387 | 06:00 | 380 | 11:00
BIPTC | 405 | 04:00 | 396 | 19:00
Bogura | 394 | 08:00 | 374 | 00:00
Gopalganj | 395 | 06:00 | 384 | 23:00
Kaliakoir | 373 | 18:00 | 360 | 11:00
Madunaghat | 391 | 06:00 | 385 | 12:00
Meghnaghat | 382 | 04:00 | 373 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 07:00 | 218 | 11:00 | Kaliakoir | 232 | 04:00 | 222 | 11:00
AKSML | 230 | 06:00 | 223 | 12:00 | Keranigonj | 223 | 04:00 | 215 | 11:00
Aminbazar | 228 | 13:00 | 219 | 11:00 | Khulna(S) | 231 | 06:00 | 218 | 18:30
Ashuganj | 233 | 06:00 | 220 | 11:00 | Madunaghat | 230 | 17:00 | 224 | 12:00
Ashuganj-400 | 233 | 06:00 | 220 | 11:00 | Madunaghat-400 | 231 | 07:00 | 226 | 12:00
Baghabari | 234 | 06:00 | 225 | 00:00 | Maniknagar | 219 | 04:00 | 210 | 11:00
Barapukuria | 223 | 07:00 | 216 | 22:00 | Meghnaghat | 227 | 03:00 | 219 | 13:00
Barapukuria-230 | 223 | 07:00 | 216 | 22:00 | Meghnaghat-400 | 223 | 04:00 | 216 | 11:00
Barishal | 227 | 06:00 | 220 | 23:00 | Mirsorai | 228 | 04:00 | 221 | 12:00
Bheramara | 235 | 05:00 | 223 | 00:00 | Rajshahi | 230 | 05:00 | 216 | 00:00
Bhulta | 232 | 03:00 | 212 | 10:00 | Rampal | 230 | 06:00 | 220 | 18:30
Bibiana | 227 | 07:00 | 221 | 16:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 08:00 | 223 | 00:00 | Rampura | 232 | 06:00 | 210 | 11:00
Bogura | 235 | 07:00 | 223 | 00:00 | Shikalbaha | 229 | 17:00 | 223 | 12:00
Bogura-400 | 235 | 06:00 | 224 | 00:00 | Shyampur | 222 | 04:00 | 214 | 11:00
Borhanuddin | 232 | 05:00 | 227 | 23:00 | Siddhirganj | 219 | 04:00 | 212 | 11:00
BSRM | 227 | 04:00 | 220 | 12:00 | Sirajgonj | 240 | 05:00 | 233 | 00:00
Cumilla(N) | 223 | 07:00 | 216 | 11:00 | Sreepur | 229 | 05:00 | 220 | 11:00
Faridpur | 224 | 05:00 | 217 | 00:00 | Tongi | 228 | 19:30 | 215 | 11:00
Fenchuganj | 230 | 07:00 | 225 | 00:00
Ghorashal | 230 | 00:00 | 225 | 15:00
Ghorashal-230 | 230 | 06:00 | 215 | 11:00
Gopalganj | 225 | 06:00 | 218 | 23:00
GPH | 229 | 07:00 | 223 | 12:00
Haripur | 220 | 04:00 | 212 | 11:00
Hasnabad | 222 | 07:00 | 215 | 12:00
Hathazari | 227 | 04:00 | 221 | 15:00
Ishurdi | 237 | 05:00 | 223 | 00:00
Jhenaidah | 232 | 05:00 | 217 | 18:30
Kachua | 219 | 06:00 | 212 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 125 | 11:00 | Lalmonirhat | 127 | 06:00 | 120 | 18:30
Agargaon | 137 | 06:00 | 129 | 11:00 | Madanganj | 128 | 18:00 | 123 | 11:00
Agrabad | 131 | 20:00 | 126 | 12:00 | Madaripur | 134 | 05:00 | 130 | 00:00
AKS | 128 | 04:00 | 124 | 12:00 | Madartek | 136 | 06:00 | 124 | 16:00
Aminbazar | 134 | 04:00 | 121 | 00:00 | Madunaghat | 133 | 17:00 | 129 | 12:00
Amnura | 137 | 07:00 | 123 | 00:00 | Magura | 135 | 06:00 | 123 | 18:30
Ashuganj | 142 | 06:00 | 137 | 00:00 | Mahasthangarh | 131 | 06:00 | 123 | 00:00
Bagerhat | 134 | 08:00 | 119 | 18:30 | Maijdee | 117 | 07:00 | 110 | 23:00
Bajitpur | 131 | 05:00 | 126 | 23:00 | Manikganj | 128 | 04:00 | 119 | 11:00
Bakulia | 131 | 05:00 | 126 | 12:00 | Maniknagar | 133 | 03:00 | 126 | 11:00
Banani | 136 | 03:00 | 122 | 11:00 | Matarbari | 119 | 17:00 | 109 | 00:00
Bangabhaban | 132 | 03:00 | 125 | 11:00 | Matuail | 128 | 05:00 | 123 | 12:00
Barapukuria | 137 | 18:00 | 128 | 01:00 | Millgate | 133 | 03:00 | 123 | 12:00
Barguna | 134 | 08:00 | 130 | 00:00 | Mirpur | 132 | 05:00 | 128 | 10:00
Barishal | 133 | 06:00 | 127 | 23:00 | Mirzapur | 130 | 19:00 | 124 | 11:00
Barishal-230 | 133 | 04:00 | 127 | 23:00 | Mithapukur | 130 | 06:00 | 123 | 01:00
Baroaulia | 131 | 07:00 | 127 | 11:00 | MI_Cement | 130 | 04:00 | 124 | 11:00
Baroirhat | 124 | 06:00 | 118 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 03:00 | 122 | 11:00 | Mogbazar | 137 | 07:00 | 125 | 11:00
BashundharaCement | 128 | 18:00 | 123 | 11:00 | Mongla | 134 | 08:00 | 121 | 18:30
Beanibazar | 128 | 06:00 | 124 | 23:00 | Motijheel | 132 | 03:00 | 125 | 11:00
Benapole | 133 | 08:00 | 120 | 18:30 | Muktagacha | 129 | 19:00 | 115 | 22:00
Bhaluka | 157 | 12:00 | 124 | 18:30 | Munshiganj | 128 | 04:00 | 123 | 12:00
Bhandaria | 129 | 08:00 | 119 | 23:00 | Muradnagar | 125 | 18:00 | 119 | 23:00
Bhangura | 134 | 06:00 | 127 | 00:00 | Mymensingh | 127 | 06:00 | 112 | 23:00
Bheramara | 137 | 08:00 | 128 | 00:00 | Naogaon | 129 | 07:00 | 119 | 00:00
Bheramara(GK) | 136 | 05:00 | 128 | 00:00 | Narail | 134 | 09:00 | 121 | 18:30
Bhulta | 122 | 05:00 | 118 | 12:00 | Narinda | 133 | 03:00 | 126 | 11:00
Bog-Sherpur | 132 | 06:00 | 124 | 00:00 | Narshingdi | 138 | 20:00 | 115 | 10:00
Bogura | 133 | 07:00 | 126 | 00:00 | Natore | 129 | 04:00 | 120 | 00:00
Bogura-230 | 133 | 07:00 | 125 | 00:00 | Nawabganj | 137 | 07:00 | 130 | 11:00
Brahmanbaria | 136 | 06:00 | 129 | 23:00 | Netrakona | 125 | 07:00 | 116 | 22:00
Cantonment | 136 | 03:00 | 129 | 11:00 | New | 134 | 05:00 | 124 | 11:00
Chandina | 128 | 18:00 | 123 | 23:00 | Niamatpur | 138 | 07:00 | 131 | 00:00
Chandpur | 128 | 18:30 | 122 | 23:00 | Noapara | 135 | 09:00 | 124 | 18:30
Chandraghona | 133 | 06:00 | 130 | 11:00 | Pabna | 135 | 08:00 | 127 | 18:30
Chapai | 137 | 11:00 | 132 | 01:00 | Palashbari | 130 | 09:00 | 120 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 04:00 | 124 | 10:00 | Panchagarh | 136 | 18:00 | 123 | 01:00
Chauddagram | 124 | 07:00 | 117 | 14:00 | Patiya | 130 | 17:00 | 124 | 12:00
Chhatak | 128 | 06:00 | 122 | 00:00 | Patuakhali | 134 | 05:00 | 131 | 00:00
Chowmuhani | 119 | 07:00 | 113 | 00:00 | Payra | 135 | 03:00 | 133 | 00:00
Chuadanga | 134 | 08:00 | 120 | 23:00 | PHP | 124 | 18:00 | 116 | 14:00
Coxsbazar | 114 | 04:00 | 109 | 18:30 | Postogola | 132 | 06:00 | 127 | 10:00
Cumilla(N) | 128 | 05:00 | 122 | 12:00 | Purbachal | 137 | 05:00 | 121 | 11:00
Cumilla(S) | 132 | 04:00 | 122 | 11:00 | Purbasadipur | 132 | 18:00 | 123 | 01:00
Daganbhuiyan | 120 | 07:00 | 113 | 14:00 | Rahanpur | 140 | 08:00 | 133 | 00:00
Daudkandi | 122 | 05:00 | 116 | 10:00 | Rahanpur-400 | 140 | 07:00 | 134 | 00:00
DhakaUniversity | 136 | 05:00 | 122 | 11:00 | Rahim | 128 | 00:00 | 124 | 10:00
Dhamrai | 132 | 05:00 | 126 | 10:00 | Rajbari | 132 | 06:00 | 125 | 23:00
Dhanmondi | 137 | 05:00 | 122.6 | 11:00 | Rajendrapur | 136 | 19:30 | 124 | 15:00
Dohazari | 127 | 18:00 | 119 | 15:00 | Rajshahi | 131 | 05:00 | 123 | 00:00
Faridpur | 133 | 06:00 | 130 | 00:00 | Rajshahi-230 | 132 | 09:00 | 123 | 00:00
Fatullah | 132 | 06:00 | 126 | 10:00 | Ramganj | 121 | 06:00 | 115 | 00:00
Fenchuganj | 136 | 07:00 | 132 | 00:00 | Rampur | 130 | 20:00 | 125 | 12:00
Feni | 122 | 07:00 | 117 | 14:00 | Rampura | 136 | 03:00 | 121 | 11:00
Ghatail | 135 | 18:30 | 116 | 23:00 | Rangamati | 132 | 04:00 | 129 | 11:00
Ghorashal | 137 | 20:00 | 131 | 14:00 | Rangpur | 130 | 09:00 | 125 | 22:00
Goalpara | 138 | 06:00 | 124 | 22:00 | Ruppur | 137 | 06:00 | 130 | 18:30
Gollamari | 138 | 09:00 | 128 | 18:30 | Saidpur | 131 | 18:00 | 123 | 01:00
Gopalganj | 135 | 09:00 | 126 | 23:00 | Satkhira | 135 | 09:00 | 120 | 23:00
Gopalganj-400 | 135 | 04:00 | 130 | 23:00 | Satmasjid | 136 | 05:00 | 129 | 11:00
Gulshan | 136 | 05:00 | 123 | 11:00 | Savar | 133 | 17:00 | 128 | 08:00
Halishahar | 131 | 18:00 | 126 | 12:00 | SevenRings | 137 | 03:00 | 130 | 11:00
Haripur | 129 | 04:00 | 125 | 11:00 | ShahCement | 129 | 04:00 | 124 | 10:00
HaripurSBU | 129 | 04:00 | 124 | 11:00 | Shahjadpur | 135 | 04:00 | 131 | 00:00
Hasnabad | 132 | 07:00 | 126 | 11:00 | Shahjibazar | 136 | 06:00 | 129 | 23:00
Hathazari | 132 | 02:00 | 129 | 13:00 | Shahmirpur | 131 | 07:00 | 126 | 11:00
Ishurdi | 138 | 05:00 | 131 | 00:00 | Shariatpur | 133 | 06:00 | 127 | 22:00
Jaldhaka | 130 | 05:00 | 122 | 01:00 | Sherpur | 132 | 19:00 | 110 | 23:00
Jamalpur | 131 | 19:00 | 115 | 23:00 | Shikalbaha | 121 | 07:00 | 116 | 12:00
Jashore | 136 | 09:00 | 122 | 18:30 | Shikalbaha-230 | 133 | 17:00 | 126 | 14:00
Jhenaidah | 137 | 06:00 | 116 | 18:30 | Shitalakhya | 130 | 04:00 | 124 | 11:00
Jhenaidah-230 | 138 | 09:00 | 126 | 18:30 | Sholosohor | 133 | 20:00 | 129 | 12:00
Joydebpur | 140 | 13:00 | 129 | 11:00 | Shyampur | 132 | 06:00 | 127 | 10:00
Joypurhat | 128 | 07:00 | 117 | 00:00 | Shyampur-230 | 131 | 03:00 | 127 | 10:00
Juldah | 131 | 19:30 | 126 | 12:00 | Siddhirganj | 129 | 05:00 | 124 | 11:00
Kabirpur | 132 | 00:00 | 120 | 11:00 | Sirajganj | 132 | 07:00 | 125 | 00:00
Kachua | 130 | 06:00 | 124 | 23:00 | Sonargaon | 127 | 05:00 | 121 | 11:00
Kaliakoir | 134 | 07:00 | 128 | 11:00 | Sreemongol | 134 | 07:00 | 128 | 00:00
Kallyanpur | 133 | 01:00 | 129 | 11:00 | Sreepur | 134 | 06:00 | 127 | 18:30
Kalurghat | 133 | 17:00 | 129 | 12:00 | Srinagar | 138 | 06:00 | 131 | 12:00
Kamrangirchar | 138 | 06:00 | 130 | 11:00 | SSM | 134 | 07:00 | 130 | 14:00
Kaptai | 133 | 6:00 | 124 | 13:00 | Sunamganj | 125 | 07:00 | 120 | 22:00
Kasba | 124 | 08:00 | 118 | 23:00 | Sylhet | 130 | 07:00 | 126 | 00:00
Kazla | 133 | 05:00 | 125 | 12:00 | Sylhet-132 | 129 | 08:00 | 127 | 00:00
Keranigonj | 138 | 05:00 | 131 | 11:00 | Tangail | 134 | 18:30 | 118 | 23:00
Khagrachori | 132 | 07:00 | 128 | 12:00 | Taraganj | 130 | 09:00 | 120 | 11:00
Khulna | 137 | 09:00 | 127 | 00:00 | Thakurgaon | 135 | 18:00 | 122 | 01:00
Khulna(S) | 138 | 06:00 | 128 | 18:30 | TK | 132 | 04:00 | 129 | 12:00
Khulshi | 129 | 06:00 | 124 | 13:00 | Tongi | 134 | 19:30 | 126 | 12:00
Kishoreganj | 130 | 07:00 | 123 | 23:00 | Ullahpara | 134 | 07:00 | 127 | 00:00
Kodda | 136 | 21:00 | 124 | 11:00 | Ullon | 136 | 05:00 | 123 | 11:00
KSRM | 132 | 04:00 | 126 | 12:00 | Uttara | 132 | 04:00 | 127 | 23:00
Kulaura | 134 | 05:00 | 131 | 00:00 | UttaraNew | 132 | 02:00 | 127 | 11:00
Kurigram | 129 | 05:00 | 119 | 22:00 | Zigatola | 138 | 06:00 | 131 | 11:00
Kushtia | 134 | 09:00 | 121 | 18:30
Laksam | 128 | 07:00 | 123 | 23:00
Lakshmipur | 116 | 07:00 | 107 | 23:00
Lalbag | 137 | 06:00 | 131 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division