## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15421.79 | 105 |  | 15531.52
1:00 | 15043.41 | 89 |  | 15136.42
2:00 | 14541.63 | 72 |  | 14616.87
3:00 | 14022.44 | 61 |  | 14086.19
4:00 | 13860.44 | 53 |  | 13915.83
5:00 | 13545.95 | 49 |  | 13597.16
6:00 | 13085.19 | 42 |  | 13129.08
7:00 | 13036.59 | 39 |  | 13077.35
8:00 | 13153.57 | 26 |  | 13180.74
9:00 | 13284.28 | 0 |  | 13284.28
10:00 | 13376.02 | 0 |  | 13376.02
11:00 | 13627.05 | 0 |  | 13627.05
12:00 | 13916.94 | 0 |  | 13916.94
13:00 | 14404.22 | 0 |  | 14404.22
14:00 | 14119.12 | 132 |  | 14257.12
15:00 | 14399.27 | 129 |  | 14534.27
16:00 | 14138.33 | 0 |  | 14138.33
17:00 | 14002.55 | 0 |  | 14002.55
18:00 | 14662.24 | 37 |  | 14701.24
19:00 | 16057.01 | 138 |  | 16201.01
19:30 | 16133.4 | 141 |  | 16280.4
20:00 | 15919.12 | 126 |  | 16051.12
21:00 | 15792.3 | 133 |  | 15931.3
22:00 | 15774.8 | 120 |  | 15899.8
23:00 | 15748.3 | 117 |  | 15870.3
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 21-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3429 | 2269.8 | 901 | 38 | 52 | 1447.99 | 221 | 4520 | 0 | 645 | 1890 | 0 | 0 | 8 | 105 | DAILY ENERGY CURVE
00:30 | 3442.5 | 2263.8 | 899 | 38 | 52 | 1450.7 | 220 | 4464 | 0 | 603.5 | 1795.1 | 0 | 0 | 4 | 97 | 21-09-2025
01:00 | 3456 | 2257.8 | 897 | 38 | 52 | 1453.41 | 219 | 4408 | 0 | 562 | 1700.2 | 0 | 0 | 0 | 89
01:30 | 3522.5 | 2254.8 | 899 | 38 | 51 | 1455.52 | 219 | 4322 | 0 | 520 | 1510.7 | 0 | 0 | 0 | 80.5 | Energy Generated | 348.4355 |  | MKWHr
02:00 | 3589 | 2251.8 | 901 | 38 | 50 | 1457.63 | 219 | 4236 | 0 | 478 | 1321.2 | 0 | 0 | 0 | 72 | Energy not Served | 1.468 |  | MKWHr
02:30 | 3635.5 | 2241.3 | 901 | 38 | 49 | 1382.435 | 219 | 4170.5 | 0 | 477 | 1168.3 | 0 | 0 | 0 | 66.5 | Total Energy Requirement | 349.9035 |  | MKWHr
03:00 | 3682 | 2230.8 | 901 | 38 | 48 | 1307.24 | 219 | 4105 | 0 | 476 | 1015.4 | 0 | 0 | 0 | 61
03:30 | 3675.5 | 2230.8 | 901 | 38 | 48 | 1309.24 | 219 | 4099 | 0 | 457 | 963.9 | 0 | 0 | 0 | 57
04:00 | 3669 | 2230.8 | 901 | 38 | 48 | 1311.24 | 219 | 4093 | 0 | 438 | 912.4 | 0 | 0 | 0 | 53
04:30 | 3631.5 | 2245.3 | 900.5 | 38 | 48 | 1311.495 | 219 | 4092 | 0 | 429.5 | 787.9 | 0 | 0 | 0 | 51
05:00 | 3594 | 2259.8 | 900 | 38 | 48 | 1311.75 | 219 | 4091 | 0 | 421 | 663.4 | 0 | 0 | 0 | 49
05:30 | 3570.5 | 2205.3 | 900 | 38 | 46 | 1283.345 | 219.5 | 4042 | 2.725 | 407 | 587.2 | 0 | 0 | 14 | 45.5
06:00 | 3547 | 2150.8 | 900 | 38 | 44 | 1254.94 | 220 | 3993 | 5.45 | 393 | 511 | 0 | 0 | 28 | 42
06:30 | 3582 | 2190.65 | 901 | 38 | 43 | 1186.03 | 220.5 | 4008 | 49.71 | 360 | 467.5 | 0 | 0 | 14.5 | 40.5
07:00 | 3617 | 2230.5 | 902 | 38 | 42 | 1117.12 | 221 | 4023 | 93.97 | 327 | 424 | 0 | 0 | 1 | 39
07:30 | 3586.5 | 2281.5 | 904.5 | 38 | 41 | 1109.06 | 220.5 | 4017 | 173.52 | 318 | 404.5 | 0 | 0 | 1 | 32.5
08:00 | 3556 | 2332.5 | 907 | 38 | 40 | 1101 | 220 | 4011 | 253.07 | 309 | 385 | 0 | 0 | 1 | 26
08:30 | 3570 | 2341 | 907 | 38 | 39 | 1074.5 | 220.5 | 4012.5 | 338.525 | 290.4 | 387 | 0 | 0 | 0.5 | 13
09:00 | 3584 | 2349.5 | 907 | 38 | 38 | 1048 | 221 | 4014 | 423.98 | 271.8 | 389 | 0 | 0 | 0 | 0
09:30 | 3591.5 | 2320 | 907 | 38 | 39 | 978.5 | 221 | 4067.5 | 490.25 | 272.4 | 405 | 0 | 0 | 0 | 0
10:00 | 3599 | 2290.5 | 907 | 38 | 40 | 909 | 221 | 4121 | 556.52 | 273 | 421 | 0 | 0 | 0 | 0
10:30 | 3586.5 | 2273.5 | 907 | 38 | 42 | 909.5 | 221 | 4170.5 | 606.035 | 273 | 474.5 | 0 | 0 | 0 | 0
11:00 | 3574 | 2256.5 | 907 | 38 | 44 | 910 | 221 | 4220 | 655.55 | 273 | 528 | 0 | 0 | 0 | 0
11:30 | 3595.5 | 2257.5 | 912.5 | 38 | 45 | 913 | 220.5 | 4238.5 | 646.995 | 273.5 | 631 | 0 | 0 | 0 | 0
12:00 | 3617 | 2258.5 | 918 | 38 | 46 | 916 | 220 | 4257 | 638.44 | 274 | 734 | 0 | 0 | 0 | 0
12:30 | 3672.5 | 2259 | 918 | 38 | 46 | 911.5 | 220.5 | 4210.5 | 604.08 | 329.5 | 951 | 0 | 0 | 0 | 0
13:00 | 3728 | 2259.5 | 918 | 38 | 46 | 907 | 221 | 4164 | 569.72 | 385 | 1168 | 0 | 0 | 0 | 0
13:30 | 3550 | 2252 | 918.5 | 38 | 48 | 961.815 | 220.5 | 4145.5 | 531.905 | 377.5 | 1217.95 | 0 | 0 | 0 | 66
14:00 | 3372 | 2244.5 | 919 | 38 | 50 | 1016.63 | 220 | 4127 | 494.09 | 370 | 1267.9 | 0 | 0 | 0 | 132
14:30 | 3372.5 | 2314.25 | 918.5 | 38 | 43 | 1018.665 | 220 | 4146.5 | 423.98 | 385 | 1378.8 | 0 | 0 | 0 | 130.5
15:00 | 3373 | 2384 | 918 | 38 | 36 | 1020.7 | 220 | 4166 | 353.87 | 400 | 1489.7 | 0 | 0 | 0 | 129
15:30 | 3325 | 2427 | 917.5 | 38 | 39 | 1013.795 | 220 | 4078.5 | 281.205 | 412 | 1516.8 | 0 | 0 | 0 | 64.5
16:00 | 3277 | 2470 | 917 | 38 | 42 | 1006.89 | 220 | 3991 | 208.54 | 424 | 1543.9 | 0 | 0 | 0 | 0
16:30 | 3282 | 2456.75 | 917.5 | 38 | 40 | 1004.24 | 219.5 | 3986.5 | 142 | 427.5 | 1556.45 | 0 | 0 | 0 | 0
17:00 | 3287 | 2443.5 | 918 | 38 | 38 | 1001.59 | 219 | 3982 | 75.46 | 431 | 1569 | 0 | 0 | 0 | 0
17:30 | 3339.5 | 2402.85 | 918 | 38 | 41 | 1113.215 | 219.5 | 4046 | 37.73 | 473.5 | 1703.1 | 0 | 0 | 0 | 18.5
18:00 | 3392 | 2362.2 | 918 | 38 | 44 | 1224.84 | 220 | 4110 | 0 | 516 | 1837.2 | 0 | 0 | 0 | 37
18:30 | 3529.5 | 2317.9 | 904.5 | 38 | 46 | 1335.375 | 220.5 | 4321.5 | 0 | 587 | 2047.85 | 0 | 0 | 11.5 | 87.5
19:00 | 3667 | 2273.6 | 891 | 38 | 48 | 1445.91 | 221 | 4533 | 0 | 658 | 2258.5 | 0 | 0 | 23 | 138
19:30 | 3597 | 2275.2 | 892 | 38 | 48 | 1441.5 | 221 | 4584 | 0 | 678 | 2343.7 | 0 | 0 | 15 | 141
20:00 | 3521 | 2267 | 891 | 38 | 48 | 1450.32 | 221 | 4553 | 0 | 681 | 2224.8 | 0 | 0 | 24 | 126
20:30 | 3531.5 | 2263.9 | 891 | 38 | 47 | 1448.66 | 221 | 4567.5 | 0 | 677.5 | 2154.15 | 0 | 0 | 15.5 | 129.5
21:00 | 3542 | 2260.8 | 891 | 38 | 46 | 1447 | 221 | 4582 | 0 | 674 | 2083.5 | 0 | 0 | 7 | 133
21:30 | 3546.5 | 2276.8 | 891 | 38 | 46 | 1445 | 221 | 4600.5 | 0 | 674.5 | 2033.75 | 0 | 0 | 10.5 | 126.5
22:00 | 3551 | 2292.8 | 891 | 38 | 46 | 1443 | 221 | 4619 | 0 | 675 | 1984 | 0 | 0 | 14 | 120
22:30 | 3512.5 | 2296.8 | 891.5 | 38 | 48 | 1444 | 221.5 | 4637.5 | 0 | 670 | 1989.25 | 0 | 0 | 12.5 | 118.5
23:00 | 3474 | 2300.8 | 892 | 38 | 50 | 1445 | 222 | 4656 | 0 | 665 | 1994.5 | 0 | 0 | 11 | 117
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8229.8 | 7191.99 | 15421.79 | DAILY GENERATION CURVE
00:30 | 8090.9 | 7141.7 | 15232.6
01:00 | 7952 | 7091.41 | 15043.41 | 21-09-2025
01:30 | 7762 | 7030.52 | 14792.52
02:00 | 7572 | 6969.63 | 14541.63
02:30 | 7400.6 | 6881.435 | 14282.035
03:00 | 7229.2 | 6793.24 | 14022.44
03:30 | 7144.2 | 6797.24 | 13941.44
04:00 | 7059.2 | 6801.24 | 13860.44
04:30 | 6969.7 | 6733.495 | 13703.195
05:00 | 6880.2 | 6665.75 | 13545.95
05:30 | 6782.365 | 6533.205 | 13315.57
06:00 | 6684.53 | 6400.66 | 13085.19
06:30 | 6670.125 | 6390.765 | 13060.89
07:00 | 6655.72 | 6380.87 | 13036.59
07:30 | 6670.975 | 6424.105 | 13095.08
08:00 | 6686.23 | 6467.34 | 13153.57
08:30 | 6701.235 | 6517.69 | 13218.925
09:00 | 6716.24 | 6568.04 | 13284.28
09:30 | 6738.525 | 6591.625 | 13330.15
10:00 | 6760.81 | 6615.21 | 13376.02
10:30 | 6815.28 | 6686.255 | 13501.535
11:00 | 6869.75 | 6757.3 | 13627.05
11:30 | 6967.78 | 6804.215 | 13771.995
12:00 | 7065.81 | 6851.13 | 13916.94
12:30 | 7307.21 | 6853.37 | 14160.58
13:00 | 7548.61 | 6855.61 | 14404.22
13:30 | 7382.555 | 6879.115 | 14261.67
14:00 | 7216.5 | 6902.62 | 14119.12
14:30 | 7397.835 | 6861.36 | 14259.195
15:00 | 7579.17 | 6820.1 | 14399.27
15:30 | 7689.405 | 6579.395 | 14268.8
16:00 | 7799.64 | 6338.69 | 14138.33
16:30 | 7858.99 | 6211.45 | 14070.44
17:00 | 7918.34 | 6084.21 | 14002.55
17:30 | 8021.37 | 6311.025 | 14332.395
18:00 | 8124.4 | 6537.84 | 14662.24
18:30 | 8256.25 | 7103.375 | 15359.625
19:00 | 8388.1 | 7668.91 | 16057.01
19:30 | 8347.9 | 7785.5 | 16133.4
20:00 | 8262.8 | 7656.32 | 15919.12
20:30 | 8196.05 | 7659.66 | 15855.71 |  | Executive Engineer
21:00 | 8129.3 | 7663 | 15792.3 |  | Network Operation Division
21:30 | 8139.05 | 7644.5 | 15783.55
22:00 | 8148.8 | 7626 | 15774.8
22:30 | 8170.55 | 7591 | 15761.55
23:00 | 8192.3 | 7556 | 15748.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13916.94 | MW | 12:00 Hr. | Energy Generated |  |  | 348.4355 |  | MKWHr.
| Day Peak Demand |  |  | 13916.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.468 |  | MKWHr.
| Evening Peak Generation |  |  | 16133.4 | MW | 19:30 Hr. | Energy Demand |  |  | 349.9035 |  | MKWHr.
| Evening Peak Demand |  |  | 16280.4 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.7 |  | °C
| Minimum Generation of the Day |  |  | 13036.59 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1030.19 |  | MMCFD
| Maximum Generation of the Day |  |  | 16133.4 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.5538 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.3619 | 0 | 18.4115 | 0 | 0 | 0.19142 | 0 | 0 | 57.9648 | Gas | 141.1603 | Gas | 510411524.8606
| Chattogram Zone |  |  | 5.5521 | 32.5455 | 7.7757 | 0 | 5.3187 | 0.085501 | 0 | 0.1008 | 51.3783 | Coal | 102.5409 | Coal | 614083327.8237
| Cumilla Zone |  |  | 29.5563 | 0 | 8.3644 | 0 | 0 | 0.18149 | 1.0656 | 0 | 39.1678 | HFO | 42.0706 | HFO | 781020527.372
| Mymensingh Zone |  |  | 1.8202 | 0 | 2.5146 | 0 | 0 | 0.31286 | 0 | 0 | 4.6476 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8108 | Hydro | 5.3187 | Hydro | 531874.7
| Khulna Zone |  |  | 7.3639 | 26.8 | 0 | 0 | 0 | 0.52056 | 22.808 | 0 | 57.4924 | Solar | 4.3504 | Solar | 66397274.124
| Barishal Zone |  |  | 8.1624 | 38.4408 | 0.1212 | 0 | 0 | 0.003612 | 0 | 0 | 46.728 | Import | 52.8937 | Import | 309646190.44
| Rajshahi Zone |  |  | 21.5328 | 0 | 2.2582 | 0 | 0 | 1.4805 | 29.0201 | 0 | 54.2916 | Wind | 0.1008 | Wind | 1485792
| Rangpur Zone |  |  | 0 | 4.7546 | 2.625 | 0 | 0 | 1.5745 | 0 | 0 | 8.9542
| Total |  |  | 141.1603 | 102.5409 | 42.0706 | 0 | 5.3187 | 4.3504 | 52.8937 | 0.1008 | 348.4355
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 510411524.8606 |  | Hydro | 531874.7
|  |  |  | Coal | 614083327.8237 |  | Solar | 66397274.124
|  |  |  | HFO | 781020527.372 |  | Import | 309646190.44
|  |  |  | HSD | 0 |  | Wind | 1485792
[5 empty] | Total: | 228,35,76,511 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.896 | Peak Hr Flow | 892.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 62341855.38 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.0201 | Peak Hr Flow | 1441.50 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2412 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0656 | Peak Hr Flow | 48.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2908 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.9817 | Peak Hr Flow | 2381.50 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5580
|  |  |  | Chattogram |  | 0 |  | 1464
|  |  |  | Cumilla |  | 0 |  | 1421
|  |  |  | Mymensingh |  | 141 |  | 1237
|  |  |  | Sylhet |  | 0 |  | 722
|  |  |  | Khulna |  | 0 |  | 1935
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1590
|  |  |  | Rangpur |  | 0 |  | 1071
|  |  |  | Total |  | 141 |  | 15498
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:05 | 20:51 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Partial
Discharge Testing
| 09:06 | 20:51 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Partial
Discharge Testing
| 09:34 | 21:39 | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to Connection loop extension
between 33 KV CT and CB.
| 09:35 | 21:39 | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to Connection loop extension
between 33 KV CT and CB.
| 10:24 |  | T2 33 KV CB open in Satiya 132/33 KV S/S.
| 10:45 | 15:48 | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to LILO wok at
bonpara and from Natore 132/33kV end Due to Jumper wire connection
| 10:45 | 15:50 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end. and from Natore
132/33kV end Due to Jumper wire connection
| 10:56 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 11:00 | 11:24 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing df/dt relays. | [7 empty] | 38.0MW load
interrup.
| 11:00 | 11:12 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing df/dt relays. | [7 empty] | 53.0MW load
interrup.
| 11:13 | 16:21 | New Tongi S/S Tr-1 (4061-3) Scheduled S/D Due to DESCO SAS System Testing and Operation
| 12:00 |  | At Rooppur 400kV Substation, the bus coupler between Bus-1 and Bus-2 was switched on for
the first time at 12:00 hrs today. A load flow of around 28 MW is occurring from
Gopalganj to Rooppur, and 4 MW from Bogura (West) to the Rooppur bus. The load flow
depends on the demand at Rooppur.
| 12:00 |  | Day Peak Generation: 13913 MW
| 12:49 | 17:02 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to From other end by NLDC
| 12:53 | 17:04 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Forced S/D Due to Bus DS finger
maintenance work
| 13:20 |  | Haripur 412 MW CCPP Tripped with remarks:- ST
| 13:22 | 14:18 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to According to Direction of NLDC | [7 empty] | 65.0MW load
interrup.
| 13:22 |  | Haripur 412 MW CCPP Tripped with remarks:- GT
| 13:22 |  | Haripur EGCB 412 MW CCPP tripped due to the pressure falling at close cooling water at
13:22 hrs.
| 14:20 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
| 14:22 |  | Siddhirganj 335 MW CCPP GT was sync.
| 15:30 |  | Siddhirganj 2x120 MW GT-1 was sync.
| 16:23 |  | Siddhirganj 335 MW CCPP ST was sync.
| 17:21 | 18:00 | Kasba 132/33kV S/S TR-1 LT Forced S/D Due to red hot | [7 empty] | 17.0MW load
interrup.
| 00:24 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 00:59 |  | Sirajgonj 225MW CCPP Unit-3 ST Shutdown with remarks:- As instructed by NLDC
| 01:08 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown
| 01:08 |  | Sirajgonj 225MW CCPP Unit-3 GT Shutdown with remarks:- As instructed by NLDC
| 01:12 |  | Gopalganj-Madhumati 132kV Ckt-1 Tripped from Gopalganj 132/33kV end showing RRD 670
relays Due to Distance trip
| 01:40 | 02:50 | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing General
Trip Distance trip Rph Distance trip Sph Distance trip Tph relays Due to Trip
| 01:40 | 02:13 | Aminbazar-Mirpur 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing General
Trip Distance trip Rph Distance trip Sph Distance trip Tph relays Due to Trip
| 02:14 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 02:41 | 04:08 | Gopalganj (O) - Gopalgan (N) Ckt-1 Tripped from Gopalganj 132/33kV end showing Siprotec
7sa87 relays Due to Def.EF
| 02:41 | 04:13 | Gopalganj 132/33kV S/S Gallamari-1 Tripped showing Distance trip relays Due to Distance
trip
| 02:41 | 04:52 | Gopalganj 132/33kV S/S Gallamari-2 Tripped showing Distance trip siprotec 7A52 relays
Due to Distance trip
| 02:42 | 03:36 | Goalpara-Labanchura 132kV Ckt-2 Tripped from Goalpara 132/33kV end showing Distance | [7 empty] | 52.0MW load
|  |  | Protection Relay 442 relays. | [7 empty] | interrup. Goalpara
132/33kV end
| 02:42 | 03:21 | Bagerhat-Goalpara 132 kV Ckt-1 Tripped from Goalpara 132/33kV end showing Distance | [7 empty] | 52.0MW load
|  |  | Protection P-442 relays. | [7 empty] | interrup. Goalpara
132/33kV end
| 02:43 | 04:14 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Tripped showing Distance Relay
relays Due to Trip
| 02:51 | 03:30 | Mongla 132/33kV S/S T-2 LT Forced S/D Due to Power out from bagerhat | [7 empty] | 35.0MW load
interrup.
| 02:51 | 03:30 | Mongla 132/33kV S/S T-1 LT Forced S/D Due to Power out from bagerhat | [7 empty] | 35.0MW load
interrup.
| 02:55 | 03:29 | Mongla 132/33kV S/S T-2 HT Forced S/D Due to Power out from bagerhat | [7 empty] | 35.0MW load
interrup.
| 02:55 | 03:29 | Mongla 132/33kV S/S T-1 HT Forced S/D Due to Power out from bagerhat | [7 empty] | 35.0MW load
interrup.
| 02:58 | 03:41 | Mongla 132/33kV S/S 100MW ERBL Solar PS Forced S/D Due to Power out from bagerhat
| 03:05 |  | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to t-2 transformer
closing problem
| 03:35 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 03:35 |  | Unique Meghnaghat Power Limited (UMPL) ST Shutdown with remarks:- CCPP shut down as per
NLDC due to gas shortage
| 03:42 |  | Unique Meghnaghat Power Limited (UMPL) GT Shutdown with remarks:- GT shutdown 3:42 hrs as
per NLDC due to gas shortage.
| 03:42 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 03:54 | 04:32 | Mongla 132/33kV S/S T-2 LT Tripped showing Lockout relay relays Due to Auxiliary ⇨2 trip | [7 empty] | 5.0MW load
interrup.
| 03:59 |  | BIPTC S/S 20DF22 Tripped showing 87.1 differential relay relays.
| 05:48 | 06:05 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Distance Realy
Trip(21) Def Trip(21) Aided Trip(21) relays.
| 05:48 |  | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing 2 phase Over Current | [7 empty] | 5.0MW load
|  |  | relay (R &Y) relays Due to unknown | [7 empty] | interrup.
| 06:37 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Demand 140MW @22:23 hrs on
21-Sep-2025
| 07:00 |  | Minimum Generation: 10926 MW.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-1 LT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:18 |  | Hasnabad 230/132kV S/S AUTO TR-1 HT Tripped showing O/C and E/F relay operated relays Due | [7 empty] | 87.0MW load
|  |  | to 132 kV bus trip | [7 empty] | interrup.
| 07:20 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Shitalakhya 132/33kV end showing Gen. Trip ,
Z-2/Z-3, R-Y-B Phase relays Due to Hasnabad End Problem
| 07:20 |  | Hasnabad 132/33kV S/S 132kV Reserve Bus Tripped showing Over current relays Due to | [7 empty] | 50.0MW load
|  |  | Fatullah line fault, Fatullah line trial an 132 kv bus trip at a time. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 4863600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8396500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 6893644 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 745274 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 36 | 1060000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 2089865 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 151056 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.5 | 659160 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 121 | 2345760 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 795240 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 727032 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27.2 | 508200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 488880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 466080 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 276 | 3091451 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2735280 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 1281600 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2306880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 191417 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 310680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 270 | 8421818.18 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 385 | 6639365 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2796000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2792.7 | 57964782.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 206042.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 77220 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 892320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5318747 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5112418 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1142472 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 76 | 1463736 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1006814 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 439680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1112640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 8281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 97 | 887380 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 164345 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 75 | 899927 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1129 | 26181816 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 15 | 100800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6363636.36 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2453 | 51378274.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 187 | 4743000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8646900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7976000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 879264 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 34 | 817440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 95 | 2676364 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1246080 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 128 | 1585745 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 492576 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2189490 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 118 | 1735680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1065600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 810893 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 381810 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 2023500 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 43680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1672320 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 181491 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1755.2 | 39167833
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1820160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 199200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 74 | 1812000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 300910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298560 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 204840 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 166 | 4647620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1328400 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3539700 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709248 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2014080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 3394950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 427000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 11 | 175392 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7513000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 363 | 8709000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 1181 | 27810770
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 21896000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 272 | 7363872 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 520560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1194 | 26800000 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2396 | 57492432
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 302 | 7199280 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2753000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 26398545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5409360 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 121200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 272 | 4843000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3612 | -
Barishal Area Total |  |  |  |  | 2236 | 2148 | 46727997.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 394612 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 258092 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 177544 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 181 | 4332364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 176 | 4403818 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 4287445 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 390 | 8509163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 73000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 95664 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 637552 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 646368 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 108 | 369984 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35220 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1441.5 | 29020148 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 379496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 671160 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2813.5 | 54291630
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 43 | 1003636 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3751000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1252656 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41087.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1372393 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199257 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1334160 | -
Rangpur Area Total |  |  |  |  | 950 | 428 | 8954189.4
Eastern Grid Total |  |  |  |  | 17385.715 | 8347.9 | 180969279.94
Western Grid Total |  |  |  |  | 10444.16 | 7785.5 | 167466248.85
National Grid Total |  |  |  |  | 27829.875 | 16133.4 | 348435528.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-09-2025 | during | 22-09-2025 | during | 22-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 383 | 0 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 250 | 280 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 36 | 208.13 | 208.13 | 98 | 98 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 50 | 0 | 50 | 0 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 47.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 76 | 121 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 27.2 | 33 | 33 | 22 | 22 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 276 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 125 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 87.5 | 87.5 | 51 | 87 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 152 | 144 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 270 | 270 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 416 | 385 | 718 | 718 | 416 | 416 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 125 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2330.5 | 2792.7 | 5555.34 | 5575.34 | 4435.75 | 4509.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 219 | 195 | 195 | 195 | 195 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 97 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 76 | 56 | 70 | 56 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 24 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 30 | 85 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.5 | 0 | 3.88 | 0 | 3.88 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 97 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 75 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1060 | 1129 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 15 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 265 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1892.5 | 2453 | 3265.6 | 3278.72 | 3010.24 | 3023.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 187 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 37 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 34 | 34 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 86 | 95 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 128 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 1 | 27 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 90 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 118 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 46 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20.83 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 49 | 96 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 41 | 90 | 115 | 115 | 92 | 92 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 14 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1406 | 1755.2 | 2445.89 | 2379.56 | 2188.06 | 2127.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-09-2025 | during | 22-09-2025 | during | 22-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 69 | 71 | 157.5 | 157.5 | 104 | 104 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 74 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.81 | 0 | 30.37 | 0 | 30.37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 216.81 | 166 | 352.97 | 320.5 | 251.97 | 219.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 149 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 164 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 11 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 383 | 363 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1220 | 1181 | 1261 | 1261 | 1187 | 1187
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 362 | 272 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1160 | 1194 | 1234.2 | 1234.2 | 1234 | 1234 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2545 | 2396 | 3607.2 | 3552.2 | 3412 | 3357
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 297 | 302 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1222 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 135 | 135 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 272 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1903.49 | 2148 | 2147 | 2146 | 2132 | 2131
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 50.49 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 185 | 181 | 214 | 214 | 198 | 198 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 176 | 220 | 220 | 200 | 200 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 180 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 390 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 18 | 18 | 18 | 18 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.49 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 916 | 1441.5 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.06 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1962.04 | 2813.5 | 3180.37 | 3013.87 | 3070.99 | 2904.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 44 | 43 | 45 | 45 | 45 | 45 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 157 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 195 | 0 | 188.07 | 0 | 188.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 440.6 | 428 | 672.07 | 453 | 672.07 | 453
System Total |  |  |  |  | 28823.2 | 27829.875 | 13916.94 | 16133.4 | 22487.44 | 21980.19 | 20360.08 | 19912.16
Forecast Scenario (22-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15532 |  | 0 |  | 15532
|  |  |  | 1:00 | 15136 |  | 0 |  | 15136
|  |  |  | 2:00 | 14617 |  | 0 |  | 14617
|  |  |  | 3:00 | 14086 |  | 0 |  | 14086
|  |  |  | 4:00 | 13916 |  | 0 |  | 13916
|  |  |  | 5:00 | 13597 |  | 0 |  | 13597
|  |  |  | 6:00 | 13129 |  | 0 |  | 13129
|  |  |  | 7:00 | 13077 |  | 0 |  | 13077
|  |  |  | 8:00 | 13181 |  | 0 |  | 13181
|  |  |  | 9:00 | 13284 |  | 0 |  | 13284
|  |  |  | 10:00 | 13376 |  | 0 |  | 13376
|  |  |  | 11:00 | 13627 |  | 0 |  | 13627
|  |  |  | 12:00 | 13917 |  | 0 |  | 13917
|  |  |  | 13:00 | 14404 |  | 0 |  | 14404
|  |  |  | 14:00 | 14257 |  | 0 |  | 14257
|  |  |  | 15:00 | 14534 |  | 0 |  | 14534
|  |  |  | 16:00 | 14138 |  | 0 |  | 14138
|  |  |  | 17:00 | 14003 |  | 0 |  | 14003
|  |  |  | 18:00 | 14701 |  | 0 |  | 14701
|  |  |  | 18:30 | 15500 |  | 0 |  | 15500
|  |  |  | 19:00 | 16201 |  | 0 |  | 16201
|  |  |  | 19:30 | 16280 |  | 0 |  | 16280
|  |  |  | 20:00 | 16051 |  | 0 |  | 16051
|  |  |  | 21:00 | 15931 |  | 0 |  | 15931
|  |  |  | 22:00 | 15775 |  | 0 |  | 15775
|  |  |  | 23:00 | 15600 |  | 0 |  | 15600
Probable Maximum Temperature: |  |  | 35.50°C
Probable Maximum Demand at Day Peak: |  |  | 13917.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16280.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16280.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 346.07 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:28 hrs on 22-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-09-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10282.83 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5074 | MW
i) Dhaka area |  |  | 5579.58 |  | MW | i) Khulna area |  |  |  | 1935 | MW
ii) Chattogram area |  |  | 1464.4 |  | MW | ii) Barishal area |  |  |  | 478 | MW
iii) Cumilla area |  |  | 1420.85 |  | MW | iii) Rajshahi area |  |  |  | 1590 | MW
iv) Mymensingh area |  |  | 1096 |  | MW | iv) Rangpur area |  |  |  | 1071 | MW
v) Sylhet area |  |  | 722 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15356.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 18:30 | 133 | PHP | 8 | 05:00
2 | AKSML | 98 | 23:00 | 68 | Ishurdi | 89 | 19:30 | 134 | Pabna | 130 | 18:30
3 | Aftabnagar | 42 | 18:30 | 69 | Jaldhaka | 90 | 22:00 | 135 | Palashbari | 122 | 19:30
4 | Agargaon | 143 | 15:00 | 70 | Jamalpur | 110 | 16:00 | 136 | Panchagarh | 63 | 19:00
5 | Agrabad | 102 | 18:30 | 71 | Jashore | 150 | 19:00 | 137 | Patiya | 12 | 00:00
6 | Amnura | 32 | 22:00 | 72 | Jhenaidah | 143 | 19:00 | 138 | Patuakhali | 71.5 | 21:00
7 | Ashuganj | 103 | 06:00 | 73 | Joydebpur | 172 | 19:00 | 139 | Payra | 38 | 23:00
8 | BSRM | 151 | 19:30 | 74 | Joypurhat | 66 | 22:00 | 140 | Postogola | 72 | 12:00
9 | Bagerhat | 86 | 19:00 | 75 | Juldah | 18 | 12:00 | 141 | Purbachal | 23 | 00:00
10 | Bajitpur | 97 | 22:00 | 76 | KSRM | 22 | 19:00 | 142 | Purbasadipur | 130 | 20:00
11 | Bakulia | 96 | 16:00 | 77 | Kabirpur | 266 | 09:00 | 143 | Rahanpur | 41 | 22:00
12 | Banani | 54.8 | 13:00 | 78 | Kachua | 96 | 21:00 | 144 | Rahim | 31 | 09:00
13 | Bangabhaban | 25 | 10:00 | 79 | Kallyanpur | 114 | 23:00 | 145 | Rajbari | 90 | 18:30
14 | Barapukuria | 74 | 21:00 | 80 | Kalurghat | 40 | 11:00 | 146 | Rajendrapur | 135 | 21:00
15 | Barguna | 24 | 23:00 | 81 | Kamrangirchar | 80 | 13:00 | 147 | Rajshahi | 112 | 22:00
16 | Barishal | 118 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 104 | 21:00
17 | Barishal-230 | 102 | 22:00 | 83 | Kasba | 38 | 19:30 | 149 | Ramganj | 112 | 22:00
18 | Baroaulia | 68 | 13:00 | 84 | Kazla | 99 | 20:00 | 150 | Rampur | 46 | 00:00
19 | Baroirhat | 70 | 18:30 | 85 | Keranigonj | 95 | 18:30 | 151 | Rangamati | 17 | 18:00
20 | Bashundhara | 214 | 15:00 | 86 | Khagrachori | 34 | 19:00 | 152 | Rangpur | 149 | 20:00
21 | BashundharaCement | 0 | 00:00 | 87 | Khulna | 81 | 13:00 | 153 | Ruppur | 8.2 | 11:00
22 | Beanibazar | 86 | 20:00 | 88 | Khulshi | 189 | 18:00 | 154 | SSM | 12 | 23:00
23 | Benapole | 66 | 21:00 | 89 | Kishoreganj | 140 | 00:00 | 155 | Saidpur | 117 | 18:30
24 | Bhaluka | 150 | 16:00 | 90 | Kodda | 287 | 19:30 | 156 | Satkhira | 135 | 22:00
25 | Bhandaria | 57 | 21:00 | 91 | Kulaura | 58 | 18:30 | 157 | Satmasjid | 110 | 19:00
26 | Bhangura | 42 | 18:30 | 92 | Kurigram | 70 | 18:30 | 158 | Savar | 241 | 16:00
27 | Bheramara(GK) | 73 | 21:00 | 93 | Kushtia | 170 | 18:30 | 159 | SevenRings | 20.41 | 02:00
28 | Bhulta | 213 | 12:00 | 94 | Laksam | 35 | 00:00 | 160 | ShahCement | 32 | 05:00
29 | Bog-Sherpur | 80 | 21:00 | 95 | Lakshmipur | 34 | 23:00 | 161 | Shahjadpur | 92 | 19:00
30 | Bogura | 168 | 19:00 | 96 | Lalbag | 61 | 13:00 | 162 | Shahjibazar | 144 | 21:00
31 | Borhanuddin | 94 | 20:00 | 97 | Lalmonirhat | 71 | 18:30 | 163 | Shahmirpur | 57 | 07:00
32 | Brahmanbaria | 142 | 00:00 | 98 | MI_Cement | 5.7 | 12:00 | 164 | Shariatpur | 94 | 19:30
33 | Cantonment | 150 | 18:30 | 99 | Madanganj | 38 | 00:00 | 165 | Sherpur | 134 | 07:00
34 | Chandina | 25.3 | 19:00 | 100 | Madaripur | 131 | 22:00 | 166 | Shikalbaha | 29 | 00:00
35 | Chandpur | 88 | 18:30 | 101 | Madartek | 100 | 23:00 | 167 | Shitalakhya | 92 | 13:00
36 | Chandraghona | 40 | 18:30 | 102 | Madunaghat | 56 | 00:00 | 168 | Sholosohor | 50 | 15:00
37 | Chapai | 72 | 21:00 | 103 | Magura | 72 | 18:30 | 169 | Shyampur | 93 | 15:00
38 | Charsaidpur | 30 | 00:00 | 104 | Mahasthangarh | 82 | 20:00 | 170 | Siddhirganj | 128 | 11:00
39 | Chauddagram | 76 | 00:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sirajganj | 125 | 19:00
40 | Chhatak | 44 | 23:00 | 106 | Manikganj | 138 | 22:00 | 172 | Sonargaon | 126 | 00:00
41 | Chowmuhani | 183 | 19:30 | 107 | Maniknagar | 68 | 13:00 | 173 | Sreemongol | 90 | 00:00
42 | Chuadanga | 125 | 18:30 | 108 | Matarbari | 54 | 00:00 | 174 | Sreepur | 111 | 19:30
43 | Coxsbazar | 134 | 18:00 | 109 | Matuail | 78 | 12:00 | 175 | Srinagar | 52.55 | 22:00
44 | Cumilla(N) | 143 | 13:00 | 110 | Millgate | 134 | 16:00 | 176 | Sunamganj | 65 | 19:30
45 | Cumilla(S) | 152 | 14:00 | 111 | Mirpur | 132 | 18:30 | 177 | Sylhet | 59 | 19:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 100 | 04:00 | 178 | Sylhet-132 | 147 | 18:00
47 | Daudkandi | 148 | 04:00 | 113 | Mirzapur | 45 | 12:00 | 179 | TK | 27 | 00:00
48 | DhakaUniversity | 114 | 13:00 | 114 | Mithapukur | 78 | 18:30 | 180 | Tangail | 184 | 23:00
49 | Dhamrai | 126 | 19:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 24 | 19:30
50 | Dhanmondi | 150 | 13:00 | 116 | Mogbazar | 108.1 | 15:00 | 182 | Thakurgaon | 116 | 19:00
51 | Dohazari | 105 | 18:30 | 117 | Mongla | 47 | 15:00 | 183 | Tongi | 146 | 15:00
52 | Faridpur | 188 | 23:00 | 118 | Motijheel | 49 | 13:00 | 184 | Ullahpara | 43 | 19:00
53 | Fatullah | 112 | 10:00 | 119 | Muktagacha | 35 | 00:00 | 185 | Ullon | 59 | 23:00
54 | Fenchuganj | 53 | 20:00 | 120 | Munshiganj | 116 | 00:00 | 186 | Uttara | 91 | 16:00
55 | Feni | 120 | 00:00 | 121 | Muradnagar | 43 | 18:30 | 187 | UttaraNew | 66 | 22:00
56 | GPH | 9 | 16:00 | 122 | Mymensingh | 202 | 21:00 | 188 | Zigatola | 80 | 19:00
57 | Ghatail | 72 | 00:00 | 123 | Naogaon | 142 | 18:30
58 | Ghorashal | 22 | 15:00 | 124 | Narail | 63 | 20:00
59 | Ghorashal-230 | 97 | 20:00 | 125 | Narinda | 68 | 14:00
60 | Goalpara | 36 | 18:30 | 126 | Narshingdi | 188 | 22:00
61 | Gollamari | 100 | 23:00 | 127 | Natore | 165 | 22:00
62 | Gopalganj | 120 | 18:30 | 128 | Nawabganj | 70.2 | 14:00
63 | Gulshan | 130 | 13:00 | 129 | Netrakona | 140 | 18:00
64 | Halishahar | 71 | 15:00 | 130 | New | 48 | 18:00
65 | HaripurSBU | 162 | 09:00 | 131 | Niamatpur | 81 | 21:00
66 | Hasnabad | 102 | 23:00 | 132 | Noapara | 48 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 372 | 11:00 | Payra | 414 | 06:00 | 408 | 23:00
Ashuganj | 405 | 6:00 | 396 | 14:00 | Rahanpur | 397 | 09:00 | 384 | 00:00
Bhulta | 398 | 06:00 | 365 | 04:00 | Rampal | 406 | 06:00 | 390 | 22:00
Bibiana | 386 | 05:00 | 378 | 14:00
BIPTC | 407 | 09:00 | 396 | 20:00
Bogura | 384 | 09:00 | 369 | 00:00
Gopalganj | 398 | 06:00 | 384 | 22:00
Kaliakoir | 375 | 06:00 | 361 | 12:00
Madunaghat | 394 | 18:00 | 387 | 11:00
Meghnaghat | 388 | 08:00 | 378 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 219 | 11:00 | Kaliakoir | 234 | 06:00 | 222 | 12:00
AKSML | 233 | 16:00 | 224 | 11:00 | Keranigonj | 225 | 05:00 | 217 | 11:00
Aminbazar | 229 | 06:00 | 220 | 09:00 | Khulna(S) | 232 | 06:00 | 216 | 20:00
Ashuganj | 232 | 06:00 | 220 | 14:00 | Madunaghat | 233 | 16:00 | 227 | 11:00
Ashuganj-400 | 232 | 06:00 | 220 | 14:00 | Madunaghat-400 | 234 | 18:00 | 228 | 10:00
Baghabari | 233 | 05:00 | 224 | 18:30 | Maniknagar | 220 | 05:00 | 213 | 11:00
Barapukuria | 218 | 02:00 | 213 | 19:00 | Meghnaghat | 227 | 18:00 | 221 | 11:00
Barapukuria-230 | 218 | 02:00 | 213 | 19:00 | Meghnaghat-400 | 225 | 05:00 | 218 | 11:00
Barishal | 228 | 06:00 | 220 | 21:00 | Mirsorai | 236 | 16:00 | 221 | 10:00
Bheramara | 235 | 03:00 | 223 | 18:30 | Rajshahi | 228 | 05:00 | 219 | 13:00
Bhulta | 229 | 06:00 | 211 | 12:00 | Rampal | 232 | 06:00 | 218 | 22:00
Bibiana | 229 | 05:00 | 222 | 11:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 06:00 | 223 | 18:30 | Rampura | 227 | 05:00 | 209 | 11:00
Bogura | 229 | 09:00 | 222 | 00:00 | Shikalbaha | 235 | 19:30 | 226 | 10:00
Bogura-400 | 229 | 09:00 | 222 | 00:00 | Shyampur | 224 | 05:00 | 217 | 10:00
Borhanuddin | 232 | 05:00 | 227 | 21:00 | Siddhirganj | 222 | 07:00 | 215 | 12:00
BSRM | 233 | 16:00 | 222 | 10:00 | Sirajgonj | 238 | 06:00 | 233 | 01:00
Cumilla(N) | 225 | 16:00 | 217 | 11:00 | Sreepur | 228 | 06:00 | 220 | 10:00
Faridpur | 225 | 06:00 | 216 | 22:00 | Tongi | 228 | 05:00 | 213 | 11:00
Fenchuganj | 230 | 06:00 | 223 | 18:30
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 229 | 06:00 | 211 | 11:00
Gopalganj | 226 | 05:00 | 219 | 20:00
GPH | 233 | 16:00 | 225 | 10:00
Haripur | 222 | 05:00 | 216 | 10:00
Hasnabad | 225 | 05:00 | 216 | 12:00
Hathazari | 230 | 05:00 | 224 | 10:00
Ishurdi | 236 | 06:00 | 223 | 18:30
Jhenaidah | 232 | 06:00 | 216 | 18:30
Kachua | 227 | 16:00 | 212 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 123 | 11:00 | Lalmonirhat | 124 | 03:00 | 112 | 18:30
Agargaon | 138 | 06:00 | 130 | 11:00 | Madanganj | 132 | 08:00 | 124 | 11:00
Agrabad | 132 | 17:00 | 127 | 09:00 | Madaripur | 135 | 07:00 | 128 | 21:00
AKS | 130 | 17:00 | 125 | 15:00 | Madartek | 136 | 21:00 | 122 | 12:00
Aminbazar | 134 | 06:00 | 128 | 09:00 | Madunaghat | 135 | 16:00 | 131 | 09:00
Amnura | 135 | 17:00 | 125 | 12:00 | Magura | 134 | 06:00 | 121 | 22:00
Ashuganj | 140 | 06:00 | 133 | 15:00 | Mahasthangarh | 126 | 08:00 | 121 | 00:00
Bagerhat | 133 | 06:00 | 116 | 19:30 | Maijdee | 126 | 16:00 | 109 | 00:00
Bajitpur | 128 | 04:00 | 122 | 18:00 | Manikganj | 128 | 06:00 | 118 | 11:00
Bakulia | 133 | 16:00 | 128 | 10:00 | Maniknagar | 134 | 05:00 | 127 | 12:00
Banani | 136 | 03:00 | 123 | 12:00 | Matarbari | 126 | 06:00 | 112 | 00:00
Bangabhaban | 134 | 05:00 | 127 | 12:00 | Matuail | 129.5 | 06:00 | 124 | 11:00
Barapukuria | 132 | 01:00 | 124 | 19:00 | Millgate | 133 | 05:00 | 123 | 10:00
Barguna | 134 | 08:00 | 131 | 00:00 | Mirpur | 133 | 02:00 | 127 | 11:00
Barishal | 133 | 16:00 | 128 | 20:00 | Mirzapur | 131 | 00:00 | 125 | 14:00
Barishal-230 | 134 | 06:00 | 127 | 22:00 | Mithapukur | 127 | 03:00 | 120 | 19:00
Baroaulia | 134 | 16:00 | 128 | 10:00 | MI_Cement | 131 | 05:00 | 125 | 11:00
Baroirhat | 129 | 16:00 | 120 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 136 | 04:00 | 122 | 12:00 | Mogbazar | 137 | 06:00 | 125 | 09:00
BashundharaCement | 132 | 08:00 | 124 | 11:00 | Mongla | 133 | 05:00 | 118 | 19:00
Beanibazar | 126 | 08:00 | 121 | 18:30 | Motijheel | 134 | 06:00 | 127 | 12:00
Benapole | 132 | 05:00 | 117 | 23:00 | Muktagacha | 129 | 05:00 | 123 | 13:00
Bhaluka | 128 | 05:00 | 121 | 14:00 | Munshiganj | 130 | 16:00 | 125 | 09:00
Bhandaria | 128 | 09:00 | 118 | 21:00 | Muradnagar | 129 | 16:00 | 118 | 00:00
Bhangura | 132 | 05:00 | 126 | 22:00 | Mymensingh | 128 | 06:00 | 110 | 18:00
Bheramara | 136 | 03:00 | 131 | 00:00 | Naogaon | 125 | 16:00 | 117 | 00:00
Bheramara(GK) | 136 | 05:00 | 130 | 00:00 | Narail | 133 | 06:00 | 119 | 18:30
Bhulta | 127 | 15:00 | 121 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 129 | 09:00 | 124 | 00:00 | Narshingdi | 135 | 00:00 | 120 | 00:00
Bogura | 129 | 09:00 | 28 | 06:00 | Natore | 129 | 16:00 | 119 | 00:00
Bogura-230 | 137 | 15:00 | 124 | 00:00 | Nawabganj | 136 | 05:00 | 130 | 11:00
Brahmanbaria | 134 | 06:00 | 124 | 15:00 | Netrakona | 119 | 16:00 | 108 | 18:00
Cantonment | 137 | 06:00 | 130 | 11:00 | New | 133 | 20:00 | 123 | 11:00
Chandina | 132 | 16:00 | 124 | 10:00 | Niamatpur | 135 | 09:00 | 129 | 00:00
Chandpur | 135 | 16:00 | 122 | 00:00 | Noapara | 135 | 05:00 | 24 | 18:30
Chandraghona | 135 | 16:00 | 131 | 10:00 | Pabna | 134 | 05:00 | 127 | 18:30
Chapai | 134 | 17:00 | 126 | 00:00 | Palashbari | 123 | 09:00 | 116 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 05:00 | 12 | 03:00 | Panchagarh | 137 | 04:00 | 120 | 17:00
Chauddagram | 130 | 16:00 | 119 | 00:00 | Patiya | 133 | 06:00 | 127 | 10:00
Chhatak | 126 | 06:00 | 119 | 19:00 | Patuakhali | 134 | 08:00 | 132 | 00:00
Chowmuhani | 126 | 16:00 | 110 | 00:00 | Payra | 136 | 08:00 | 134 | 00:00
Chuadanga | 133 | 06:00 | 117 | 18:30 | PHP | 128 | 16:00 | 118 | 00:00
Coxsbazar | 128 | 06:00 | 111 | 00:00 | Postogola | 133 | 06:00 | 127 | 11:00
Cumilla(N) | 132 | 16:00 | 124 | 00:00 | Purbachal | 136 | 00:00 | 122 | 12:00
Cumilla(S) | 132 | 15:00 | 123 | 10:00 | Purbasadipur | 131 | 04:00 | 117 | 19:00
Daganbhuiyan | 127 | 16:00 | 116 | 02:00 | Rahanpur | 136 | 16:00 | 131 | 00:00
Daudkandi | 127 | 16:00 | 115 | 14:00 | Rahanpur-400 | 136 | 08:00 | 131 | 00:00
DhakaUniversity | 137 | 04:00 | 123 | 14:00 | Rahim | 129 | 05:00 | 125 | 10:00
Dhamrai | 135 | 20:00 | 126 | 10:00 | Rajbari | 133 | 06:00 | 125 | 20:00
Dhanmondi | 136.7 | 05:00 | 125 | 11:00 | Rajendrapur | 135 | 02:00 | 120 | 14:00
Dohazari | 132 | 06:00 | 123 | 11:00 | Rajshahi | 129 | 17:00 | 121 | 00:00
Faridpur | 134 | 07:00 | 128 | 00:00 | Rajshahi-230 | 130 | 06:00 | 124 | 00:00
Fatullah | 133 | 05:00 | 127 | 11:00 | Ramganj | 131 | 16:00 | 114 | 00:00
Fenchuganj | 135 | 04:00 | 130 | 19:00 | Rampur | 133 | 07:00 | 126 | 10:00
Feni | 128 | 16:00 | 116 | 01:00 | Rampura | 136 | 00:00 | 123 | 12:00
Ghatail | 127 | 05:00 | 121 | 23:00 | Rangamati | 134 | 16:00 | 130 | 08:00
Ghorashal | 135 | 00:00 | 128 | 11:00 | Rangpur | 127 | 18:00 | 118 | 19:00
Goalpara | 138 | 06:00 | 124 | 22:00 | Ruppur | 137 | 05:00 | 131 | 18:30
Gollamari | 137 | 06:00 | 126 | 18:30 | Saidpur | 128 | 18:00 | 119 | 19:00
Gopalganj | 135 | 06:00 | 126 | 18:30 | Satkhira | 135 | 06:00 | 118 | 22:00
Gopalganj-400 | 136 | 05:00 | 130 | 21:00 | Satmasjid | 137 | 05:00 | 129 | 13:00
Gulshan | 136 | 00:00 | 124 | 11:00 | Savar | 132 | 00:00 | 126 | 09:00
Halishahar | 133 | 06:00 | 128 | 10:00 | SevenRings | 136 | 03:00 | 127 | 11:00
Haripur | 130 | 05:00 | 126 | 10:00 | ShahCement | 131 | 05:00 | 125 | 11:00
HaripurSBU | 130 | 05:00 | 127 | 00:00 | Shahjadpur | 136 | 19:00 | 131 | 22:00
Hasnabad | 132 | 03:00 | 127 | 10:00 | Shahjibazar | 134 | 07:00 | 126 | 15:00
Hathazari | 135 | 05:00 | 130 | 11:00 | Shahmirpur | 136 | 13:00 | 128 | 09:00
Ishurdi | 138 | 03:00 | 131 | 18:30 | Shariatpur | 134 | 06:00 | 126 | 20:00
Jaldhaka | 128 | 04:00 | 114 | 19:00 | Sherpur | 122 | 03:00 | 113 | 23:00
Jamalpur | 126 | 05:00 | 117 | 18:00 | Shikalbaha | 124 | 16:00 | 118 | 10:00
Jashore | 136 | 06:00 | 120 | 19:00 | Shikalbaha-230 | 135 | 16:00 | 131 | 09:00
Jhenaidah | 137 | 06:00 | 119 | 18:30 | Shitalakhya | 131 | 05:00 | 125 | 11:00
Jhenaidah-230 | 138 | 06:00 | 126 | 18:30 | Sholosohor | 135 | 16:00 | 130 | 10:00
Joydebpur | 137 | 23:00 | 122 | 11:00 | Shyampur | 133 | 08:00 | 128 | 11:00
Joypurhat | 123 | 09:00 | 14 | 23:00 | Shyampur-230 | 133 | 05:00 | 128 | 11:00
Juldah | 133 | 18:30 | 128 | 11:00 | Siddhirganj | 130 | 06:00 | 125 | 10:00
Kabirpur | 134 | 23:00 | 119 | 12:00 | Sirajganj | 130 | 15:00 | 122 | 20:00
Kachua | 136 | 16:00 | 125 | 00:00 | Sonargaon | 128 | 03:00 | 123 | 11:00
Kaliakoir | 136 | 05:00 | 128 | 12:00 | Sreemongol | 132 | 07:00 | 126 | 15:00
Kallyanpur | 133 | 05:00 | 129 | 09:00 | Sreepur | 131 | 06:00 | 126 | 15:00
Kalurghat | 135 | 16:00 | 130 | 10:00 | Srinagar | 137 | 06:00 | 130 | 11:00
Kamrangirchar | 137 | 06:00 | 129 | 12:00 | SSM | 138 | 17:00 | 132 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 122 | 07:00 | 117 | 00:00
Kasba | 129 | 16:00 | 118 | 22:00 | Sylhet | 128 | 06:00 | 123 | 18:30
Kazla | 133 | 05:00 | 127 | 12:00 | Sylhet-132 | 127 | 01:00 | 125 | 15:00
Keranigonj | 137 | 05:00 | 131 | 11:00 | Tangail | 128 | 03:00 | 121 | 23:00
Khagrachori | 133 | 06:00 | 129 | 10:00 | Taraganj | 124 | 18:00 | 117 | 19:00
Khulna | 137 | 06:00 | 124 | 22:00 | Thakurgaon | 135 | 04:00 | 118 | 07:00
Khulna(S) | 138 | 06:00 | 126 | 19:00 | TK | 135 | 16:00 | 130 | 10:00
Khulshi | 132 | 07:00 | 127 | 10:00 | Tongi | 135 | 06:00 | 126 | 11:00
Kishoreganj | 125 | 06:00 | 119 | 00:00 | Ullahpara | 131 | 05:00 | 126 | 00:00
Kodda | 134 | 01:00 | 122 | 09:00 | Ullon | 136 | 00:00 | 123 | 12:00
KSRM | 134 | 15:00 | 128 | 09:00 | Uttara | 132 | 01:00 | 127 | 10:00
Kulaura | 133 | 06:00 | 129 | 18:30 | UttaraNew | 132 | 01:00 | 127 | 10:00
Kurigram | 125 | 03:00 | 112 | 18:30 | Zigatola | 137 | 05:00 | 130 | 11:00
Kushtia | 133 | 08:00 | 125 | 00:00
Laksam | 131 | 15:00 | 123 | 00:00
Lakshmipur | 127 | 16:00 | 110 | 00:00
Lalbag | 135 | 04:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-09-2025 | [28 empty] | Date: | 21-09-2025 | [28 empty] | Date: | 21-09-2025 | [28 empty] | Date: | 21-09-2025 | [28 empty] | Date: | 21-09-2025 | [14 empty] | Date: | 21-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 133 | 122 | 210 | 30 | 35 | 152 | 0 | 400 | 299 | 0 | 0 | 55 | 0 | 97 | 0 | 0 | 125 | 21.8 | 21 | 0 | 480 | 45 | 0 | 98 | 0 | 8 | 66 | 75 | 0 | 0 | 0 | 0 | 221 | 105 | 28 | 260 | 16 | 0 | 32 | 17 | 97 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 125 | 143 | 0 | 348 | 330 | 36 | 198 | 37 | 68 | 95 | 51 | 0 | 19 | 114 | 52 | 43 | 0 | 36 | 315 | 0 | 336 | 0 | 57 | 146 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 85 | 0 | 0 | 12 | 8229.8 | 901 | 50 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 1447.99 | 0 | 0 | 0 | 35 | 35 | 0 | 94 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 175 | 0 | 178 | 0 | 178 | 0 | 356 | 0 | 0 | 152 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 300 | 1110 | 17 | 7191.99 | 15421.79 | 108.27
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 133 | 122 | 160 | 30 | 35 | 142 | 0 | 400 | 293 | 0 | 0 | 55 | 0 | 97 | 0 | 0 | 125 | 21.8 | 21 | 0 | 480 | 30 | 0 | 98 | 0 | 0 | 53 | 75 | 0 | 0 | 0 | 0 | 219 | 97 | 34 | 262 | 0 | 0 | 33 | 17 | 93 | 218 | 0 | 0 | 0 | 1140 | 0 | 51 | 80 | 143 | 0 | 349 | 330 | 37 | 193 | 37 | 68 | 96 | 51 | 0 | 19 | 114 | 52 | 52.2 | 0 | 36 | 310 | 0 | 314 | 0 | 58 | 138 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 85 | 0 | 0 | 12 | 7952 | 897 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1197 | 0 | 1453.41 | 0 | 0 | 0 | 0 | 35 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 170 | 0 | 170 | 0 | 343 | 0 | 0 | 153 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 115 | 220 | 0 | 300 | 1090 | 17 | 7091.41 | 15043.41 | 108.28
02:00 | 0 | 52 | 18 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 0 | 118 | 106 | 45 | 30 | 0 | 90 | 0 | 400 | 291 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 125 | 21.8 | 21 | 0 | 480 | 0 | 0 | 98 | 0 | 0 | 66 | 75 | 0 | 0 | 0 | 0 | 219 | 68 | 36 | 260 | 0 | 0 | 33 | 0 | 92 | 218 | 0 | 0 | 0 | 1140 | 0 | 51 | 50 | 143 | 0 | 350 | 330 | 36 | 192 | 37 | 68 | 96 | 51 | 0 | 19 | 114 | 50 | 52.2 | 0 | 36 | 305 | 0 | 314 | 0 | 58 | 138 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 87 | 0 | 0 | 12 | 7572 | 901 | 290 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 1457.63 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 170 | 0 | 170 | 0 | 341 | 0 | 0 | 151 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 300 | 1090 | 0 | 6969.63 | 14541.63 | 108.29
03:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 6 | 36.2 | 0 | 80 | 106 | 0 | 0 | 0 | 0 | 0 | 400 | 293 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 125 | 21.8 | 21 | 0 | 450 | 0 | 0 | 78 | 0 | 0 | 66 | 75 | 0 | 0 | 0 | 0 | 219 | 0 | 36 | 262 | 0 | 0 | 33 | 0 | 93 | 218 | 0 | 0 | 0 | 1060 | 0 | 51 | 50 | 143 | 0 | 350 | 330 | 36 | 195 | 37 | 68 | 96 | 51 | 0 | 19 | 114 | 48 | 52.2 | 0 | 36 | 305 | 0 | 322 | 0 | 58 | 139 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 101 | 0 | 0 | 12 | 7229.2 | 901 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1034 | 0 | 1307.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 172 | 0 | 171 | 0 | 348 | 0 | 0 | 150 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 115 | 220 | 0 | 300 | 1086 | 0 | 6793.24 | 14022.44 | 108.3
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 5 | 36.2 | 0 | 78 | 76 | 0 | 0 | 0 | 0 | 0 | 400 | 291 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 125 | 21.8 | 21 | 0 | 450 | 0 | 0 | 47 | 0 | 0 | 66 | 75 | 0 | 0 | 0 | 0 | 219 | 0 | 30 | 263 | 0 | 0 | 33 | 0 | 75 | 218 | 0 | 0 | 0 | 1035 | 0 | 51 | 0 | 145 | 0 | 352 | 330 | 37 | 190 | 37 | 68 | 95 | 51 | 0 | 19 | 114 | 48 | 52.2 | 0 | 28 | 310 | 0 | 316 | 0 | 58 | 140 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 101 | 0 | 0 | 12 | 7059.2 | 901 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 1311.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 173 | 0 | 172 | 0 | 338 | 0 | 0 | 153 | 43 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 115 | 220 | 0 | 300 | 1088 | 0 | 6801.24 | 13860.44 | 108.31
05:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 32 | 36.2 | 0 | 78 | 76 | 0 | 0 | 0 | 0 | 0 | 400 | 293 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 108 | 21.8 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 66 | 75 | 0 | 0 | 0 | 0 | 219 | 0 | 30 | 262 | 0 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 147 | 0 | 352 | 330 | 36 | 191 | 37 | 68 | 95 | 51 | 0 | 19 | 114 | 48 | 52.2 | 0 | 28 | 310 | 0 | 310 | 0 | 58 | 139 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 35 | 76 | 9 | 101 | 0 | 0 | 12 | 6880.2 | 900 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 1311.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 171 | 0 | 171 | 0 | 340 | 0 | 0 | 150 | 43 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 115 | 220 | 0 | 300 | 1090 | 0 | 6665.75 | 13545.95 | 108.32
06:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 32 | 36 | 0 | 78 | 76 | 0 | 0 | 0 | 0 | 0 | 350 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 21.8 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 28 | 66 | 75 | 0 | 0 | 0 | 0.03 | 220 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 147 | 0 | 353 | 330 | 36 | 188 | 37 | 68 | 95 | 51 | 0 | 19 | 114 | 44 | 43 | 1 | 0 | 305 | 0 | 315 | 0 | 58 | 138 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 24 | 76 | 9 | 101 | 0 | 0.7 | 12 | 6684.53 | 900 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 1254.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0.27 | 167 | 0 | 169 | 0 | 169 | 0 | 334 | 0 | 0.03 | 125 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 0 | 164 | 115 | 220 | 0 | 300 | 1020 | 0 | 6400.66 | 13085.19 | 108.33
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 95 | 0 | 0 | 78 | 76 | 0 | 0 | 0 | 0 | 0 | 350 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 108 | 21.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 75 | 0 | 0 | 0 | 0.21 | 221 | 0 | 24 | 263 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1064 | 0 | 51 | 0 | 147 | 0 | 348 | 330 | 36 | 200 | 37 | 68 | 95 | 51 | 7 | 19 | 80 | 42 | 43 | 4 | 0 | 310 | 0 | 335 | 0 | 57 | 145 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 93 | 0 | 9.01 | 12 | 6655.72 | 902 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1050 | 0 | 1117.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.23 | 9 | 0 | 0 | 5.75 | 173 | 0 | 173 | 0 | 167 | 0 | 363 | 0 | 0.62 | 139 | 42 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 30 | 0.15 | 0 | 170 | 115 | 220 | 0 | 295 | 1000 | 0 | 6380.87 | 13036.59 | 108.34
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 222 | 0 | 0 | 78 | 76 | 0 | 0 | 17 | 0 | 0 | 350 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 90 | 21.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 75 | 0 | 0 | 0 | 0.78 | 220 | 0 | 6 | 262 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1045 | 5 | 51 | 0 | 147 | 0 | 350 | 330 | 36 | 189 | 37 | 68 | 95 | 51 | 8 | 19 | 50 | 40 | 16 | 8 | 0 | 315 | 0 | 330 | 0 | 57 | 143 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 93 | 0 | 17.95 | 12 | 6686.23 | 907 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1042 | 0 | 1101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.82 | 30 | 0 | 0 | 17.77 | 174 | 0 | 167 | 0 | 149 | 0 | 340 | 0 | 1.68 | 157 | 43 | 0 | 15 | 0 | 0 | 0 | 0 | 2.9 | 81 | 0.17 | 0 | 169 | 115 | 220 | 0 | 295 | 998 | 0 | 6467.34 | 13153.57 | 108.34
09:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 415 | 0 | 0 | 78 | 76 | 0 | 0 | 35 | 0 | 0 | 350 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 90 | 21.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 0 | 0 | 0 | 1.34 | 221 | 0 | 2 | 262 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1052 | 0 | 51 | 0 | 86 | 0 | 346 | 330 | 37 | 196 | 37 | 58 | 93 | 51 | 9 | 19 | 46 | 38 | 16 | 15 | 0 | 305 | 0 | 370 | 0 | 57 | 139 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 82 | 1 | 27.6 | 12 | 6716.24 | 907 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1038 | 0 | 1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.03 | 50 | 0 | 0 | 39.59 | 170 | 0 | 163 | 0 | 145 | 0 | 346 | 0 | 3.53 | 157 | 44 | 0 | 23 | 0 | 0 | 0 | 0 | 4.6 | 139 | 0.29 | 0 | 173 | 115 | 220 | 0 | 296 | 992 | 0 | 6568.04 | 13284.28 | 108.34
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 415 | 0 | 0 | 78 | 76 | 0 | 0 | 35 | 55 | 0 | 300 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 90 | 21.5 | 21 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 2.64 | 221 | 0 | 2 | 265 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1064 | 11 | 51 | 0 | 86 | 0 | 338 | 330 | 35 | 207 | 36 | 31 | 92 | 51 | 9 | 16 | 50 | 40 | 16 | 27 | 0 | 315 | 0 | 370 | 0 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 69 | 1 | 37.67 | 12 | 6760.81 | 907 | 358 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1110 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.85 | 80 | 0 | 0 | 53.12 | 183 | 0 | 177 | 0 | 158 | 0 | 300 | 0 | 4.76 | 157 | 43 | 0 | 29 | 0 | 0 | 0 | 0 | 6 | 170 | 0.48 | 0 | 175 | 115 | 220 | 0 | 297 | 1010 | 0 | 6615.21 | 13376.02 | 108.34
11:00 | 7 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 416 | 0 | 15 | 85 | 76 | 0 | 14 | 35 | 64 | 0 | 300 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 90 | 21.5 | 21 | 0 | 270 | 0 | 0 | 13 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1.2 | 221 | 0 | 2 | 265 | 0 | 0 | 43 | 0 | 0 | 216 | 0 | 0 | 0 | 1054 | 15 | 51 | 0 | 86 | 0 | 342 | 330 | 34 | 201 | 36 | 33 | 92 | 51 | 8 | 19 | 48 | 44 | 16 | 62 | 0 | 320 | 0 | 373 | 0 | 57 | 154 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 69 | 1 | 45.05 | 12 | 6869.75 | 907 | 358 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 1148 | 0 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.64 | 100 | 0 | 0 | 59.37 | 178 | 0 | 172 | 0 | 153 | 0 | 300 | 0 | 5.26 | 158 | 44 | 0 | 22 | 0 | 0 | 0 | 0 | 7.3 | 165 | 0.73 | 0 | 169 | 115 | 220 | 0 | 295 | 1087 | 0 | 6757.3 | 13627.05 | 108.34
12:00 | 7 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 416 | 0 | 35 | 125 | 76 | 0 | 15 | 35 | 152 | 0 | 300 | 250 | 0 | 0 | 30 | 0 | 0 | 0 | 28 | 90 | 21.5 | 20 | 0 | 270 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.5 | 220 | 0 | 2 | 265 | 0 | 0 | 50 | 0 | 0 | 217 | 0 | 0 | 0 | 1060 | 18 | 51 | 2 | 86 | 0 | 335 | 330 | 34 | 204 | 36 | 41 | 91 | 51 | 0 | 19 | 49 | 46 | 16 | 14 | 1 | 325 | 0 | 383 | 0 | 57 | 153 | 8 | 0 | 83 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 69 | 2 | 49.81 | 12 | 7065.81 | 918 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1160 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.49 | 110 | 0 | 0 | 56.06 | 185 | 0 | 179 | 0 | 160 | 0 | 300 | 0 | 5.49 | 160 | 44 | 0 | 34 | 0 | 0 | 0 | 0 | 7.6 | 195 | 0.49 | 0 | 171 | 115 | 220 | 0 | 297 | 1100 | 0 | 6851.13 | 13916.94 | 108.34
13:00 | 7 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 416 | 15 | 35 | 132 | 76 | 95 | 40 | 35 | 157 | 0 | 300 | 250 | 0 | 0 | 55 | 0 | 0 | 0 | 27 | 125 | 21.5 | 21 | 0 | 270 | 0 | 0 | 33 | 0 | 0 | 49 | 38 | 0 | 0 | 0 | 0.28 | 221 | 19 | 12 | 264 | 66 | 0 | 50 | 3 | 24 | 218 | 0 | 0 | 0 | 1059 | 10 | 51 | 45 | 86 | 0 | 335 | 330 | 34 | 204 | 36 | 80 | 90 | 97 | 0 | 19 | 48 | 46 | 16 | 10 | 20 | 315 | 0 | 365 | 0 | 57 | 153 | 8 | 0 | 83 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 66 | 2 | 45.83 | 12 | 7548.61 | 918 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1156 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.12 | 101 | 0 | 0 | 59.04 | 195 | 0 | 192 | 0 | 173 | 0 | 402 | 0 | 5.39 | 153 | 44 | 20 | 31 | 0 | 0 | 0 | 0 | 6.7 | 155 | 0.36 | 0 | 171 | 115 | 220 | 0 | 297 | 1020 | 0 | 6855.61 | 14404.22 | 108.34
14:00 | 7 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 48.9 | 17 | 132 | 76 | 95 | 40 | 35 | 155 | 0 | 300 | 247 | 0 | 0 | 35 | 0 | 0 | 0 | 23 | 125 | 21.5 | 15 | 0 | 270 | 0 | 0 | 30 | 0 | 0 | 33 | 38 | 0 | 0 | 0 | 0.16 | 220 | 33 | 6 | 265 | 67 | 0 | 50 | 17 | 31 | 218 | 0 | 0 | 0 | 1048 | 6 | 51 | 92 | 86 | 0 | 336 | 330 | 32 | 201 | 36 | 86 | 90 | 104 | 0 | 19 | 46 | 50 | 16 | 9 | 21 | 310 | 0 | 378 | 0 | 57 | 152 | 8 | 0 | 83 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 66 | 2 | 42.94 | 12 | 7216.5 | 919 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 1148 | 0 | 1016.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.98 | 73 | 0 | 0 | 49.95 | 195 | 0 | 194 | 0 | 201 | 0 | 404 | 0 | 4.78 | 154 | 44 | 35 | 30 | 0 | 0 | 0 | 0 | 5.8 | 160 | 0.48 | 0 | 171 | 115 | 220 | 0 | 297 | 1000 | 0 | 6902.62 | 14119.12 | 108.34
15:00 | 7 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 37.7 | 17 | 132 | 100 | 180 | 50 | 40 | 161 | 0 | 340 | 297 | 0 | 0 | 55 | 3 | 0 | 0 | 20 | 125 | 0 | 21 | 0 | 350 | 0 | 0 | 34 | 0 | 0 | 33 | 38 | 0 | 0 | 0 | 0.11 | 220 | 33 | 2 | 265 | 85 | 0 | 50 | 17 | 33 | 218 | 0 | 0 | 0 | 1064 | 6 | 51 | 102 | 86 | 0 | 336 | 330 | 31 | 201 | 35 | 89 | 90 | 100 | 0 | 10 | 102 | 36 | 34 | 1 | 27 | 315 | 0 | 378 | 0 | 57 | 152 | 8 | 0 | 83 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 71 | 1 | 17.36 | 12 | 7579.17 | 918 | 312 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1167 | 0 | 1020.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.77 | 62 | 0 | 0 | 16.79 | 201 | 0 | 198 | 0 | 203 | 0 | 414 | 0 | 2.41 | 154 | 44 | 35 | 23 | 0 | 0 | 0 | 0 | 1.2 | 133 | 0.23 | 0 | 170 | 115 | 220 | 0 | 295 | 1007 | 0 | 6820.1 | 14399.27 | 108.34
16:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 44.9 | 17 | 132 | 106 | 260 | 55 | 45 | 147 | 0 | 420 | 286 | 0 | 0 | 55 | 10 | 97 | 0 | 8 | 125 | 0 | 21 | 0 | 380 | 0 | 0 | 77 | 0 | 0 | 33 | 65 | 0 | 0 | 0 | 0.55 | 220 | 30 | 2 | 265 | 134 | 0 | 50 | 17 | 29 | 218 | 0 | 0 | 0 | 1068 | 1 | 51 | 92 | 90 | 0 | 340 | 330 | 31 | 188 | 35 | 89 | 90 | 68 | 0 | 3 | 56 | 42 | 43 | 2 | 27 | 300 | 0 | 318 | 0 | 57 | 149 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 72 | 1 | 8.19 | 12 | 7799.64 | 917 | 304 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1090 | 0 | 1006.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.84 | 28 | 0 | 0 | 23.6 | 190 | 0 | 179 | 0 | 187 | 0 | 336 | 0 | 1.87 | 154 | 44 | 0 | 14 | 0 | 0 | 0 | 0 | 1.3 | 72 | 0.19 | 0 | 165 | 115 | 220 | 0 | 295 | 910 | 0 | 6338.69 | 14138.33 | 108.34
17:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 46 | 46 | 132 | 111 | 277 | 55 | 55 | 150 | 0 | 340 | 290 | 0 | 0 | 55 | 78 | 96 | 0 | 3 | 125 | 21.5 | 21 | 0 | 380 | 0 | 0 | 95 | 0 | 0 | 33 | 67 | 0 | 0 | 0 | 0.13 | 219 | 32 | 12 | 265 | 135 | 0 | 50 | 17 | 29 | 218 | 0 | 0 | 0 | 1126 | 0 | 51 | 95 | 90 | 0 | 348 | 330 | 33 | 190 | 35 | 90 | 90 | 34 | 0 | 7 | 30 | 38 | 43 | 1 | 27 | 310 | 0 | 316 | 0 | 57 | 151 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 0 | 75 | 9 | 69 | 0 | 4.71 | 12 | 7918.34 | 918 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 1040 | 0 | 1001.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.51 | 7 | 0 | 0 | 8.43 | 175 | 0 | 168 | 0 | 152 | 0 | 343 | 0 | 0.76 | 154 | 44 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 25 | 0.02 | 0 | 168 | 115 | 220 | 0 | 295 | 890 | 0 | 6084.21 | 14002.55 | 108.34
18:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 44.2 | 25 | 132 | 120 | 276 | 55 | 55 | 141 | 0 | 340 | 300 | 0 | 0 | 55 | 168 | 96 | 0 | 0 | 125 | 26.2 | 21 | 0 | 340 | 0 | 0 | 96 | 0 | 0 | 57 | 67 | 0 | 0 | 0 | 0 | 220 | 30 | 14 | 265 | 150 | 0 | 50 | 17 | 30 | 218 | 0 | 0 | 0 | 1148 | 0 | 51 | 117 | 95 | 0 | 346 | 330 | 34 | 198 | 34 | 90 | 90 | 37 | 0 | 7 | 103 | 44 | 43 | 0 | 27 | 305 | 0 | 334 | 0 | 57 | 150 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 74 | 9 | 69 | 0 | 0 | 12 | 8124.4 | 918 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 1224.84 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 9 | 0 | 0 | 0 | 7 | 0 | 0 | 162 | 0 | 163 | 0 | 151 | 0 | 360 | 0 | 0 | 154 | 44 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 115 | 180 | 0 | 304 | 980 | 0 | 6537.84 | 14662.24 | 108.34
19:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 47.5 | 17 | 132 | 120 | 276 | 55 | 55 | 153 | 0 | 300 | 282 | 0 | 0 | 55 | 332 | 97 | 0 | 0 | 125 | 26.6 | 21 | 0 | 270 | 13 | 0 | 106 | 0 | 23 | 66 | 76 | 0 | 0 | 0 | 0 | 221 | 68 | 16 | 265 | 134 | 0 | 50 | 17 | 101 | 219 | 0 | 0 | 0 | 1110 | 0 | 51 | 123 | 95 | 0 | 353 | 330 | 34 | 185 | 37 | 90 | 90 | 111 | 0 | 10 | 94 | 48 | 43 | 0 | 27 | 320 | 0 | 352 | 0 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 74 | 9 | 70 | 0 | 0 | 12 | 8388.1 | 891 | 280 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 0 | 1445.91 | 0 | 49 | 0 | 90 | 64 | 0 | 94 | 23 | 8 | 0 | 0 | 10 | 0 | 0 | 192 | 0 | 181 | 0 | 180 | 0 | 385 | 0 | 0 | 154 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 302 | 1210 | 17 | 7668.91 | 16057.01 | 108.34
19:30 | 50 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 47.5 | 17 | 132 | 121 | 276 | 55 | 55 | 144 | 0 | 300 | 280 | 0 | 0 | 55 | 328 | 36 | 0 | 0 | 125 | 27.2 | 21 | 0 | 270 | 17 | 0 | 85 | 0 | 15 | 66 | 76 | 0 | 0 | 0 | 0 | 221 | 97 | 24 | 265 | 75 | 0 | 50 | 17 | 97 | 219 | 0 | 0 | 0 | 1129 | 0 | 51 | 128 | 95 | 0 | 353 | 330 | 34 | 187 | 37 | 90 | 90 | 118 | 0 | 19 | 96 | 48 | 52.2 | 0 | 27 | 305 | 0 | 363 | 0 | 57 | 149 | 11 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 74 | 9 | 71 | 0 | 0 | 12 | 8347.9 | 892 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 1441.5 | 0 | 48 | 0 | 108 | 108 | 0 | 94 | 37 | 34 | 0 | 0 | 16 | 0 | 0 | 181 | 0 | 176 | 0 | 180 | 0 | 390 | 0 | 0 | 157 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 302 | 1222 | 17 | 7785.5 | 16133.4 | 108.34
20:00 | 65 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 43.8 | 17 | 132 | 121 | 276 | 55 | 55 | 139 | 0 | 300 | 285 | 0 | 0 | 55 | 331 | 36 | 0 | 0 | 125 | 27 | 21 | 0 | 270 | 27 | 0 | 88 | 0 | 24 | 66 | 76 | 0 | 0 | 0 | 0 | 221 | 102 | 28 | 265 | 73 | 0 | 50 | 17 | 93 | 220 | 0 | 0 | 0 | 1084 | 0 | 51 | 128 | 95 | 0 | 353 | 330 | 24 | 185 | 37 | 90 | 90 | 100 | 0 | 19 | 93 | 48 | 25 | 0 | 27 | 300 | 0 | 350 | 0 | 57 | 148 | 10 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 74 | 9 | 71 | 0 | 0 | 12 | 8262.8 | 891 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 0 | 1450.32 | 0 | 48 | 0 | 35 | 110 | 0 | 94 | 38 | 16 | 0 | 0 | 18 | 0 | 0 | 183 | 0 | 177 | 0 | 177 | 0 | 330 | 0 | 0 | 158 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 220 | 0 | 301 | 1226 | 17 | 7656.32 | 15919.12 | 108.34
21:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 43.5 | 17 | 132 | 121 | 293 | 55 | 55 | 140 | 0 | 300 | 286 | 0 | 0 | 55 | 328 | 36 | 0 | 0 | 125 | 26.8 | 21 | 0 | 270 | 21 | 0 | 50 | 0 | 7 | 66 | 74 | 0 | 0 | 0 | 0 | 221 | 96 | 24 | 265 | 45 | 0 | 50 | 17 | 95 | 220 | 0 | 0 | 0 | 1110 | 0 | 51 | 128 | 95 | 0 | 352 | 330 | 20 | 189 | 37 | 72 | 90 | 88 | 0 | 19 | 95 | 46 | 25 | 0 | 27 | 300 | 0 | 362 | 0 | 57 | 149 | 10 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 74 | 9 | 71 | 0 | 0 | 12 | 8129.3 | 891 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 1447 | 0 | 48 | 0 | 35 | 113 | 0 | 94 | 38 | 16 | 0 | 0 | 13 | 0 | 0 | 181 | 0 | 179 | 0 | 179 | 0 | 345 | 0 | 0 | 156 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 302 | 1225 | 17 | 7663 | 15792.3 | 108.34
22:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 44 | 17 | 133 | 121 | 293 | 55 | 55 | 139 | 0 | 300 | 291 | 0 | 0 | 55 | 328 | 36 | 0 | 0 | 125 | 26.8 | 21 | 0 | 270 | 15 | 0 | 41 | 0 | 14 | 66 | 74 | 0 | 0 | 0 | 0 | 221 | 85 | 27 | 265 | 15 | 0 | 50 | 17 | 93 | 221 | 0 | 0 | 0 | 1135 | 0 | 51 | 128 | 95 | 0 | 353 | 330 | 38 | 190 | 37 | 51 | 90 | 93 | 0 | 19 | 114 | 46 | 25 | 0 | 28 | 305 | 0 | 366 | 0 | 57 | 150 | 10 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 76 | 9 | 71 | 0 | 0 | 12 | 8148.8 | 891 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 1443 | 0 | 48 | 0 | 35 | 70 | 0 | 94 | 38 | 16 | 0 | 0 | 13 | 0 | 0 | 182 | 0 | 181 | 0 | 181 | 0 | 345 | 0 | 0 | 157 | 43 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 302 | 1230 | 17 | 7626 | 15774.8 | 108.34
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 45.5 | 17 | 149 | 121 | 293 | 55 | 55 | 143 | 0 | 300 | 293 | 0 | 0 | 55 | 326 | 36 | 0 | 0 | 125 | 26.8 | 21 | 0 | 270 | 13 | 0 | 45 | 0 | 11 | 66 | 67 | 0 | 0 | 0 | 0 | 222 | 67 | 31 | 265 | 16 | 0 | 50 | 17 | 93 | 220 | 0 | 0 | 0 | 1149 | 0 | 51 | 128 | 95 | 0 | 350 | 330 | 38 | 196 | 37 | 51 | 90 | 100 | 0 | 19 | 114 | 50 | 25 | 0 | 28 | 305 | 0 | 386 | 0 | 57 | 152 | 10 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 70 | 0 | 0 | 12 | 8192.3 | 892 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 1445 | 0 | 48 | 0 | 35 | 70 | 0 | 94 | 35 | 16 | 0 | 0 | 13 | 0 | 0 | 165 | 0 | 140 | 0 | 140 | 0 | 358 | 0 | 0 | 159 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 302 | 1232 | 17 | 7556 | 15748.3 | 108.34
Total KWH | 151056 | 1281600 | 466080 | 0 | 0 | 0 | 0 | 0 | 4863600 | 0 | 6639365 | 659160 | 310680 | 2735280 | 2345760 | 3091451 | 745274 | 795240 | 2306880 | 0 | 8396500 | 6893644 | 0 | 0 | 727032 | 2089865 | 1060000 | 0 | 191417 | 2796000 | 508200 | 488880 | 0 | 8421818.18 | 164345 | 0 | 1112640 | 0 | 100800 | 1006814 | 1463736 | 0 | 0 | 0 | 8281 | 5318747 | 887380 | 439680 | 6363636.36 | 899927 | 0 | 892320 | 206042.4 | 1142472 | 5112418 | 0 | 0 | 0 | 26181816 | 77220 | 1246080 | 1585745 | 2676364 | 0 | 8646900 | 7976000 | 817440 | 4743000 | 879264 | 1672320 | 2189490 | 1735680 | 43680 | 381810 | 2023500 | 1065600 | 810893 | 181491 | 492576 | 7513000 | 0 | 8709000 | 0 | 1328400 | 3539700 | 175392 | 0 | 2014080 | 709248 | 0 | 427000 | 3394950 | 204840 | 1812000 | 199200 | 1820160 | 11950 | 300910 | 298560 | 180969279.94 | 21896000 | 7363872 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 520560 | 26800000 | 0 | 29020148 | 0 | 258092 | 0 | 369984 | 646368 | 0 | 637552 | 177544 | 95664 | 394612 | 671160 | 73000 | 0 | 379496 | 4332364 | 0 | 4403818 | 0 | 4287445 | 0 | 8509163 | 0 | 35220 | 3751000 | 1003636 | 1372393 | 199257 | 1252656 | 0 | 0 | 0 | 41087.4 | 1334160 | 3612 | 0 | 4843000 | 2753000 | 5409360 | 0 | 7199280 | 26398545.45 | 121200 | 167466248.85 | 348435528.79