## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-09-2025 | during | 23-09-2025 | during | 23-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 398 | 334 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 314 | 290 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 98 | 98 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 270 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 102 | 0 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 44.9 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 90 | 122 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24.5 | 24 | 33 | 33 | 28 | 28 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 245 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 53 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 87.5 | 87.5 | 51 | 87 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 32 | 144 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 12 | 21 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 480 | 480 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 380 | 718 | 718 | 425 | 425 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 1882.5 | 2614.9 | 5785.34 | 5857.34 | 4279.5 | 4405.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 218 | 195 | 200 | 195 | 200 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 72 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 67 | 48 | 78 | 48 | 78 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 20 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 36 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.17 | 0 | 0.5 | 0 | 0.5 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 40 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1194 | 1157 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 36 | 13 | 3 | 3 | 3 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 265 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1966.17 | 2226 | 3260.22 | 3298.72 | 3004.86 | 3043.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 211 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 350 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 37 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 93 | 195 | 195 | 147 | 147 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 122 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 12 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 96 | 96 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 11 | 86 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 88 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 9 | 81 | 115 | 115 | 92 | 92 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1179 | 1571 | 2419.56 | 2379.56 | 2106.06 | 2075.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-09-2025 | during | 23-09-2025 | during | 23-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 33 | 157.5 | 157.5 | 101 | 101 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 75 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 23.63 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 8 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 150.63 | 117 | 372.5 | 320.5 | 268.5 | 216.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 5 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 10 | 25 | 25 | 11 | 11 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 360 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1216 | 1182 | 1261 | 1261 | 1174 | 1174
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 242 | 232 | 410 | 410 | 362 | 362 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 42 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1048 | 1107 | 1234.2 | 1234.2 | 1234 | 1234
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2261 | 2268 | 3602.2 | 3552.2 | 3359 | 3309
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 303 | 471 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 100 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1140 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 181 | 220 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.08 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1819.08 | 2151 | 2147 | 2146 | 2132 | 2131
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 21.47 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 201 | 173 | 214 | 214 | 198 | 198 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 180 | 220 | 220 | 220 | 220 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 409 | 403 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.33 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1066.89 | 1446 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 28.45 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 29 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1956.14 | 2394 | 3189.37 | 3022.87 | 3099.11 | 2932.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 43 | 45 | 45 | 45 | 45 | 45 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 130 | 159 | 130 | 130 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 197 | 0 | 185.39 | 0 | 185.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 477.6 | 431 | 644.39 | 423 | 674.39 | 453
System Total |  |  |  |  | 28823.2 | 27829.875 | 12908.12 | 14954.9 | 22681.58 | 22261.19 | 20097.42 | 19740.03
Forecast Scenario (23-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14550 |  | 0 |  | 14550
|  |  |  | 1:00 | 14120 |  | 0 |  | 14120
|  |  |  | 2:00 | 13750 |  | 0 |  | 13750
|  |  |  | 3:00 | 13150 |  | 0 |  | 13150
|  |  |  | 4:00 | 12650 |  | 0 |  | 12650
|  |  |  | 5:00 | 12310 |  | 0 |  | 12310
|  |  |  | 6:00 | 11850 |  | 0 |  | 11850
|  |  |  | 7:00 | 10920 |  | 0 |  | 10920
|  |  |  | 8:00 | 10620 |  | 0 |  | 10620
|  |  |  | 9:00 | 11360 |  | 0 |  | 11360
|  |  |  | 10:00 | 12120 |  | 0 |  | 12120
|  |  |  | 11:00 | 12460 |  | 0 |  | 12460
|  |  |  | 12:00 | 12900 |  | 0 |  | 12900
|  |  |  | 13:00 | 13320 |  | 0 |  | 13320
|  |  |  | 14:00 | 13460 |  | 0 |  | 13460
|  |  |  | 15:00 | 13580 |  | 0 |  | 13580
|  |  |  | 16:00 | 13230 |  | 0 |  | 13230
|  |  |  | 17:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:00 | 13770 |  | 0 |  | 13770
|  |  |  | 18:30 | 14400 |  | 0 |  | 14400
|  |  |  | 19:00 | 15200 |  | 0 |  | 15200
|  |  |  | 19:30 | 15400 |  | 0 |  | 15400
|  |  |  | 20:00 | 15500 |  | 0 |  | 15500
|  |  |  | 21:00 | 15400 |  | 0 |  | 15400
|  |  |  | 22:00 | 15200 |  | 0 |  | 15200
|  |  |  | 23:00 | 15000 |  | 0 |  | 15000
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 12900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.52 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:54 hrs on 23-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-09-2025 | [28 empty] | Date: | 22-09-2025 | [28 empty] | Date: | 22-09-2025 | [28 empty] | Date: | 22-09-2025 | [28 empty] | Date: | 22-09-2025 | [14 empty] | Date: | 22-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 45.8 | 0 | 149 | 121 | 293 | 55 | 44 | 144 | 0 | 300 | 288 | 0 | 0 | 55 | 328 | 35 | 0 | 0 | 125 | 26.8 | 21 | 0 | 270 | 13 | 0 | 44 | 0 | 1 | 66 | 67 | 0 | 0 | 0 | 0 | 221 | 67 | 36 | 265 | 15 | 0 | 33 | 17 | 95 | 220 | 0 | 0 | 0 | 1107 | 0 | 51 | 130 | 95 | 0 | 355 | 330 | 37 | 183 | 37 | 51 | 90 | 100 | 0 | 19 | 114 | 50 | 25 | 0 | 28 | 310 | 0 | 354 | 0 | 57 | 152 | 10 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 70 | 0 | 0 | 12 | 8063.6 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 1444 | 0 | 48 | 0 | 35 | 70 | 0 | 94 | 28 | 16 | 0 | 0 | 13 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 330 | 0 | 0 | 152 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 220 | 0 | 303 | 1230 | 17 | 7476 | 15539.6 | 108.34
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 385 | 44.1 | 0 | 115 | 90 | 195 | 30 | 35 | 140 | 0 | 300 | 291 | 0 | 0 | 50 | 328 | 0 | 0 | 0 | 125 | 26.8 | 21 | 0 | 270 | 0 | 0 | 40 | 0 | 5 | 66 | 60 | 0 | 0 | 0 | 0 | 220 | 61 | 36 | 265 | 0 | 0 | 33 | 0 | 90 | 220 | 0 | 0 | 0 | 1131 | 0 | 51 | 130 | 95 | 0 | 320 | 330 | 38 | 189 | 37 | 51 | 0 | 100 | 0 | 19 | 114 | 48 | 25 | 0 | 28 | 305 | 0 | 366 | 0 | 57 | 137 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0 | 12 | 7625.9 | 891 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 0 | 1449 | 0 | 40 | 0 | 35 | 70 | 0 | 94 | 21 | 0 | 0 | 0 | 13 | 0 | 0 | 140 | 0 | 140 | 0 | 69 | 0 | 300 | 0 | 0 | 131 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 180 | 0 | 303 | 1120 | 17 | 7122 | 14747.9 | 108.33
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 385 | 41.5 | 0 | 79 | 90 | 45 | 0 | 0 | 90 | 0 | 300 | 287 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 125 | 0 | 21 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 66 | 60 | 0 | 0 | 0 | 0 | 219 | 17 | 36 | 265 | 0 | 0 | 19 | 0 | 68 | 217 | 0 | 0 | 0 | 1106 | 0 | 51 | 80 | 95 | 0 | 320 | 330 | 38 | 181 | 37 | 51 | 0 | 100 | 0 | 19 | 114 | 46 | 0 | 0 | 28 | 300 | 0 | 354 | 0 | 57 | 139 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0 | 12 | 7033.5 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 1452 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 132 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 115 | 180 | 0 | 303 | 1090 | 0 | 6842 | 13875.5 | 108.33
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 385 | 29 | 0 | 68 | 90 | 45 | 0 | 0 | 54 | 0 | 300 | 285 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 125 | 8 | 21 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 0 | 0 | 0 | 0 | 218 | 0 | 36 | 265 | 0 | 0 | 19 | 0 | 17 | 217 | 0 | 0 | 0 | 1150 | 0 | 51 | 20 | 95 | 0 | 320 | 330 | 38 | 185 | 37 | 51 | 0 | 100 | 0 | 19 | 47 | 44 | 0 | 0 | 28 | 300 | 0 | 357 | 0 | 57 | 137 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0 | 7 | 6782 | 890 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 1284 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 135 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 115 | 180 | 0 | 303 | 1000 | 0 | 6407 | 13189 | 108.33
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 385 | 29.5 | 0 | 68 | 90 | 0 | 0 | 0 | 44 | 0 | 300 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 23 | 0 | 0 | 0 | 0 | 217 | 0 | 38 | 265 | 0 | 0 | 19 | 0 | 15 | 217 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 95 | 0 | 320 | 330 | 38 | 192 | 37 | 51 | 0 | 85 | 0 | 19 | 17 | 36 | 0 | 0 | 0 | 305 | 0 | 376 | 0 | 57 | 142 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0 | 3 | 6475.5 | 891 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 330 | 0 | 0 | 131 | 43 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 180 | 0 | 303 | 990 | 0 | 6128 | 12603.5 | 108.33
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 385 | 0 | 0 | 60 | 90 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 38 | 265 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1065 | 0 | 51 | 0 | 95 | 0 | 320 | 330 | 38 | 193 | 37 | 40 | 0 | 51 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 305 | 0 | 386 | 0 | 57 | 140 | 8 | 0 | 79 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0 | 8 | 6303 | 891 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 0 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 330 | 0 | 0 | 129 | 43 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 115 | 180 | 0 | 303 | 988 | 0 | 5982 | 12285 | 108.32
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 385 | 0 | 0 | 50 | 90 | 0 | 0 | 0 | 0 | 0 | 300 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.08 | 219 | 0 | 38 | 265 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 95 | 0 | 300 | 305 | 38 | 186 | 34 | 16 | 0 | 17 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 350 | 0 | 57 | 142 | 8 | 0 | 79 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 71 | 0 | 0.41 | 12 | 5973.99 | 892 | 269 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 971 | 0 | 1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 328 | 0 | 0.01 | 131 | 43 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 161 | 115 | 180 | 0 | 303 | 950 | 0 | 5877.01 | 11851 | 108.32
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 385 | 0 | 0 | 50 | 90 | 0 | 0 | 0 | 0 | 0 | 300 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.81 | 220 | 0 | 39 | 265 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 809 | 2 | 10 | 0 | 25 | 0 | 300 | 280 | 35 | 181 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 0 | 325 | 0 | 57 | 136 | 8 | 0 | 41 | 30 | 0 | 18 | 165 | 0 | 82 | 9 | 70 | 0 | 6.5 | 12 | 5492.31 | 892 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 846 | 0 | 938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 4.86 | 140 | 0 | 140 | 0 | 0 | 0 | 329 | 0 | 0.42 | 131 | 43 | 35 | 5 | 34 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 165 | 100 | 180 | 0 | 305 | 800 | 0 | 5436.28 | 10928.59 | 108.32
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 26 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 312 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1.54 | 220 | 0 | 16 | 265 | 0 | 0 | 15 | 0 | 0 | 180 | 0 | 0 | 0 | 893 | 5 | 10 | 0 | 25 | 0 | 300 | 280 | 10 | 209 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 34 | 0 | 2 | 0 | 310 | 0 | 370 | 0 | 57 | 143 | 8 | 0 | 41 | 30 | 0 | 18 | 166 | 0 | 82 | 9 | 64 | 0 | 8.82 | 12 | 5254.36 | 891 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 790 | 0 | 821.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 3 | 0 | 0 | 3.52 | 140 | 0 | 140 | 0 | 0 | 0 | 393 | 0 | 0.33 | 130 | 44 | 35 | 15 | 34 | 0 | 0 | 0 | 3 | 94 | 0 | 0 | 180 | 100 | 180 | 0 | 305 | 750 | 0 | 5365.9 | 10620.26 | 108.32
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 0 | 0 | 0 | 420 | 310 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 2.08 | 220 | 0 | 3 | 265 | 0 | 0 | 18 | 0 | 0 | 218 | 0 | 0 | 0 | 963 | 6 | 17 | 0 | 25 | 0 | 352 | 330 | 15 | 210 | 34 | 0 | 0 | 0 | 0 | 5 | 0 | 32 | 0 | 9 | 0 | 315 | 0 | 373 | 0 | 57 | 158 | 8 | 0 | 68 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 27 | 0 | 8.54 | 12 | 5738.62 | 892 | 274 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 844 | 0 | 820.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 3 | 0 | 0 | 9.52 | 178 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 0.49 | 130 | 43 | 35 | 25 | 34 | 0 | 0 | 0 | 5 | 108 | 0 | 0 | 178 | 115 | 220 | 0 | 303 | 790 | 0 | 5623.07 | 11361.69 | 108.32
10:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 50 | 60 | 0 | 0 | 10 | 0 | 0 | 450 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 90 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.9 | 221 | 0 | 2 | 265 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1119 | 6 | 51 | 0 | 26 | 0 | 355 | 330 | 32 | 192 | 35 | 0 | 0 | 0 | 2 | 5 | 0 | 30 | 0 | 20 | 0 | 310 | 0 | 355 | 0 | 57 | 156 | 8 | 0 | 79 | 30 | 0 | 18 | 165 | 0 | 82 | 9 | 30 | 2 | 27.55 | 12 | 6069.45 | 891 | 269 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 996 | 0 | 927.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 13 | 0 | 0 | 13.91 | 190 | 0 | 193 | 0 | 0 | 0 | 408 | 0 | 1.24 | 129 | 43 | 35 | 31 | 34 | 0 | 0 | 0 | 6 | 109 | 0.06 | 0 | 170 | 115 | 220 | 0 | 302 | 910 | 0 | 6055.21 | 12124.66 | 108.32
11:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 12 | 50 | 60 | 0 | 0 | 35 | 0 | 0 | 450 | 335 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 90 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.86 | 220 | 0 | 2 | 265 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1150 | 5 | 51 | 0 | 26 | 0 | 353 | 330 | 34 | 195 | 35 | 0 | 0 | 0 | 8 | 5 | 0 | 38 | 0 | 20 | 0 | 310 | 0 | 380 | 0 | 57 | 154 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 32 | 2 | 41.45 | 12 | 6210.81 | 892 | 264 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 977 | 0 | 958.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6 | 23 | 0 | 0 | 18.42 | 190 | 0 | 199 | 0 | 0 | 0 | 404 | 0 | 1.55 | 132 | 43 | 35 | 29 | 34 | 0 | 0 | 0 | 5.6 | 180 | 0.09 | 0 | 170 | 115 | 220 | 0 | 302 | 965 | 0 | 6249.23 | 12460.04 | 108.32
12:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 12 | 50 | 90 | 0 | 0 | 35 | 32 | 0 | 450 | 314 | 0 | 0 | 0 | 331 | 0 | 0 | 13 | 70 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 4.17 | 221 | 0 | 3 | 265 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1194 | 7 | 51 | 0 | 26 | 0 | 344 | 330 | 36 | 209 | 33 | 9 | 0 | 11 | 0 | 17 | 34 | 38 | 0 | 41 | 0 | 315 | 0 | 385 | 0 | 57 | 155 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 77 | 9 | 32 | 1 | 23.63 | 8 | 6394.3 | 891 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 1048 | 0 | 1066.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.47 | 29 | 0 | 0 | 28.45 | 201 | 0 | 198 | 0 | 0 | 0 | 409 | 0 | 2.33 | 130 | 43 | 35 | 31 | 34 | 0 | 0 | 0 | 7.6 | 197 | 0.08 | 0 | 181 | 115 | 220 | 0 | 303 | 1000 | 0 | 6513.82 | 12908.12 | 108.32
13:00 | 0 | 34 | 12 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 42 | 17 | 90 | 90 | 60 | 0 | 36 | 151 | 0 | 450 | 295 | 0 | 0 | 30 | 335 | 0 | 0 | 6 | 70 | 23.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 1.12 | 220 | 0 | 12 | 265 | 0 | 0 | 35 | 0 | 18 | 217 | 0 | 0 | 0 | 1140 | 8 | 51 | 51 | 26 | 0 | 349 | 330 | 38 | 192 | 34 | 61 | 0 | 71 | 0 | 17 | 34 | 40 | 0 | 35 | 0 | 310 | 0 | 373 | 0 | 57 | 154 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 85 | 9 | 32 | 2 | 40.36 | 6 | 6793.68 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1096 | 0 | 1038.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.98 | 47 | 3 | 0 | 21.47 | 202 | 0 | 191 | 0 | 0 | 0 | 405 | 0 | 2.47 | 129 | 41 | 35 | 18 | 34 | 0 | 0 | 0 | 7.4 | 176 | 0.22 | 0 | 169 | 115 | 220 | 0 | 303 | 1000 | 0 | 6527.98 | 13321.66 | 108.32
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 10 | 48.5 | 35 | 132 | 90 | 60 | 0 | 47 | 149 | 0 | 450 | 298 | 0 | 0 | 55 | 332 | 0 | 0 | 22 | 70 | 23.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.93 | 219 | 0 | 4 | 265 | 0 | 0 | 50 | 0 | 33 | 218 | 0 | 0 | 0 | 1165 | 10 | 51 | 107 | 26 | 0 | 347 | 330 | 39 | 195 | 34 | 91 | 0 | 95 | 0 | 6 | 30 | 42 | 0 | 17 | 0 | 300 | 0 | 383 | 0 | 57 | 151 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 76 | 9 | 32 | 1 | 44.2 | 6 | 7014.83 | 891 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 1076 | 0 | 1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.84 | 78 | 0 | 0 | 46.07 | 191 | 0 | 187 | 0 | 0 | 0 | 353 | 0 | 4.86 | 129 | 43 | 35 | 5 | 34 | 0 | 0 | 0 | 6.4 | 120 | 0.17 | 0 | 170 | 115 | 220 | 0 | 323 | 992 | 0 | 6445.34 | 13460.17 | 108.32
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 15 | 49 | 28 | 126 | 107 | 60 | 0 | 55 | 158 | 0 | 450 | 297 | 0 | 0 | 55 | 332 | 0 | 0 | 18 | 35 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 0.07 | 219 | 0 | 3 | 265 | 0 | 0 | 50 | 0 | 32 | 215 | 0 | 0 | 0 | 1144 | 7 | 51 | 113 | 43 | 0 | 346 | 330 | 38 | 193 | 34 | 88 | 0 | 99 | 0 | 18 | 32 | 42 | 0 | 19 | 0 | 305 | 0 | 386 | 0 | 57 | 153 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 76 | 9 | 32 | 1 | 28.76 | 6 | 7050.83 | 891 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1093 | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.22 | 67 | 0 | 0 | 34.03 | 193 | 0 | 185 | 0 | 0 | 0 | 355 | 0 | 3.55 | 129 | 44 | 35 | 18 | 34 | 0 | 0 | 0 | 4.1 | 139 | 0.03 | 0 | 170 | 115 | 220 | 0 | 327 | 994 | 0 | 6478.93 | 13529.76 | 108.32
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 10 | 46.4 | 35 | 97 | 122 | 60 | 0 | 55 | 147 | 0 | 450 | 295 | 0 | 0 | 17 | 332 | 0 | 0 | 10 | 35 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 0.72 | 221 | 0 | 4 | 265 | 0 | 0 | 50 | 0 | 33 | 215 | 0 | 0 | 0 | 1145 | 4 | 51 | 80 | 53 | 0 | 346 | 330 | 37 | 192 | 34 | 90 | 0 | 85 | 0 | 18 | 14 | 38 | 0 | 16 | 0 | 305 | 0 | 376 | 0 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 33 | 1 | 10.97 | 6 | 6878.09 | 892 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 1079 | 0 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.77 | 16 | 0 | 0 | 12.46 | 182 | 0 | 184 | 0 | 0 | 0 | 353 | 0 | 1.4 | 131 | 44 | 35 | 12 | 0 | 0 | 0 | 0 | 3 | 55 | 0.12 | 0 | 169 | 115 | 220 | 0 | 370 | 1062 | 0 | 6360.75 | 13238.84 | 108.32
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 78 | 39 | 24 | 64 | 122 | 60 | 0 | 55 | 125 | 0 | 450 | 295 | 0 | 0 | 17 | 332 | 0 | 0 | 5 | 35 | 24 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 28 | 0 | 0 | 0 | 0.28 | 221 | 0 | 6 | 265 | 0 | 0 | 50 | 0 | 33 | 215 | 0 | 0 | 0 | 1150 | 1 | 51 | 80 | 53 | 0 | 347 | 330 | 37 | 193 | 38 | 50 | 0 | 51 | 3 | 18 | 14 | 34 | 0 | 4 | 0 | 310 | 0 | 373 | 0 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 33 | 0 | 5.05 | 0 | 6771.33 | 892 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 1061 | 0 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.52 | 5 | 0 | 0 | 5.24 | 181 | 0 | 181 | 0 | 0 | 0 | 354 | 0 | 0.54 | 166 | 44 | 35 | 3 | 0 | 0 | 0 | 0 | 0.5 | 16 | 0.03 | 0 | 170 | 115 | 220 | 0 | 368 | 1090 | 0 | 6331.83 | 13103.16 | 108.32
18:00 | 7 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 350 | 15 | 30 | 53 | 122 | 95 | 4 | 55 | 140 | 0 | 450 | 295 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 7 | 0 | 11 | 38 | 33 | 0 | 0 | 0 | 0 | 222 | 4 | 7 | 265 | 47 | 0 | 50 | 3 | 36 | 215 | 0 | 0 | 0 | 1160 | 0 | 51 | 92 | 53 | 0 | 320 | 300 | 37 | 192 | 38 | 51 | 0 | 47 | 9 | 16 | 53 | 44 | 3 | 0 | 0 | 310 | 0 | 331 | 0 | 57 | 145 | 8 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 33 | 0 | 0 | 0 | 7086 | 892 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 0 | 1327 | 0 | 0 | 0 | 10 | 1 | 0 | 52 | 7 | 25 | 0 | 0 | 12 | 0 | 0 | 172 | 0 | 181 | 0 | 0 | 0 | 350 | 0 | 0 | 163 | 44 | 75 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 220 | 0 | 368 | 1090 | 0 | 6591 | 13677 | 108.32
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 380 | 44.9 | 21 | 53 | 122 | 245 | 30 | 55 | 144 | 0 | 350 | 290 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 0 | 0 | 0 | 36 | 0 | 13 | 66 | 67 | 0 | 0 | 0 | 0 | 222 | 40 | 20 | 265 | 0 | 0 | 50 | 0 | 72 | 218 | 0 | 0 | 0 | 1157 | 0 | 51 | 122 | 93 | 0 | 350 | 330 | 37 | 211 | 38 | 81 | 0 | 86 | 9 | 19 | 88 | 44 | 0 | 0 | 12 | 300 | 0 | 360 | 5 | 57 | 152 | 10 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 75 | 9 | 33 | 0 | 0 | 0 | 7710.9 | 891 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 1446 | 0 | 48 | 0 | 0 | 0 | 0 | 96 | 25 | 0 | 0 | 0 | 23 | 0 | 0 | 173 | 0 | 180 | 0 | 0 | 0 | 403 | 0 | 0 | 159 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 100 | 220 | 0 | 471 | 1140 | 0 | 7244 | 14954.9 | 108.32
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 385 | 44.9 | 17 | 53 | 122 | 130 | 0 | 55 | 147 | 0 | 350 | 288 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 66 | 67 | 0 | 0 | 0 | 0 | 222 | 48 | 25 | 265 | 0 | 0 | 50 | 0 | 82 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 100 | 0 | 350 | 330 | 37 | 212 | 37 | 90 | 0 | 60 | 9 | 19 | 88 | 46 | 0 | 0 | 29 | 315 | 0 | 361 | 20 | 57 | 152 | 10 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7589.4 | 892 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1459 | 0 | 48 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 178 | 0 | 0 | 0 | 406 | 0 | 0 | 165 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 115 | 220 | 0 | 470 | 1162 | 0 | 7223 | 14812.4
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 385 | 46.7 | 17 | 53 | 122 | 60 | 0 | 55 | 148 | 0 | 350 | 288 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 67 | 0 | 0 | 0 | 0 | 222 | 50 | 28 | 265 | 0 | 0 | 50 | 0 | 83 | 218 | 0 | 0 | 0 | 1152 | 0 | 51 | 80 | 132 | 0 | 353 | 330 | 37 | 213 | 37 | 90 | 0 | 65 | 9 | 19 | 88 | 46 | 0 | 0 | 29 | 310 | 0 | 370 | 20 | 57 | 154 | 10 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7525.2 | 891 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 1448 | 0 | 48 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 178 | 0 | 0 | 0 | 402 | 0 | 0 | 135 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 471 | 1162 | 0 | 7267 | 14792.2 | 108.32
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 386 | 46.4 | 17 | 53 | 122 | 0 | 0 | 55 | 146 | 0 | 320 | 285 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 16 | 0 | 0 | 0 | 0 | 221 | 48 | 14 | 265 | 0 | 0 | 18 | 6 | 82 | 221 | 0 | 0 | 0 | 1153 | 0 | 51 | 40 | 137 | 0 | 355 | 330 | 41 | 213 | 39 | 90 | 0 | 62 | 0 | 19 | 88 | 44 | 0 | 0 | 29 | 305 | 0 | 376 | 20 | 57 | 153 | 10 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7348.9 | 891 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1193 | 0 | 1455.73 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 178 | 0 | 0 | 0 | 403 | 0 | 0 | 125 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 511 | 1162 | 0 | 7300.73 | 14649.63 | 108.32
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 386 | 36.2 | 0 | 53 | 122 | 0 | 0 | 55 | 142 | 0 | 320 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 0 | 0 | 0 | 222 | 34 | 28 | 265 | 0 | 0 | 40 | 8 | 50 | 222 | 0 | 0 | 0 | 1153 | 0 | 51 | 0 | 100 | 0 | 356 | 330 | 41 | 206 | 39 | 90 | 0 | 62 | 0 | 19 | 88 | 48 | 0 | 0 | 29 | 310 | 0 | 366 | 20 | 57 | 150 | 10 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7163.2 | 892 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1451.57 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 178 | 0 | 0 | 0 | 400 | 0 | 0 | 164 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 562 | 1155 | 0 | 7366.57 | 14529.77 | 108.32
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 386 | 30.5 | 0 | 23 | 123 | 0 | 0 | 55 | 144 | 0 | 320 | 302 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 26 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 29 | 265 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 100 | 0 | 355 | 330 | 41 | 184 | 39 | 90 | 0 | 65 | 0 | 19 | 105 | 48 | 0 | 0 | 29 | 305 | 0 | 385 | 0 | 57 | 144 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 50 | 0 | 0 | 0 | 6922.5 | 892 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 0 | 1455.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 178 | 0 | 0 | 0 | 355 | 0 | 0 | 164 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 598 | 1156 | 0 | 7315.23 | 14237.73 | 108.32
Total KWH | 8640 | 798720 | 276960 | 0 | 0 | 0 | 0 | 0 | 7729200 | 0 | 5967530 | 615960 | 269280 | 1537344 | 2290560 | 1151171 | 106216 | 783770 | 2102400 | 0 | 8857500 | 7143215 | 0 | 0 | 399154 | 7607149 | 22080 | 0 | 75463 | 2173200 | 456000 | 460440 | 0 | 1050909.09 | 28855 | 10036 | 85440 | 0 | 305760 | 501364 | 470980 | 0 | 0 | 0 | 16316 | 5098960 | 318650 | 477120 | 6370909.09 | 45164 | 0 | 680640 | 44463.6 | 811272 | 5033872 | 0 | 0 | 0 | 26361815 | 64260 | 1182868 | 1167563 | 1672727 | 0 | 8484800 | 7860000 | 854880 | 4798000 | 862920 | 1296960 | 116280 | 1412160 | 47880 | 291460 | 1112640 | 945600 | 58459 | 212855 | 246800 | 7475000 | 0 | 9230000 | 63000 | 1339200 | 3558518 | 189384 | 0 | 1866240 | 719424 | 0 | 426000 | 4405890 | 0 | 1880400 | 201600 | 1110720 | 8500 | 232840 | 157440 | 164097745.78 | 21582545 | 6050016 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 290880 | 25054500 | 0 | 28825398 | 0 | 253570 | 0 | 121536 | 209280 | 0 | 402208 | 44696 | 26909 | 135881 | 295560 | 64620 | 0 | 204752 | 4158818 | 0 | 4289291 | 0 | 385873 | 0 | 8848727 | 0 | 19800 | 3418000 | 993599 | 1720784 | 211569 | 1547529 | 0 | 0 | 0 | 47310.72 | 1245600 | 868 | 0 | 4931000 | 2722000 | 5235000 | 0 | 8813664 | 25605818.18 | 20400 | 158690001.9 | 322787747.68

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12908.12 | MW | 12:00 Hr. | Energy Generated |  |  | 322.7877 |  | MKWHr.
| Day Peak Demand |  |  | 12908.12 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.198 |  | MKWHr.
| Evening Peak Generation |  |  | 14954.9 | MW | 19:00 Hr. | Energy Demand |  |  | 323.9857 |  | MKWHr.
| Evening Peak Demand |  |  | 15105.38 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.3 |  | °C
| Minimum Generation of the Day |  |  | 10620.26 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 974.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 15539.6 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.0148 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.294 | 0 | 12.5134 | 0 | 0 | 0.075463 | 0 | 0 | 51.8829 | Gas | 133.0021 | Gas | 478867361.4753
| Chattogram Zone |  |  | 5.511 | 32.7327 | 2.9969 | 0 | 5.099 | 0.080576 | 0 | 0.30576 | 46.7259 | Coal | 101.5493 | Coal | 597251492.6194
| Cumilla Zone |  |  | 26.1239 | 0 | 5.3425 | 0 | 0 | 0.21285 | 0.9456 | 0 | 32.6249 | HFO | 27.5037 | HFO | 504586729.258
| Mymensingh Zone |  |  | 1.1107 | 0 | 2.2394 | 0 | 0 | 0.24134 | 0 | 0 | 3.5915 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2727 | Hydro | 5.099 | Hydro | 509896
| Khulna Zone |  |  | 6.05 | 25.0545 | 0 | 0 | 0 | 0.29088 | 22.4945 | 0 | 53.8899 | Solar | 3.0625 | Solar | 49990267.5812
| Barishal Zone |  |  | 7.957 | 39.3505 | 0.0204 | 0 | 0 | 0.000868 | 0 | 0 | 47.3288 | Import | 52.2655 | Import | 305789299.89
| Rajshahi Zone |  |  | 17.6827 | 0 | 1.1228 | 0 | 0 | 0.65599 | 28.8254 | 0 | 48.2869 | Wind | 0.30576 | Wind | 4506902.4
| Rangpur Zone |  |  | 0 | 4.4116 | 3.2683 | 0 | 0 | 1.5045 | 0 | 0 | 9.1844
| Total |  |  | 133.0021 | 101.5493 | 27.5037 | 0 | 5.099 | 3.0625 | 52.2655 | 0.30576 | 322.7877
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 478867361.4753 |  | Hydro | 509896
|  |  |  | Coal | 597251492.6194 |  | Solar | 49990267.5812
|  |  |  | HFO | 504586729.258 |  | Import | 305789299.89
|  |  |  | HSD | 0 |  | Wind | 4506902.4
[5 empty] | Total: | 194,15,01,949 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5825 | Peak Hr Flow | 891.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33355464.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.8254 | Peak Hr Flow | 1446.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2334 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9456 | Peak Hr Flow | 44.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2872 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.3535 | Peak Hr Flow | 2381.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5192
|  |  |  | Chattogram |  | 0 |  | 1384
|  |  |  | Cumilla |  | 0 |  | 1329
|  |  |  | Mymensingh |  | 144 |  | 1188
|  |  |  | Sylhet |  | 0 |  | 669
|  |  |  | Khulna |  | 0 |  | 1682
|  |  |  | Barishal |  | 0 |  | 423
|  |  |  | Rajshahi |  | 0 |  | 1474
|  |  |  | Rangpur |  | 0 |  | 1035
|  |  |  | Total |  | 144 |  | 14376
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:16 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 08:16 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 08:16 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 08:22 | Hasnabad 230/132kV S/S AUTO TR-3 LT is restored.
|  | 08:22 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 08:22 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 08:23 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
|  | 08:23 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 08:24 | Hasnabad 132/33kV S/S 132kV Main Bus is restored.
|  | 08:24 | Hasnabad 132/33kV S/S 132kV Reserve Bus is restored.
|  | 08:24 | Hasnabad 132/33kV S/S 132kV Reserve Bus is restored.
| 08:37 | 12:23 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to TR-06 Shutdown Bus Section-05
Taken by PBS
| 08:39 | 12:22 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to TR-06 Shutdown Bus Section-05
Taken by PBS
| 08:44 | 17:19 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Partial
discharge monitor checking
| 08:44 | 17:19 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Partial
discharge monitor checking
| 08:50 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 09:29 |  | Madunaghat 132/33kV S/S ATR-1(705T) LT Scheduled S/D Due to Maintenance of fire
protection system
| 09:30 |  | Madunaghat 132/33kV S/S ATR-1(705T) HT Scheduled S/D
|  | 09:42 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
| 09:48 | 09:48 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Forced S/D Due to Emergency maintenance
work.
| 09:49 | 10:11 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Tripped showing REL670 relays.
| 10:17 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is OFF with remarks:-
|  | 10:49 | Gopalganj-Madhumati 132kV Ckt-1 is restored.
|  | 10:50 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT is restored.
|  | 10:50 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT is restored.
| 11:05 | 14:15 | Palashbari 132/33kV S/S TR2-404T LT Forced S/D Due to T-2 ট্রান্সফরমারের ৩৩ কেভি B phase
bushing to Jac BUS twin conductor loop এর Strands কেটে যাওয়ায় তা পরিবর্তন কাজের জন্য
| 11:06 | 14:14 | Palashbari 132/33kV S/S TR2-404T HT Forced S/D Due to T-2 ট্রান্সফরমারের ৩৩ কেভি B phase
bushing to Jac BUS twin conductor loop এর Strands কেটে যাওয়ায় তা পরিবর্তন কাজের জন্য
|  | 11:15 | BIPTC S/S 20DF22 is restored.
|  | 13:04 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 13:04 | 15:31 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Maintenance work
| 13:04 | 15:32 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Maintenance work
| 13:07 | 14:35 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to
Construction safety net remove
| 13:09 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT11 was sync.
| 14:10 |  | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Naogaon 132/33kV end Due to Pile
casting work of terminal gantry under G to G project.
| 14:15 | 16:18 | Srinagar 132/33kV S/S Tr-01 HT Tripped showing Bus-bar protection P742 relay relays Due | [7 empty] | 15.0MW load
|  |  | to ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ ট্রিপ | [7 empty] | interrup.
করে।
| 14:15 | 16:18 | Srinagar 132/33kV S/S Tr-01 LT Tripped showing Overcurrent protection P142 relay relays | [7 empty] | 15.0MW load
|  |  | Due to ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ | [7 empty] | interrup.
ট্রিপ করে।
| 14:15 |  | At Sreenagar 132/33kV substation, a sky wire tore and fell on the 33kV bus. Consequently,
the 33kV incomers of both T-1 and T-2 transformers tripped, causing a full
interruption of about 34 MW.
| 14:33 | 15:03 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance
Relay and Lock out relay relays Due to Transient Fault
| 14:49 | 17:32 | New Tongi S/S Tr-2(4161-3) Scheduled S/D Due to DESCO Project work.
| 14:59 |  | Around 120 MW interruption occurred from 14:59 hrs to 15:16 hrs at Mymensingh 132/33kV
grid substation, as both T-1 and T-2 transformers tripped due to a fault on the 33kV Aqua
feeder. At 15:16 hrs, only T-2 transformer was switched on and is running in parallel
with T-3 transformer. T-1 transformer could not be switched on due to a problem with its
33kV incomer breaker, which requires inspection as informed by the grid personnel. At
present, around 50 MW load shedding is occurring.
| 15:03 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT12 was sync.
| 15:07 | 16:18 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ | [7 empty] | 15.0MW load
|  |  | কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ ট্রিপ করে। ফলে ট্রান্সফরমার-০২ শাট ডাউন করা | [7 empty] | interrup.
প্রয়োজন হয়।
| 15:07 | 16:18 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ | [7 empty] | 15.0MW load
|  |  | কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ ট্রিপ করে। ফলে ট্রান্সফরমার-০২ শাট ডাউন করা | [7 empty] | interrup.
প্রয়োজন হয়।
| 15:22 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT12 tripped.
| 15:43 |  | A 522MVA 400/230kV transformer was charged from the 400kV side at Rooppur Substation for
the first time.
| 16:01 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT12 was sync.
| 16:18 |  | At Sreenagar 132/33kV substation, both T-1 and T-2 transformers were switched on, now no
interruption is occurring.
| 17:15 |  | JERA Meghnaghat Power Limited 718 MW CCPP ST was sync.
| 19:00 |  | Evening Peak Generation is 14954 MW.
| 20:10 | 21:44 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to 33 kv Bus Redhot Maintenance | [7 empty] | 40.0MW load
interrup.
| 20:11 | 21:42 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to 33 kv Bus Redhot Maintenance | [7 empty] | 40.0MW load
interrup.
| 06:00 |  | Minimum Generation 12364 MW
| 06:23 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 06:26 |  | Maniknagar 132/33kV S/S Transformer GT-2 HT Scheduled S/D Due to To built Cable Trench,by
DPDC.
| 06:45 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from BSRM 230/33kV end Due to Feni 230kV SS
work
| 06:46 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to Feni 230kV SS
work
| 07:01 |  | Bhandaria 132/33kV S/S Transformer-2 HT Project Work S/D Due to to change heat shrink
tube of termination kit of 33kv u/g cable
| 07:01 |  | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D Due to to change heat shrink
tube of termination kit of 33kv u/g cable
| 07:03 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to High temp point maintenance
| 07:03 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to High temp point maintenance
| 07:24 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to PDB's Redhot maintenace
| 07:25 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to PDB's Redhot maintenace
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 334 | 7729200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8857500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7143215 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 106216 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 22080 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 7607149 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 8640 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.9 | 615960 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 2290560 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 783770 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 399154 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 456000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 460440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 276960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 1151171 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 53 | 1537344 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 798720 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2102400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 75463 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 21 | 269280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 1050909.09 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 380 | 5967530 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2173200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2614.9 | 51882861.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 44463.6 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 64260 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 680640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5098960 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5033872 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 72 | 811272 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 470980 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 501364 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 477120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 36 | 85440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16316 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 10036 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 40 | 318650 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 28855 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 45164 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1157 | 26361815 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 305760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6370909.09 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2226 | 46725876.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 211 | 4798000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 350 | 8484800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7860000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 862920 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 37 | 854880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 93 | 1672727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1182868 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 1167563 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 12 | 246800 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 116280 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 86 | 1412160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 44 | 945600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 58459 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 291460 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1112640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 47880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 81 | 1296960 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 212855 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1571 | 32624852
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1110720 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 201600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1880400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 232840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 157440 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 117 | 3591500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 5 | 63000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1339200 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3558518 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719424 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1866240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4405890 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 426000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 189384 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7475000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 9230000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1182 | 29272656
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21582545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 232 | 6050016 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 290880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1107 | 25054500 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2268 | 53889941
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 471 | 8813664 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2722000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1140 | 25605818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5235000 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 20400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 220 | 4931000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 868 | -
Barishal Area Total |  |  |  |  | 2236 | 2151 | 47328750.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 135881 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 253570 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 44696 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 173 | 4158818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4289291 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 385873 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 403 | 8848727 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 64620 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 26909 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 402208 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 209280 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 121536 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446 | 28825398 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 204752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 295560 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2394 | 48286919
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 993599 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3418000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1547529 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47310.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1720784 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211569 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1245600 | -
Rangpur Area Total |  |  |  |  | 950 | 431 | 9184391.72
Eastern Grid Total |  |  |  |  | 17385.715 | 7710.9 | 164097745.78
Western Grid Total |  |  |  |  | 10444.16 | 7244 | 158690001.9
National Grid Total |  |  |  |  | 27829.875 | 14954.9 | 322787747.68
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-09-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9618.38 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4614.2 | MW
i) Dhaka area |  |  | 5192.06 |  | MW | i) Khulna area |  |  |  | 1682 | MW
ii) Chattogram area |  |  | 1384.5 |  | MW | ii) Barishal area |  |  |  | 422.8 | MW
iii) Cumilla area |  |  | 1328.82 |  | MW | iii) Rajshahi area |  |  |  | 1474.4 | MW
iv) Mymensingh area |  |  | 1044 |  | MW | iv) Rangpur area |  |  |  | 1035 | MW
v) Sylhet area |  |  | 669 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14232.58 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 84 | 18:30 | 133 | PHP | 9 | 07:00
2 | AKSML | 94 | 14:00 | 68 | Ishurdi | 82 | 19:00 | 134 | Pabna | 106 | 01:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 92 | 19:00 | 135 | Palashbari | 122 | 00:00
4 | Agargaon | 134 | 13:00 | 70 | Jamalpur | 128 | 07:00 | 136 | Panchagarh | 62 | 19:00
5 | Agrabad | 100 | 18:00 | 71 | Jashore | 146 | 00:00 | 137 | Patiya | 10.8 | 00:00
6 | Amnura | 32 | 00:00 | 72 | Jhenaidah | 135 | 00:00 | 138 | Patuakhali | 66 | 00:00
7 | Ashuganj | 88 | 00:00 | 73 | Joydebpur | 154 | 15:00 | 139 | Payra | 36 | 00:00
8 | BSRM | 146 | 04:00 | 74 | Joypurhat | 65 | 00:00 | 140 | Postogola | 73 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 16 | 15:00 | 141 | Purbachal | 22 | 00:00
10 | Bajitpur | 95 | 00:00 | 76 | KSRM | 30 | 19:30 | 142 | Purbasadipur | 129 | 18:30
11 | Bakulia | 95 | 18:30 | 77 | Kabirpur | 258 | 15:00 | 143 | Rahanpur | 40 | 00:00
12 | Banani | 50 | 13:00 | 78 | Kachua | 92 | 22:00 | 144 | Rahim | 29 | 09:00
13 | Bangabhaban | 22 | 10:00 | 79 | Kallyanpur | 114 | 00:00 | 145 | Rajbari | 86 | 01:00
14 | Barapukuria | 70 | 01:00 | 80 | Kalurghat | 40 | 10:00 | 146 | Rajendrapur | 131 | 18:30
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 79 | 16:00 | 147 | Rajshahi | 112 | 00:00
16 | Barishal | 102 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 102 | 13:00
17 | Barishal-230 | 90 | 18:30 | 83 | Kasba | 36 | 21:00 | 149 | Ramganj | 108 | 00:00
18 | Baroaulia | 68 | 16:00 | 84 | Kazla | 101 | 18:30 | 150 | Rampur | 41 | 00:00
19 | Baroirhat | 69 | 00:00 | 85 | Keranigonj | 91 | 18:00 | 151 | Rangamati | 17 | 18:30
20 | Bashundhara | 199 | 14:00 | 86 | Khagrachori | 34 | 18:30 | 152 | Rangpur | 166 | 18:30
21 | BashundharaCement | 0 | 00:00 | 87 | Khulna | 71 | 13:00 | 153 | Ruppur | 7.4 | 16:00
22 | Beanibazar | 88 | 20:00 | 88 | Khulshi | 183 | 19:00 | 154 | SSM | 14 | 00:00
23 | Benapole | 66 | 00:00 | 89 | Kishoreganj | 142 | 00:00 | 155 | Saidpur | 111 | 18:30
24 | Bhaluka | 156 | 19:00 | 90 | Kodda | 283 | 21:00 | 156 | Satkhira | 132 | 00:00
25 | Bhandaria | 88 | 13:00 | 91 | Kulaura | 56 | 00:00 | 157 | Satmasjid | 104 | 00:00
26 | Bhangura | 40 | 00:00 | 92 | Kurigram | 69 | 18:30 | 158 | Savar | 237 | 15:00
27 | Bheramara(GK) | 70 | 00:00 | 93 | Kushtia | 157 | 18:30 | 159 | SevenRings | 18.89 | 00:00
28 | Bhulta | 207 | 00:00 | 94 | Laksam | 33 | 00:00 | 160 | ShahCement | 20 | 15:00
29 | Bog-Sherpur | 82 | 00:00 | 95 | Lakshmipur | 34 | 00:00 | 161 | Shahjadpur | 92 | 18:30
30 | Bogura | 175 | 19:30 | 96 | Lalbag | 62 | 12:00 | 162 | Shahjibazar | 140 | 00:00
31 | Borhanuddin | 92 | 00:00 | 97 | Lalmonirhat | 67 | 18:30 | 163 | Shahmirpur | 53.5 | 04:00
32 | Brahmanbaria | 136 | 21:00 | 98 | MI_Cement | 7.9 | 04:00 | 164 | Shariatpur | 90 | 00:00
33 | Cantonment | 140 | 13:00 | 99 | Madanganj | 34 | 00:00 | 165 | Sherpur | 130 | 01:00
34 | Chandina | 22.18 | 04:00 | 100 | Madaripur | 122 | 00:00 | 166 | Shikalbaha | 27 | 00:00
35 | Chandpur | 84 | 00:00 | 101 | Madartek | 102 | 00:00 | 167 | Shitalakhya | 80.6 | 16:00
36 | Chandraghona | 35 | 19:00 | 102 | Madunaghat | 51 | 19:00 | 168 | Sholosohor | 47 | 18:30
37 | Chapai | 70 | 00:00 | 103 | Magura | 69 | 00:00 | 169 | Shyampur | 92 | 00:00
38 | Charsaidpur | 19 | 01:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Siddhirganj | 117 | 12:00
39 | Chauddagram | 69 | 00:00 | 105 | Maijdee | 16 | 13:00 | 171 | Sirajganj | 117 | 20:00
40 | Chhatak | 48 | 00:00 | 106 | Manikganj | 133 | 00:00 | 172 | Sonargaon | 120 | 18:00
41 | Chowmuhani | 171 | 00:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sreemongol | 89 | 00:00
42 | Chuadanga | 111 | 01:00 | 108 | Matarbari | 42 | 00:00 | 174 | Sreepur | 101 | 12:00
43 | Coxsbazar | 134 | 18:00 | 109 | Matuail | 71 | 16:00 | 175 | Srinagar | 49.77 | 00:00
44 | Cumilla(N) | 131 | 00:00 | 110 | Millgate | 127 | 16:00 | 176 | Sunamganj | 66 | 00:00
45 | Cumilla(S) | 137 | 18:00 | 111 | Mirpur | 123 | 18:00 | 177 | Sylhet | 58 | 00:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 11 | 11:00 | 178 | Sylhet-132 | 157 | 18:00
47 | Daudkandi | 148 | 19:30 | 113 | Mirzapur | 40 | 04:00 | 179 | TK | 24 | 00:00
48 | DhakaUniversity | 100 | 13:00 | 114 | Mithapukur | 77 | 18:30 | 180 | Tangail | 172 | 01:00
49 | Dhamrai | 130 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 24 | 00:00
50 | Dhanmondi | 135 | 13:00 | 116 | Mogbazar | 99.5 | 14:00 | 182 | Thakurgaon | 115 | 21:00
51 | Dohazari | 104 | 19:30 | 117 | Mongla | 36 | 00:00 | 183 | Tongi | 137 | 15:00
52 | Faridpur | 184 | 00:00 | 118 | Motijheel | 44 | 13:00 | 184 | Ullahpara | 51 | 18:30
53 | Fatullah | 98 | 15:00 | 119 | Muktagacha | 36 | 06:00 | 185 | Ullon | 58 | 00:00
54 | Fenchuganj | 52 | 00:00 | 120 | Munshiganj | 122 | 00:00 | 186 | Uttara | 80 | 18:00
55 | Feni | 114 | 19:00 | 121 | Muradnagar | 40 | 20:00 | 187 | UttaraNew | 65 | 00:00
56 | GPH | 86 | 23:00 | 122 | Mymensingh | 197 | 01:00 | 188 | Zigatola | 72 | 00:00
57 | Ghatail | 84 | 01:00 | 123 | Naogaon | 139 | 00:00
58 | Ghorashal | 19 | 00:00 | 124 | Narail | 60 | 00:00
59 | Ghorashal-230 | 96 | 00:00 | 125 | Narinda | 65 | 13:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 186 | 00:00
61 | Gollamari | 100 | 00:00 | 127 | Natore | 161 | 00:00
62 | Gopalganj | 100 | 18:30 | 128 | Nawabganj | 53.8 | 22:00
63 | Gulshan | 120 | 13:00 | 129 | Netrakona | 142 | 07:00
64 | Halishahar | 70 | 11:00 | 130 | New | 48 | 18:00
65 | HaripurSBU | 149 | 10:00 | 131 | Niamatpur | 78 | 00:00
66 | Hasnabad | 93 | 00:00 | 132 | Noapara | 47 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15539.6 | 107 |  | 15651.42
1:00 | 14747.9 | 70 |  | 14820.9
2:00 | 13875.5 | 72 |  | 13950.5
3:00 | 13189 | 58 |  | 13250
4:00 | 12603.5 | 45 |  | 12650.5
5:00 | 12285 | 33 |  | 12319
6:00 | 11851 | 0 |  | 11851
7:00 | 10928.59 | 0 |  | 10928.59
8:00 | 10620.26 | 0 |  | 10620.26
9:00 | 11361.69 | 0 |  | 11361.69
10:00 | 12124.66 | 0 |  | 12124.66
11:00 | 12460.04 | 0 |  | 12460.04
12:00 | 12908.12 | 0 |  | 12908.12
13:00 | 13321.66 | 0 |  | 13321.66
14:00 | 13460.17 | 0 |  | 13460.17
15:00 | 13529.76 | 50 |  | 13582.01
16:00 | 13238.84 | 0 |  | 13238.84
17:00 | 13103.16 | 0 |  | 13103.16
18:00 | 13677 | 98 |  | 13779.41
19:00 | 14954.9 | 144 |  | 15105.38
19:30 | 14812.4 | 122 |  | 14939.89
20:00 | 14792.2 | 104 |  | 14901.2
21:00 | 14649.63 | 126 |  | 14781.63
22:00 | 14529.77 | 135 |  | 14670.85
23:00 | 14237.73 | 156 |  | 14400.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8063.6 | 7476 | 15539.6 | DAILY GENERATION CURVE
00:30 | 7844.75 | 7299 | 15143.75
01:00 | 7625.9 | 7122 | 14747.9 | 22-09-2025
01:30 | 7329.7 | 6982 | 14311.7
02:00 | 7033.5 | 6842 | 13875.5
02:30 | 6907.75 | 6624.5 | 13532.25
03:00 | 6782 | 6407 | 13189
03:30 | 6628.75 | 6267.5 | 12896.25
04:00 | 6475.5 | 6128 | 12603.5
04:30 | 6389.25 | 6055 | 12444.25
05:00 | 6303 | 5982 | 12285
05:30 | 6138.495 | 5929.505 | 12068
06:00 | 5973.99 | 5877.01 | 11851
06:30 | 5733.15 | 5656.645 | 11389.795
07:00 | 5492.31 | 5436.28 | 10928.59
07:30 | 5373.335 | 5401.09 | 10774.425
08:00 | 5254.36 | 5365.9 | 10620.26
08:30 | 5496.49 | 5494.485 | 10990.975
09:00 | 5738.62 | 5623.07 | 11361.69
09:30 | 5904.035 | 5839.14 | 11743.175
10:00 | 6069.45 | 6055.21 | 12124.66
10:30 | 6140.13 | 6152.22 | 12292.35
11:00 | 6210.81 | 6249.23 | 12460.04
11:30 | 6302.555 | 6381.525 | 12684.08
12:00 | 6394.3 | 6513.82 | 12908.12
12:30 | 6593.99 | 6520.9 | 13114.89
13:00 | 6793.68 | 6527.98 | 13321.66
13:30 | 6904.255 | 6486.66 | 13390.915
14:00 | 7014.83 | 6445.34 | 13460.17
14:30 | 7032.83 | 6462.135 | 13494.965
15:00 | 7050.83 | 6478.93 | 13529.76
15:30 | 6964.46 | 6419.84 | 13384.3
16:00 | 6878.09 | 6360.75 | 13238.84
16:30 | 6824.71 | 6346.29 | 13171
17:00 | 6771.33 | 6331.83 | 13103.16
17:30 | 6928.665 | 6461.415 | 13390.08
18:00 | 7086 | 6591 | 13677
18:30 | 7398.45 | 6917.5 | 14315.95
19:00 | 7710.9 | 7244 | 14954.9
19:30 | 7589.4 | 7223 | 14812.4
20:00 | 7525.2 | 7267 | 14792.2
20:30 | 7437.05 | 7283.865 | 14720.915 |  | Executive Engineer
21:00 | 7348.9 | 7300.73 | 14649.63 |  | Network Operation Division
21:30 | 7256.05 | 7333.65 | 14589.7
22:00 | 7163.2 | 7366.57 | 14529.77
22:30 | 7042.85 | 7340.9 | 14383.75
23:00 | 6922.5 | 7315.23 | 14237.73

## En-Curve
QF-LDC-12
Date | 22-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3382 | 2304.8 | 891 | 38 | 50 | 1444 | 221 | 4596 | 0 | 658 | 1953.8 | 0 | 0 | 1 | 107 | DAILY ENERGY CURVE
00:30 | 3267 | 2275.8 | 891 | 38 | 49 | 1446.5 | 220.5 | 4515.5 | 0 | 610 | 1827.45 | 0 | 0 | 3 | 88.5 | 22-09-2025
01:00 | 3152 | 2246.8 | 891 | 38 | 48 | 1449 | 220 | 4435 | 0 | 562 | 1701.1 | 0 | 0 | 5 | 70
01:30 | 3131.5 | 2229.9 | 891 | 38 | 47 | 1450.5 | 219.5 | 4396.5 | 0 | 504.5 | 1400.8 | 0 | 0 | 2.5 | 71 | Energy Generated | 322.7877 |  | MKWHr
02:00 | 3111 | 2213 | 891 | 38 | 46 | 1452 | 219 | 4358 | 0 | 447 | 1100.5 | 0 | 0 | 0 | 72 | Energy not Served | 1.198 |  | MKWHr
02:30 | 3114 | 2213.5 | 890.5 | 38 | 45 | 1368 | 218.5 | 4285 | 0 | 424 | 935.75 | 0 | 0 | 0 | 65 | Total Energy Requirement | 323.9857 |  | MKWHr
03:00 | 3117 | 2214 | 890 | 38 | 44 | 1284 | 218 | 4212 | 0 | 401 | 771 | 0 | 0 | 0 | 58
03:30 | 3247.5 | 2095.5 | 890.5 | 38 | 40 | 1272 | 217.5 | 4100.5 | 0 | 328 | 664.25 | 0 | 0 | 2.5 | 51.5
04:00 | 3378 | 1977 | 891 | 38 | 36 | 1260 | 217 | 3989 | 0 | 255 | 557.5 | 0 | 0 | 5 | 45
04:30 | 3414 | 1965.5 | 891 | 38 | 33 | 1222 | 217.5 | 3966 | 0 | 243.5 | 443.25 | 0 | 0 | 10.5 | 39
05:00 | 3450 | 1954 | 891 | 38 | 30 | 1184 | 218 | 3943 | 0 | 232 | 329 | 0 | 0 | 16 | 33
05:30 | 3390 | 1954.25 | 891.5 | 38 | 30 | 1156.5 | 218.5 | 3843.5 | 1.75 | 232 | 297 | 0 | 0 | 15 | 16.5
06:00 | 3330 | 1954.5 | 892 | 38 | 30 | 1129 | 219 | 3744 | 3.5 | 232 | 265 | 0 | 0 | 14 | 0
06:30 | 3253 | 1849.25 | 892 | 38 | 32 | 1033.5 | 219.5 | 3554 | 31.545 | 227.5 | 243.5 | 0 | 0 | 16 | 0
07:00 | 3176 | 1744 | 892 | 38 | 34 | 938 | 220 | 3364 | 59.59 | 223 | 222 | 0 | 0 | 18 | 0
07:30 | 3273 | 1552 | 891.5 | 38 | 34 | 879.51 | 220 | 3360.5 | 98.415 | 191.5 | 217.5 | 0 | 0 | 18.5 | 0
08:00 | 3370 | 1360 | 891 | 38 | 34 | 821.02 | 220 | 3357 | 137.24 | 160 | 213 | 0 | 0 | 19 | 0
08:30 | 3527 | 1472.5 | 891.5 | 38 | 33 | 820.76 | 220 | 3436.5 | 160.215 | 168.5 | 207.5 | 0 | 0 | 15.5 | 0
09:00 | 3684 | 1585 | 892 | 38 | 32 | 820.5 | 220 | 3516 | 183.19 | 177 | 202 | 0 | 0 | 12 | 0
09:30 | 3693 | 1635 | 891.5 | 38 | 31 | 873.775 | 220.5 | 3725 | 214.4 | 184.5 | 227.5 | 0 | 0 | 9 | 0
10:00 | 3702 | 1685 | 891 | 38 | 30 | 927.05 | 221 | 3934 | 245.61 | 192 | 253 | 0 | 0 | 6 | 0
10:30 | 3700 | 1704.75 | 891.5 | 38 | 34 | 943.01 | 220.5 | 3969 | 315.59 | 192 | 272 | 0 | 0 | 12 | 0
11:00 | 3698 | 1724.5 | 892 | 38 | 38 | 958.97 | 220 | 4004 | 385.57 | 192 | 291 | 0 | 0 | 18 | 0
11:30 | 3705.5 | 1724.5 | 891.5 | 38 | 38 | 1012.93 | 220.5 | 4084 | 417.15 | 197 | 328 | 0 | 0 | 27 | 0
12:00 | 3713 | 1724.5 | 891 | 38 | 38 | 1066.89 | 221 | 4164 | 448.73 | 202 | 365 | 0 | 0 | 36 | 0
12:30 | 3700.5 | 1716.85 | 891 | 38 | 39 | 1052.665 | 220.5 | 4153.5 | 455.375 | 205.5 | 615 | 0 | 0 | 27 | 0
13:00 | 3688 | 1709.2 | 891 | 38 | 40 | 1038.44 | 220 | 4143 | 462.02 | 209 | 865 | 0 | 0 | 18 | 0
13:30 | 3645 | 1700.2 | 891 | 38 | 41 | 1050.72 | 219.5 | 4153 | 450.745 | 209.5 | 978.75 | 0 | 0 | 13.5 | 0
14:00 | 3602 | 1691.2 | 891 | 38 | 42 | 1063 | 219 | 4163 | 439.47 | 210 | 1092.5 | 0 | 0 | 9 | 0
14:30 | 3606 | 1710.1 | 891 | 38 | 42 | 1081.5 | 219 | 4164.5 | 415.615 | 215 | 1098.75 | 0 | 0 | 13.5 | 25
15:00 | 3610 | 1729 | 891 | 38 | 42 | 1100 | 219 | 4166 | 391.76 | 220 | 1105 | 0 | 0 | 18 | 50
15:30 | 3585.5 | 1730 | 891.5 | 38 | 40 | 1106 | 220 | 4215.5 | 292.1 | 227.5 | 1020.2 | 0 | 0 | 18 | 25
16:00 | 3561 | 1731 | 892 | 38 | 38 | 1112 | 221 | 4265 | 192.44 | 235 | 935.4 | 0 | 0 | 18 | 0
16:30 | 3564 | 1769 | 892 | 38 | 36 | 1126 | 221 | 4289.5 | 124.3 | 235 | 860.2 | 0 | 0 | 16 | 0
17:00 | 3567 | 1807 | 892 | 38 | 34 | 1140 | 221 | 4314 | 56.16 | 235 | 785 | 0 | 0 | 14 | 0
17:30 | 3492 | 1927 | 892 | 38 | 39 | 1233.5 | 221.5 | 4281 | 28.08 | 292 | 933.5 | 0 | 0 | 12.5 | 49
18:00 | 3417 | 2047 | 892 | 38 | 44 | 1327 | 222 | 4248 | 0 | 349 | 1082 | 0 | 0 | 11 | 98
18:30 | 3462.5 | 2049 | 891.5 | 38 | 44 | 1386.5 | 222 | 4406 | 0 | 492 | 1312.45 | 0 | 0 | 12 | 121
19:00 | 3508 | 2051 | 891 | 38 | 44 | 1446 | 222 | 4564 | 0 | 635 | 1542.9 | 0 | 0 | 13 | 144
19:30 | 3584 | 2083.5 | 892 | 38 | 46 | 1459 | 222 | 4590 | 0 | 563 | 1321.9 | 0 | 0 | 13 | 122
20:00 | 3599 | 2115.5 | 891 | 38 | 46 | 1448 | 222 | 4656 | 0 | 542 | 1224.7 | 0 | 0 | 10 | 104
20:30 | 3622.5 | 2094 | 891 | 38 | 45 | 1451.865 | 221.5 | 4692.5 | 0 | 501 | 1153.05 | 0 | 0 | 10.5 | 115
21:00 | 3646 | 2072.5 | 891 | 38 | 44 | 1455.73 | 221 | 4729 | 0 | 460 | 1081.4 | 0 | 0 | 11 | 126
21:30 | 3629.5 | 2062.75 | 891.5 | 38 | 46 | 1453.65 | 221.5 | 4766.5 | 0 | 443.5 | 1026.3 | 0 | 0 | 10.5 | 130.5
22:00 | 3613 | 2053 | 892 | 38 | 48 | 1451.57 | 222 | 4804 | 0 | 427 | 971.2 | 0 | 0 | 10 | 135
22:30 | 3585 | 2047 | 892 | 38 | 48 | 1453.4 | 222 | 4827.5 | 0 | 357.5 | 899.35 | 0 | 0 | 14 | 145.5
23:00 | 3557 | 2041 | 892 | 38 | 48 | 1455.23 | 222 | 4851 | 0 | 288 | 827.5 | 0 | 0 | 18 | 156
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 391 | 07:00 | 365 | 12:00 | Payra | 417 | 07:00 | 403 | 23:00
Ashuganj | 409 | 7:00 | 371 | 12:00 | Rahanpur | 403 | 07:00 | 384 | 22:00
Bhulta | 407 | 07:00 | 368 | 12:00 | Rampal | 408 | 07:00 | 389 | 21:00
Bibiana | 390 | 07:00 | 377 | 23:00
BIPTC | 406 | 06:00 | 396 | 00:00
Bogura | 393 | 08:00 | 369 | 23:00
Gopalganj | 404 | 07:00 | 379 | 22:00
Kaliakoir | 381 | 07:00 | 357 | 12:00
Madunaghat | 395 | 07:00 | 385 | 12:00
Meghnaghat | 393 | 07:00 | 369 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 07:00 | 216 | 12:00 | Kaliakoir | 239 | 07:00 | 220 | 12:00
AKSML | 234 | 18:30 | 223 | 23:00 | Keranigonj | 233 | 07:00 | 214 | 12:00
Aminbazar | 237 | 07:00 | 216 | 12:00 | Khulna(S) | 233 | 06:00 | 216 | 23:00
Ashuganj | 235 | 07:00 | 218 | 12:00 | Madunaghat | 232 | 03:00 | 224 | 23:00
Ashuganj-400 | 235 | 7:00 | 216 | 12:00 | Madunaghat-400 | 233 | 06:00 | 227 | 12:00
Baghabari | 234 | 06:00 | 223 | 18:30 | Maniknagar | 230 | 07:00 | 213 | 12:00
Barapukuria | 221 | 11:00 | 212 | 22:00 | Meghnaghat | 233 | 08:00 | 221 | 12:00
Barapukuria-230 | 221 | 11:00 | 212 | 21:00 | Meghnaghat-400 | 233 | 07:00 | 217 | 12:00
Barishal | 234 | 07:00 | 220 | 21:00 | Mirsorai | 235 | 19:00 | 222 | 12:00
Bheramara | 233 | 07:00 | 222 | 19:00 | Rajshahi | 230 | 04:00 | 218 | 23:00
Bhulta | 235 | 07:00 | 210 | 12:00 | Rampal | 234 | 07:00 | 218 | 23:00
Bibiana | 231 | 07:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 236 | 07:00 | 222 | 19:00 | Rampura | 233 | 07:00 | 206 | 12:00
Bogura | 234 | 08:00 | 220 | 22:00 | Shikalbaha | 230 | 00:00 | 222 | 23:00
Bogura-400 | 233 | 07:00 | 221 | 22:00 | Shyampur | 232 | 07:00 | 214 | 12:00
Borhanuddin | 237 | 07:00 | 227 | 22:00 | Siddhirganj | 231 | 06:00 | 217 | 15:00
BSRM | 234 | 07:00 | 221 | 23:00 | Sirajgonj | 240 | 07:00 | 230 | 23:00
Cumilla(N) | 230 | 07:00 | 216 | 12:00 | Sreepur | 231 | 07:00 | 217 | 23:00
Faridpur | 233 | 08:00 | 215 | 23:00 | Tongi | 228 | 04:00 | 212 | 11:00
Fenchuganj | 230 | 09:00 | 223 | 23:00
Ghorashal | 235 | 08:00 | 225 | 22:00
Ghorashal-230 | 232 | 07:00 | 209 | 12:00
Gopalganj | 233 | 07:00 | 225 | 17:00
GPH | 233 | 07:00 | 226 | 10:00
Haripur | 231 | 07:00 | 215 | 12:00
Hasnabad | 230 | 06:00 | 218 | 11:00
Hathazari | 231 | 05:00 | 221 | 12:00
Ishurdi | 235 | 07:00 | 224 | 23:00
Jhenaidah | 233 | 07:00 | 216 | 18:30
Kachua | 227 | 04:00 | 206 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 124 | 12:00 | Lalmonirhat | 125 | 10:00 | 116 | 00:00
Agargaon | 142 | 07:00 | 128 | 11:00 | Madanganj | 137 | 07:00 | 125 | 11:00
Agrabad | 131 | 00:00 | 127 | 10:00 | Madaripur | 139 | 07:00 | 127 | 23:00
AKS | 130 | 00:00 | 126 | 11:00 | Madartek | 138 | 19:30 | 124 | 12:00
Aminbazar | 140 | 07:00 | 123 | 11:00 | Madunaghat | 134 | 04:00 | 125 | 21:00
Amnura | 136 | 07:00 | 125 | 23:00 | Magura | 137 | 07:00 | 121 | 18:30
Ashuganj | 143 | 07:00 | 134 | 23:00 | Mahasthangarh | 129 | 10:00 | 120 | 19:30
Bagerhat | 136 | 04:00 | 119 | 00:00 | Maijdee | 127 | 03:00 | 108 | 22:00
Bajitpur | 129 | 15:00 | 121 | 20:00 | Manikganj | 130 | 07:00 | 119 | 12:00
Bakulia | 134 | 18:30 | 128 | 23:00 | Maniknagar | 140 | 07:00 | 127 | 12:00
Banani | 137 | 06:00 | 123 | 12:00 | Matarbari | 127 | 00:00 | 115 | 05:00
Bangabhaban | 140 | 07:00 | 127 | 12:00 | Matuail | 136 | 07:00 | 124 | 12:00
Barapukuria | 134 | 10:00 | 124 | 19:00 | Millgate | 136 | 07:00 | 121 | 12:00
Barguna | 135 | 06:00 | 129 | 23:00 | Mirpur | 138 | 07:00 | 123 | 12:00
Barishal | 138 | 07:00 | 126 | 22:00 | Mirzapur | 131 | 00:00 | 122 | 17:00
Barishal-230 | 139 | 07:00 | 127 | 21:00 | Mithapukur | 128 | 10:00 | 118 | 19:00
Baroaulia | 133 | 05:00 | 128 | 12:00 | MI_Cement | 137 | 07:00 | 125 | 12:00
Baroirhat | 129 | 03:00 | 119 | 11:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 07:00 | 120 | 12:00 | Mogbazar | 138 | 07:00 | 125 | 08:00
BashundharaCement | 135 | 08:00 | 125 | 12:00 | Mongla | 137 | 04:00 | 120 | 00:00
Beanibazar | 127 | 06:00 | 122 | 20:00 | Motijheel | 140 | 07:00 | 127 | 12:00
Benapole | 134 | 06:00 | 119 | 00:00 | Muktagacha | 127 | 13:00 | 118 | 17:00
Bhaluka | 130 | 06:00 | 120 | 12:00 | Munshiganj | 135 | 06:00 | 125 | 12:00
Bhandaria | 137 | 07:00 | 119 | 21:00 | Muradnagar | 132 | 06:00 | 118 | 00:00
Bhangura | 133 | 07:00 | 125 | 21:00 | Mymensingh | 126 | 00:00 | 110 | 20:00
Bheramara | 136 | 06:00 | 131 | 19:00 | Naogaon | 127 | 08:00 | 115 | 22:00
Bheramara(GK) | 136 | 06:00 | 131 | 18:30 | Narail | 136 | 06:00 | 119 | 19:00
Bhulta | 130 | 08:00 | 122 | 00:00 | Narinda | 140 | 7:00 | 127 | 12:00
Bog-Sherpur | 131 | 07:00 | 122 | 22:00 | Narshingdi | 136 | 00:00 | 120 | 00:00
Bogura | 131 | 06:00 | 123 | 22:00 | Natore | 132 | 07:00 | 124 | 19:30
Bogura-230 | 132 | 07:00 | 123 | 21:00 | Nawabganj | 140 | 06:00 | 124 | 12:00
Brahmanbaria | 136 | 06:00 | 126 | 23:00 | Netrakona | 128 | 15:00 | 107 | 20:00
Cantonment | 142 | 07:00 | 127 | 11:00 | New | 136 | 07:00 | 122 | 12:00
Chandina | 134 | 06:00 | 123 | 12:00 | Niamatpur | 137 | 06:00 | 129 | 22:00
Chandpur | 133 | 06:00 | 118 | 11:00 | Noapara | 137 | 07:00 | 124 | 00:00
Chandraghona | 134 | 06:00 | 130 | 23:00 | Pabna | 133 | 06:00 | 127 | 19:30
Chapai | 135 | 10:00 | 129 | 22:00 | Palashbari | 126 | 10:00 | 115 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 138 | 07:00 | 126 | 12:00 | Panchagarh | 132 | 03:00 | 121 | 19:00
Chauddagram | 130 | 06:00 | 118 | 22:00 | Patiya | 133 | 18:30 | 127 | 23:00
Chhatak | 126 | 05:00 | 119 | 00:00 | Patuakhali | 137 | 07:00 | 129 | 23:00
Chowmuhani | 127 | 03:00 | 112 | 00:00 | Payra | 137 | 07:00 | 132 | 19:00
Chuadanga | 135 | 08:00 | 120 | 18:30 | PHP | 128 | 04:00 | 116 | 23:00
Coxsbazar | 125 | 19:30 | 114 | 20:00 | Postogola | 139 | 07:00 | 127 | 12:00
Cumilla(N) | 134 | 05:00 | 123 | 22:00 | Purbachal | 137 | 06:00 | 122 | 12:00
Cumilla(S) | 133 | 05:00 | 121 | 23:00 | Purbasadipur | 129 | 06:00 | 117 | 19:00
Daganbhuiyan | 128 | 04:00 | 115 | 11:00 | Rahanpur | 138 | 06:00 | 131 | 22:00
Daudkandi | 133 | 06:00 | 114 | 11:00 | Rahanpur-400 | 138 | 07:00 | 131 | 22:00
DhakaUniversity | 137 | 07:00 | 123 | 12:00 | Rahim | 137 | 07:00 | 126 | 12:00
Dhamrai | 140 | 08:00 | 124 | 12:00 | Rajbari | 137 | 08:00 | 125 | 00:00
Dhanmondi | 137 | 06:00 | 122 | 12:00 | Rajendrapur | 138 | 00:00 | 117 | 12:00
Dohazari | 128 | 00:00 | 123 | 23:00 | Rajshahi | 133 | 02:00 | 125 | 19:30
Faridpur | 138 | 08:00 | 128 | 00:00 | Rajshahi-230 | 132 | 07:00 | 124 | 23:00
Fatullah | 139 | 07:00 | 127 | 12:00 | Ramganj | 130 | 03:00 | 113 | 22:00
Fenchuganj | 135 | 07:00 | 131 | 18:30 | Rampur | 132 | 18:30 | 127 | 23:00
Feni | 128 | 03:00 | 116 | 22:00 | Rampura | 136 | 00:00 | 122 | 12:00
Ghatail | 127 | 00:00 | 116 | 17:00 | Rangamati | 134 | 06:00 | 129 | 23:00
Ghorashal | 141 | 07:00 | 128 | 17:00 | Rangpur | 129 | 05:00 | 120 | 19:00
Goalpara | 140 | 07:00 | 125 | 00:00 | Ruppur | 136 | 06:00 | 131 | 18:30
Gollamari | 138 | 03:00 | 127 | 18:30 | Saidpur | 129 | 06:00 | 118 | 19:00
Gopalganj | 138 | 07:00 | 126 | 23:00 | Satkhira | 135 | 06:00 | 121 | 00:00
Gopalganj-400 | 140 | 07:00 | 129 | 22:00 | Satmasjid | 142 | 07:00 | 125 | 12:00
Gulshan | 137 | 06:00 | 125 | 10:00 | Savar | 137 | 07:00 | 124 | 11:00
Halishahar | 133 | 07:00 | 127 | 10:00 | SevenRings | 140 | 07:00 | 125 | 12:00
Haripur | 137 | 07:00 | 127 | 00:00 | ShahCement | 138 | 07:00 | 126 | 12:00
HaripurSBU | 134 | 08:00 | 125 | 12:00 | Shahjadpur | 135 | 04:00 | 130 | 19:30
Hasnabad | 136 | 05:00 | 127 | 12:00 | Shahjibazar | 135 | 06:00 | 126 | 23:00
Hathazari | 133 | 08:00 | 130 | 05:00 | Shahmirpur | 133 | 00:00 | 128 | 23:00
Ishurdi | 137 | 07:00 | 131 | 19:00 | Shariatpur | 137 | 06:00 | 125 | 22:00
Jaldhaka | 126 | 11:00 | 114 | 19:00 | Sherpur | 120 | 11:00 | 112 | 07:00
Jamalpur | 125 | 13:00 | 115 | 04:00 | Shikalbaha | 123 | 02:00 | 117 | 22:00
Jashore | 138 | 08:00 | 120 | 18:30 | Shikalbaha-230 | 134 | 00:00 | 128 | 23:00
Jhenaidah | 138 | 04:00 | 122 | 18:30 | Shitalakhya | 137 | 07:00 | 125 | 12:00
Jhenaidah-230 | 139 | 07:00 | 125 | 18:30 | Sholosohor | 135 | 07:00 | 129 | 23:00
Joydebpur | 140 | 00:00 | 122 | 12:00 | Shyampur | 139 | 07:00 | 131 | 11:00
Joypurhat | 125 | 07:00 | 112 | 22:00 | Shyampur-230 | 139 | 07:00 | 127 | 12:00
Juldah | 132 | 00:00 | 127 | 23:00 | Siddhirganj | 134 | 08:00 | 126 | 12:00
Kabirpur | 135 | 00:00 | 118 | 12:00 | Sirajganj | 130 | 06:00 | 121 | 19:30
Kachua | 136 | 04:00 | 123 | 11:00 | Sonargaon | 136 | 07:00 | 124 | 12:00
Kaliakoir | 140 | 08:00 | 127 | 12:00 | Sreemongol | 133 | 06:00 | 125 | 23:00
Kallyanpur | 137 | 05:00 | 125 | 12:00 | Sreepur | 134 | 07:00 | 124 | 23:00
Kalurghat | 134 | 06:00 | 131 | 10:00 | Srinagar | 140 | 06:00 | 123 | 12:00
Kamrangirchar | 139 | 07:00 | 123 | 12:00 | SSM | 138 | 00:00 | 132 | 08:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 123 | 05:00 | 117 | 00:00
Kasba | 132 | 06:00 | 119 | 00:00 | Sylhet | 128 | 07:00 | 123 | 18:30
Kazla | 140 | 08:00 | 128 | 12:00 | Sylhet-132 | 129 | 07:00 | 125 | 00:00
Keranigonj | 139 | 06:00 | 124 | 12:00 | Tangail | 127 | 00:00 | 118 | 17:00
Khagrachori | 134 | 06:00 | 128 | 23:00 | Taraganj | 126 | 11:00 | 118 | 19:30
Khulna | 139 | 07:00 | 126 | 23:00 | Thakurgaon | 131 | 03:00 | 121 | 19:00
Khulna(S) | 140 | 07:00 | 127 | 18:30 | TK | 134 | 00:00 | 130 | 12:00
Khulshi | 131 | 07:00 | 125 | 12:00 | Tongi | 134 | 04:00 | 125 | 11:00
Kishoreganj | 130 | 15:00 | 118 | 20:00 | Ullahpara | 132 | 04:00 | 120 | 02:00
Kodda | 137 | 00:00 | 118 | 12:00 | Ullon | 136 | 00:00 | 123 | 12:00
KSRM | 133 | 06:00 | 128 | 13:00 | Uttara | 137 | 08:00 | 123 | 12:00
Kulaura | 134 | 07:00 | 129 | 18:00 | UttaraNew | 135 | 07:00 | 123 | 12:00
Kurigram | 126 | 11:00 | 114 | 19:00 | Zigatola | 140 | 06:00 | 125 | 12:00
Kushtia | 133 | 09:00 | 126 | 18:30
Laksam | 134 | 07:00 | 122 | 12:00
Lakshmipur | 128 | 03:00 | 110 | 22:00
Lalbag | 138 | 07:00 | 125 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division