## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-09-2025 | during | 24-09-2025 | during | 24-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 370 | 321 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 225 | 225 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 250 | 288 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 7 | 0 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 50.7 | 44.9 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 121 | 121 | 133 | 133 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 20 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25.2 | 27 | 33 | 33 | 27 | 27 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 65 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 35 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 87.5 | 87.5 | 34 | 52 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 149 | 126 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 468 | 407 | 718 | 718 | 450 | 450 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 108 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2344.9 | 2432.9 | 5575.54 | 5552.54 | 4467.08 | 4480.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 48 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 212 | 195 | 200 | 195 | 200 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 93 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 76 | 56 | 78 | 56 | 78 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 29 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.83 | 0 | 5.2 | 0 | 5.2 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 97 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 27 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 135 | 159.86 | 159.86 | 145 | 145 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1106 | 1150 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 10 | 4 | 8 | 4 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 264 | 265 | 265 | 265 | 265 | 265 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1875.83 | 2576 | 3270.92 | 3304.72 | 3015.56 | 3049.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 207 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 334 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 33 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 39 | 39 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 71 | 195 | 195 | 137 | 137 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 61 | 123 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 91 | 170 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 7 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 68 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 77 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1357 | 1660 | 2449.56 | 2379.56 | 2097.06 | 2036.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-09-2025 | during | 24-09-2025 | during | 24-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 50 | 157.5 | 157.5 | 71 | 71 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 76 | 75 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 13.47 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 139.47 | 134 | 372.6 | 320.5 | 215.6 | 163.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 20 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 70 | 70 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 81 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 0 | 25 | 25 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 369 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 383 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1218 | 1196 | 1654 | 1654 | 1171 | 1171
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 241 | 231 | 410 | 410 | 275 | 275 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 83 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 790 | 1162 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2043 | 2322 | 3632.2 | 3552.2 | 3302.2 | 3222.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 622 | 621 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 852 | 1150 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 48 | 150 | 150 | 135 | 135 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 193 | 274 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2002.69 | 2460 | 2147 | 2146 | 2132 | 2131
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 59.54 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 140 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 401 | 336 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.59 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1039.81 | 1454 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.67 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 114 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2048.61 | 2537 | 3189.37 | 3022.87 | 3115.99 | 2949.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 46 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 168 | 162 | 160 | 160 | 130 | 130 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 197.03 | 0 | 197.03 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 441.2 | 436 | 691.03 | 458 | 661.03 | 428
System Total |  |  |  |  | 28823.2 | 27829.875 | 13470.7 | 15753.9 | 22982.22 | 22390.39 | 20177.52 | 19630.69
Forecast Scenario (24-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14381 |  | 0 |  | 14381
|  |  |  | 1:00 | 14011 |  | 0 |  | 14011
|  |  |  | 2:00 | 13681 |  | 0 |  | 13681
|  |  |  | 3:00 | 13280 |  | 0 |  | 13280
|  |  |  | 4:00 | 12950 |  | 0 |  | 12950
|  |  |  | 5:00 | 12770 |  | 0 |  | 12770
|  |  |  | 6:00 | 12432 |  | 0 |  | 12432
|  |  |  | 7:00 | 12527 |  | 0 |  | 12527
|  |  |  | 8:00 | 12303 |  | 0 |  | 12303
|  |  |  | 9:00 | 12663 |  | 0 |  | 12663
|  |  |  | 10:00 | 12815 |  | 0 |  | 12815
|  |  |  | 11:00 | 13043 |  | 0 |  | 13043
|  |  |  | 12:00 | 13526 |  | 0 |  | 13526
|  |  |  | 13:00 | 13896 |  | 0 |  | 13896
|  |  |  | 14:00 | 14098 |  | 0 |  | 14098
|  |  |  | 15:00 | 14302 |  | 0 |  | 14302
|  |  |  | 16:00 | 14079 |  | 0 |  | 14079
|  |  |  | 17:00 | 13803 |  | 0 |  | 13803
|  |  |  | 18:00 | 14450 |  | 0 |  | 14450
|  |  |  | 18:30 | 15100 |  | 0 |  | 15100
|  |  |  | 19:00 | 15851 |  | 0 |  | 15851
|  |  |  | 19:30 | 16000 |  | 0 |  | 16000
|  |  |  | 20:00 | 15970 |  | 0 |  | 15970
|  |  |  | 21:00 | 16031 |  | 0 |  | 16031
|  |  |  | 22:00 | 15900 |  | 0 |  | 15900
|  |  |  | 23:00 | 14408 |  | 0 |  | 14408
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13526.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16031.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16031.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.17 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:16 hrs on 24-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-09-2025 | [28 empty] | Date: | 23-09-2025 | [28 empty] | Date: | 23-09-2025 | [28 empty] | Date: | 23-09-2025 | [28 empty] | Date: | 23-09-2025 | [14 empty] | Date: | 23-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 385 | 31.9 | 0 | 15 | 123 | 0 | 0 | 55 | 152 | 0 | 320 | 304 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 53 | 0 | 351 | 330 | 40 | 175 | 39 | 90 | 0 | 85 | 0 | 19 | 105 | 48 | 0 | 0 | 29 | 315 | 0 | 393 | 0 | 57 | 149 | 0 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 9 | 50 | 0 | 0 | 0 | 6931.9 | 891 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1181 | 0 | 1444.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 178 | 0 | 0 | 0 | 406 | 0 | 0 | 164 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 115 | 220 | 0 | 622 | 1157 | 0 | 7291.7 | 14223.6 | 108.32
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 386 | 31.5 | 0 | 15 | 123 | 0 | 0 | 47 | 150 | 0 | 320 | 285 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 33 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1128 | 0 | 51 | 0 | 16 | 0 | 355 | 330 | 41 | 213 | 39 | 90 | 0 | 85 | 0 | 19 | 105 | 46 | 0 | 0 | 29 | 310 | 0 | 354 | 0 | 57 | 153 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 78 | 9 | 50 | 0 | 0 | 0 | 6769.5 | 891 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 1446.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 178 | 0 | 0 | 0 | 392 | 0 | 0 | 164 | 44 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 115 | 220 | 0 | 622 | 1100 | 0 | 7087.22 | 13856.72 | 108.32
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 385 | 24.3 | 0 | 15 | 123 | 0 | 0 | 35 | 144 | 0 | 320 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 10 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 16 | 0 | 354 | 330 | 41 | 194 | 39 | 90 | 0 | 85 | 0 | 19 | 105 | 44 | 0 | 0 | 29 | 300 | 0 | 381 | 0 | 57 | 154 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 78 | 9 | 50 | 0 | 0 | 0 | 6698.3 | 892 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 0 | 1440.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 178 | 0 | 0 | 0 | 404 | 0 | 0 | 135 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 622 | 1000 | 0 | 6843.74 | 13542.04 | 108.32
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 385 | 15.3 | 0 | 15 | 123 | 0 | 0 | 0 | 72 | 0 | 320 | 289 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 16 | 0 | 355 | 330 | 40 | 193 | 39 | 90 | 0 | 68 | 0 | 19 | 70 | 42 | 0 | 0 | 29 | 310 | 0 | 386 | 0 | 57 | 155 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 78 | 9 | 50 | 0 | 0 | 0 | 6557.3 | 891 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 1361.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 178 | 0 | 0 | 0 | 403 | 0 | 0 | 136 | 44 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 115 | 220 | 0 | 622 | 898 | 0 | 6604.02 | 13161.32 | 108.32
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 385 | 0 | 0 | 15 | 123 | 0 | 0 | 0 | 35 | 0 | 320 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1110 | 0 | 51 | 0 | 16 | 0 | 352 | 330 | 41 | 200 | 39 | 90 | 0 | 68 | 0 | 19 | 52 | 40 | 0 | 0 | 29 | 310 | 0 | 386 | 0 | 57 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 50 | 0 | 0 | 0 | 6496 | 892 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 1259.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0 | 135 | 44 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 622 | 801 | 0 | 6345.33 | 12841.33 | 108.32
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 386 | 0 | 0 | 15 | 108 | 0 | 0 | 0 | 0 | 0 | 320 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 16 | 0 | 355 | 330 | 40 | 198 | 39 | 90 | 0 | 68 | 0 | 19 | 52 | 42 | 0 | 0 | 29 | 315 | 0 | 370 | 0 | 57 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 50 | 0 | 0 | 0 | 6428 | 892 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 1262.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 0 | 134 | 44 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 621 | 798 | 0 | 6256.32 | 12684.32 | 108.32
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 387 | 0 | 0 | 15 | 108 | 0 | 0 | 0 | 0 | 0 | 320 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.09 | 220 | 0 | 30 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 945 | 0 | 51 | 0 | 16 | 0 | 355 | 330 | 41 | 192 | 39 | 90 | 0 | 34 | 0 | 19 | 34 | 38 | 0 | 2 | 0 | 315 | 0 | 365 | 0 | 57 | 154 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 50 | 0 | 0.58 | 0 | 6156.67 | 891 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 794 | 0 | 1261.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 0 | 0 | 0.52 | 182 | 0 | 185 | 0 | 0 | 0 | 398 | 0 | 0.05 | 134 | 45 | 70 | 0 | 40 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 170 | 115 | 220 | 0 | 622 | 798 | 0 | 6209 | 12365.67 | 108.32
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 387 | 0 | 0 | 15 | 123 | 0 | 0 | 0 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 35 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 1.15 | 221 | 0 | 29 | 265 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 952 | 3 | 51 | 0 | 16 | 0 | 354 | 330 | 41 | 195 | 39 | 74 | 0 | 34 | 4 | 19 | 34 | 36 | 0 | 19 | 0 | 310 | 0 | 340 | 0 | 57 | 155 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 78 | 9 | 50 | 0 | 11.19 | 0 | 6177.34 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 861 | 0 | 1115.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.27 | 7 | 0 | 0 | 10.19 | 184 | 0 | 186 | 0 | 0 | 0 | 404 | 0 | 1.2 | 133 | 47 | 70 | 4 | 34 | 0 | 0 | 0 | 1.1 | 40 | 0 | 0 | 170 | 115 | 220 | 0 | 623 | 842 | 0 | 6264.04 | 12441.38 | 108.32
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 385 | 0 | 0 | 15 | 123 | 0 | 0 | 4 | 0 | 0 | 320 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 12 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2.04 | 221 | 0 | 10 | 265 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 892 | 7 | 51 | 0 | 16 | 0 | 354 | 330 | 41 | 189 | 39 | 72 | 0 | 17 | 9 | 19 | 17 | 36 | 0 | 41 | 0 | 305 | 0 | 310 | 0 | 57 | 149 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 78 | 9 | 44 | 1 | 24.41 | 0 | 6014.45 | 891 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 865 | 0 | 951.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.08 | 14 | 0 | 0 | 16.57 | 172 | 0 | 186 | 0 | 0 | 0 | 339 | 0 | 1.93 | 133 | 47 | 35 | 13 | 34 | 0 | 0 | 0 | 2.9 | 98 | 0.03 | 0 | 166 | 115 | 220 | 0 | 623 | 898 | 0 | 6153.8 | 12168.25 | 108.32
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 385 | 12 | 0 | 15 | 123 | 0 | 0 | 26 | 30 | 0 | 320 | 289 | 0 | 0 | 0 | 335 | 0 | 0 | 20 | 35 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 2.82 | 219 | 0 | 4 | 265 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 867 | 18 | 51 | 1 | 16 | 0 | 354 | 330 | 40 | 211 | 39 | 54 | 0 | 17 | 0 | 17 | 17 | 34 | 0 | 58 | 0 | 310 | 0 | 339 | 0 | 57 | 144 | 5 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 44 | 1 | 20.17 | 1 | 6163.99 | 892 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 885 | 0 | 1018.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.28 | 27 | 0 | 0 | 52.49 | 165 | 0 | 175 | 0 | 0 | 0 | 334 | 0 | 4.4 | 131 | 48 | 35 | 21 | 0 | 0 | 0 | 0 | 4.3 | 148 | 0.03 | 0 | 165 | 115 | 220 | 0 | 622 | 930 | 0 | 6390.77 | 12554.76 | 108.32
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 450 | 15 | 0 | 15 | 122 | 30 | 0 | 35 | 80 | 0 | 300 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 26 | 37 | 24.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.52 | 219 | 0 | 4 | 265 | 0 | 0 | 25 | 0 | 0 | 216 | 0 | 0 | 0 | 893 | 18 | 51 | 20 | 16 | 0 | 300 | 330 | 39 | 194 | 35 | 50 | 0 | 17 | 0 | 17 | 17 | 36 | 0 | 69 | 0 | 305 | 0 | 374 | 0 | 57 | 139 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 32 | 1 | 32.6 | 5 | 6260.62 | 892 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 825 | 0 | 1017.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.86 | 103 | 0 | 0 | 59.46 | 161 | 0 | 163 | 0 | 0 | 0 | 343 | 0 | 4.58 | 133 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 4.6 | 173 | 0.21 | 0 | 169 | 115 | 220 | 0 | 622 | 990 | 0 | 6485.29 | 12745.91 | 108.32
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 450 | 28 | 0 | 28 | 122 | 30 | 0 | 35 | 146 | 0 | 300 | 309 | 0 | 0 | 0 | 250 | 0 | 0 | 36 | 125 | 25.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 4.23 | 219 | 0 | 4 | 265 | 0 | 0 | 33 | 0 | 0 | 215 | 0 | 0 | 0 | 905 | 19 | 51 | 31 | 16 | 0 | 340 | 300 | 39 | 205 | 35 | 51 | 0 | 45 | 0 | 5 | 17 | 38 | 0 | 76 | 0 | 310 | 0 | 390 | 0 | 57 | 148 | 13 | 0 | 78 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 32 | 1 | 15.79 | 6 | 6553.22 | 892 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95 | 788 | 0 | 1020.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.19 | 115 | 0 | 0 | 63.74 | 170 | 0 | 171 | 0 | 0 | 0 | 382 | 0 | 5.64 | 140 | 49 | 0 | 34 | 0 | 0 | 0 | 0 | 6.8 | 183 | 0.28 | 0 | 172 | 100 | 180 | 0 | 622 | 900 | 0 | 6435.03 | 12988.25 | 108.32
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 468 | 50.7 | 17 | 35 | 121 | 30 | 0 | 35 | 149 | 0 | 300 | 250 | 0 | 0 | 20 | 250 | 0 | 0 | 35 | 125 | 25.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.83 | 220 | 0 | 4 | 264 | 0 | 0 | 48 | 0 | 0 | 212 | 0 | 0 | 0 | 1106 | 15 | 51 | 61 | 16 | 0 | 334 | 330 | 39 | 207 | 35 | 52 | 0 | 91 | 0 | 7 | 17 | 40 | 0 | 77 | 0 | 315 | 0 | 390 | 0 | 57 | 156 | 13 | 0 | 76 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 3 | 13.47 | 6 | 6935.2 | 891 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 790 | 0 | 1039.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.54 | 114 | 0 | 0 | 63.67 | 183 | 0 | 182 | 0 | 0 | 0 | 401 | 0 | 5.59 | 168 | 48 | 0 | 20 | 0 | 0 | 0 | 0 | 5.2 | 200 | 0.69 | 0 | 193 | 115 | 220 | 0 | 622 | 852 | 0 | 6535.5 | 13470.7 | 108.32
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 450 | 51.8 | 17 | 35 | 118 | 30 | 0 | 35 | 161 | 0 | 300 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 33 | 125 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 4.11 | 219 | 8 | 13 | 265 | 0 | 0 | 50 | 4 | 34 | 214 | 0 | 0 | 0 | 1163 | 18 | 51 | 98 | 33 | 0 | 336 | 330 | 38 | 201 | 36 | 50 | 0 | 131 | 0 | 19 | 46 | 42 | 1 | 18 | 0 | 310 | 0 | 385 | 0 | 48 | 156 | 0 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 2 | 37.3 | 6 | 7207.21 | 892 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 870 | 0 | 1106.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.28 | 93 | 0 | 0 | 59.4 | 192 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 5.45 | 160 | 48 | 35 | 9 | 34 | 0 | 0 | 0 | 2.6 | 175 | 0.75 | 0 | 222 | 115 | 220 | 0 | 621 | 850 | 0 | 6689.13 | 13896.34 | 108.32
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 458 | 50.3 | 17 | 35 | 105 | 32 | 0 | 35 | 142 | 0 | 300 | 305 | 0 | 0 | 55 | 250 | 0 | 0 | 30 | 125 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 3.03 | 219 | 17 | 10 | 265 | 0 | 0 | 46 | 17 | 50 | 213 | 0 | 0 | 0 | 1167 | 16 | 51 | 110 | 35 | 0 | 337 | 330 | 37 | 205 | 36 | 51 | 0 | 156 | 0 | 19 | 46 | 46 | 43 | 60 | 0 | 310 | 0 | 388 | 0 | 48 | 155 | 0 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 2 | 45.56 | 6 | 7351.89 | 891 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 897 | 0 | 1213.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.92 | 44 | 0 | 0 | 47.73 | 188 | 0 | 168 | 0 | 0 | 0 | 414 | 0 | 0.93 | 158 | 47 | 35 | 22 | 34 | 0 | 0 | 0 | 1.6 | 121 | 0.74 | 0 | 223 | 115 | 220 | 0 | 621 | 875 | 0 | 6745.83 | 14097.72 | 108.32
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 438 | 50 | 17 | 35 | 104 | 32 | 4 | 35 | 162 | 0 | 300 | 284 | 0 | 0 | 55 | 250 | 0 | 0 | 23 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 2.4 | 220 | 0 | 2 | 265 | 28 | 0 | 47 | 17 | 33 | 213 | 0 | 0 | 0 | 1148 | 5 | 51 | 112 | 53 | 0 | 341 | 330 | 37 | 190 | 36 | 51 | 0 | 161 | 5 | 12 | 77 | 44 | 43 | 51 | 0 | 305 | 0 | 373 | 0 | 48 | 153 | 0 | 0 | 77 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 2 | 36.79 | 2 | 7294.39 | 891 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 963 | 0 | 1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.19 | 81 | 0 | 0 | 41.98 | 189 | 0 | 166 | 0 | 0 | 0 | 387 | 0 | 4.04 | 130 | 48 | 35 | 23 | 34 | 0 | 0 | 0 | 3 | 136 | 0.64 | 0 | 214 | 115 | 220 | 0 | 622 | 900 | 0 | 6881.85 | 14176.24 | 108.32
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 430 | 46.4 | 17 | 35 | 104 | 32 | 45 | 35 | 162 | 0 | 300 | 284 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 125 | 25.5 | 22 | 0 | 0 | 0 | 0 | 27 | 0 | 18 | 9 | 0 | 0 | 0 | 0 | 1.39 | 220 | 0 | 3 | 263 | 30 | 0 | 50 | 17 | 32 | 213 | 0 | 0 | 0 | 1100 | 9 | 51 | 108 | 53 | 0 | 340 | 330 | 38 | 190 | 25 | 52 | 0 | 152 | 9 | 12 | 98 | 44 | 43 | 29 | 0 | 300 | 0 | 371 | 0 | 48 | 153 | 0 | 0 | 80 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 1 | 21.65 | 1 | 7221.94 | 891 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 978 | 0 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.72 | 8 | 0 | 0 | 25.3 | 198 | 0 | 140 | 0 | 0 | 0 | 389 | 0 | 2.46 | 160 | 48 | 35 | 15 | 34 | 0 | 0 | 0 | 3.2 | 42 | 0.07 | 0 | 216 | 115 | 220 | 0 | 621 | 930 | 0 | 6713.75 | 13935.69 | 108.32
17:00 | 7 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 420 | 43.5 | 17 | 35 | 104 | 32 | 55 | 35 | 156 | 0 | 340 | 279 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 125 | 25.5 | 22 | 0 | 0 | 0 | 0 | 77 | 0 | 15 | 33 | 0 | 0 | 0 | 0 | 0.07 | 220 | 16 | 3 | 263 | 29 | 0 | 50 | 17 | 43 | 213 | 0 | 0 | 0 | 1022 | 3 | 51 | 102 | 53 | 0 | 342 | 330 | 38 | 182 | 20 | 54 | 0 | 152 | 10 | 12 | 93 | 40 | 43 | 9 | 0 | 305 | 0 | 300 | 20 | 48 | 148 | 0 | 0 | 80 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 32 | 0 | 6.35 | 0 | 7163.42 | 892 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 962 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.65 | 1 | 0 | 0 | 7.45 | 195 | 0 | 140 | 0 | 0 | 0 | 323 | 0 | 0.67 | 166 | 45 | 35 | 6 | 34 | 0 | 0 | 0 | 1 | 14 | 0.1 | 0 | 208 | 115 | 220 | 0 | 621 | 920 | 0 | 6549.87 | 13713.29 | 108.32
18:00 | 7 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 405 | 45.5 | 20 | 35 | 122 | 32 | 55 | 48 | 143 | 0 | 300 | 304 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 125 | 25.5 | 22 | 0 | 0 | 0 | 0 | 103 | 0 | 14 | 33 | 16 | 0 | 0 | 0 | 0 | 221 | 38 | 6 | 265 | 38 | 0 | 50 | 17 | 48 | 212 | 0 | 0 | 0 | 1170 | 0 | 51 | 103 | 53 | 0 | 320 | 330 | 38 | 200 | 25 | 68 | 0 | 156 | 0 | 12 | 100 | 48 | 43 | 0 | 35 | 310 | 0 | 386 | 20 | 48 | 140 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 32 | 0 | 0 | 0 | 7561 | 891 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 1322 | 0 | 48 | 0 | 35 | 3 | 0 | 44 | 13 | 18 | 0 | 0 | 10 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 359 | 0 | 0 | 164 | 45 | 53 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 115 | 220 | 0 | 621 | 930 | 0 | 6741 | 14302 | 108.32
19:00 | 7 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 405 | 52.5 | 35 | 35 | 121 | 32 | 55 | 55 | 126 | 0 | 300 | 285 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 125 | 26.5 | 22 | 0 | 0 | 2 | 10 | 105 | 0 | 8 | 66 | 62 | 0 | 0 | 0 | 0 | 222 | 81 | 16 | 265 | 140 | 0 | 50 | 17 | 84 | 213 | 0 | 0 | 0 | 1133 | 0 | 51 | 112 | 71 | 0 | 345 | 330 | 37 | 190 | 25 | 74 | 0 | 187 | 0 | 13 | 114 | 50 | 43 | 0 | 36 | 315 | 0 | 371 | 20 | 48 | 154 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 76 | 9 | 32 | 0 | 0 | 0 | 7903 | 891 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 0 | 1440 | 0 | 40 | 0 | 100 | 96 | 0 | 95 | 38 | 52 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 335 | 0 | 0 | 165 | 45 | 110 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 272 | 115 | 220 | 0 | 621 | 1055 | 2 | 7604 | 15507 | 108.32
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 405 | 54 | 35 | 35 | 121 | 32 | 55 | 55 | 126 | 0 | 300 | 285 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 26 | 30 | 105 | 0 | 8 | 66 | 78 | 0 | 0 | 0 | 0 | 222 | 98 | 16 | 265 | 136 | 0 | 50 | 17 | 85 | 213 | 0 | 0 | 0 | 1139 | 0 | 51 | 115 | 71 | 0 | 346 | 330 | 37 | 189 | 25 | 90 | 0 | 178 | 0 | 19 | 97 | 50 | 43 | 0 | 36 | 305 | 0 | 365 | 20 | 57 | 148 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 75 | 9 | 32 | 0 | 0 | 0 | 7944 | 891 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 1440 | 0 | 40 | 0 | 113 | 108 | 0 | 95 | 38 | 52 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 163 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 274 | 115 | 220 | 0 | 621 | 1140 | 35 | 7784 | 15728
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 405 | 47 | 35 | 35 | 121 | 32 | 55 | 55 | 126 | 0 | 300 | 286 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 27.5 | 22 | 0 | 0 | 27 | 30 | 102 | 0 | 9 | 66 | 78 | 0 | 0 | 0 | 0 | 222 | 104 | 18 | 262 | 135 | 0 | 50 | 17 | 90 | 212 | 0 | 0 | 0 | 1144 | 0 | 51 | 115 | 71 | 0 | 346 | 330 | 38 | 190 | 28 | 90 | 0 | 179 | 0 | 19 | 78 | 50 | 43 | 0 | 36 | 305 | 0 | 366 | 20 | 57 | 150 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 32 | 0 | 0 | 0 | 7936.5 | 891 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1181 | 0 | 1441 | 0 | 40 | 0 | 113 | 111 | 0 | 94 | 38 | 52 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 163 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 274 | 115 | 220 | 0 | 622 | 1140 | 45 | 7769 | 15705.5 | 108.32
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 407 | 44.9 | 35 | 35 | 121 | 65 | 55 | 55 | 126 | 0 | 300 | 288 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 27 | 30 | 97 | 0 | 10 | 66 | 76 | 0 | 0 | 0 | 0 | 222 | 97 | 29 | 265 | 135 | 0 | 50 | 17 | 93 | 212 | 0 | 0 | 0 | 1150 | 0 | 51 | 123 | 71 | 0 | 347 | 330 | 39 | 192 | 33 | 90 | 0 | 170 | 0 | 19 | 68 | 48 | 43 | 0 | 36 | 305 | 0 | 369 | 20 | 57 | 151 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 75 | 9 | 50 | 0 | 0 | 0 | 7998.9 | 891 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 1454 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 336 | 0 | 0 | 162 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 274 | 115 | 220 | 0 | 621 | 1150 | 48 | 7755 | 15753.9 | 108.32
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 407 | 46.5 | 19 | 35 | 121 | 65 | 55 | 55 | 90 | 0 | 300 | 291 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 90 | 27 | 22 | 0 | 0 | 30 | 30 | 102 | 0 | 11 | 66 | 76 | 0 | 0 | 0 | 0 | 222 | 101 | 3 | 265 | 138 | 0 | 0 | 17 | 96 | 213 | 0 | 0 | 0 | 1162 | 0 | 51 | 125 | 98 | 0 | 350 | 330 | 41 | 194 | 33 | 79 | 0 | 174 | 0 | 19 | 62 | 52 | 43 | 0 | 36 | 310 | 0 | 387 | 20 | 57 | 154 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7955.5 | 891 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 0 | 1444.27 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 344 | 0 | 0 | 162 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 278 | 115 | 220 | 0 | 618 | 1110 | 46 | 7706.27 | 15661.77 | 108.32
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 407 | 46.2 | 17 | 35 | 122 | 65 | 55 | 55 | 90 | 0 | 300 | 286 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 28 | 30 | 93 | 0 | 3 | 66 | 76 | 0 | 0 | 0 | 0 | 222 | 96 | 35 | 265 | 135 | 0 | 29 | 17 | 93 | 213 | 0 | 0 | 0 | 1145 | 0 | 51 | 125 | 100 | 0 | 350 | 330 | 42 | 189 | 34 | 62 | 0 | 172 | 0 | 19 | 60 | 52 | 43 | 0 | 36 | 305 | 0 | 376 | 20 | 57 | 152 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 47 | 0 | 0 | 0 | 7933.2 | 891 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1443.43 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 339 | 0 | 0 | 165 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 272 | 115 | 220 | 0 | 622 | 1090 | 46 | 7760.63 | 15693.83 | 108.32
Total KWH | 25776 | 801600 | 345120 | 0 | 0 | 0 | 0 | 0 | 8164800 | 0 | 10261470 | 741600 | 294120 | 654192 | 2814240 | 566804 | 477326 | 794787 | 2358720 | 0 | 7701500 | 6974604 | 0 | 0 | 685911 | 7215103 | 0 | 0 | 207158 | 2023200 | 584400 | 491040 | 0 | 0 | 144273 | 175636 | 807360 | 0 | 304320 | 609334 | 420336 | 0 | 0 | 0 | 25441 | 5308947 | 674945 | 411360 | 6349090.91 | 851418 | 0 | 659040 | 191304 | 809599 | 5128141 | 0 | 0 | 0 | 25909088 | 122040 | 1288363 | 1478690 | 1003636 | 0 | 8584800 | 7928000 | 951840 | 4780000 | 828288 | 1680000 | 0 | 2649120 | 47880 | 357790 | 1519620 | 1045440 | 466445 | 522936 | 387584 | 7476000 | 0 | 9212000 | 144000 | 1284000 | 3646964 | 50040 | 0 | 1950720 | 714912 | 0 | 428000 | 3404490 | 0 | 1790400 | 206400 | 929280 | 11400 | 307880 | 38160 | 170200221.91 | 21576727 | 5613408 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 620640 | 22923700 | 0 | 30489602 | 0 | 267901 | 0 | 628416 | 662688 | 0 | 554720 | 197541 | 194050 | 413613 | 648860 | 145877 | 0 | 449248 | 4282182 | 0 | 4170727 | 0 | 0 | 0 | 9096290 | 0 | 39780 | 3641000 | 1073891 | 1636474 | 230685 | 1591257 | 0 | 0 | 0 | 42133.92 | 1264320 | 3838 | 178080 | 5040000 | 2741000 | 5404540 | 0 | 14936688 | 23648000 | 220800 | 165540676.92 | 335740898.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13470.7 | MW | 12:00 Hr. | Energy Generated |  |  | 335.7409 |  | MKWHr.
| Day Peak Demand |  |  | 13525.7 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.058 |  | MKWHr.
| Evening Peak Generation |  |  | 15753.9 | MW | 21:00 Hr. | Energy Demand |  |  | 338.7989 |  | MKWHr.
| Evening Peak Demand |  |  | 16030.83 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12168.25 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 969.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15753.9 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2039 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.3929 | 0 | 12.5834 | 0 | 0 | 0.20716 | 0 | 0 | 54.1835 | Gas | 133.2037 | Gas | 478744057.82
| Chattogram Zone |  |  | 5.5395 | 32.2582 | 5.3432 | 0 | 5.3089 | 0.14748 | 0 | 0.30432 | 48.9017 | Coal | 103.5215 | Coal | 570952769.6632
| Cumilla Zone |  |  | 25.7227 | 0 | 8.2293 | 0 | 0 | 0.52294 | 1.0454 | 0 | 35.5204 | HFO | 34.4687 | HFO | 637507124.15
| Mymensingh Zone |  |  | 0.92928 | 0 | 2.035 | 0 | 0 | 0.31928 | 0 | 0 | 3.2835 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3111 | Hydro | 5.3089 | Hydro | 530894.7
| Khulna Zone |  |  | 5.6134 | 22.9237 | 0 | 0 | 0 | 0.62064 | 22.4887 | 0 | 51.6465 | Solar | 4.91 | Solar | 73133276.4432
| Barishal Zone |  |  | 8.1455 | 43.6247 | 0.39888 | 0 | 0 | 0.003838 | 0 | 0 | 52.1729 | Import | 54.0238 | Import | 317551670.83
| Rajshahi Zone |  |  | 17.5492 | 0 | 2.6512 | 0 | 0 | 1.5515 | 30.4896 | 0 | 52.2415 | Wind | 0.30432 | Wind | 4485676.8
| Rangpur Zone |  |  | 0 | 4.7149 | 3.2277 | 0 | 0 | 1.5371 | 0 | 0 | 9.4798
| Total |  |  | 133.2037 | 103.5215 | 34.4687 | 0 | 5.3089 | 4.91 | 54.0238 | 0.30432 | 335.7409
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 478744057.82 |  | Hydro | 530894.7
|  |  |  | Coal | 570952769.6632 |  | Solar | 73133276.4432
|  |  |  | HFO | 637507124.15 |  | Import | 317551670.83
|  |  |  | HSD | 0 |  | Wind | 4485676.8
[5 empty] | Total: | 208,29,05,470 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5767 | Peak Hr Flow | 891.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54061414.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.4896 | Peak Hr Flow | 1454.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2510 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0454 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2948 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.1118 | Peak Hr Flow | 2393.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 50 |  | 5343
|  |  |  | Chattogram |  | 0 |  | 1576
|  |  |  | Cumilla |  | 0 |  | 1516
|  |  |  | Mymensingh |  | 215 |  | 1266
|  |  |  | Sylhet |  | 0 |  | 714
|  |  |  | Khulna |  | 0 |  | 1834
|  |  |  | Barishal |  | 0 |  | 480
|  |  |  | Rajshahi |  | 0 |  | 1593
|  |  |  | Rangpur |  | 0 |  | 1066
|  |  |  | Total |  | 265 |  | 15388
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:28 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 08:30 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
|  | 08:59 | Maniknagar 132/33kV S/S Transformer GT-2 HT is restored.
| 09:00 | 10:17 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Red hot maintenance by PBS | [7 empty] | 25.0MW load
interrup.
| 09:00 | 10:17 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Red hot maintenance by PBS | [7 empty] | 25.0MW load
interrup.
| 09:01 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Minimum @ 08:25 hr by Fahad
Mahmud, XEN, NLDC
|  | 09:02 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 09:03 | Khulna (C) S/S TR-1 425T LT is restored.
| 09:12 | 10:44 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to for temperature reduce
| 09:13 | 10:43 | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to for temperature reduce
| 09:28 | 14:57 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to CRM test Project Work
| 10:32 | 16:43 | Chandina 132/33kV S/S TR-3 LT Scheduled S/D Due to Project Work | [7 empty] | 6.0MW load
interrup.
|  | 11:20 | BIPTC S/S 20DF11 is restored.
| 11:28 | 16:41 | Chandina 132/33kV S/S TR-3 HT Scheduled S/D Due to Project work | [7 empty] | 6.0MW load
interrup.
| 11:41 | 14:45 | Chandina 132/33kV S/S TR-2 LT Scheduled S/D Due to Project Work
| 12:00 |  | Day peak generation: 13471 MW
| 12:02 | 14:37 | Chandina 132/33kV S/S TR-2 HT Scheduled S/D Due to project work
|  | 13:27 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 13:28 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 16:52 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
|  | 16:53 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
| 17:24 |  | Chowmuhani 230/132kV, 250/350 MVA T-1 transformer was switched ON.
| 21:00 |  | Evening Peak Generation is 15753 MW
| 21:08 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 21:24 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 06:00 |  | Minimum Generation 12976 MW
| 06:03 |  | Meghnaghat 450 MW GT-1 was shut down due to Combustion Chamber Inspection
| 06:03 |  | Meghnaghat 450MW CCPP GT1 was shut down due to an inspection at the combustion chamber.
| 06:12 | 07:06 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Jhalokathi WZPDCL 33kV incoming | [7 empty] | 30.0MW load
|  |  | DS Red hot Maintenance | [7 empty] | interrup.
| 06:13 | 07:05 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Jhalokathi WZPDCL 33kV incoming | [7 empty] | 30.0MW load
|  |  | DS Red hot Maintenance | [7 empty] | interrup.
| 07:14 |  | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS maintenance work | [7 empty] | 60.0MW load
interrup.
| 07:15 |  | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS maintenance work | [7 empty] | 60.0MW load
interrup.
| 07:41 |  | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to temperature reduce
| 07:42 |  | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to temperature reduce
| 07:49 |  | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to WZPDCL Bus loop red hot | [7 empty] | 6.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:49 |  | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to WZPDCL Bus loop red hot | [7 empty] | 6.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 321 | 8164800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7701500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 6974604 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 477326 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7215103 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 25776 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.9 | 741600 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 121 | 2814240 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 794787 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 685911 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27 | 584400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 491040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 345120 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 65 | 566804 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 654192 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 801600 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2358720 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 207158 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 294120 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 407 | 10261470 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2023200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2432.9 | 54183471
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 191304 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122040 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 659040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5308947 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 212 | 5128141 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 93 | 809599 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 76 | 420336 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 609334 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 411360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 807360 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 175636 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 97 | 674945 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 27 | 144273 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 135 | 851418 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 25909088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 304320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6349090.91 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2576 | 48901672.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4780000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 8584800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7928000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 828288 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 39 | 951840 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 71 | 1003636 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1288363 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 1478690 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 387584 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 2649120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1045440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 466445 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 357790 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 68 | 1519620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 47880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1680000 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 522936 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1660 | 35520432
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 50 | 929280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 206400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1790400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 307880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 38160 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 134 | 3283520
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 20 | 144000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1284000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3646964 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714912 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1950720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3404490 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 428000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 50040 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7476000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 9212000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1196 | 28311126
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21576727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 231 | 5613408 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 620640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1162 | 22923700 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2322 | 51646475
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 621 | 14936688 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 178080 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2741000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1150 | 23648000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5404540 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 48 | 220800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5040000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3838 | -
Barishal Area Total |  |  |  |  | 2236 | 2460 | 52172946
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 413613 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 267901 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 197541 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4282182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4170727 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 336 | 9096290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 145877 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 194050 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 554720 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 662688 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 628416 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1454 | 30489602 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 449248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 648860 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2537 | 52241495
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1073891 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 3641000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1591257 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42133.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1636474 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230685 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1264320 | -
Rangpur Area Total |  |  |  |  | 950 | 436 | 9479760.92
Eastern Grid Total |  |  |  |  | 17385.715 | 7998.9 | 170200221.91
Western Grid Total |  |  |  |  | 10444.16 | 7755 | 165540676.92
National Grid Total |  |  |  |  | 27829.875 | 15753.9 | 335740898.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-09-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10148.71 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4973.3 | MW
i) Dhaka area |  |  | 5292.71 |  | MW | i) Khulna area |  |  |  | 1834.5 | MW
ii) Chattogram area |  |  | 1575.5 |  | MW | ii) Barishal area |  |  |  | 480 | MW
iii) Cumilla area |  |  | 1515.5 |  | MW | iii) Rajshahi area |  |  |  | 1592.8 | MW
iv) Mymensingh area |  |  | 1051 |  | MW | iv) Rangpur area |  |  |  | 1066 | MW
v) Sylhet area |  |  | 714 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15122.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 87 | 19:00 | 133 | PHP | 7 | 02:00
2 | AKSML | 91 | 22:00 | 68 | Ishurdi | 83 | 19:00 | 134 | Pabna | 108 | 19:00
3 | Aftabnagar | 40 | 18:30 | 69 | Jaldhaka | 92 | 18:30 | 135 | Palashbari | 124 | 21:00
4 | Agargaon | 136 | 13:00 | 70 | Jamalpur | 106 | 00:00 | 136 | Panchagarh | 62 | 19:30
5 | Agrabad | 110 | 20:00 | 71 | Jashore | 145 | 19:00 | 137 | Patiya | 11 | 21:00
6 | Amnura | 30 | 21:00 | 72 | Jhenaidah | 138 | 18:30 | 138 | Patuakhali | 68 | 21:00
7 | Ashuganj | 86 | 01:00 | 73 | Joydebpur | 148 | 14:00 | 139 | Payra | 36 | 22:00
8 | BSRM | 139 | 19:30 | 74 | Joypurhat | 66 | 21:00 | 140 | Postogola | 68 | 13:00
9 | Bagerhat | 80 | 19:00 | 75 | Juldah | 17.5 | 13:00 | 141 | Purbachal | 22 | 23:00
10 | Bajitpur | 91 | 20:00 | 76 | KSRM | 43 | 16:00 | 142 | Purbasadipur | 131 | 19:00
11 | Bakulia | 100 | 18:30 | 77 | Kabirpur | 239 | 14:00 | 143 | Rahanpur | 40 | 22:00
12 | Banani | 53.5 | 13:00 | 78 | Kachua | 98 | 22:00 | 144 | Rahim | 23 | 04:00
13 | Bangabhaban | 24 | 10:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rajbari | 84 | 19:00
14 | Barapukuria | 70 | 21:00 | 80 | Kalurghat | 42 | 15:00 | 146 | Rajendrapur | 130 | 21:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 85 | 13:00 | 147 | Rajshahi | 108 | 23:00
16 | Barishal | 111 | 18:30 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 100 | 20:00
17 | Barishal-230 | 100 | 21:00 | 83 | Kasba | 38 | 20:00 | 149 | Ramganj | 114 | 22:00
18 | Baroaulia | 67 | 10:00 | 84 | Kazla | 102 | 13:00 | 150 | Rampur | 42 | 19:00
19 | Baroirhat | 66 | 18:30 | 85 | Keranigonj | 103 | 19:00 | 151 | Rangamati | 19 | 18:30
20 | Bashundhara | 207 | 15:00 | 86 | Khagrachori | 38 | 18:30 | 152 | Rangpur | 159 | 18:30
21 | BashundharaCement | 0 | 00:00 | 87 | Khulna | 71 | 19:30 | 153 | Ruppur | 7.8 | 09:00
22 | Beanibazar | 90 | 20:00 | 88 | Khulshi | 188 | 18:00 | 154 | SSM | 14 | 03:00
23 | Benapole | 62 | 22:00 | 89 | Kishoreganj | 127 | 18:30 | 155 | Saidpur | 114 | 18:30
24 | Bhaluka | 154 | 17:00 | 90 | Kodda | 282 | 18:00 | 156 | Satkhira | 122 | 19:30
25 | Bhandaria | 66 | 19:00 | 91 | Kulaura | 57 | 21:00 | 157 | Satmasjid | 103 | 19:00
26 | Bhangura | 42 | 18:30 | 92 | Kurigram | 68 | 19:00 | 158 | Savar | 239 | 11:00
27 | Bheramara(GK) | 70 | 20:00 | 93 | Kushtia | 162 | 18:30 | 159 | SevenRings | 15.83 | 05:00
28 | Bhulta | 215 | 21:00 | 94 | Laksam | 33 | 23:00 | 160 | ShahCement | 18 | 10:00
29 | Bog-Sherpur | 80 | 21:00 | 95 | Lakshmipur | 33 | 19:30 | 161 | Shahjadpur | 96 | 19:00
30 | Bogura | 178 | 19:30 | 96 | Lalbag | 62 | 13:00 | 162 | Shahjibazar | 137 | 18:30
31 | Borhanuddin | 93 | 20:00 | 97 | Lalmonirhat | 69 | 18:30 | 163 | Shahmirpur | 50 | 18:00
32 | Brahmanbaria | 139 | 23:00 | 98 | MI_Cement | 15.9 | 21:00 | 164 | Shariatpur | 91 | 22:00
33 | Cantonment | 146 | 13:00 | 99 | Madanganj | 34 | 19:30 | 165 | Sherpur | 116 | 05:00
34 | Chandina | 17.79 | 19:00 | 100 | Madaripur | 110 | 21:00 | 166 | Shikalbaha | 23 | 15:00
35 | Chandpur | 88 | 19:00 | 101 | Madartek | 94 | 23:00 | 167 | Shitalakhya | 85.5 | 15:00
36 | Chandraghona | 41 | 19:00 | 102 | Madunaghat | 53 | 13:00 | 168 | Sholosohor | 50 | 19:00
37 | Chapai | 71 | 22:00 | 103 | Magura | 66 | 18:30 | 169 | Shyampur | 98 | 11:00
38 | Charsaidpur | 22 | 15:00 | 104 | Mahasthangarh | 84 | 23:00 | 170 | Siddhirganj | 127 | 12:00
39 | Chauddagram | 74 | 22:00 | 105 | Maijdee | 15 | 21:00 | 171 | Sirajganj | 132 | 20:00
40 | Chhatak | 43 | 23:00 | 106 | Manikganj | 135 | 21:00 | 172 | Sonargaon | 124 | 18:30
41 | Chowmuhani | 194 | 18:30 | 107 | Maniknagar | 64 | 13:00 | 173 | Sreemongol | 94 | 19:30
42 | Chuadanga | 124 | 19:00 | 108 | Matarbari | 54 | 20:00 | 174 | Sreepur | 108 | 18:30
43 | Coxsbazar | 133 | 19:00 | 109 | Matuail | 74 | 15:00 | 175 | Srinagar | 49.39 | 22:00
44 | Cumilla(N) | 153 | 18:00 | 110 | Millgate | 130 | 15:00 | 176 | Sunamganj | 64 | 00:00
45 | Cumilla(S) | 163 | 18:30 | 111 | Mirpur | 127 | 14:00 | 177 | Sylhet | 56 | 20:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 12 | 12:00 | 178 | Sylhet-132 | 146 | 18:00
47 | Daudkandi | 157 | 19:00 | 113 | Mirzapur | 42 | 12:00 | 179 | TK | 26 | 23:00
48 | DhakaUniversity | 106 | 13:00 | 114 | Mithapukur | 81 | 18:30 | 180 | Tangail | 162 | 19:30
49 | Dhamrai | 132 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 24 | 00:00
50 | Dhanmondi | 125 | 13:00 | 116 | Mogbazar | 103.6 | 16:00 | 182 | Thakurgaon | 116 | 19:30
51 | Dohazari | 117 | 18:30 | 117 | Mongla | 48 | 18:30 | 183 | Tongi | 140 | 15:00
52 | Faridpur | 176 | 21:00 | 118 | Motijheel | 46 | 12:00 | 184 | Ullahpara | 42 | 19:00
53 | Fatullah | 112 | 12:00 | 119 | Muktagacha | 36 | 06:00 | 185 | Ullon | 53 | 22:00
54 | Fenchuganj | 50 | 23:00 | 120 | Munshiganj | 119 | 23:00 | 186 | Uttara | 87 | 13:00
55 | Feni | 126 | 19:00 | 121 | Muradnagar | 45 | 22:00 | 187 | UttaraNew | 62 | 15:00
56 | GPH | 100 | 01:00 | 122 | Mymensingh | 206 | 19:30 | 188 | Zigatola | 73 | 19:00
57 | Ghatail | 80 | 07:00 | 123 | Naogaon | 139 | 23:00
58 | Ghorashal | 20 | 18:30 | 124 | Narail | 58 | 19:00
59 | Ghorashal-230 | 97 | 19:30 | 125 | Narinda | 69 | 13:00
60 | Goalpara | 36 | 20:00 | 126 | Narshingdi | 186 | 23:00
61 | Gollamari | 94 | 23:00 | 127 | Natore | 157 | 22:00
62 | Gopalganj | 112 | 22:00 | 128 | Nawabganj | 60.2 | 21:00
63 | Gulshan | 130 | 13:00 | 129 | Netrakona | 132 | 18:00
64 | Halishahar | 71 | 17:00 | 130 | New | 45 | 16:00
65 | HaripurSBU | 160 | 12:00 | 131 | Niamatpur | 78 | 22:00
66 | Hasnabad | 84 | 23:00 | 132 | Noapara | 45 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14223.6 | 151 |  | 14381.4
1:00 | 13856.72 | 147 |  | 14010.72
2:00 | 13542.04 | 133 |  | 13681.04
3:00 | 13161.32 | 114 |  | 13280.32
4:00 | 12841.33 | 104 |  | 12950.33
5:00 | 12684.32 | 82 |  | 12770.32
6:00 | 12365.67 | 63 |  | 12431.51
7:00 | 12441.38 | 82 |  | 12527.07
8:00 | 12168.25 | 129 |  | 12303.25
9:00 | 12554.76 | 103 |  | 12662.76
10:00 | 12745.91 | 66 |  | 12814.91
11:00 | 12988.25 | 53 |  | 13043.25
12:00 | 13470.7 | 53 |  | 13525.7
13:00 | 13896.34 | 0 |  | 13896.34
14:00 | 14097.72 | 0 |  | 14097.72
15:00 | 14176.24 | 121 |  | 14302.69
16:00 | 13935.69 | 137 |  | 14078.86
17:00 | 13713.29 | 86 |  | 13803.16
18:00 | 14302 | 142 |  | 14450.39
19:00 | 15507 | 329 |  | 15850.81
19:30 | 15728 | 260 |  | 15999.7
20:00 | 15705.5 | 253 |  | 15969.89
21:00 | 15753.9 | 265 |  | 16030.83
22:00 | 15661.77 | 228 |  | 15900.03
23:00 | 15693.83 | 217 |  | 15920.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6931.9 | 7291.7 | 14223.6 | DAILY GENERATION CURVE
00:30 | 6850.7 | 7189.46 | 14040.16
01:00 | 6769.5 | 7087.22 | 13856.72 | 23-09-2025
01:30 | 6733.9 | 6965.48 | 13699.38
02:00 | 6698.3 | 6843.74 | 13542.04
02:30 | 6627.8 | 6723.88 | 13351.68
03:00 | 6557.3 | 6604.02 | 13161.32
03:30 | 6526.65 | 6474.675 | 13001.325
04:00 | 6496 | 6345.33 | 12841.33
04:30 | 6462 | 6300.825 | 12762.825
05:00 | 6428 | 6256.32 | 12684.32
05:30 | 6292.335 | 6232.66 | 12524.995
06:00 | 6156.67 | 6209 | 12365.67
06:30 | 6167.005 | 6236.52 | 12403.525
07:00 | 6177.34 | 6264.04 | 12441.38
07:30 | 6095.895 | 6208.92 | 12304.815
08:00 | 6014.45 | 6153.8 | 12168.25
08:30 | 6089.22 | 6272.285 | 12361.505
09:00 | 6163.99 | 6390.77 | 12554.76
09:30 | 6212.305 | 6438.03 | 12650.335
10:00 | 6260.62 | 6485.29 | 12745.91
10:30 | 6406.92 | 6460.16 | 12867.08
11:00 | 6553.22 | 6435.03 | 12988.25
11:30 | 6744.21 | 6485.265 | 13229.475
12:00 | 6935.2 | 6535.5 | 13470.7
12:30 | 7071.205 | 6612.315 | 13683.52
13:00 | 7207.21 | 6689.13 | 13896.34
13:30 | 7279.55 | 6717.48 | 13997.03
14:00 | 7351.89 | 6745.83 | 14097.72
14:30 | 7323.14 | 6813.84 | 14136.98
15:00 | 7294.39 | 6881.85 | 14176.24
15:30 | 7258.165 | 6797.8 | 14055.965
16:00 | 7221.94 | 6713.75 | 13935.69
16:30 | 7192.68 | 6631.81 | 13824.49
17:00 | 7163.42 | 6549.87 | 13713.29
17:30 | 7362.21 | 6645.435 | 14007.645
18:00 | 7561 | 6741 | 14302
18:30 | 7732 | 7172.5 | 14904.5
19:00 | 7903 | 7604 | 15507
19:30 | 7944 | 7784 | 15728
20:00 | 7936.5 | 7769 | 15705.5
20:30 | 7967.7 | 7762 | 15729.7 |  | Executive Engineer
21:00 | 7998.9 | 7755 | 15753.9 |  | Network Operation Division
21:30 | 7977.2 | 7730.635 | 15707.835
22:00 | 7955.5 | 7706.27 | 15661.77
22:30 | 7944.35 | 7733.45 | 15677.8
23:00 | 7933.2 | 7760.63 | 15693.83

## En-Curve
QF-LDC-12
Date | 23-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3619 | 2009 | 891 | 38 | 48 | 1444.7 | 222 | 4799 | 0 | 288 | 848.9 | 0 | 0 | 16 | 151 | DAILY ENERGY CURVE
00:30 | 3607.5 | 1985.5 | 891 | 38 | 47 | 1445.46 | 221 | 4679 | 0 | 266.5 | 843.7 | 0 | 0 | 15.5 | 149 | 23-09-2025
01:00 | 3596 | 1962 | 891 | 38 | 46 | 1446.22 | 220 | 4559 | 0 | 245 | 838.5 | 0 | 0 | 15 | 147
01:30 | 3605.5 | 1948 | 891.5 | 38 | 45 | 1443.48 | 219 | 4418 | 0 | 245 | 825.9 | 0 | 0 | 20 | 140 | Energy Generated | 335.7409 |  | MKWHr
02:00 | 3615 | 1934 | 892 | 38 | 44 | 1440.74 | 218 | 4277 | 0 | 245 | 813.3 | 0 | 0 | 25 | 133 | Energy not Served | 3.058 |  | MKWHr
02:30 | 3621 | 1948 | 891.5 | 38 | 43 | 1400.88 | 217.5 | 4198 | 0 | 245 | 727.3 | 0 | 0 | 21.5 | 123.5 | Total Energy Requirement | 338.7989 |  | MKWHr
03:00 | 3627 | 1962 | 891 | 38 | 42 | 1361.02 | 217 | 4119 | 0 | 245 | 641.3 | 0 | 0 | 18 | 114
03:30 | 3637 | 1964.5 | 891.5 | 38 | 41 | 1310.175 | 217.5 | 4059 | 0 | 245 | 585.15 | 0 | 0 | 12.5 | 109
04:00 | 3647 | 1967 | 892 | 38 | 40 | 1259.33 | 218 | 3999 | 0 | 245 | 529 | 0 | 0 | 7 | 104
04:30 | 3643 | 1970.5 | 892 | 38 | 41 | 1260.825 | 218.5 | 3968.5 | 0 | 230 | 490 | 0 | 0 | 10.5 | 93
05:00 | 3639 | 1974 | 892 | 38 | 42 | 1262.32 | 219 | 3938 | 0 | 215 | 451 | 0 | 0 | 14 | 82
05:30 | 3623.5 | 1976.5 | 891.5 | 38 | 40 | 1261.8 | 219.5 | 3855.5 | 3.195 | 191.5 | 410 | 0 | 0 | 14 | 72.5
06:00 | 3608 | 1979 | 891 | 38 | 38 | 1261.28 | 220 | 3773 | 6.39 | 168 | 369 | 0 | 0 | 14 | 63
06:30 | 3604.5 | 1974.5 | 891 | 38 | 37 | 1188.28 | 220.5 | 3833 | 63.745 | 175.5 | 360.5 | 0 | 0 | 17 | 72.5
07:00 | 3601 | 1970 | 891 | 38 | 36 | 1115.28 | 221 | 3893 | 121.1 | 183 | 352 | 0 | 0 | 20 | 82
07:30 | 3530.5 | 1941.5 | 891 | 38 | 36 | 1033.285 | 221 | 3891 | 204.03 | 183 | 321 | 0 | 0 | 14.5 | 105.5
08:00 | 3460 | 1913 | 891 | 38 | 36 | 951.29 | 221 | 3889 | 286.96 | 183 | 290 | 0 | 0 | 9 | 129
08:30 | 3479.5 | 1921 | 891.5 | 38 | 35 | 984.78 | 220 | 3901 | 391.225 | 195.5 | 291.5 | 0 | 0 | 12.5 | 116
09:00 | 3499 | 1929 | 892 | 38 | 34 | 1018.27 | 219 | 3913 | 495.49 | 208 | 293 | 0 | 0 | 16 | 103
09:30 | 3438 | 1942.25 | 892 | 38 | 35 | 1017.925 | 219 | 3930 | 574.66 | 208.5 | 343.5 | 0 | 0 | 11.5 | 84.5
10:00 | 3377 | 1955.5 | 892 | 38 | 36 | 1017.58 | 219 | 3947 | 653.83 | 209 | 394 | 0 | 0 | 7 | 66
10:30 | 3408.5 | 1948.85 | 892 | 38 | 37 | 1018.98 | 219 | 3894 | 686.75 | 253 | 464.5 | 0 | 0 | 6.5 | 59.5
11:00 | 3440 | 1942.2 | 892 | 38 | 38 | 1020.38 | 219 | 3841 | 719.67 | 297 | 535 | 0 | 0 | 6 | 53
11:30 | 3495 | 1948.2 | 891.5 | 38 | 39 | 1030.095 | 219.5 | 3942 | 708.83 | 296.5 | 615.85 | 0 | 0 | 5 | 53
12:00 | 3550 | 1954.2 | 891 | 38 | 40 | 1039.81 | 220 | 4043 | 697.99 | 296 | 696.7 | 0 | 0 | 4 | 53
12:30 | 3543.5 | 1984.6 | 891.5 | 38 | 41 | 1073.23 | 219.5 | 4121 | 635.44 | 294.5 | 831.75 | 0 | 0 | 9.5 | 26.5
13:00 | 3537 | 2015 | 892 | 38 | 42 | 1106.65 | 219 | 4199 | 572.89 | 293 | 966.8 | 0 | 0 | 15 | 0
13:30 | 3525.5 | 2020 | 891.5 | 38 | 44 | 1160.28 | 219 | 4226 | 554.2 | 286.5 | 1014.55 | 0 | 0 | 17.5 | 0
14:00 | 3514 | 2025 | 891 | 38 | 46 | 1213.91 | 219 | 4253 | 535.51 | 280 | 1062.3 | 0 | 0 | 20 | 0
14:30 | 3488.5 | 2002.6 | 891 | 38 | 45 | 1256.455 | 219.5 | 4271.5 | 528.275 | 279.5 | 1091.15 | 0 | 0 | 25.5 | 60.5
15:00 | 3463 | 1980.2 | 891 | 38 | 44 | 1299 | 220 | 4290 | 521.04 | 279 | 1120 | 0 | 0 | 31 | 121
15:30 | 3437 | 1975.85 | 891 | 38 | 44 | 1311.5 | 220 | 4303 | 367.415 | 283.5 | 1160.2 | 0 | 0 | 24.5 | 129
16:00 | 3411 | 1971.5 | 891 | 38 | 44 | 1324 | 220 | 4316 | 213.79 | 288 | 1200.4 | 0 | 0 | 18 | 137
16:30 | 3349.5 | 1984 | 891.5 | 38 | 42 | 1340 | 220 | 4261.5 | 143.54 | 300 | 1237.95 | 0 | 0 | 16.5 | 111.5
17:00 | 3288 | 1996.5 | 892 | 38 | 40 | 1356 | 220 | 4207 | 73.29 | 312 | 1275.5 | 0 | 0 | 15 | 86
17:30 | 3356.5 | 1982 | 891.5 | 38 | 44 | 1339 | 220.5 | 4298 | 36.645 | 404 | 1383 | 0 | 0 | 14.5 | 114
18:00 | 3425 | 1967.5 | 891 | 38 | 48 | 1322 | 221 | 4389 | 0 | 496 | 1490.5 | 0 | 0 | 14 | 142
18:30 | 3407.5 | 1982 | 891 | 38 | 49 | 1381 | 221.5 | 4561.5 | 0 | 586 | 1776 | 0 | 0 | 11 | 235.5
19:00 | 3390 | 1996.5 | 891 | 38 | 50 | 1440 | 222 | 4734 | 0 | 676 | 2061.5 | 0 | 0 | 8 | 329
19:30 | 3390 | 1987 | 891 | 38 | 50 | 1440 | 222 | 4858 | 0 | 675 | 2169 | 0 | 0 | 8 | 260
20:00 | 3390 | 1993.5 | 891 | 38 | 50 | 1441 | 222 | 4832 | 0 | 674 | 2165 | 0 | 0 | 9 | 253
20:30 | 3408 | 2001.75 | 891 | 38 | 49 | 1447.5 | 222 | 4831 | 0 | 672.5 | 2159.45 | 0 | 0 | 9.5 | 259
21:00 | 3426 | 2010 | 891 | 38 | 48 | 1454 | 222 | 4830 | 0 | 671 | 2153.9 | 0 | 0 | 10 | 265
21:30 | 3448 | 2017 | 891 | 38 | 50 | 1449.135 | 222 | 4813.5 | 0 | 662 | 2106.7 | 0 | 0 | 10.5 | 246.5
22:00 | 3470 | 2024 | 891 | 38 | 52 | 1444.27 | 222 | 4797 | 0 | 653 | 2059.5 | 0 | 0 | 11 | 228
22:30 | 3456.5 | 2035.5 | 891 | 38 | 52 | 1443.85 | 222 | 4817.6 | 0 | 662.5 | 2051.85 | 0 | 0 | 7 | 222.5
23:00 | 3443 | 2047 | 891 | 38 | 52 | 1443.43 | 222 | 4838.2 | 0 | 672 | 2044.2 | 0 | 0 | 3 | 217
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 06:00 | 367 | 14:00 | Payra | 409 | 05:00 | 401 | 19:30
Ashuganj | 396 | 3:00 | 374 | 15:00 | Rahanpur | 402 | 08:00 | 384 | 00:00
Bhulta | 394 | 03:00 | 369 | 14:00 | Rampal | 401 | 06:00 | 387 | 18:30
Bibiana | 384 | 07:00 | 377 | 15:00
BIPTC | 406 | 04:00 | 395 | 19:00
Bogura | 390 | 08:00 | 370 | 00:00
Gopalganj | 390 | 05:00 | 377 | 19:30
Kaliakoir | 369 | 06:00 | 357 | 14:00
Madunaghat | 391 | 18:00 | 385 | 00:00
Meghnaghat | 379 | 05:00 | 372 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 04:00 | 217 | 12:00 | Kaliakoir | 230 | 02:00 | 220 | 14:00
AKSML | 233 | 17:00 | 224 | 01:00 | Keranigonj | 223 | 06:00 | 215 | 12:00
Aminbazar | 225 | 06:00 | 218 | 14:00 | Khulna(S) | 229 | 06:00 | 214 | 18:30
Ashuganj | 228 | 06:00 | 219 | 14:00 | Madunaghat | 233 | 17:00 | 225 | 00:00
Ashuganj-400 | 228 | 06:00 | 219 | 14:00 | Madunaghat-400 | 233 | 20:00 | 226 | 00:00
Baghabari | 233 | 08:00 | 223 | 00:00 | Maniknagar | 219 | 04:00 | 212 | 12:00
Barapukuria | 221 | 08:00 | 212 | 00:00 | Meghnaghat | 226 | 04:00 | 221 | 11:00
Barapukuria-230 | 221 | 08:00 | 212 | 00:00 | Meghnaghat-400 | 223 | 05:00 | 215 | 12:00
Barishal | 227 | 06:00 | 218 | 21:00 | Mirsorai | 234 | 17:00 | 221 | 00:00
Bheramara | 234 | 06:00 | 223 | 00:00 | Rajshahi | 233 | 08:00 | 219 | 00:00
Bhulta | 227 | 02:00 | 211 | 14:00 | Rampal | 229 | 06:00 | 216 | 18:30
Bibiana | 225 | 05:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 223 | 00:00 | Rampura | 226 | 03:00 | 208 | 15:00
Bogura | 233 | 08:00 | 221 | 00:00 | Shikalbaha | 232 | 19:00 | 222 | 00:00
Bogura-400 | 232 | 08:00 | 221 | 00:00 | Shyampur | 221 | 05:00 | 215 | 12:00
Borhanuddin | 232 | 08:00 | 226 | 18:00 | Siddhirganj | 220 | 07:00 | 215 | 12:00
BSRM | 233 | 17:00 | 221 | 00:00 | Sirajgonj | 238 | 08:00 | 231 | 00:00
Cumilla(N) | 221 | 04:00 | 214 | 14:00 | Sreepur | 223 | 03:00 | 217 | 00:00
Faridpur | 224 | 08:00 | 213 | 21:00 | Tongi | 222 | 05:00 | 212 | 15:00
Fenchuganj | 228 | 06:00 | 224 | 00:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 224 | 03:00 | 211 | 15:00
Gopalganj | 225 | 08:00 | 216 | 21:00
GPH | 232 | 16:00 | 222 | 00:00
Haripur | 221 | 06:00 | 215 | 12:00
Hasnabad | 222 | 05:00 | 215 | 12:00
Hathazari | 230 | 17:00 | 219 | 18:30
Ishurdi | 235 | 05:00 | 224 | 00:00
Jhenaidah | 230 | 06:00 | 215 | 18:30
Kachua | 221 | 18:00 | 208 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 124 | 13:00 | Lalmonirhat | 126 | 06:00 | 114 | 19:00
Agargaon | 136 | 05:00 | 129 | 12:00 | Madanganj | 129 | 05:00 | 125 | 12:00
Agrabad | 132 | 17:00 | 126 | 00:00 | Madaripur | 132 | 07:00 | 126 | 19:00
AKS | 130 | 19:30 | 124 | 14:00 | Madartek | 136 | 03:00 | 122 | 12:00
Aminbazar | 132 | 00:00 | 129 | 11:00 | Madunaghat | 134 | 17:00 | 129 | 00:00
Amnura | 136 | 08:00 | 125 | 00:00 | Magura | 133 | 07:00 | 120 | 18:30
Ashuganj | 137 | 06:00 | 133 | 20:00 | Mahasthangarh | 130 | 08:00 | 120 | 00:00
Bagerhat | 130 | 06:00 | 115 | 23:00 | Maijdee | 126 | 18:00 | 110 | 00:00
Bajitpur | 126 | 03:00 | 121 | 14:00 | Manikganj | 127 | 05:00 | 119 | 12:00
Bakulia | 133 | 17:00 | 127 | 00:00 | Maniknagar | 133 | 04:00 | 127 | 12:00
Banani | 135 | 02:00 | 123 | 15:00 | Matarbari | 118 | 10:00 | 107 | 00:00
Bangabhaban | 133 | 05:00 | 127 | 12:00 | Matuail | 128 | 02:00 | 124.3 | 12:00
Barapukuria | 134 | 06:00 | 124 | 19:00 | Millgate | 132 | 04:00 | 122 | 15:00
Barguna | 132 | 04:00 | 129 | 18:30 | Mirpur | 131 | 00:00 | 127 | 12:00
Barishal | 133 | 07:00 | 125 | 21:00 | Mirzapur | 129 | 08:00 | 122 | 14:00
Barishal-230 | 132 | 05:00 | 126 | 22:00 | Mithapukur | 127 | 06:00 | 119 | 00:00
Baroaulia | 133 | 21:00 | 126 | 00:00 | MI_Cement | 130 | 04:00 | 125 | 23:00
Baroirhat | 128 | 18:00 | 119 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 03:00 | 121 | 14:00 | Mogbazar | 138 | 03:00 | 125 | 12:00
BashundharaCement | 129 | 05:00 | 125 | 12:00 | Mongla | 131 | 08:00 | 118 | 18:30
Beanibazar | 128 | 08:00 | 120 | 19:30 | Motijheel | 133 | 05:00 | 127 | 12:00
Benapole | 130 | 07:00 | 117 | 18:30 | Muktagacha | 128 | 07:00 | 118 | 22:00
Bhaluka | 129 | 19:00 | 119 | 20:00 | Munshiganj | 129 | 04:00 | 125 | 10:00
Bhandaria | 128 | 07:00 | 115 | 18:30 | Muradnagar | 126 | 17:00 | 119 | 00:00
Bhangura | 132 | 06:00 | 126 | 00:00 | Mymensingh | 125 | 06:00 | 109 | 20:00
Bheramara | 137 | 09:00 | 131 | 00:00 | Naogaon | 128 | 10:00 | 115 | 00:00
Bheramara(GK) | 136 | 06:00 | 131 | 00:00 | Narail | 132 | 09:00 | 117 | 18:30
Bhulta | 126 | 02:00 | 121 | 12:00 | Narinda | 133 | 04:00 | 127 | 12:00
Bog-Sherpur | 131 | 08:00 | 123 | 00:00 | Narshingdi | 128 | 01:00 | 119 | 11:00
Bogura | 132 | 08:00 | 124 | 00:00 | Natore | 133 | 09:00 | 124 | 00:00
Bogura-230 | 132 | 08:00 | 123 | 00:00 | Nawabganj | 131 | 17:00 | 123 | 12:00
Brahmanbaria | 132 | 08:00 | 124 | 19:30 | Netrakona | 123 | 19:00 | 105 | 18:00
Cantonment | 135 | 02:00 | 128 | 14:00 | New | 132 | 06:00 | 124 | 16:00
Chandina | 128 | 18:00 | 123 | 00:00 | Niamatpur | 137 | 07:00 | 129 | 00:00
Chandpur | 134 | 18:00 | 120 | 10:00 | Noapara | 134 | 09:00 | 121 | 18:30
Chandraghona | 134 | 17:00 | 129 | 00:00 | Pabna | 135 | 08:00 | 128 | 00:00
Chapai | 136 | 09:00 | 129 | 00:00 | Palashbari | 126 | 08:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 05:00 | 125 | 12:00 | Panchagarh | 134 | 06:00 | 120 | 12:00
Chauddagram | 126 | 18:00 | 118 | 00:00 | Patiya | 130 | 20:00 | 125 | 00:00
Chhatak | 126 | 04:00 | 119 | 19:00 | Patuakhali | 133 | 07:00 | 130 | 00:00
Chowmuhani | 126 | 21:00 | 112 | 00:00 | Payra | 134 | 04:00 | 131 | 19:00
Chuadanga | 132 | 08:00 | 119 | 18:30 | PHP | 128 | 18:00 | 118 | 00:00
Coxsbazar | 122 | 11:00 | 108 | 00:00 | Postogola | 132 | 03:00 | 127 | 12:00
Cumilla(N) | 128 | 17:00 | 123 | 00:00 | Purbachal | 136 | 02:00 | 121 | 15:00
Cumilla(S) | 133 | 04:00 | 121 | 12:00 | Purbasadipur | 130 | 06:00 | 117 | 19:00
Daganbhuiyan | 124 | 17:00 | 113 | 02:00 | Rahanpur | 138 | 08:00 | 131 | 00:00
Daudkandi | 122 | 17:00 | 116 | 11:00 | Rahanpur-400 | 138 | 08:00 | 131 | 00:00
DhakaUniversity | 135 | 04:00 | 124 | 14:00 | Rahim | 129 | 04:00 | 125 | 11:00
Dhamrai | 132 | 03:00 | 125 | 13:00 | Rajbari | 131 | 06:00 | 123 | 23:00
Dhanmondi | 137 | 03:00 | 123 | 15:00 | Rajendrapur | 127 | 17:00 | 118 | 14:00
Dohazari | 126 | 17:00 | 119 | 00:00 | Rajshahi | 133 | 08:00 | 125 | 00:00
Faridpur | 133 | 05:00 | 126 | 21:00 | Rajshahi-230 | 133 | 08:00 | 125 | 00:00
Fatullah | 132 | 06:00 | 127 | 12:00 | Ramganj | 129 | 18:00 | 112 | 00:00
Fenchuganj | 134 | 06:00 | 131 | 23:00 | Rampur | 131 | 18:30 | 126 | 01:00
Feni | 127 | 18:00 | 115 | 10:00 | Rampura | 137 | 03:00 | 123 | 15:00
Ghatail | 125 | 08:00 | 116 | 22:00 | Rangamati | 132 | 17:00 | 129 | 00:00
Ghorashal | 136 | 22:00 | 127 | 14:00 | Rangpur | 128 | 06:00 | 119 | 19:00
Goalpara | 135 | 08:00 | 123 | 19:00 | Ruppur | 137 | 08:00 | 131 | 00:00
Gollamari | 136 | 23:00 | 126 | 17:00 | Saidpur | 129 | 06:00 | 118 | 19:00
Gopalganj | 133 | 08:00 | 124 | 19:00 | Satkhira | 132 | 04:00 | 118 | 18:30
Gopalganj-400 | 134 | 08:00 | 128 | 19:00 | Satmasjid | 135 | 06:00 | 129 | 12:00
Gulshan | 136 | 04:00 | 124 | 12:00 | Savar | 133 | 00:00 | 128 | 08:00
Halishahar | 132 | 19:00 | 126 | 00:00 | SevenRings | 134 | 06:00 | 127 | 15:00
Haripur | 129 | 03:00 | 125 | 12:00 | ShahCement | 130 | 05:00 | 125 | 12:00
HaripurSBU | 129 | 03:00 | 126 | 10:00 | Shahjadpur | 136 | 04:00 | 130 | 00:00
Hasnabad | 132 | 04:00 | 127 | 11:00 | Shahjibazar | 133 | 08:00 | 124 | 21:00
Hathazari | 134 | 19:30 | 128 | 00:00 | Shahmirpur | 133 | 17:00 | 127 | 00:00
Ishurdi | 138 | 08:00 | 131 | 00:00 | Shariatpur | 132 | 07:00 | 123 | 22:00
Jaldhaka | 126 | 06:00 | 115 | 19:00 | Sherpur | 124 | 07:00 | 112 | 14:00
Jamalpur | 127 | 07:00 | 116 | 14:00 | Shikalbaha | 123 | 17:00 | 116 | 00:00
Jashore | 132 | 09:00 | 118 | 18:30 | Shikalbaha-230 | 135 | 19:00 | 128 | 00:00
Jhenaidah | 135 | 07:00 | 121 | 18:30 | Shitalakhya | 130 | 04:00 | 125.4 | 12:00
Jhenaidah-230 | 135 | 08:00 | 124 | 18:30 | Sholosohor | 133 | 19:00 | 129 | 00:00
Joydebpur | 127 | 03:00 | 119 | 14:00 | Shyampur | 133 | 17:00 | 127 | 11:00
Joypurhat | 126 | 08:00 | 112 | 00:00 | Shyampur-230 | 132 | 04:00 | 127 | 12:00
Juldah | 132 | 19:00 | 127 | 00:00 | Siddhirganj | 129 | 05:00 | 125 | 11:00
Kabirpur | 132 | 02:00 | 120 | 19:30 | Sirajganj | 129 | 04:00 | 123 | 00:00
Kachua | 132 | 17:00 | 124 | 00:00 | Sonargaon | 127 | 05:00 | 122 | 12:00
Kaliakoir | 134 | 02:00 | 127 | 12:00 | Sreemongol | 131 | 08:00 | 124 | 19:30
Kallyanpur | 132 | 01:00 | 128 | 12:00 | Sreepur | 129 | 06:00 | 124 | 00:00
Kalurghat | 134 | 19:30 | 130 | 08:00 | Srinagar | 132 | 17:00 | 124 | 12:00
Kamrangirchar | 131 | 17:00 | 123 | 12:00 | SSM | 135 | 21:00 | 130 | 00:00
Kaptai | 132 | 6:00 | 125 | 13:00 | Sunamganj | 124 | 08:00 | 116 | 20:00
Kasba | 123 | 05:00 | 119 | 00:00 | Sylhet | 128 | 07:00 | 123 | 19:00
Kazla | 133 | 05:00 | 127 | 12:00 | Sylhet-132 | 128 | 08:00 | 124 | 19:30
Keranigonj | 131 | 18:00 | 124 | 12:00 | Tangail | 126 | 08:00 | 118 | 20:00
Khagrachori | 131 | 08:00 | 128 | 00:00 | Taraganj | 128 | 05:00 | 117 | 18:30
Khulna | 134 | 04:00 | 124 | 18:00 | Thakurgaon | 132 | 06:00 | 118 | 12:00
Khulna(S) | 135 | 06:00 | 124 | 18:30 | TK | 134 | 17:00 | 129 | 12:00
Khulshi | 130 | 18:00 | 125 | 00:00 | Tongi | 132 | 05:00 | 125 | 15:00
Kishoreganj | 127 | 19:00 | 118 | 19:30 | Ullahpara | 133 | 09:00 | 125 | 00:00
Kodda | 130 | 04:00 | 120 | 14:00 | Ullon | 137 | 03:00 | 123 | 15:00
KSRM | 133 | 17:00 | 127 | 00:00 | Uttara | 133 | 02:00 | 127 | 12:00
Kulaura | 133 | 07:00 | 128 | 20:00 | UttaraNew | 133 | 01:00 | 126 | 14:00
Kurigram | 125 | 13:00 | 114 | 19:00 | Zigatola | 132 | 18:00 | 125 | 12:00
Kushtia | 134 | 09:00 | 126 | 18:30
Laksam | 131 | 18:00 | 123 | 00:00
Lakshmipur | 126 | 18:00 | 111 | 00:00
Lalbag | 131 | 08:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division