## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-09-2025 | during | 28-09-2025 | during | 28-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 359 | 370 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 305 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 12 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 125 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 25.8 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 276 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 139 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 50 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 406 | 380 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 52 | 142 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2409 | 2835.8 | 5677.34 | 5737.34 | 5109.54 | 5129.54
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 5 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 214 | 195 | 195 | 195 | 195 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 56 | 99 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 68 | 70 | 70 | 56 | 70 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 24 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 106 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.8 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 99 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 41 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 8 | 102 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 108 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 143 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 795 | 602 | 1224 | 1224 | 1224 | 1224 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 11 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 265 | 265 | 265 | 265 | 265 | 265 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1683.8 | 2285 | 3285.47 | 3278.72 | 3271.47 | 3278.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 191 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 342 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 125 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 29 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 78 | 178 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 48 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 5 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 15 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 103 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 0 | 113 | 113 | 113 | 113
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 63 | 90 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 75 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1246 | 1574 | 2289.56 | 2219.56 | 2110.56 | 2040.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-09-2025 | during | 28-09-2025 | during | 28-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 81 | 65 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 76 | 76 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.24 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 22 | 22 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 223.24 | 162 | 372.6 | 320.5 | 372.6 | 320.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 56 | 57 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 10 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 390 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1256 | 1254 | 1293 | 1293 | 1215 | 1215
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 893 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 375 | 303 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.57 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 928 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2332.57 | 2479.2 | 3622.2 | 3552.2 | 3056.2 | 2986.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 402 | 622 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 63 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 970 | 1222 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.76 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1768.76 | 2456 | 2147 | 2146 | 2147 | 2146
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 50.7 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 196 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 25 | 25 | 27 | 27 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 95 | 95 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.87 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1016.42 | 1267.35 | 748 | 748 | 1250 | 1250 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.51 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2038.5 | 2530.35 | 2499.49 | 2332.99 | 2916.71 | 2750.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 141 | 139 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 109 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.8 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 194 | 0 | 182.71 | 0 | 182.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 367.8 | 363 | 616.71 | 398 | 616.71 | 398
System Total |  |  |  |  | 28823.2 | 27829.875 | 13325.67 | 15939.35 | 21803.37 | 21278.31 | 20815.79 | 20264.73
Forecast Scenario (28-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15630 |  | 0 |  | 15630
|  |  |  | 1:00 | 15230 |  | 0 |  | 15230
|  |  |  | 2:00 | 14710 |  | 0 |  | 14710
|  |  |  | 3:00 | 14180 |  | 0 |  | 14180
|  |  |  | 4:00 | 14010 |  | 0 |  | 14010
|  |  |  | 5:00 | 13690 |  | 0 |  | 13690
|  |  |  | 6:00 | 13220 |  | 0 |  | 13220
|  |  |  | 7:00 | 13170 |  | 0 |  | 13170
|  |  |  | 8:00 | 13280 |  | 0 |  | 13280
|  |  |  | 9:00 | 13380 |  | 0 |  | 13380
|  |  |  | 10:00 | 13470 |  | 0 |  | 13470
|  |  |  | 11:00 | 13720 |  | 0 |  | 13720
|  |  |  | 12:00 | 14010 |  | 0 |  | 14010
|  |  |  | 13:00 | 14500 |  | 0 |  | 14500
|  |  |  | 14:00 | 14350 |  | 0 |  | 14350
|  |  |  | 15:00 | 14630 |  | 0 |  | 14630
|  |  |  | 16:00 | 14230 |  | 0 |  | 14230
|  |  |  | 17:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:00 | 14800 |  | 0 |  | 14800
|  |  |  | 18:30 | 15300 |  | 0 |  | 15300
|  |  |  | 19:00 | 16300 |  | 0 |  | 16300
|  |  |  | 19:30 | 16380 |  | 0 |  | 16380
|  |  |  | 20:00 | 16150 |  | 0 |  | 16150
|  |  |  | 21:00 | 16030 |  | 0 |  | 16030
|  |  |  | 22:00 | 16000 |  | 0 |  | 16000
|  |  |  | 23:00 | 15970 |  | 0 |  | 15970
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 14010.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16380.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16380.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.76 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:53 hrs on 28-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-09-2025 | [28 empty] | Date: | 27-09-2025 | [28 empty] | Date: | 27-09-2025 | [28 empty] | Date: | 27-09-2025 | [28 empty] | Date: | 27-09-2025 | [14 empty] | Date: | 27-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 442 | 17 | 17 | 141 | 60 | 293 | 15 | 17 | 83 | 0 | 420 | 183 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 108 | 16 | 41 | 0 | 3 | 66 | 22 | 54.36 | 25 | 25 | 0 | 217 | 101 | 42 | 265 | 72 | 0 | 19 | 0 | 98 | 218 | 0 | 0 | 0 | 606 | 0 | 51 | 50 | 8 | 0 | 350 | 330 | 39 | 179 | 37 | 57 | 0 | 179 | 0 | 20 | 60 | 50 | 43 | 0 | 34 | 315 | 0 | 369 | 30 | 57 | 156 | 10 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 102 | 0 | 0 | 0 | 7578.36 | 894 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1216 | 0 | 47 | 0 | 113 | 113 | 0 | 95 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 199 | 0 | 193 | 0 | 0 | 0 | 399 | 0 | 0 | 137 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 110 | 0 | 624 | 1232 | 0 | 7672.2 | 15250.56 | 108.43
01:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 405 | 17 | 0 | 149 | 45 | 293 | 15 | 32 | 125 | 0 | 350 | 283 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 72 | 16 | 38 | 0 | 8 | 66 | 22 | 54.36 | 25 | 25 | 0 | 218 | 96 | 42 | 265 | 30 | 0 | 19 | 0 | 90 | 218 | 0 | 0 | 0 | 602 | 0 | 51 | 50 | 8 | 0 | 354 | 330 | 37 | 180 | 37 | 73 | 0 | 154 | 0 | 20 | 30 | 50 | 16 | 0 | 36 | 305 | 0 | 376 | 30 | 57 | 151 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 102 | 0 | 0 | 0 | 7392.36 | 893 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 1210 | 0 | 47 | 0 | 113 | 113 | 0 | 95 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 187 | 0 | 188 | 0 | 0 | 0 | 391 | 0 | 0 | 139 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 115 | 110 | 0 | 624 | 1140 | 0 | 7406 | 14798.36 | 108.43
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 415 | 17 | 0 | 149 | 45 | 195 | 15 | 35 | 142 | 0 | 300 | 283 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 17 | 16 | 19 | 0 | 21 | 66 | 22 | 0 | 25 | 25 | 0 | 217 | 96 | 42 | 265 | 0 | 0 | 19 | 0 | 92 | 218 | 0 | 0 | 0 | 600 | 0 | 51 | 50 | 8 | 0 | 353 | 330 | 10 | 203 | 37 | 90 | 0 | 142 | 0 | 20 | 31 | 50 | 0 | 0 | 36 | 305 | 0 | 377 | 30 | 57 | 150 | 6 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 102 | 0 | 0 | 0 | 7099 | 893 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 1210 | 0 | 47 | 0 | 113 | 113 | 0 | 41 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 186 | 0 | 188 | 0 | 0 | 0 | 398 | 0 | 0 | 140 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 115 | 110 | 0 | 623 | 1110 | 0 | 7273 | 14372 | 108.43
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 398 | 17 | 0 | 149 | 45 | 95 | 15 | 35 | 142 | 0 | 300 | 282 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 18 | 22 | 0 | 0 | 17 | 16 | 0 | 0 | 13 | 66 | 22 | 0 | 25 | 25 | 0 | 215 | 95 | 42 | 265 | 0 | 0 | 19 | 0 | 90 | 218 | 0 | 0 | 0 | 602 | 0 | 51 | 50 | 8 | 0 | 356 | 330 | 10 | 208 | 37 | 90 | 0 | 138 | 0 | 20 | 31 | 48 | 0 | 0 | 36 | 300 | 0 | 351 | 30 | 57 | 150 | 6 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 102 | 0 | 0 | 0 | 6921 | 894 | 379 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 1210 | 0 | 47 | 0 | 113 | 113 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 186 | 0 | 187 | 0 | 0 | 0 | 387 | 0 | 0 | 141 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 115 | 110 | 0 | 623 | 1085 | 0 | 7188 | 14109 | 108.43
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 416 | 17 | 0 | 149 | 15 | 45 | 0 | 0 | 141 | 0 | 300 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 66 | 0 | 0 | 25 | 25 | 0 | 215 | 33 | 42 | 265 | 0 | 0 | 19 | 0 | 87 | 218 | 0 | 0 | 0 | 600 | 0 | 51 | 50 | 8 | 0 | 355 | 330 | 10 | 205 | 37 | 90 | 0 | 133 | 0 | 20 | 0 | 46 | 0 | 0 | 36 | 305 | 0 | 376 | 30 | 57 | 150 | 6 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 102 | 0 | 0 | 0 | 6645 | 894 | 383 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 1208 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 186 | 0 | 0 | 0 | 401 | 0 | 0 | 142 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 115 | 110 | 0 | 623 | 1080 | 0 | 6921 | 13566 | 108.42
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 420 | 17 | 0 | 149 | 15 | 45 | 0 | 0 | 119 | 0 | 300 | 294 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 66 | 0 | 0 | 25 | 25 | 0 | 217 | 33 | 42 | 265 | 0 | 0 | 19 | 0 | 34 | 218 | 0 | 0 | 0 | 600 | 0 | 51 | 40 | 8 | 0 | 353 | 330 | 10 | 205 | 37 | 90 | 0 | 140 | 0 | 20 | 0 | 46 | 0 | 0 | 0 | 310 | 0 | 386 | 30 | 57 | 153 | 6 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 103 | 0 | 0 | 0 | 6474 | 894 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 190 | 0 | 0 | 0 | 411 | 0 | 0 | 141 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 110 | 0 | 625 | 1080 | 0 | 6856 | 13330 | 108.42
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 393 | 17 | 0 | 149 | 15 | 45 | 0 | 0 | 54 | 0 | 300 | 286 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 33 | 0 | 0 | 25 | 25 | 0 | 217 | 0 | 42 | 265 | 0 | 0 | 19 | 0 | 25 | 218 | 0 | 0 | 0 | 603 | 0 | 51 | 24 | 8 | 0 | 356 | 330 | 10 | 205 | 37 | 68 | 0 | 68 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 372 | 30 | 57 | 157 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 104 | 0 | 1.03 | 0 | 6166.03 | 893 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1123 | 0 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 0.43 | 193 | 0 | 194 | 0 | 0 | 0 | 402 | 0 | 0.04 | 141 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 169 | 115 | 110 | 0 | 624 | 1050 | 0 | 6799.49 | 12965.52 | 108.42
07:00 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 408 | 17 | 0 | 136 | 30 | 45 | 0 | 0 | 17 | 0 | 300 | 292 | 0 | 0 | 0 | 270 | 0 | 0 | 2 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 33 | 0 | 0 | 25 | 25 | 0.39 | 217 | 0 | 26 | 265 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 600 | 6 | 51 | 24 | 8 | 0 | 352 | 330 | 10 | 205 | 37 | 65 | 0 | 64 | 0 | 20 | 0 | 34 | 0 | 5 | 0 | 320 | 0 | 388 | 30 | 57 | 158 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 103 | 0 | 11.45 | 0 | 6150.84 | 893 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1033 | 0 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.48 | 17 | 0 | 0 | 6.61 | 195 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0.58 | 143 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0.6 | 14 | 0.07 | 0 | 170 | 115 | 110 | 0 | 623 | 1000 | 0 | 6715.34 | 12866.18 | 108.41
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 392 | 17 | 0 | 149 | 30 | 15 | 0 | 13 | 15 | 0 | 300 | 290 | 0 | 0 | 0 | 270 | 0 | 0 | 5 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 17 | 0 | 0 | 25 | 25 | 0.96 | 217 | 0 | 6 | 261 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 600 | 5 | 51 | 24 | 8 | 0 | 352 | 330 | 10 | 203 | 37 | 61 | 0 | 61 | 0 | 20 | 0 | 30 | 0 | 23 | 0 | 305 | 0 | 388 | 30 | 57 | 152 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 104 | 1 | 11.5 | 0 | 6064.46 | 885 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 959 | 0 | 1216.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.98 | 52 | 0 | 0 | 14.62 | 194 | 0 | 189 | 0 | 0 | 0 | 400 | 0 | 1.45 | 144 | 0 | 35 | 7 | 34 | 0 | 0 | 0 | 1.1 | 54 | 0.16 | 0 | 170 | 115 | 110 | 0 | 623 | 980 | 0 | 6682.37 | 12746.83 | 108.41
09:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 395 | 17 | 0 | 149 | 30 | 15 | 0 | 35 | 40 | 0 | 300 | 290 | 0 | 0 | 0 | 270 | 0 | 0 | 22 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 25 | 25 | 1.55 | 220 | 0 | 4 | 265 | 0 | 0 | 29 | 0 | 9 | 218 | 0 | 0 | 0 | 600 | 7 | 51 | 24 | 0 | 0 | 350 | 330 | 10 | 208 | 37 | 60 | 0 | 34 | 0 | 20 | 0 | 32 | 0 | 32 | 0 | 305 | 0 | 368 | 30 | 57 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 77 | 9 | 102 | 1 | 38.62 | 5 | 6157.17 | 885 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 897 | 0 | 1123.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.93 | 70 | 0 | 0 | 38.85 | 182 | 0 | 183 | 0 | 0 | 0 | 375 | 0 | 3.37 | 145 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 2 | 58 | 0.31 | 0 | 168 | 115 | 110 | 0 | 612 | 950 | 0 | 6496.43 | 12653.6 | 108.41
10:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 404 | 35 | 0 | 149 | 15 | 15 | 0 | 35 | 100 | 0 | 300 | 302 | 0 | 0 | 0 | 300 | 0 | 0 | 26 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 25 | 25 | 3.13 | 220 | 0 | 2 | 265 | 0 | 0 | 50 | 0 | 32 | 217 | 0 | 0 | 0 | 660 | 12 | 51 | 0 | 0 | 0 | 347 | 330 | 10 | 210 | 20 | 61 | 0 | 31 | 0 | 20 | 0 | 32 | 0 | 62 | 0 | 310 | 0 | 389 | 30 | 57 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 77 | 9 | 99 | 2 | 48.15 | 6 | 6395.28 | 889 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 903 | 0 | 1048.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.84 | 85 | 0 | 0 | 18.07 | 174 | 0 | 175 | 0 | 0 | 0 | 354 | 0 | 1.75 | 144 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 7.3 | 113 | 0.7 | 0 | 170 | 115 | 110 | 0 | 533 | 942 | 0 | 6361.55 | 12756.83 | 108.4
11:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 434 | 35 | 6 | 149 | 15 | 35 | 0 | 35 | 108 | 0 | 300 | 305 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 108 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 25 | 25 | 3.6 | 220 | 0 | 2 | 265 | 0 | 0 | 50 | 0 | 31 | 215 | 0 | 0 | 0 | 795 | 19 | 51 | 0 | 0 | 0 | 338 | 330 | 10 | 205 | 20 | 66 | 0 | 33 | 0 | 20 | 0 | 32 | 0 | 74 | 0 | 315 | 0 | 389 | 30 | 57 | 157 | 12 | 0 | 84 | 30 | 0 | 15 | 166 | 0 | 75 | 9 | 94 | 2 | 51.25 | 6 | 6638.85 | 888 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33.41 | 915 | 0 | 1037.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.45 | 114 | 0 | 0 | 42.35 | 178 | 0 | 179 | 0 | 0 | 0 | 394 | 0 | 4.2 | 141 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 7.2 | 119 | 0.49 | 0 | 174 | 115 | 110 | 0 | 401 | 948 | 0 | 6311.71 | 12950.56 | 108.4
12:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 406 | 35 | 17 | 139 | 45 | 145 | 12 | 35 | 108 | 0 | 300 | 299 | 0 | 0 | 35 | 300 | 0 | 0 | 34 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 3.8 | 220 | 8 | 5 | 265 | 0 | 0 | 50 | 5 | 56 | 215 | 0 | 0 | 0 | 795 | 11 | 51 | 20 | 0 | 0 | 339 | 330 | 10 | 199 | 20 | 63 | 0 | 78 | 8 | 20 | 0 | 28 | 5 | 75 | 0 | 320 | 0 | 386 | 30 | 56 | 158 | 12 | 0 | 83 | 30 | 0 | 15 | 166 | 0 | 76 | 9 | 81 | 1 | 50.24 | 6 | 6818.04 | 893 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98.57 | 928 | 0 | 1016.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.7 | 110 | 0 | 0 | 66.51 | 189 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 5.87 | 141 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 7.8 | 194 | 0.76 | 0 | 171 | 115 | 110 | 0 | 402 | 970 | 0 | 6507.63 | 13325.67 | 108.39
13:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 407 | 35 | 17 | 132 | 60 | 195 | 50 | 35 | 108 | 0 | 300 | 296 | 0 | 0 | 35 | 326 | 0 | 0 | 34 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 5 | 0 | 9 | 0 | 0 | 0 | 25 | 25 | 3.36 | 220 | 23 | 10 | 265 | 8 | 0 | 50 | 17 | 89 | 214 | 0 | 0 | 0 | 790 | 3 | 51 | 72 | 6 | 0 | 334 | 330 | 10 | 200 | 20 | 49 | 0 | 125 | 8 | 20 | 32 | 44 | 28 | 71 | 0 | 320 | 0 | 389 | 30 | 57 | 156 | 12 | 0 | 83 | 30 | 0 | 15 | 166 | 0 | 76 | 9 | 70 | 1 | 48.03 | 6 | 7161.39 | 893 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 1036 | 0 | 1061.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.92 | 110 | 0 | 0 | 50.21 | 202 | 0 | 203 | 0 | 0 | 0 | 414 | 0 | 4.57 | 141 | 0 | 35 | 30 | 34 | 0 | 0 | 0 | 7.5 | 89 | 0.7 | 0 | 190 | 115 | 110 | 0 | 402 | 1040 | 0 | 6673.43 | 13834.82 | 108.38
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 409 | 54 | 17 | 145 | 60 | 195 | 55 | 35 | 108 | 0 | 300 | 288 | 0 | 0 | 35 | 300 | 0 | 0 | 27 | 52 | 19.5 | 22 | 0 | 0 | 0 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 25 | 25 | 2.4 | 220 | 51 | 8 | 265 | 30 | 0 | 50 | 17 | 97 | 214 | 0 | 0 | 0 | 790 | 4 | 51 | 102 | 8 | 0 | 340 | 330 | 10 | 193 | 20 | 50 | 0 | 103 | 11 | 20 | 30 | 44 | 34 | 62 | 0 | 320 | 0 | 387 | 30 | 57 | 151 | 12 | 0 | 83 | 30 | 0 | 15 | 166 | 0 | 77 | 9 | 69 | 2 | 42.56 | 6 | 7266.46 | 894 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1075 | 0 | 1125.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.43 | 110 | 0 | 0 | 47.13 | 193 | 0 | 196 | 0 | 0 | 0 | 394 | 0 | 4.34 | 139 | 0 | 35 | 31 | 34 | 0 | 0 | 0 | 5.9 | 174 | 0.66 | 0 | 219 | 115 | 110 | 0 | 402 | 1090 | 0 | 6900.02 | 14166.48 | 108.37
15:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 435 | 54 | 17 | 149 | 60 | 220 | 55 | 17 | 108 | 0 | 300 | 304 | 0 | 0 | 17 | 300 | 0 | 0 | 22 | 52 | 19.5 | 22 | 0 | 0 | 0 | 0 | 70 | 0 | 13 | 0 | 0 | 0 | 25 | 25 | 2.6 | 220 | 51 | 2 | 265 | 84 | 0 | 50 | 17 | 89 | 212 | 0 | 0 | 0 | 790 | 5 | 51 | 107 | 8 | 0 | 333 | 330 | 10 | 205 | 20 | 51 | 0 | 104 | 12 | 20 | 70 | 44 | 34 | 21 | 0 | 325 | 0 | 379 | 30 | 57 | 153 | 8 | 0 | 83 | 30 | 0 | 15 | 165 | 0 | 76 | 9 | 70 | 2 | 38.21 | 6 | 7363.31 | 904 | 361 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75.58 | 1114 | 0 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.26 | 86 | 0 | 0 | 11.86 | 186 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 0 | 137 | 0 | 35 | 24 | 34 | 0 | 0 | 0 | 4.7 | 104 | 0.45 | 0 | 221 | 115 | 110 | 0 | 403 | 1110 | 0 | 6835.85 | 14199.16 | 108.36
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 409 | 54 | 17 | 144 | 86 | 275 | 55 | 35 | 108 | 0 | 300 | 180 | 0 | 0 | 35 | 300 | 0 | 0 | 4 | 52 | 20.5 | 22 | 0 | 0 | 0 | 0 | 70 | 0 | 2 | 0 | 0 | 0 | 25 | 25 | 0.27 | 218 | 51 | 5 | 265 | 83 | 0 | 50 | 17 | 88 | 214 | 0 | 0 | 0 | 790 | 7 | 51 | 110 | 8 | 0 | 339 | 330 | 10 | 195 | 20 | 51 | 0 | 104 | 0 | 20 | 60 | 42 | 43 | 28 | 0 | 320 | 0 | 386 | 30 | 57 | 153 | 13 | 0 | 83 | 30 | 0 | 15 | 166 | 0 | 76 | 9 | 70 | 1 | 21.44 | 6 | 7272.21 | 904 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1105 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.62 | 34 | 0 | 0 | 8.76 | 183 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0.75 | 137 | 0 | 35 | 17 | 34 | 0 | 0 | 0 | 2.9 | 42 | 0.08 | 0 | 218 | 115 | 110 | 0 | 402 | 1101 | 0 | 6760.11 | 14032.32 | 108.35
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 362 | 54 | 26 | 133 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 200 | 0 | 0 | 55 | 300 | 0 | 0 | 5 | 52 | 20.5 | 22 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0.04 | 217 | 49 | 10 | 265 | 73 | 0 | 50 | 17 | 91 | 214 | 0 | 0 | 0 | 790 | 3 | 51 | 110 | 8 | 0 | 327 | 315 | 10 | 182 | 20 | 51 | 0 | 104 | 0 | 17 | 60 | 40 | 39 | 10 | 0 | 310 | 0 | 326 | 30 | 57 | 153 | 13 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 76 | 9 | 70 | 0 | 2.9 | 6 | 7133.44 | 904 | 345 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1077 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 6 | 0 | 0 | 3.26 | 173 | 0 | 181 | 0 | 0 | 0 | 336 | 0 | 0.28 | 137 | 0 | 35 | 7 | 34 | 0 | 0 | 0 | 0.9 | 16 | 0.03 | 0 | 210 | 115 | 110 | 0 | 373 | 1096 | 0 | 6478.35 | 13611.79 | 108.34
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 450 | 54 | 35 | 133 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 291 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 125 | 21.5 | 22 | 0 | 0 | 8 | 20 | 75 | 0 | 0 | 66 | 27 | 4 | 25 | 25 | 0 | 218 | 46 | 12 | 265 | 108 | 0 | 50 | 17 | 93 | 214 | 0 | 0 | 0 | 730 | 0 | 51 | 108 | 8 | 0 | 322 | 290 | 10 | 201 | 20 | 52 | 0 | 144 | 0 | 17 | 72 | 44 | 34 | 0 | 18 | 305 | 0 | 385 | 30 | 57 | 150 | 10 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 76 | 9 | 70 | 0 | 0 | 11 | 7529.5 | 905 | 337 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 1267 | 0 | 0 | 0 | 40 | 10 | 0 | 52 | 10 | 8 | 0 | 0 | 10 | 0 | 0 | 169 | 0 | 177 | 0 | 0 | 0 | 388 | 0 | 0 | 139 | 0 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 280 | 115 | 110 | 0 | 450 | 1040 | 7 | 6768.29 | 14297.79 | 108.33
19:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 408 | 54 | 35 | 137 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 289 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 69 | 67 | 99 | 0 | 0 | 66 | 64 | 17 | 25 | 25 | 0 | 219 | 93 | 10 | 265 | 152 | 0 | 50 | 17 | 103 | 215 | 0 | 0 | 0 | 670 | 0 | 51 | 115 | 8 | 0 | 342 | 330 | 10 | 198 | 20 | 84 | 0 | 180 | 0 | 17 | 100 | 44 | 34 | 0 | 29 | 315 | 0 | 388 | 30 | 57 | 156 | 10 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 76 | 9 | 69 | 0 | 0 | 12 | 8041 | 905 | 328 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1271 | 0 | 48 | 0 | 100 | 90 | 0 | 94 | 31 | 16 | 0 | 0 | 26 | 0 | 0 | 193 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 0 | 139 | 0 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 307 | 115 | 110 | 0 | 625 | 1165 | 17 | 7700.2 | 15741.2 | 108.33
19:30 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 385 | 54 | 35 | 137 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 296 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 125 | 25.5 | 22 | 0 | 0 | 108 | 99 | 106 | 0 | 0 | 66 | 68 | 17 | 25 | 25 | 0 | 220 | 95 | 14 | 265 | 151 | 0 | 50 | 17 | 98 | 216 | 0 | 0 | 0 | 612 | 0 | 51 | 125 | 8 | 0 | 342 | 330 | 10 | 198 | 20 | 90 | 0 | 180 | 0 | 17 | 105 | 46 | 34 | 0 | 29 | 310 | 0 | 388 | 30 | 57 | 155 | 10 | 0 | 84 | 30 | 0 | 16 | 164 | 0 | 77 | 9 | 65 | 0 | 0 | 12 | 8056.5 | 905 | 321 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1270 | 0 | 40 | 0 | 113 | 102 | 0 | 94 | 36 | 25 | 0 | 0 | 26 | 0 | 0 | 181 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 307 | 115 | 110 | 0 | 623 | 1220 | 17 | 7755.2 | 15811.7
20:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 380 | 54 | 31 | 140 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 299 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 140 | 25.8 | 22 | 0 | 0 | 108 | 99 | 106 | 0 | 1 | 66 | 68 | 17 | 25 | 25 | 0 | 219 | 101 | 20 | 265 | 154 | 0 | 50 | 17 | 97 | 216 | 0 | 0 | 0 | 604 | 0 | 51 | 125 | 8 | 0 | 342 | 330 | 10 | 204 | 20 | 90 | 0 | 180 | 0 | 17 | 105 | 48 | 34 | 0 | 29 | 305 | 0 | 386 | 30 | 57 | 155 | 10 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 9 | 65 | 0 | 0 | 12 | 8079.8 | 904 | 316 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1267 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 31 | 35 | 0 | 0 | 26 | 0 | 0 | 184 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 0 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 307 | 115 | 110 | 0 | 624 | 1220 | 17 | 7791.2 | 15871 | 108.32
21:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 380 | 54 | 17 | 149 | 125 | 276 | 55 | 55 | 108 | 0 | 300 | 305 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 142 | 25.8 | 22 | 0 | 0 | 108 | 99 | 106 | 0 | 11 | 66 | 68 | 41 | 25 | 25 | 0 | 220 | 102 | 24 | 265 | 143 | 0 | 50 | 17 | 99 | 214 | 0 | 0 | 0 | 602 | 0 | 51 | 125 | 8 | 0 | 342 | 330 | 10 | 191 | 20 | 90 | 0 | 178 | 0 | 15 | 103 | 48 | 34 | 0 | 29 | 315 | 0 | 390 | 30 | 57 | 155 | 10 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 65 | 0 | 0 | 12 | 8110.8 | 904 | 303 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1267.35 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 38 | 43 | 0 | 0 | 26 | 0 | 0 | 186 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 139 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 307 | 115 | 110 | 0 | 622 | 1222 | 17 | 7828.55 | 15939.35 | 108.32
22:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 380 | 23.7 | 17 | 149 | 125 | 293 | 55 | 55 | 90 | 0 | 300 | 300 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 142 | 24 | 22 | 0 | 0 | 108 | 69 | 101 | 0 | 5 | 66 | 68 | 54.36 | 25 | 25 | 0 | 220 | 105 | 25 | 265 | 144 | 0 | 40 | 17 | 96 | 214 | 0 | 0 | 0 | 602 | 0 | 51 | 127 | 8 | 0 | 348 | 330 | 10 | 174 | 20 | 77 | 0 | 181 | 0 | 17 | 98 | 48 | 34 | 0 | 29 | 310 | 0 | 386 | 30 | 57 | 156 | 10 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 77 | 9 | 61 | 0 | 0 | 12 | 8005.06 | 905 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1266.38 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 36 | 43 | 0 | 0 | 26 | 0 | 0 | 187 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 141 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 115 | 140 | 0 | 623 | 1224 | 17 | 7870.58 | 15875.64 | 108.31
23:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 330 | 21.5 | 17 | 149 | 125 | 297 | 55 | 55 | 90 | 0 | 300 | 284 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 52 | 24.5 | 22 | 0 | 0 | 108 | 16 | 103 | 0 | 4 | 66 | 68 | 54.36 | 25 | 25 | 0 | 217 | 105 | 26 | 256 | 140 | 0 | 37 | 17 | 90 | 214 | 0 | 0 | 0 | 602 | 0 | 51 | 122 | 8 | 0 | 349 | 330 | 10 | 167 | 20 | 60 | 0 | 180 | 0 | 17 | 100 | 48 | 34 | 0 | 29 | 300 | 0 | 387 | 30 | 57 | 157 | 10 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 78 | 9 | 60 | 0 | 0 | 12 | 7721.36 | 905 | 280 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1260.58 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 36 | 43 | 0 | 0 | 26 | 0 | 0 | 192 | 0 | 196 | 0 | 0 | 0 | 411 | 0 | 0 | 140 | 0 | 95 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 214 | 0 | 623 | 1225 | 17 | 7939.78 | 15661.14 | 108.31
Total KWH | 0 | 1066560 | 324000 | 0 | 0 | 0 | 0 | 0 | 846000 | 0 | 9628460 | 777960 | 301680 | 3508704 | 1591680 | 4288789 | 739500 | 794023 | 2368800 | 0 | 7674000 | 6751127 | 0 | 0 | 688502 | 7362094 | 0 | 0 | 205615 | 2457600 | 456600 | 529200 | 0 | 0 | 817964 | 451636 | 1025280 | 0 | 203520 | 872287 | 458448 | 340095 | 597120 | 603840 | 20277 | 5304200 | 1351564 | 525600 | 6320000 | 1296364 | 0 | 919680 | 207531 | 1723745 | 5002155 | 0 | 0 | 0 | 16069089 | 99495 | 1239048 | 1787818 | 167273 | 0 | 8526300 | 7938000 | 266880 | 4804000 | 6503476 | 1664640 | 0 | 2936640 | 43680 | 432040 | 1054500 | 1014512 | 463018 | 488436 | 339680 | 7580000 | 0 | 9445000 | 716000 | 1340520 | 3705300 | 237312 | 0 | 1980480 | 719904 | 0 | 407000 | 4395050 | 0 | 1824000 | 201600 | 1928640 | 13150 | 317660 | 139440 | 171191781 | 21716363 | 8720640 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 627120 | 26094550 | 0 | 27681818 | 0 | 385599 | 0 | 1083072 | 1120320 | 0 | 694372 | 269505 | 198845 | 279782 | 729890 | 228190 | 0 | 325496 | 4499635 | 0 | 4798755 | 0 | 0 | 0 | 9586400 | 0 | 27300 | 3470000 | 0 | 1646354 | 201329 | 1679280 | 0 | 0 | 0 | 42907.56 | 1091520 | 4204 | 444960 | 5367000 | 2753000 | 2798500 | 0 | 13089600 | 26753454.55 | 115200 | 169436961.11 | 340628742.11

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13325.67 | MW | 12:00 Hr. | Energy Generated |  |  | 340.6287 |  | MKWHr.
| Day Peak Demand |  |  | 13359.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.86 |  | MKWHr.
| Evening Peak Generation |  |  | 15939.35 | MW | 21:00 Hr. | Energy Demand |  |  | 342.4887 |  | MKWHr.
| Evening Peak Demand |  |  | 16091.35 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 12653.6 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 974.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 15939.35 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6791 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.2475 | 0 | 18.9078 | 0 | 0 | 0.20561 | 0 | 0 | 52.3609 | Gas | 134.2644 | Gas | 483386334.36
| Chattogram Zone |  |  | 5.5278 | 22.3891 | 10.6656 | 0 | 5.3042 | 0.11977 | 0 | 0.20352 | 44.2099 | Coal | 97.1637 | Coal | 537050323.7035
| Cumilla Zone |  |  | 29.877 | 0 | 8.29 | 0 | 0 | 0.48844 | 1.0145 | 0 | 39.6699 | HFO | 47.8941 | HFO | 883220402.58
| Mymensingh Zone |  |  | 1.9286 | 0 | 2.165 | 0 | 0 | 0.33081 | 0 | 0 | 4.4245 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.5266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5266 | Hydro | 5.3042 | Hydro | 530420
| Khulna Zone |  |  | 8.7206 | 26.0946 | 0 | 0 | 0 | 0.62712 | 22.6284 | 0 | 58.0707 | Solar | 4.4742 | Solar | 68318194.7776
| Barishal Zone |  |  | 5.5515 | 45.2101 | 0.56016 | 0 | 0 | 0.004204 | 0 | 0 | 51.3259 | Import | 51.3247 | Import | 299588752.15
| Rajshahi Zone |  |  | 18.8848 | 0 | 3.9799 | 0 | 0 | 1.3625 | 27.6818 | 0 | 51.909 | Wind | 0.20352 | Wind | 2999884.8
| Rangpur Zone |  |  | 0 | 3.47 | 3.3256 | 0 | 0 | 1.3358 | 0 | 0 | 8.1314
| Total |  |  | 134.2644 | 97.1637 | 47.8941 | 0 | 5.3042 | 4.4742 | 51.3247 | 0.20352 | 340.6287
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 483386334.36 |  | Hydro | 530420
|  |  |  | Coal | 537050323.7035 |  | Solar | 68318194.7776
|  |  |  | HFO | 883220402.58 |  | Import | 299588752.15
|  |  |  | HSD | 0 |  | Wind | 2999884.8
[5 empty] | Total: | 227,50,94,312 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7164 | Peak Hr Flow | 904.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41420074.23 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.6818 | Peak Hr Flow | 1267.35 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2518 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0145 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2741 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.4127 | Peak Hr Flow | 2219.35 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5401
|  |  |  | Chattogram |  | 0 |  | 1497
|  |  |  | Cumilla |  | 0 |  | 1519
|  |  |  | Mymensingh |  | 145 |  | 1248
|  |  |  | Sylhet |  | 0 |  | 703
|  |  |  | Khulna |  | 0 |  | 1894
|  |  |  | Barishal |  | 0 |  | 501
|  |  |  | Rajshahi |  | 0 |  | 1612
|  |  |  | Rangpur |  | 0 |  | 1015
|  |  |  | Total |  | 145 |  | 15390
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 17:02 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to For project work
| 08:22 | 17:35 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Bus coupler GCB
Maintenance work and from Daganbhuiyan 132/33kV end Due to Project work
|  | 08:30 | Sylhet 132/33kV S/S T1 LT is restored.
|  | 08:30 | Sylhet 132/33kV S/S T1 HT is restored.
| 08:32 | 16:50 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to
Project work
| 09:49 | 15:08 | Bog-Sherpur 132/33kV S/S Station Supply-PGCB LT Scheduled S/D Due to Annual maintenance
| 09:50 | 13:18 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to PRD cable change
| 09:50 | 13:19 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to PRD cable Change
| 09:53 | 15:04 | Bog-Sherpur 132/33kV S/S Station Supply-PGCB HT Scheduled S/D Due to Annual Maintenance
| 11:09 | 11:22 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Tripped from Patuakhali 132/33kV | [7 empty] | 10.0MW load
|  |  | end showing E/F & O/C, Distance relay relays Due to E/F, R phase | [7 empty] | interrup.
Patuakhali 132/33kV
end
| 12:00 |  | Day Peak Generation: 13320 MW
|  | 14:47 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 14:49 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
| 15:22 | 20:49 | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to D/S 324 B - phase Finger
maintenance.
| 15:22 | 20:50 | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to D/S 324 B - phase Finger
maintenance.
| 15:50 |  | Meghnaghat Summit 335 MW CCPP ST tripped.
| 16:41 |  | Meghnaghat Summit 335 MW CCPP ST was sync.
| 18:17 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 19:06 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
| 20:05 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
| 20:28 |  | Ashuganj-Ghorashal 230kV ckt-1 was switched on.
|  | 20:38 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation: 15939 MW.
| 21:07 |  | Bhola Nutan Biddut BD LTD Synchronized
| 21:07 |  | Bhola Nutan Biddut BD LTD GT-2 Synchronized with remarks:- GT-12 was started and
synchronized to grid at 21:07 hrs on 27th September 2025 .
| 00:04 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:-
| 00:24 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 04:37 |  | Adani U-1 FSD
| 04:41 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 07:00 |  | Minimum Generation is 12984 MW
| 07:00 |  | Minimum Gen. is 12984 MW.
| 07:06 | 07:39 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Forced S/D Due to Red Hot 132 kV side (CT-R | [7 empty] | 230.0MW load
|  |  | phase, CB-Y phase) | [7 empty] | interrup.
| 07:22 | 07:44 | Sylhet 132/33kV S/S T1 LT Tripped showing O/C relays Due to 33kv IC-1 Feeder trip due to | [7 empty] | 20.0MW load
|  |  | O/C Fault | [7 empty] | interrup.
|  | 07:33 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 07:46 |  | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Forced S/D Due to Red Hot 132 kV Side (CT-Y | [7 empty] | 230.0MW load
|  |  | phase, CB-B phase) | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 370 | 846000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7674000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 305 | 6751127 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 739500 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7362094 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 777960 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1591680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 794023 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 688502 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25.8 | 456600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 529200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 324000 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 276 | 4288789 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3508704 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 1066560 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 2368800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205615 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 301680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 380 | 9628460 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2457600 | -
Dhaka Area Total |  |  |  |  | 6657.724 | 2835.8 | 52360894
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 207531 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 99495 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 919680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5304200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5002155 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 1723745 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 458448 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 872287 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 597120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 525600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 106 | 1025280 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20277 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 99 | 451636 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 41 | 340095 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 1351564 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 603840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 817964 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 143 | 1296364 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 602 | 16069089 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 203520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 265 | 6320000 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2285 | 44209890
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 191 | 4804000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 342 | 8526300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7938000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 6503476 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 266880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 167273 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1239048 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1787818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 339680 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 2936640 | -
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1014512 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 463018 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 432040 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 1054500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 43680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1664640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 488436 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1574 | 39669941
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 65 | 1928640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 201600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 76 | 1824000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 317660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 139440 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 162 | 4424490
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1340520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3705300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719904 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1980480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4395050 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 407000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 237312 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7580000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 9445000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1254 | 30526566
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21716363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 303 | 8720640 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 627120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 26094550 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2479.2 | 58070673
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 622 | 13089600 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 63 | 444960 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2753000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 26753454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2798500 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 115200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5367000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4204 | -
Barishal Area Total |  |  |  |  | 2236 | 2456 | 51325918.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 279782 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 385599 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 269505 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4499635 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4798755 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9586400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 228190 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 198845 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 694372 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1120320 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1083072 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1267.35 | 27681818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 325496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 729890 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2530.35 | 51908979
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 139 | 3470000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 109 | 1679280 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42907.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1646354 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201329 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1091520 | -
Rangpur Area Total |  |  |  |  | 950 | 363 | 8131390.56
Eastern Grid Total |  |  |  |  | 17385.715 | 8110.8 | 171191781
Western Grid Total |  |  |  |  | 10444.16 | 7828.55 | 169436961.11
National Grid Total |  |  |  |  | 27829.875 | 15939.35 | 340628742.11
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-09-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10223.35 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5021.4 | MW
i) Dhaka area |  |  | 5401.33 |  | MW | i) Khulna area |  |  |  | 1893.8 | MW
ii) Chattogram area |  |  | 1497.09 |  | MW | ii) Barishal area |  |  |  | 501 | MW
iii) Cumilla area |  |  | 1518.93 |  | MW | iii) Rajshahi area |  |  |  | 1611.6 | MW
iv) Mymensingh area |  |  | 1103 |  | MW | iv) Rangpur area |  |  |  | 1015 | MW
v) Sylhet area |  |  | 703 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15244.75 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 10:00 | 67 | Hathazari | 89 | 22:00 | 133 | PHP | 5 | 04:00
2 | AKSML | 84 | 02:00 | 68 | Ishurdi | 82 | 18:30 | 134 | Pabna | 110 | 19:30
3 | Aftabnagar | 40 | 23:00 | 69 | Jaldhaka | 89 | 18:30 | 135 | Palashbari | 132 | 00:00
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 124 | 14:00 | 136 | Panchagarh | 62 | 19:00
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 146 | 19:00 | 137 | Patiya | 12.36 | 11:00
6 | Amnura | 35 | 00:00 | 72 | Jhenaidah | 138 | 19:00 | 138 | Patuakhali | 75 | 00:00
7 | Ashuganj | 85 | 23:00 | 73 | Joydebpur | 156 | 18:30 | 139 | Payra | 40 | 23:00
8 | BSRM | 149 | 05:00 | 74 | Joypurhat | 69 | 00:00 | 140 | Postogola | 74 | 13:00
9 | Bagerhat | 86 | 22:00 | 75 | Juldah | 18.5 | 13:00 | 141 | Purbachal | 22 | 00:00
10 | Bajitpur | 108 | 23:00 | 76 | KSRM | 36 | 16:00 | 142 | Purbasadipur | 130 | 19:00
11 | Bakulia | 100 | 18:30 | 77 | Kabirpur | 267 | 16:00 | 143 | Rahanpur | 43 | 23:00
12 | Banani | 44 | 12:00 | 78 | Kachua | 98 | 21:00 | 144 | Rahim | 21 | 11:00
13 | Bangabhaban | 11 | 11:00 | 79 | Kallyanpur | 108 | 13:00 | 145 | Rajbari | 81 | 00:00
14 | Barapukuria | 71 | 21:00 | 80 | Kalurghat | 40 | 10:00 | 146 | Rajendrapur | 134 | 22:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 77 | 12:00 | 147 | Rajshahi | 113 | 23:00
16 | Barishal | 121 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 103 | 13:00
17 | Barishal-230 | 104 | 21:00 | 83 | Kasba | 39 | 21:00 | 149 | Ramganj | 122 | 23:00
18 | Baroaulia | 69 | 11:00 | 84 | Kazla | 118 | 17:00 | 150 | Rampur | 44 | 23:00
19 | Baroirhat | 72 | 20:00 | 85 | Keranigonj | 90 | 18:30 | 151 | Rangamati | 18 | 19:00
20 | Bashundhara | 207 | 15:00 | 86 | Khagrachori | 32 | 18:00 | 152 | Rangpur | 150 | 19:00
21 | BashundharaCement | 12 | 19:30 | 87 | Khulna | 73 | 13:00 | 153 | Ruppur | 5.6 | 16:00
22 | Beanibazar | 90 | 23:00 | 88 | Khulshi | 208 | 19:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 68 | 00:00 | 89 | Kishoreganj | 147 | 21:00 | 155 | Saidpur | 114 | 19:00
24 | Bhaluka | 151 | 22:00 | 90 | Kodda | 295 | 16:00 | 156 | Satkhira | 132 | 23:00
25 | Bhandaria | 60 | 22:00 | 91 | Kulaura | 58 | 20:00 | 157 | Satmasjid | 105 | 14:00
26 | Bhangura | 40 | 18:30 | 92 | Kurigram | 64 | 02:00 | 158 | Savar | 234 | 12:00
27 | Bheramara(GK) | 72 | 22:00 | 93 | Kushtia | 172 | 18:30 | 159 | SevenRings | 18.35 | 15:00
28 | Bhulta | 216 | 20:00 | 94 | Laksam | 36 | 21:00 | 160 | ShahCement | 31 | 09:00
29 | Bog-Sherpur | 80 | 00:00 | 95 | Lakshmipur | 36 | 19:00 | 161 | Shahjadpur | 87 | 20:00
30 | Bogura | 179 | 20:00 | 96 | Lalbag | 60 | 12:00 | 162 | Shahjibazar | 134 | 21:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 66 | 18:30 | 163 | Shahmirpur | 60.5 | 18:00
32 | Brahmanbaria | 139 | 22:00 | 98 | MI_Cement | 18.8 | 12:00 | 164 | Shariatpur | 96 | 22:00
33 | Cantonment | 145 | 13:00 | 99 | Madanganj | 42 | 20:00 | 165 | Sherpur | 130 | 23:00
34 | Chandina | 17.49 | 23:00 | 100 | Madaripur | 120 | 23:00 | 166 | Shikalbaha | 28 | 18:00
35 | Chandpur | 86 | 00:00 | 101 | Madartek | 84 | 23:00 | 167 | Shitalakhya | 90.1 | 13:00
36 | Chandraghona | 36 | 21:00 | 102 | Madunaghat | 59 | 18:30 | 168 | Sholosohor | 49 | 16:00
37 | Chapai | 75 | 00:00 | 103 | Magura | 71 | 18:30 | 169 | Shyampur | 92 | 16:00
38 | Charsaidpur | 29 | 01:00 | 104 | Mahasthangarh | 90 | 00:00 | 170 | Siddhirganj | 126 | 11:00
39 | Chauddagram | 78 | 23:00 | 105 | Maijdee | 24 | 22:00 | 171 | Sirajganj | 118 | 19:30
40 | Chhatak | 44 | 22:00 | 106 | Manikganj | 133 | 19:00 | 172 | Sonargaon | 139 | 23:00
41 | Chowmuhani | 195 | 23:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sreemongol | 93 | 19:00
42 | Chuadanga | 118 | 00:00 | 108 | Matarbari | 54 | 19:00 | 174 | Sreepur | 121 | 19:00
43 | Coxsbazar | 145 | 20:00 | 109 | Matuail | 72 | 11:00 | 175 | Srinagar | 52.5 | 22:00
44 | Cumilla(N) | 154 | 22:00 | 110 | Millgate | 134 | 15:00 | 176 | Sunamganj | 67 | 21:00
45 | Cumilla(S) | 152 | 16:00 | 111 | Mirpur | 128 | 18:00 | 177 | Sylhet | 62 | 20:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 00:00 | 178 | Sylhet-132 | 141 | 16:00
47 | Daudkandi | 156 | 21:00 | 113 | Mirzapur | 44 | 12:00 | 179 | TK | 25.5 | 19:30
48 | DhakaUniversity | 84 | 13:00 | 114 | Mithapukur | 78 | 02:00 | 180 | Tangail | 174 | 00:00
49 | Dhamrai | 136 | 22:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 23 | 00:00
50 | Dhanmondi | 137.5 | 13:00 | 116 | Mogbazar | 87.9 | 15:00 | 182 | Thakurgaon | 116 | 19:30
51 | Dohazari | 102 | 01:00 | 117 | Mongla | 39 | 18:30 | 183 | Tongi | 126 | 08:00
52 | Faridpur | 183 | 21:00 | 118 | Motijheel | 46 | 13:00 | 184 | Ullahpara | 41 | 19:30
53 | Fatullah | 110 | 12:00 | 119 | Muktagacha | 38 | 02:00 | 185 | Ullon | 55 | 00:00
54 | Fenchuganj | 48 | 00:00 | 120 | Munshiganj | 117 | 22:00 | 186 | Uttara | 86 | 18:00
55 | Feni | 126 | 22:00 | 121 | Muradnagar | 44 | 21:00 | 187 | UttaraNew | 66 | 12:00
56 | GPH | 88 | 02:00 | 122 | Mymensingh | 202 | 18:00 | 188 | Zigatola | 76 | 13:00
57 | Ghatail | 92 | 02:00 | 123 | Naogaon | 146 | 23:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 61.5 | 18:30
59 | Ghorashal-230 | 102 | 18:00 | 125 | Narinda | 67 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 194 | 20:00
61 | Gollamari | 94 | 23:00 | 127 | Natore | 162 | 22:00
62 | Gopalganj | 111 | 19:00 | 128 | Nawabganj | 53.2 | 22:00
63 | Gulshan | 112 | 13:00 | 129 | Netrakona | 123 | 08:00
64 | Halishahar | 70 | 18:00 | 130 | New | 56.8 | 11:00
65 | HaripurSBU | 129 | 00:00 | 131 | Niamatpur | 84 | 23:00
66 | Hasnabad | 98 | 23:00 | 132 | Noapara | 46 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15250.56 | 162 |  | 15419.85
1:00 | 14798.36 | 136 |  | 14940.36
2:00 | 14372 | 74 |  | 14449
3:00 | 14109 | 20 |  | 14130
4:00 | 13566 | 23 |  | 13590
5:00 | 13330 | 0 |  | 13330
6:00 | 12965.52 | 0 |  | 12965.52
7:00 | 12866.18 | 21 |  | 12888.13
8:00 | 12746.83 | 0 |  | 12746.83
9:00 | 12653.6 | 0 |  | 12653.6
10:00 | 12756.83 | 0 |  | 12756.83
11:00 | 12950.56 | 0 |  | 12950.56
12:00 | 13325.67 | 33 |  | 13359.67
13:00 | 13834.82 | 56 |  | 13893.82
14:00 | 14166.48 | 36 |  | 14204.1
15:00 | 14199.16 | 72 |  | 14274.4
16:00 | 14032.32 | 107 |  | 14144.14
17:00 | 13611.79 | 88 |  | 13703.75
18:00 | 14297.79 | 146 |  | 14450.79
19:00 | 15741.2 | 152 |  | 15900.2
19:30 | 15811.7 | 152 |  | 15970.7
20:00 | 15871 | 143 |  | 16020
21:00 | 15939.35 | 145 |  | 16091.35
22:00 | 15875.64 | 139 |  | 16020.64
23:00 | 15661.14 | 307 |  | 15982.14
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7578.36 | 7672.2 | 15250.56 | DAILY GENERATION CURVE
00:30 | 7485.36 | 7539.1 | 15024.46
01:00 | 7392.36 | 7406 | 14798.36 | 27-09-2025
01:30 | 7245.68 | 7339.5 | 14585.18
02:00 | 7099 | 7273 | 14372
02:30 | 7010 | 7230.5 | 14240.5
03:00 | 6921 | 7188 | 14109
03:30 | 6783 | 7054.5 | 13837.5
04:00 | 6645 | 6921 | 13566
04:30 | 6559.5 | 6888.5 | 13448
05:00 | 6474 | 6856 | 13330
05:30 | 6320.015 | 6827.745 | 13147.76
06:00 | 6166.03 | 6799.49 | 12965.52
06:30 | 6158.435 | 6757.415 | 12915.85
07:00 | 6150.84 | 6715.34 | 12866.18
07:30 | 6107.65 | 6698.855 | 12806.505
08:00 | 6064.46 | 6682.37 | 12746.83
08:30 | 6110.815 | 6589.4 | 12700.215
09:00 | 6157.17 | 6496.43 | 12653.6
09:30 | 6276.225 | 6428.99 | 12705.215
10:00 | 6395.28 | 6361.55 | 12756.83
10:30 | 6517.065 | 6336.63 | 12853.695
11:00 | 6638.85 | 6311.71 | 12950.56
11:30 | 6728.445 | 6409.67 | 13138.115
12:00 | 6818.04 | 6507.63 | 13325.67
12:30 | 6989.715 | 6590.53 | 13580.245
13:00 | 7161.39 | 6673.43 | 13834.82
13:30 | 7213.925 | 6786.725 | 14000.65
14:00 | 7266.46 | 6900.02 | 14166.48
14:30 | 7314.885 | 6867.935 | 14182.82
15:00 | 7363.31 | 6835.85 | 14199.16
15:30 | 7317.76 | 6797.98 | 14115.74
16:00 | 7272.21 | 6760.11 | 14032.32
16:30 | 7202.825 | 6619.23 | 13822.055
17:00 | 7133.44 | 6478.35 | 13611.79
17:30 | 7331.47 | 6623.32 | 13954.79
18:00 | 7529.5 | 6768.29 | 14297.79
18:30 | 7785.25 | 7234.245 | 15019.495
19:00 | 8041 | 7700.2 | 15741.2
19:30 | 8056.5 | 7755.2 | 15811.7
20:00 | 8079.8 | 7791.2 | 15871
20:30 | 8095.3 | 7809.875 | 15905.175 |  | Executive Engineer
21:00 | 8110.8 | 7828.55 | 15939.35 |  | Network Operation Division
21:30 | 8057.93 | 7849.565 | 15907.495
22:00 | 8005.06 | 7870.58 | 15875.64
22:30 | 7863.21 | 7905.18 | 15768.39
23:00 | 7721.36 | 7939.78 | 15661.14

## En-Curve
QF-LDC-12
Date | 27-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3841 | 1920 | 894 | 38 | 50 | 1216 | 217 | 4371.2 | 0 | 594 | 2106.36 | 0 | 0 | 3 | 162 | DAILY ENERGY CURVE
00:30 | 3829 | 1903 | 893.5 | 38 | 50 | 1213 | 217.5 | 4253.6 | 0 | 571 | 2050.36 | 0 | 0 | 5.5 | 149 | 27-09-2025
01:00 | 3817 | 1886 | 893 | 38 | 50 | 1210 | 218 | 4136 | 0 | 548 | 1994.36 | 0 | 0 | 8 | 136
01:30 | 3835 | 1855 | 893 | 38 | 50 | 1210 | 217.5 | 4088 | 0 | 521 | 1863.18 | 0 | 0 | 14.5 | 105 | Energy Generated | 340.6287 |  | MKWHr
02:00 | 3853 | 1824 | 893 | 38 | 50 | 1210 | 217 | 4040 | 0 | 494 | 1732 | 0 | 0 | 21 | 74 | Energy not Served | 1.86 |  | MKWHr
02:30 | 3845 | 1812 | 893.5 | 38 | 49 | 1210 | 216 | 4020.5 | 0 | 470.5 | 1669 | 0 | 0 | 17 | 47 | Total Energy Requirement | 342.4887 |  | MKWHr
03:00 | 3837 | 1800 | 894 | 38 | 48 | 1210 | 215 | 4001 | 0 | 447 | 1606 | 0 | 0 | 13 | 20
03:30 | 3854 | 1815.5 | 894 | 38 | 47 | 1209 | 215 | 4002 | 0 | 365.5 | 1384.5 | 0 | 0 | 13 | 21.5
04:00 | 3871 | 1831 | 894 | 38 | 46 | 1208 | 215 | 4003 | 0 | 284 | 1163 | 0 | 0 | 13 | 23
04:30 | 3858 | 1839 | 894 | 38 | 46 | 1213 | 216 | 4012 | 0 | 249 | 1062.5 | 0 | 0 | 20.5 | 11.5
05:00 | 3845 | 1847 | 894 | 38 | 46 | 1218 | 217 | 4021 | 0 | 214 | 962 | 0 | 0 | 28 | 0
05:30 | 3837 | 1832 | 893.5 | 38 | 42 | 1213.5 | 217 | 3998 | 1.26 | 197.5 | 853.5 | 0 | 0 | 24.5 | 0
06:00 | 3829 | 1817 | 893 | 38 | 38 | 1209 | 217 | 3975 | 2.52 | 181 | 745 | 0 | 0 | 21 | 0
06:30 | 3842 | 1825.5 | 893 | 38 | 36 | 1216.5 | 217 | 3904.5 | 43.85 | 191 | 686.5 | 0 | 0 | 22 | 10.5
07:00 | 3855 | 1834 | 893 | 38 | 34 | 1224 | 217 | 3834 | 85.18 | 201 | 628 | 0 | 0 | 23 | 21
07:30 | 3839 | 1804.5 | 889 | 38 | 32 | 1220.03 | 217 | 3785.5 | 161.975 | 199 | 603.5 | 0 | 0 | 17 | 10.5
08:00 | 3823 | 1775 | 885 | 38 | 30 | 1216.06 | 217 | 3737 | 238.77 | 197 | 579 | 0 | 0 | 11 | 0
08:30 | 3791 | 1770.5 | 885 | 38 | 31 | 1170.015 | 218.5 | 3687 | 310.2 | 209 | 583.5 | 0 | 0 | 6.5 | 0
09:00 | 3759 | 1766 | 885 | 38 | 32 | 1123.97 | 220 | 3637 | 381.63 | 221 | 588 | 0 | 0 | 2 | 0
09:30 | 3758 | 1778.5 | 887 | 38 | 32 | 1086.43 | 220 | 3627 | 452.285 | 205 | 619 | 0 | 0 | 2 | 0
10:00 | 3757 | 1791 | 889 | 38 | 32 | 1048.89 | 220 | 3617 | 522.94 | 189 | 650 | 0 | 0 | 2 | 0
10:30 | 3774 | 1815.5 | 888.5 | 38 | 32 | 1043.25 | 220 | 3628 | 553.945 | 189 | 669 | 0 | 0 | 2.5 | 0
11:00 | 3791 | 1840 | 888 | 38 | 32 | 1037.61 | 220 | 3639 | 584.95 | 189 | 688 | 0 | 0 | 3 | 0
11:30 | 3798 | 1818 | 890.5 | 38 | 30 | 1027.015 | 220 | 3655.5 | 659.6 | 176 | 824 | 0 | 0 | 1.5 | 16.5
12:00 | 3805 | 1796 | 893 | 38 | 28 | 1016.42 | 220 | 3672 | 734.25 | 163 | 960 | 0 | 0 | 0 | 33
12:30 | 3830 | 1799.5 | 893 | 38 | 36 | 1038.975 | 220 | 3768 | 640.27 | 170.5 | 1141.5 | 0 | 0 | 4.5 | 44.5
13:00 | 3855 | 1803 | 893 | 38 | 44 | 1061.53 | 220 | 3864 | 546.29 | 178 | 1323 | 0 | 0 | 9 | 56
13:30 | 3810 | 1807.25 | 893.5 | 38 | 44 | 1093.545 | 220 | 3922 | 581.355 | 178 | 1402.5 | 0 | 0 | 10.5 | 46
14:00 | 3765 | 1811.5 | 894 | 38 | 44 | 1125.56 | 220 | 3980 | 616.42 | 178 | 1482 | 0 | 0 | 12 | 36
14:30 | 3772.5 | 1831 | 899 | 38 | 44 | 1128.78 | 220 | 4010 | 515.04 | 178 | 1534 | 0 | 0 | 12.5 | 54
15:00 | 3780 | 1850.5 | 904 | 38 | 44 | 1132 | 220 | 4040 | 413.66 | 178 | 1586 | 0 | 0 | 13 | 72
15:30 | 3769 | 1777.5 | 904 | 38 | 43 | 1199 | 219 | 4029 | 315.74 | 191 | 1623 | 0 | 0 | 7.5 | 89.5
16:00 | 3758 | 1704.5 | 904 | 38 | 42 | 1266 | 218 | 4018 | 217.82 | 204 | 1660 | 0 | 0 | 2 | 107
16:30 | 3644.5 | 1687 | 904 | 38 | 41 | 1264 | 217.5 | 3983 | 145.555 | 223.5 | 1673 | 0 | 0 | 1 | 97.5
17:00 | 3531 | 1669.5 | 904 | 38 | 40 | 1262 | 217 | 3948 | 73.29 | 243 | 1686 | 0 | 0 | 0 | 88
17:30 | 3542 | 1755 | 904.5 | 38 | 42 | 1264.5 | 217.5 | 3929 | 36.645 | 371 | 1854.645 | 0 | 0 | 0 | 117
18:00 | 3553 | 1840.5 | 905 | 38 | 44 | 1267 | 218 | 3910 | 0 | 499 | 2023.29 | 0 | 0 | 0 | 146
18:30 | 3681.5 | 1828.25 | 905 | 38 | 44 | 1269 | 218.5 | 4157.6 | 0 | 586.5 | 2291.145 | 0 | 0 | 0 | 149
19:00 | 3810 | 1816 | 905 | 38 | 44 | 1271 | 219 | 4405.2 | 0 | 674 | 2559 | 0 | 0 | 0 | 152
19:30 | 3772 | 1797.5 | 905 | 38 | 46 | 1270 | 220 | 4401.2 | 0 | 675 | 2687 | 0 | 0 | 0 | 152
20:00 | 3780 | 1796.8 | 904 | 38 | 48 | 1267 | 219 | 4394.2 | 0 | 685 | 2738 | 0 | 0 | 1 | 143
20:30 | 3773.5 | 1805.8 | 904 | 38 | 48 | 1267.175 | 219.5 | 4392.7 | 0 | 689.5 | 2761 | 0 | 0 | 6 | 144
21:00 | 3767 | 1814.8 | 904 | 38 | 48 | 1267.35 | 220 | 4391.2 | 0 | 694 | 2784 | 0 | 0 | 11 | 145
21:30 | 3749.5 | 1825.9 | 904.5 | 38 | 48 | 1266.865 | 220 | 4393.7 | 0 | 693 | 2760.03 | 0 | 0 | 8 | 142
22:00 | 3732 | 1837 | 905 | 38 | 48 | 1266.38 | 220 | 4396.2 | 0 | 692 | 2736.06 | 0 | 0 | 5 | 139
22:30 | 3718 | 1837.25 | 905 | 38 | 48 | 1263.48 | 218.5 | 4391.7 | 0 | 647 | 2696.96 | 0 | 0 | 4.5 | 223
23:00 | 3704 | 1837.5 | 905 | 38 | 48 | 1260.58 | 217 | 4387.2 | 0 | 602 | 2657.86 | 0 | 0 | 4 | 307
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 03:00 | 367 | 18:00 | Payra | 407 | 10:00 | 401 | 18:30
Ashuganj | 391 | 4:00 | 380 | 13:00 | Rahanpur | 400 | 10:00 | 390 | 19:00
Bhulta | 385 | 03:00 | 373 | 12:00 | Rampal | 401 | 10:00 | 386 | 23:00
Bibiana | 384 | 02:00 | 380 | 18:00
BIPTC | 402 | 06:00 | 391 | 21:00
Bogura | 388 | 11:00 | 376 | 19:00
Gopalganj | 389 | 09:00 | 378 | 19:00
Kaliakoir | 369 | 07:00 | 361 | 18:00
Madunaghat | 392 | 21:00 | 384 | 12:00
Meghnaghat | 379 | 03:00 | 374 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 03:00 | 220 | 19:30 | Kaliakoir | 230 | 17:00 | 225 | 10:00
AKSML | 233 | 21:00 | 226 | 04:00 | Keranigonj | 223 | 02:00 | 217 | 11:00
Aminbazar | 225 | 04:00 | 220 | 12:00 | Khulna(S) | 230 | 09:00 | 217 | 19:00
Ashuganj | 227 | 02:00 | 222 | 11:00 | Madunaghat | 234 | 19:30 | 227 | 11:00
Ashuganj-400 | 225 | 4:00 | 220 | 13:00 | Madunaghat-400 | 235 | 20:00 | 228 | 11:00
Baghabari | 231 | 07:00 | 225 | 19:00 | Maniknagar | 219 | 07:00 | 212 | 12:00
Barapukuria | 221 | 18:00 | 209 | 19:00 | Meghnaghat | 227 | 04:00 | 221 | 15:00
Barapukuria-230 | 221 | 18:00 | 210 | 20:00 | Meghnaghat-400 | 223 | 03:00 | 217 | 16:00
Barishal | 229 | 09:00 | 220 | 00:00 | Mirsorai | 235 | 19:30 | 224 | 06:00
Bheramara | 231 | 10:00 | 221 | 18:30 | Rajshahi | 230 | 10:00 | 219 | 18:30
Bhulta | 220 | 03:00 | 213 | 11:00 | Rampal | 230 | 10:00 | 217 | 19:00
Bibiana | 225 | 02:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 10:00 | 222 | 18:30 | Rampura | 219 | 04:00 | 211 | 11:00
Bogura | 231 | 03:00 | 224 | 19:00 | Shikalbaha | 235 | 19:30 | 225 | 12:00
Bogura-400 | 231 | 11:00 | 224 | 19:00 | Shyampur | 222 | 02:00 | 217 | 11:00
Borhanuddin | 233 | 10:00 | 225 | 00:00 | Siddhirganj | 221 | 05:00 | 215 | 11:00
BSRM | 232 | 19:30 | 224 | 05:00 | Sirajgonj | 236 | 03:00 | 231 | 19:00
Cumilla(N) | 222 | 17:00 | 218 | 01:00 | Sreepur | 224 | 04:00 | 218 | 15:00
Faridpur | 229 | 10:00 | 218 | 00:00 | Tongi | 226 | 04:00 | 217 | 12:00
Fenchuganj | 227 | 09:00 | 224 | 19:00
Ghorashal | 230 | 23:00 | 220 | 00:00
Ghorashal-230 | 223 | 02:00 | 216 | 12:00
Gopalganj | 229 | 09:00 | 220 | 07:00
GPH | 231 | 23:00 | 225 | 06:00
Haripur | 221 | 04:00 | 126 | 19:00
Hasnabad | 222 | 06:00 | 216 | 14:00
Hathazari | 232 | 19:30 | 225 | 08:00
Ishurdi | 233 | 10:00 | 224 | 00:00
Jhenaidah | 232 | 10:00 | 216 | 18:30
Kachua | 214 | 12:00 | 211 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 128 | 12:00 | Lalmonirhat | 127 | 18:00 | 114 | 18:30
Agargaon | 136 | 02:00 | 130 | 12:00 | Madanganj | 127 | 08:00 | 123 | 11:00
Agrabad | 133 | 19:30 | 128 | 07:00 | Madaripur | 135 | 09:00 | 129 | 00:00
AKS | 131 | 18:30 | 127 | 01:00 | Madartek | 134 | 03:00 | 127 | 12:00
Aminbazar | 133 | 04:00 | 128 | 14:00 | Madunaghat | 135 | 18:30 | 131 | 11:00
Amnura | 135 | 10:00 | 127 | 14:00 | Magura | 137 | 09:00 | 123 | 18:30
Ashuganj | 137 | 06:00 | 133 | 18:30 | Mahasthangarh | 129 | 18:00 | 121 | 19:00
Bagerhat | 135 | 09:00 | 117 | 20:00 | Maijdee | 125 | 12:00 | 112 | 11:00
Bajitpur | 127 | 08:00 | 122 | 18:00 | Manikganj | 126 | 00:00 | 120 | 18:30
Bakulia | 135 | 19:30 | 130 | 07:00 | Maniknagar | 133 | 04:00 | 127 | 12:00
Banani | 136 | 07:00 | 127 | 12:00 | Matarbari | 121 | 11:00 | 112 | 00:00
Bangabhaban | 133 | 04:00 | 127 | 12:00 | Matuail | 129 | 04:00 | 125 | 11:00
Barapukuria | 134 | 23:00 | 122 | 19:00 | Millgate | 132 | 01:00 | 126 | 08:00
Barguna | 136 | 09:00 | 132 | 00:00 | Mirpur | 133 | 01:00 | 127 | 12:00
Barishal | 134 | 10:00 | 127 | 00:00 | Mirzapur | 130 | 07:00 | 124 | 15:00
Barishal-230 | 134 | 09:00 | 127 | 00:00 | Mithapukur | 129 | 18:00 | 118 | 19:00
Baroaulia | 133 | 19:30 | 129 | 06:00 | MI_Cement | 129 | 04:00 | 125 | 10:00
Baroirhat | 127 | 17:00 | 123 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 04:00 | 125 | 11:00 | Mogbazar | 137 | 04:00 | 130 | 15:00
BashundharaCement | 127 | 08:00 | 123 | 11:00 | Mongla | 135 | 09:00 | 119 | 20:00
Beanibazar | 126 | 07:00 | 121 | 21:00 | Motijheel | 133 | 04:00 | 127 | 12:00
Benapole | 132 | 09:00 | 118 | 00:00 | Muktagacha | 128 | 09:00 | 121 | 05:00
Bhaluka | 129 | 04:00 | 120 | 15:00 | Munshiganj | 128 | 03:00 | 123 | 11:00
Bhandaria | 130 | 09:00 | 117 | 00:00 | Muradnagar | 124 | 09:00 | 120 | 14:00
Bhangura | 132 | 06:00 | 127 | 18:30 | Mymensingh | 129 | 10:00 | 120 | 16:00
Bheramara | 136 | 10:00 | 131 | 18:30 | Naogaon | 126 | 18:00 | 120 | 04:00
Bheramara(GK) | 136 | 09:00 | 131 | 18:30 | Narail | 137 | 09:00 | 123 | 18:30
Bhulta | 126 | 17:00 | 122 | 00:00 | Narinda | 133 | 4:00 | 127 | 12:00
Bog-Sherpur | 129 | 03:00 | 125 | 19:00 | Narshingdi | 130 | 09:00 | 119 | 00:00
Bogura | 131 | 18:00 | 127 | 13:00 | Natore | 131 | 09:00 | 126 | 18:30
Bogura-230 | 131 | 03:00 | 127 | 05:00 | Nawabganj | 135 | 05:00 | 129 | 13:00
Brahmanbaria | 136 | 00:00 | 125 | 18:30 | Netrakona | 120 | 04:00 | 107 | 18:00
Cantonment | 136 | 03:00 | 130 | 12:00 | New | 132 | 04:00 | 126 | 10:00
Chandina | 128 | 17:00 | 125 | 11:00 | Niamatpur | 135 | 05:00 | 132 | 13:00
Chandpur | 133 | 18:30 | 125 | 05:00 | Noapara | 135 | 09:00 | 130 | 16:00
Chandraghona | 135 | 18:00 | 131 | 11:00 | Pabna | 133 | 09:00 | 128 | 18:00
Chapai | 134 | 10:00 | 131 | 15:00 | Palashbari | 125 | 06:00 | 116 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 04:00 | 124 | 11:00 | Panchagarh | 135 | 23:00 | 118 | 19:00
Chauddagram | 126 | 17:00 | 121 | 11:00 | Patiya | 133 | 18:30 | 128 | 13:00
Chhatak | 126 | 06:00 | 119 | 20:00 | Patuakhali | 136 | 17:00 | 132 | 02:00
Chowmuhani | 125 | 12:00 | 120 | 00:00 | Payra | 137 | 07:00 | 134 | 00:00
Chuadanga | 133 | 09:00 | 120 | 00:00 | PHP | 127 | 18:30 | 121 | 01:00
Coxsbazar | 121 | 17:00 | 112 | 23:00 | Postogola | 131 | 01:00 | 126 | 11:00
Cumilla(N) | 128 | 17:00 | 124 | 03:00 | Purbachal | 135 | 03:00 | 128 | 12:00
Cumilla(S) | 133 | 06:00 | 123 | 10:00 | Purbasadipur | 130 | 18:00 | 115 | 12:00
Daganbhuiyan | 125 | 17:00 | 120 | 01:00 | Rahanpur | 136 | 05:00 | 134 | 00:00
Daudkandi | 122 | 03:00 | 116 | 23:00 | Rahanpur-400 | 137 | 09:00 | 133 | 19:00
DhakaUniversity | 135 | 03:00 | 129 | 11:00 | Rahim | 128 | 02:00 | 125 | 12:00
Dhamrai | 130 | 04:00 | 125 | 12:00 | Rajbari | 134 | 09:00 | 127 | 00:00
Dhanmondi | 136 | 06:00 | 127 | 12:00 | Rajendrapur | 135 | 23:00 | 119 | 15:00
Dohazari | 129 | 18:30 | 123 | 13:00 | Rajshahi | 131 | 08:00 | 126 | 00:00
Faridpur | 135 | 09:00 | 128 | 00:00 | Rajshahi-230 | 132 | 10:00 | 126 | 18:30
Fatullah | 135 | 03:00 | 130 | 12:00 | Ramganj | 127 | 18:30 | 120 | 00:00
Fenchuganj | 134 | 05:00 | 131 | 18:30 | Rampur | 133 | 19:30 | 128 | 11:00
Feni | 127 | 18:00 | 120 | 04:00 | Rampura | 135 | 04:00 | 128 | 12:00
Ghatail | 126 | 09:00 | 118 | 15:00 | Rangamati | 134 | 00:00 | 130 | 13:00
Ghorashal | 135 | 17:00 | 130 | 11:00 | Rangpur | 127 | 09:00 | 124 | 03:00
Goalpara | 139 | 09:00 | 125 | 22:00 | Ruppur | 137 | 04:00 | 131 | 18:30
Gollamari | 137 | 09:00 | 127 | 00:00 | Saidpur | 131 | 18:00 | 117 | 19:00
Gopalganj | 136 | 09:00 | 127 | 19:00 | Satkhira | 135 | 09:00 | 119 | 22:00
Gopalganj-400 | 137 | 09:00 | 131 | 00:00 | Satmasjid | 136 | 03:00 | 130 | 12:00
Gulshan | 135 | 05:00 | 128 | 12:00 | Savar | 132 | 01:00 | 128 | 12:00
Halishahar | 135 | 19:30 | 129 | 11:00 | SevenRings | 135 | 23:00 | 130 | 11:00
Haripur | 129 | 04:00 | 125 | 11:00 | ShahCement | 129 | 04:00 | 124 | 11:00
HaripurSBU | 128 | 03:00 | 125 | 11:00 | Shahjadpur | 134 | 11:00 | 130 | 18:00
Hasnabad | 131 | 03:00 | 126 | 11:00 | Shahjibazar | 132 | 08:00 | 125 | 18:30
Hathazari | 135 | 18:00 | 130 | 05:00 | Shahmirpur | 135 | 21:00 | 130 | 07:00
Ishurdi | 136 | 08:00 | 131 | 18:30 | Shariatpur | 135 | 09:00 | 126 | 00:00
Jaldhaka | 128 | 18:00 | 114 | 19:00 | Sherpur | 122 | 09:00 | 112 | 05:00
Jamalpur | 126 | 09:00 | 115 | 15:00 | Shikalbaha | 125 | 18:30 | 118 | 13:00
Jashore | 136 | 10:00 | 121 | 22:00 | Shikalbaha-230 | 136 | 18:30 | 131 | 06:00
Jhenaidah | 137 | 09:00 | 120 | 18:30 | Shitalakhya | 129 | 03:00 | 124 | 11:00
Jhenaidah-230 | 137 | 09:00 | 127 | 00:00 | Sholosohor | 135 | 21:00 | 131 | 06:00
Joydebpur | 134 | 23:00 | 124 | 12:00 | Shyampur | 135 | 00:00 | 131 | 16:00
Joypurhat | 123 | 09:00 | 117 | 00:00 | Shyampur-230 | 134 | 01:00 | 131 | 11:00
Juldah | 135 | 19:30 | 130 | 05:00 | Siddhirganj | 128 | 01:00 | 125 | 11:00
Kabirpur | 134 | 00:00 | 123 | 15:00 | Sirajganj | 129 | 06:00 | 125 | 00:00
Kachua | 131 | 12:00 | 126 | 00:00 | Sonargaon | 127 | 03:00 | 123 | 11:00
Kaliakoir | 133 | 07:00 | 129 | 10:00 | Sreemongol | 131 | 08:00 | 125 | 18:30
Kallyanpur | 133 | 02:00 | 129 | 12:00 | Sreepur | 130 | 04:00 | 125 | 14:00
Kalurghat | 134 | 18:00 | 131 | 07:00 | Srinagar | 136 | 08:00 | 130 | 12:00
Kamrangirchar | 137 | 08:00 | 130 | 11:00 | SSM | 136 | 00:00 | 132 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 07:00 | 116 | 20:00
Kasba | 123 | 08:00 | 120 | 00:00 | Sylhet | 128 | 08:00 | 123 | 20:00
Kazla | 133 | 04:00 | 127 | 12:00 | Sylhet-132 | 128 | 06:00 | 125 | 15:00
Keranigonj | 136 | 03:00 | 130 | 12:00 | Tangail | 128 | 09:00 | 120 | 15:00
Khagrachori | 132 | 17:00 | 129 | 11:00 | Taraganj | 128 | 06:00 | 116 | 18:30
Khulna | 137 | 09:00 | 124 | 22:00 | Thakurgaon | 132 | 18:00 | 117 | 19:00
Khulna(S) | 138 | 09:00 | 127 | 19:00 | TK | 135 | 20:00 | 131 | 11:00
Khulshi | 132 | 18:30 | 126 | 13:00 | Tongi | 132 | 04:00 | 127 | 10:00
Kishoreganj | 124 | 02:00 | 116 | 19:30 | Ullahpara | 130 | 05:00 | 126 | 18:30
Kodda | 134 | 00:00 | 126 | 12:00 | Ullon | 135 | 04:00 | 128 | 12:00
KSRM | 135 | 19:30 | 129 | 03:00 | Uttara | 134 | 04:00 | 127 | 12:00
Kulaura | 133 | 07:00 | 129 | 00:00 | UttaraNew | 134 | 03:00 | 127 | 12:00
Kurigram | 126 | 06:00 | 113 | 19:00 | Zigatola | 136 | 03:00 | 130 | 13:00
Kushtia | 133 | 09:00 | 124 | 18:30
Laksam | 129 | 12:00 | 121 | 19:00
Lakshmipur | 126 | 12:00 | 119 | 00:00
Lalbag | 136 | 04:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division