## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-09-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-09-2025 | during | 30-09-2025 | during | 30-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 370 | 341 | 400.75 | 400.75 | 350 | 350 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 300 | 450 | 450 | 340 | 340 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 281 | 308 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 54 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 133 | 149.36 | 149.36 | 124 | 124 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25.5 | 26 | 33 | 33 | 28 | 28 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 47 | 97 | 300 | 300 | 45 | 95 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 105 | 149 | 149 | 106 | 106 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 52 | 87 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 555 | 408 | 718 | 718 | 555 | 555 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2093 | 2681 | 5563.2 | 5529.2 | 3350.2 | 3439.2
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 160 | 209 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 213 | 195 | 200 | 195 | 200 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 101 | 100 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 60 | 68 | 75 | 75 | 75 | 75 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 49 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 17 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 54 | 103 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.65 | 0 | 3.71 | 0 | 3.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 30 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 49 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 103 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 92 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 54 | 150 | 159.86 | 159.86 | 17 | 159.86 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 663 | 854 | 1224 | 1224 | 1224 | 1224 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 0 | 1 | 2 | 1 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 540 | 630 | 650 | 650 | 840 | 840 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2260.65 | 2738.36 | 3660.43 | 3663.72 | 3195.07 | 3355.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 341 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 270 | 270 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 34 | 46.7 | 46.7 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55 | 20 | 20 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 61 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 95 | 115 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 34 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 197 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 38 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 18 | 34 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 17 | 17 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 90 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 83 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1497 | 1659 | 2550.86 | 2480.86 | 1853.66 | 1792.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-09-2025 | during | 30-09-2025 | during | 30-09-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 44 | 33 | 157.5 | 157.5 | 64 | 64 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 76 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.88 | 0 | 30.37 | 0 | 30.37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 201.88 | 136 | 352.97 | 320.5 | 188.97 | 173.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 56 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 8 | 25 | 25 | 15 | 15 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 364 | 383 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1217 | 1242 | 1291 | 1291 | 1203 | 1203
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 222 | 194 | 410 | 410 | 272 | 272 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1000 | 1227 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2253 | 2410 | 3642.2 | 3552.2 | 3309.2 | 3219.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 625 | 625 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 1.6 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1104 | 1224 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 271 | 277 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.35 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2371.95 | 2588 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 30.99 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 205 | 203 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 200 | 188 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 395 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 65 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.93 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 662.95 | 657 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.86 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1826.73 | 1921 | 2492.58 | 2325.99 | 2419.2 | 2252.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 43 | 0 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 139 | 140 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 109 | 109 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.5 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 159 | 0 | 182.7 | 0 | 182.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 558.5 | 407 | 616.7 | 448 | 616.7 | 398
System Total |  |  |  |  | 28823.2 | 27829.875 | 14279.71 | 15782.36 | 22316.94 | 21757.47 | 18100 | 17796.39
Forecast Scenario (30-09-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15800 |  | 0 |  | 15800
|  |  |  | 1:00 | 15490 |  | 0 |  | 15490
|  |  |  | 2:00 | 15050 |  | 0 |  | 15050
|  |  |  | 3:00 | 14530 |  | 0 |  | 14530
|  |  |  | 4:00 | 14200 |  | 0 |  | 14200
|  |  |  | 5:00 | 13930 |  | 0 |  | 13930
|  |  |  | 6:00 | 13440 |  | 0 |  | 13440
|  |  |  | 7:00 | 13380 |  | 0 |  | 13380
|  |  |  | 8:00 | 13270 |  | 0 |  | 13270
|  |  |  | 9:00 | 13540 |  | 0 |  | 13540
|  |  |  | 10:00 | 13850 |  | 0 |  | 13850
|  |  |  | 11:00 | 14020 |  | 0 |  | 14020
|  |  |  | 12:00 | 14550 |  | 0 |  | 14550
|  |  |  | 13:00 | 14660 |  | 0 |  | 14660
|  |  |  | 14:00 | 14770 |  | 0 |  | 14770
|  |  |  | 15:00 | 15080 |  | 0 |  | 15080
|  |  |  | 16:00 | 14940 |  | 0 |  | 14940
|  |  |  | 17:00 | 14650 |  | 0 |  | 14650
|  |  |  | 18:00 | 15000 |  | 0 |  | 15000
|  |  |  | 18:30 | 15300 |  | 0 |  | 15300
|  |  |  | 19:00 | 15650 |  | 0 |  | 15650
|  |  |  | 19:30 | 16000 |  | 0 |  | 16000
|  |  |  | 20:00 | 16100 |  | 0 |  | 16100
|  |  |  | 21:00 | 16050 |  | 0 |  | 16050
|  |  |  | 22:00 | 15900 |  | 0 |  | 15900
|  |  |  | 23:00 | 15800 |  | 0 |  | 15800
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 353.1488 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:29 hrs on 30-09-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-09-2025 | [28 empty] | Date: | 29-09-2025 | [28 empty] | Date: | 29-09-2025 | [28 empty] | Date: | 29-09-2025 | [28 empty] | Date: | 29-09-2025 | [14 empty] | Date: | 29-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 413 | 17 | 0 | 124 | 80 | 195 | 55 | 35 | 126 | 0 | 340 | 304 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 27.5 | 22 | 0 | 0 | 94 | 16 | 92 | 0 | 0 | 66 | 76 | 54.36 | 12 | 0 | 0 | 208 | 104 | 36 | 478 | 17 | 0 | 33 | 17 | 100 | 215 | 0 | 0 | 0 | 602 | 0 | 51 | 130 | 0 | 0 | 346 | 330 | 10 | 171 | 36 | 51 | 0 | 161 | 0 | 17 | 97 | 46 | 34 | 0 | 36 | 320 | 0 | 393 | 30 | 57 | 157 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 78 | 9 | 50 | 0 | 0 | 0 | 7653.86 | 931 | 230 | 0 | 19 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 641.68 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 28 | 8 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 210 | 0 | 0 | 0 | 414 | 0 | 0 | 136 | 0 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 622 | 1228 | 17 | 7362.88 | 15016.74 | 108.19
01:00 | 0 | 78 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 397 | 17 | 0 | 124 | 45 | 95 | 55 | 35 | 126 | 0 | 340 | 301 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 95 | 16 | 92 | 0 | 0 | 66 | 76 | 54.36 | 12 | 0 | 0 | 209 | 105 | 36 | 478 | 17 | 0 | 19 | 17 | 99 | 215 | 0 | 0 | 0 | 600 | 0 | 51 | 130 | 0 | 0 | 347 | 330 | 10 | 173 | 36 | 66 | 0 | 120 | 0 | 17 | 114 | 44 | 34 | 0 | 32 | 315 | 0 | 388 | 30 | 57 | 158 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 7483.36 | 930 | 228 | 0 | 19 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 645.27 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 28 | 8 | 0 | 0 | 26 | 0 | 0 | 204 | 0 | 210 | 0 | 0 | 0 | 414 | 0 | 0 | 138 | 0 | 115 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 622 | 1222 | 17 | 7336.27 | 14819.63 | 108.19
02:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 418 | 17 | 0 | 59 | 45 | 45 | 55 | 35 | 126 | 0 | 340 | 300 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 96 | 16 | 92 | 0 | 0 | 50 | 76 | 54.36 | 12 | 0 | 0 | 209 | 105 | 36 | 477 | 17 | 0 | 19 | 17 | 100 | 215 | 0 | 0 | 0 | 603 | 0 | 51 | 127 | 0 | 0 | 349 | 330 | 10 | 177 | 36 | 90 | 0 | 101 | 0 | 17 | 114 | 42 | 34 | 0 | 37 | 315 | 0 | 388 | 30 | 57 | 157 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 7398.36 | 931 | 235 | 0 | 19 | 33 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 646.82 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 28 | 8 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 210 | 0 | 0 | 0 | 410 | 0 | 0 | 134 | 0 | 115 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 622 | 1222 | 17 | 7186.82 | 14585.18 | 108.18
03:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 401 | 17 | 0 | 35 | 45 | 45 | 55 | 35 | 35 | 0 | 300 | 288 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 94 | 16 | 87 | 0 | 0 | 50 | 76 | 54.36 | 12 | 0 | 0 | 208 | 103 | 36 | 477 | 17 | 0 | 19 | 17 | 98 | 215 | 0 | 0 | 0 | 600 | 0 | 51 | 122 | 0 | 0 | 352 | 330 | 10 | 185 | 36 | 90 | 0 | 102 | 0 | 17 | 114 | 42 | 8 | 0 | 37 | 310 | 0 | 384 | 30 | 57 | 157 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 7163.36 | 931 | 239 | 0 | 4 | 22 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 654.35 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 28 | 8 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 211 | 0 | 0 | 0 | 410 | 0 | 0 | 136 | 0 | 115 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 623 | 1222 | 17 | 7159.35 | 14322.71 | 108.18
04:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 394 | 17 | 0 | 35 | 45 | 45 | 55 | 0 | 35 | 0 | 300 | 268 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 87 | 16 | 48 | 0 | 0 | 50 | 76 | 54.36 | 12 | 0 | 0 | 208 | 101 | 37 | 477 | 17 | 0 | 19 | 17 | 95 | 212 | 0 | 0 | 0 | 600 | 0 | 51 | 122 | 0 | 0 | 353 | 330 | 10 | 185 | 36 | 91 | 0 | 101 | 0 | 17 | 50 | 42 | 8 | 0 | 37 | 310 | 0 | 366 | 30 | 57 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 6959.36 | 931 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 662.48 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 21 | 0 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 211 | 0 | 0 | 0 | 407 | 0 | 0 | 138 | 0 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 623 | 1222 | 17 | 7073.48 | 14032.84 | 108.17
05:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 409 | 17 | 0 | 35 | 45 | 45 | 55 | 0 | 35 | 0 | 300 | 273 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 24 | 22 | 0 | 0 | 85 | 16 | 31 | 0 | 0 | 50 | 76 | 54.36 | 12 | 0 | 0 | 207 | 95 | 37 | 477 | 17 | 0 | 19 | 17 | 91 | 212 | 0 | 0 | 0 | 602 | 0 | 51 | 128 | 0 | 0 | 352 | 330 | 10 | 191 | 36 | 89 | 0 | 102 | 0 | 17 | 47 | 42 | 8 | 0 | 37 | 300 | 0 | 366 | 30 | 57 | 150 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 6839.36 | 931 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 661.56 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 21 | 0 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 211 | 0 | 0 | 0 | 403 | 0 | 0 | 137 | 0 | 115 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 624 | 1222 | 17 | 6950.56 | 13789.92 | 108.16
06:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 397 | 17 | 0 | 35 | 45 | 45 | 15 | 0 | 35 | 0 | 300 | 278 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 50 | 76 | 17 | 12 | 0 | 0.05 | 207 | 96 | 38 | 477 | 0 | 0 | 19 | 0 | 92 | 213 | 0 | 0 | 0 | 600 | 0 | 51 | 123 | 0 | 0 | 353 | 330 | 10 | 198 | 34 | 90 | 0 | 101 | 0 | 17 | 45 | 34 | 0 | 3 | 37 | 300 | 0 | 375 | 30 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 0 | 0 | 6698.05 | 931 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.41 | 1170 | 0 | 666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0.11 | 204 | 0 | 211 | 0 | 0 | 0 | 406 | 0 | 0 | 138 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 307 | 115 | 220 | 0 | 623 | 1222 | 17 | 6616.57 | 13314.62 | 108.15
07:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 398 | 17 | 0 | 34 | 45 | 45 | 15 | 0 | 35 | 0 | 300 | 279 | 0 | 0 | 0 | 250 | 0 | 0 | 6 | 17 | 25 | 22 | 0 | 0 | 45 | 16 | 0 | 0 | 0 | 50 | 76 | 17 | 12 | 0 | 0.54 | 207 | 68 | 36 | 477 | 0 | 0 | 19 | 0 | 95 | 213 | 0 | 0 | 0 | 601 | 5 | 51 | 122 | 0 | 0 | 352 | 330 | 10 | 196 | 36 | 91 | 0 | 102 | 0 | 17 | 45 | 34 | 0 | 18 | 37 | 315 | 0 | 375 | 30 | 57 | 157 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 0 | 7.87 | 0 | 6696.41 | 931 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1005 | 0 | 660.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.78 | 17 | 0 | 0 | 10.61 | 205 | 0 | 211 | 0 | 0 | 0 | 408 | 0 | 0.89 | 139 | 0 | 50 | 5 | 49 | 0 | 0 | 0 | 1.1 | 32 | 0.03 | 0 | 307 | 115 | 220 | 0 | 624 | 1222 | 17 | 6543.05 | 13239.46 | 108.14
08:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 414 | 17 | 0 | 34 | 45 | 45 | 15 | 0 | 35 | 0 | 300 | 294 | 0 | 0 | 0 | 250 | 0 | 0 | 15 | 17 | 28 | 22 | 0 | 0 | 43 | 16 | 0 | 0 | 0 | 50 | 76 | 17 | 12 | 0 | 1.29 | 207 | 51 | 10 | 477 | 0 | 0 | 19 | 0 | 92 | 213 | 0 | 0 | 0 | 601 | 0 | 51 | 117 | 0 | 0 | 300 | 290 | 10 | 209 | 36 | 91 | 0 | 101 | 0 | 5 | 45 | 34 | 0 | 42 | 37 | 315 | 0 | 395 | 30 | 57 | 153 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 50 | 1 | 21.4 | 1 | 6634.69 | 931 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 1000 | 0 | 664.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.07 | 51 | 0 | 0 | 27.34 | 205 | 0 | 211 | 0 | 0 | 0 | 379 | 0 | 2.57 | 138 | 0 | 50 | 15 | 49 | 0 | 0 | 0 | 3.1 | 87 | 0.15 | 0 | 307 | 115 | 180 | 0 | 625 | 1120 | 17 | 6528.09 | 13162.78 | 108.13
09:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 407 | 17.5 | 0 | 35 | 45 | 47 | 15 | 17 | 35 | 0 | 300 | 294 | 0 | 0 | 0 | 250 | 0 | 0 | 21 | 17 | 27 | 22 | 0 | 0 | 47 | 16 | 0 | 0 | 7 | 34 | 76 | 17 | 12 | 0 | 3.03 | 208 | 51 | 2 | 480 | 0 | 0 | 22 | 0 | 101 | 213 | 0 | 0 | 0 | 602 | 16 | 51 | 113 | 0 | 0 | 348 | 330 | 10 | 192 | 35 | 53 | 0 | 102 | 0 | 5 | 45 | 34 | 0 | 57 | 36 | 315 | 0 | 374 | 30 | 57 | 160 | 7 | 0 | 81 | 30 | 0 | 18 | 165 | 17 | 77 | 9 | 44 | 2 | 27.5 | 6 | 6735.03 | 931 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1000 | 0 | 664.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.73 | 76 | 0 | 0 | 26.64 | 205 | 0 | 207 | 0 | 0 | 0 | 350 | 0 | 4.01 | 137 | 0 | 110 | 23 | 48 | 0 | 0 | 0 | 5.2 | 143 | 0.52 | 0 | 307 | 115 | 220 | 0 | 623 | 1102 | 17 | 6699.5 | 13434.53 | 108.12
10:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 410 | 17.5 | 0 | 35 | 45 | 47 | 20 | 35 | 72 | 0 | 300 | 282 | 0 | 0 | 17 | 250 | 0 | 0 | 30 | 17 | 26.5 | 22 | 0 | 0 | 47 | 16 | 12 | 0 | 13 | 34 | 76 | 17 | 12 | 0 | 3.41 | 160 | 58 | 2 | 540 | 0 | 0 | 46 | 0 | 100 | 213 | 0 | 0 | 0 | 603 | 18 | 51 | 108 | 0 | 0 | 320 | 330 | 10 | 200 | 34 | 50 | 0 | 101 | 0 | 17 | 45 | 30 | 10 | 68 | 35 | 310 | 0 | 370 | 30 | 57 | 158 | 7 | 0 | 81 | 30 | 0 | 18 | 166 | 17 | 77 | 9 | 44 | 2 | 45.87 | 6 | 6879.28 | 904 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 88 | 1000 | 0 | 665.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.99 | 86 | 0 | 0 | 58.55 | 205 | 0 | 204 | 0 | 0 | 0 | 403 | 0 | 5.26 | 137 | 0 | 115 | 26 | 53 | 0 | 0 | 0 | 6.1 | 165 | 0.15 | 0 | 274 | 115 | 220 | 0 | 623 | 1100 | 35 | 6803.42 | 13682.7 | 108.11
11:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 555 | 17.5 | 7 | 35 | 45 | 47 | 55 | 35 | 72 | 0 | 0 | 281 | 0 | 0 | 35 | 326 | 0 | 0 | 30 | 17 | 26 | 22 | 0 | 0 | 81 | 16 | 15 | 0 | 14 | 42 | 60 | 18 | 12 | 0 | 3.67 | 160 | 97 | 2 | 540 | 54 | 0 | 50 | 11 | 97 | 212 | 0 | 0 | 0 | 606 | 19 | 51 | 100 | 0 | 0 | 344 | 330 | 10 | 191 | 34 | 52 | 0 | 103 | 0 | 17 | 48 | 36 | 16 | 67 | 35 | 310 | 0 | 376 | 30 | 57 | 154 | 12 | 0 | 81 | 30 | 0 | 18 | 166 | 17 | 76 | 9 | 44 | 2 | 22.53 | 6 | 7003.7 | 903 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 99 | 1000 | 0 | 646.07 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 50.97 | 88 | 0 | 0 | 65.42 | 205 | 0 | 201 | 0 | 0 | 0 | 403 | 0 | 5.65 | 140 | 0 | 115 | 12 | 97 | 0 | 0 | 0 | 7.2 | 174 | 0.17 | 0 | 274 | 115 | 220 | 0 | 625 | 1090 | 20 | 6847.48 | 13851.18 | 108.1
12:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 555 | 17.5 | 17 | 35 | 45 | 47 | 55 | 35 | 72 | 0 | 0 | 281 | 0 | 0 | 35 | 327 | 0 | 0 | 33 | 17 | 25.5 | 22 | 0 | 0 | 92 | 16 | 54 | 0 | 4 | 49 | 60 | 49 | 12 | 0 | 3.65 | 160 | 105 | 2 | 540 | 54 | 0 | 50 | 17 | 101 | 211 | 0 | 0 | 0 | 663 | 18 | 51 | 95 | 0 | 0 | 346 | 330 | 10 | 208 | 31 | 50 | 0 | 103 | 0 | 17 | 90 | 42 | 18 | 71 | 35 | 305 | 0 | 364 | 30 | 57 | 156 | 12 | 0 | 81 | 30 | 0 | 16 | 166 | 17 | 76 | 9 | 44 | 2 | 47.88 | 6 | 7269.53 | 903 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 1000 | 0 | 662.95 | 0 | 0 | 0 | 90 | 65 | 0 | 0 | 0 | 0 | 30.99 | 106 | 0 | 0 | 66.86 | 205 | 0 | 200 | 0 | 0 | 0 | 395 | 0 | 4.93 | 139 | 0 | 115 | 33 | 109 | 0 | 0 | 0 | 3.5 | 159 | 0.35 | 1.6 | 271 | 115 | 220 | 0 | 625 | 1104 | 35 | 7010.18 | 14279.71 | 108.09
13:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 570 | 54 | 17 | 33 | 45 | 47 | 55 | 35 | 72 | 0 | 0 | 288 | 0 | 0 | 35 | 328 | 0 | 0 | 22 | 17 | 25.5 | 22 | 0 | 0 | 89 | 16 | 84 | 0 | 2 | 49 | 60 | 54.36 | 12 | 0 | 3.41 | 160 | 96 | 5 | 540 | 54 | 0 | 50 | 17 | 96 | 211 | 0 | 0 | 0 | 683 | 6 | 51 | 81 | 0 | 11 | 341 | 330 | 10 | 188 | 34 | 51 | 0 | 102 | 0 | 17 | 94 | 30 | 34 | 39 | 35 | 295 | 0 | 316 | 30 | 57 | 148 | 12 | 0 | 81 | 30 | 0 | 16 | 166 | 17 | 76 | 9 | 32 | 2 | 41.91 | 0 | 7167.18 | 904 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 1000 | 0 | 658.29 | 0 | 0 | 0 | 113 | 111 | 0 | 0 | 0 | 0 | 26.43 | 65 | 0 | 0 | 63.2 | 205 | 0 | 200 | 0 | 0 | 0 | 350 | 0 | 5.62 | 139 | 0 | 115 | 27 | 110 | 0 | 0 | 0 | 7 | 124 | 0.68 | 16 | 276 | 115 | 180 | 0 | 624 | 1180 | 35 | 7006.22 | 14173.4 | 108.08
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 600 | 54 | 17 | 33 | 45 | 47 | 55 | 35 | 108 | 0 | 55 | 301 | 0 | 0 | 55 | 328 | 0 | 0 | 28 | 17 | 24 | 22 | 0 | 0 | 92 | 16 | 84 | 0 | 1 | 49 | 60 | 54.36 | 12 | 0 | 2.93 | 160 | 100 | 2 | 540 | 54 | 0 | 50 | 17 | 94 | 211 | 0 | 0 | 0 | 686 | 17 | 51 | 80 | 0 | 54 | 341 | 310 | 10 | 183 | 34 | 50 | 0 | 104 | 0 | 17 | 105 | 32 | 34 | 35 | 34 | 310 | 0 | 321 | 30 | 57 | 142 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 75 | 9 | 32 | 2 | 28.36 | 0 | 7361.65 | 903 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 1001 | 0 | 642.04 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 8 | 24.38 | 45 | 0 | 0 | 55.89 | 181 | 0 | 200 | 0 | 0 | 0 | 355 | 0 | 5.01 | 140 | 0 | 115 | 32 | 95 | 0 | 0 | 0 | 5.9 | 163 | 0.11 | 16 | 276 | 115 | 180 | 0 | 623 | 1165 | 35 | 6935.33 | 14296.98 | 108.07
15:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 600 | 54 | 17 | 33 | 45 | 47 | 55 | 35 | 108 | 0 | 225 | 294 | 0 | 0 | 55 | 327 | 0 | 0 | 23 | 17 | 25.06 | 22 | 0 | 0 | 89 | 16 | 90 | 0 | 3 | 47 | 74 | 54.36 | 12 | 0 | 2.22 | 209 | 101 | 2 | 542 | 17 | 0 | 49 | 17 | 99 | 209 | 0 | 0 | 0 | 706 | 12 | 51 | 86 | 0 | 50 | 339 | 310 | 10 | 179 | 34 | 51 | 0 | 101 | 0 | 17 | 92 | 32 | 34 | 46 | 34 | 320 | 0 | 386 | 30 | 57 | 153 | 0 | 0 | 83 | 30 | 0 | 16 | 164 | 17 | 75 | 9 | 32 | 2 | 21.23 | 0 | 7650.87 | 876 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 1000 | 0 | 663 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 8 | 31.67 | 73 | 0 | 0 | 46.23 | 203 | 0 | 201 | 0 | 0 | 0 | 399 | 0 | 4.14 | 139 | 8 | 115 | 23 | 100 | 0 | 0 | 0 | 4.7 | 100 | 0.45 | 16 | 276 | 115 | 220 | 0 | 624 | 1150 | 17 | 6935.19 | 14586.06 | 108.07
16:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 567 | 54 | 32 | 33 | 50 | 47 | 55 | 35 | 108 | 0 | 250 | 284 | 0 | 0 | 35 | 327 | 0 | 0 | 13 | 17 | 25 | 22 | 0 | 0 | 91 | 16 | 97 | 0 | 8 | 32 | 74 | 54.36 | 12 | 0 | 1.2 | 209 | 103 | 2 | 549 | 17 | 0 | 50 | 17 | 102 | 209 | 0 | 0 | 0 | 702 | 7 | 51 | 97 | 0 | 10 | 320 | 300 | 10 | 147 | 34 | 50 | 0 | 104 | 1 | 20 | 105 | 34 | 34 | 26 | 34 | 310 | 0 | 358 | 30 | 57 | 153 | 12 | 0 | 83 | 30 | 0 | 16 | 164 | 17 | 75 | 9 | 32 | 1 | 8.91 | 0 | 7497.47 | 877 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 1000 | 0 | 645 | 0 | 17 | 0 | 113 | 113 | 0 | 48 | 14 | 43 | 22.43 | 45 | 0 | 0 | 6.64 | 204 | 0 | 201 | 0 | 0 | 0 | 385 | 0 | 0.87 | 140 | 44 | 115 | 14 | 100 | 0 | 0 | 0 | 2.7 | 72 | 0.04 | 16 | 270 | 115 | 220 | 0 | 624 | 1180 | 17 | 6947.68 | 14445.15 | 108.07
17:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 460 | 54 | 35 | 33 | 60 | 47 | 55 | 55 | 142 | 0 | 290 | 275 | 0 | 0 | 35 | 329 | 0 | 0 | 4 | 17 | 25 | 22 | 0 | 0 | 89 | 16 | 91 | 0 | 4 | 48 | 74 | 54.36 | 12 | 0 | 0.2 | 207 | 97 | 9 | 548 | 17 | 0 | 50 | 17 | 101 | 209 | 0 | 0 | 0 | 701 | 2 | 51 | 105 | 0 | 0 | 345 | 327 | 5 | 208 | 34 | 52 | 0 | 106 | 8 | 20 | 90 | 32 | 34 | 6 | 34 | 310 | 0 | 354 | 30 | 57 | 152 | 11 | 0 | 83 | 30 | 0 | 16 | 164 | 17 | 75 | 9 | 32 | 0 | 3.38 | 6 | 7534.94 | 876 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 1000 | 0 | 646 | 0 | 32 | 0 | 113 | 113 | 0 | 48 | 17 | 43 | 6.43 | 15 | 0 | 0 | 6.59 | 205 | 0 | 200 | 0 | 0 | 0 | 383 | 0 | 0.41 | 140 | 43 | 115 | 4 | 101 | 0 | 0 | 0 | 0.7 | 22 | 0.07 | 16 | 261 | 115 | 220 | 0 | 625 | 1180 | 17 | 6817.2 | 14352.14 | 108.07
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 490 | 54 | 35 | 57 | 100 | 97 | 55 | 55 | 162 | 0 | 300 | 297 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 17 | 27 | 22 | 0 | 0 | 86 | 32 | 100 | 0 | 1 | 50 | 74 | 54.36 | 12 | 0 | 0 | 206 | 100 | 12 | 630 | 90 | 0 | 50 | 17 | 96 | 211 | 0 | 0 | 0 | 704 | 0 | 51 | 103 | 0 | 0 | 332 | 330 | 5 | 204 | 34 | 50 | 0 | 125 | 9 | 20 | 96 | 38 | 34 | 0 | 34 | 305 | 0 | 380 | 30 | 56 | 144 | 0 | 0 | 84 | 30 | 0 | 16 | 165 | 17 | 76 | 9 | 32 | 0 | 0 | 0 | 7893.36 | 876 | 201 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 645 | 0 | 40 | 0 | 113 | 113 | 0 | 65 | 35 | 34 | 0 | 0 | 10 | 0 | 0 | 205 | 0 | 201 | 0 | 0 | 0 | 402 | 0 | 0 | 140 | 43 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 285 | 115 | 220 | 0 | 561 | 1181 | 17 | 6809 | 14702.36 | 108.07
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 400 | 54 | 17 | 102 | 131 | 97 | 55 | 55 | 162 | 0 | 300 | 306 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 0 | 91 | 32 | 104 | 0 | 0 | 50 | 68 | 54.36 | 12 | 0 | 0 | 206 | 104 | 13 | 630 | 144 | 0 | 50 | 17 | 96 | 213 | 0 | 0 | 0 | 788 | 0 | 51 | 105 | 0 | 0 | 347 | 330 | 6 | 185 | 34 | 58 | 0 | 196 | 9 | 20 | 98 | 38 | 34 | 0 | 34 | 310 | 0 | 360 | 30 | 56 | 151 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 17 | 77 | 9 | 32 | 0 | 0 | 0 | 8200.36 | 877 | 194 | 0 | 40 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 656 | 0 | 40 | 0 | 113 | 113 | 0 | 92 | 37 | 0 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 197 | 0 | 0 | 0 | 340 | 0 | 0 | 140 | 43 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 268 | 115 | 220 | 0 | 622 | 1202 | 17 | 7155 | 15355.36 | 108.07
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 400 | 54 | 17 | 106 | 133 | 97 | 55 | 55 | 162 | 0 | 300 | 306 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 0 | 91 | 16 | 106 | 0 | 0 | 50 | 68 | 54.36 | 12 | 0 | 0 | 206 | 104 | 22 | 631 | 155 | 0 | 50 | 17 | 97 | 213 | 0 | 0 | 0 | 844 | 0 | 51 | 115 | 44 | 0 | 342 | 330 | 10 | 198 | 34 | 90 | 0 | 197 | 9 | 20 | 104 | 40 | 34 | 0 | 34 | 320 | 0 | 389 | 30 | 56 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 164 | 17 | 77 | 9 | 32 | 0 | 0 | 0 | 8442.36 | 876 | 193 | 0 | 35 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 657 | 0 | 40 | 0 | 113 | 113 | 0 | 92 | 37 | 8 | 0 | 0 | 26 | 0 | 0 | 203 | 0 | 191 | 0 | 0 | 0 | 374 | 0 | 0 | 140 | 44 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 624 | 1222 | 17 | 7258 | 15700.36
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 408 | 54 | 17 | 105 | 133 | 97 | 55 | 55 | 162 | 0 | 300 | 308 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 0 | 92 | 16 | 103 | 0 | 0 | 50 | 68 | 54.36 | 12 | 0 | 0 | 209 | 103 | 17 | 630 | 150 | 0 | 50 | 17 | 100 | 213 | 0 | 0 | 0 | 854 | 0 | 51 | 115 | 61 | 0 | 341 | 330 | 10 | 198 | 34 | 83 | 0 | 197 | 8 | 20 | 105 | 38 | 34 | 0 | 34 | 315 | 0 | 383 | 30 | 56 | 155 | 8 | 0 | 84 | 30 | 0 | 16 | 165 | 17 | 77 | 9 | 33 | 0 | 0 | 0 | 8456.36 | 876 | 194 | 0 | 35 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 657 | 0 | 40 | 0 | 113 | 113 | 0 | 92 | 38 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 43 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 277 | 115 | 220 | 0 | 625 | 1224 | 17 | 7326 | 15782.36 | 108.07
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 393 | 54 | 17 | 105 | 133 | 97 | 55 | 55 | 162 | 0 | 300 | 299 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 27 | 22 | 0 | 0 | 89 | 16 | 104 | 0 | 0 | 50 | 68 | 54.36 | 12 | 0 | 0 | 213 | 101 | 20 | 647 | 145 | 0 | 50 | 17 | 94 | 213 | 0 | 0 | 0 | 830 | 0 | 51 | 117 | 63 | 0 | 346 | 330 | 10 | 193 | 35 | 89 | 0 | 197 | 0 | 20 | 102 | 40 | 34 | 0 | 34 | 310 | 0 | 371 | 30 | 56 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 164 | 17 | 76 | 9 | 47 | 0 | 0 | 0 | 8408.36 | 876 | 190 | 0 | 32 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 657.25 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 37 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 403 | 0 | 0 | 139 | 46 | 115 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 274 | 115 | 220 | 0 | 626 | 1227 | 17 | 7327.25 | 15735.61 | 108.06
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 399 | 54 | 17 | 106 | 123 | 146 | 55 | 55 | 162 | 0 | 300 | 301 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 18 | 22 | 0 | 0 | 92 | 16 | 105 | 0 | 0 | 50 | 67 | 54.36 | 12 | 0 | 0 | 213 | 102 | 23 | 650 | 17 | 0 | 50 | 17 | 98 | 213 | 0 | 0 | 0 | 868 | 0 | 51 | 118 | 85 | 0 | 345 | 330 | 10 | 194 | 35 | 90 | 34 | 197 | 0 | 20 | 100 | 40 | 34 | 0 | 34 | 320 | 0 | 388 | 30 | 56 | 156 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 17 | 76 | 9 | 47 | 0 | 0 | 0 | 8441.36 | 875 | 182 | 0 | 35 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 658.61 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 37 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 45 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 624 | 1227 | 17 | 7325.81 | 15767.17 | 108.06
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 431 | 21 | 17 | 88 | 123 | 146 | 55 | 35 | 153 | 0 | 300 | 304 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 52 | 27 | 22 | 0 | 0 | 90 | 16 | 105 | 0 | 0 | 50 | 67 | 54.36 | 12 | 0 | 0 | 212 | 101 | 26 | 650 | 17 | 0 | 50 | 17 | 94 | 213 | 0 | 0 | 0 | 760 | 0 | 51 | 120 | 86 | 0 | 344 | 330 | 12 | 201 | 35 | 71 | 92 | 197 | 0 | 20 | 102 | 40 | 34 | 0 | 35 | 315 | 0 | 390 | 30 | 57 | 156 | 8 | 0 | 84 | 30 | 0 | 18 | 164 | 17 | 76 | 9 | 47 | 0 | 0 | 0 | 8253.36 | 876 | 179 | 0 | 35 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 656.42 | 0 | 40 | 0 | 113 | 113 | 0 | 93 | 37 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 379 | 0 | 0 | 140 | 44 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 626 | 1227 | 17 | 7318.62 | 15571.98 | 108.06
Total KWH | 0 | 2118720 | 324960 | 0 | 0 | 0 | 0 | 0 | 8341200 | 0 | 10895210 | 778320 | 295200 | 1332864 | 1644960 | 1750342 | 1179293 | 795875 | 2367360 | 0 | 6253300 | 7022109 | 0 | 0 | 796849 | 6892267 | 0 | 0 | 203198 | 940800 | 621600 | 528840 | 0 | 0 | 1998491 | 416509 | 1621440 | 0 | 57120 | 1139686 | 1656074 | 1149280 | 300480 | 0 | 24840 | 5002940 | 2274909 | 444960 | 13098181.82 | 868145 | 0 | 933600 | 320814 | 2372764 | 4921196 | 0 | 0 | 0 | 16254544 | 117855 | 1220915 | 2664654 | 351273 | 103200 | 8509200 | 7850000 | 259680 | 4620000 | 838656 | 1664640 | 177940 | 3076800 | 41160 | 390960 | 2058840 | 875520 | 584592 | 505791 | 844706 | 7545500 | 0 | 9395000 | 716000 | 1328880 | 3697772.73 | 194520 | 0 | 1990080 | 715968 | 0 | 410000 | 4397760 | 428400 | 1827600 | 211200 | 964800 | 14750 | 258750 | 33360 | 180825963.55 | 21869090 | 5361120 | 0 | 228480 | 315136 | 912000 | 0 | 0 | 0 | 0 | 0 | 613440 | 26596360 | 0 | 15654980 | 0 | 499871 | 0 | 1964544 | 2096064 | 0 | 781312 | 353120 | 337205 | 339264 | 680900 | 246397 | 0 | 443992 | 5005636 | 0 | 5067064 | 0 | 0 | 0 | 9502763 | 0 | 38760 | 3425000 | 391418 | 2566569 | 228315 | 1935926 | 0 | 0 | 0 | 48200.88 | 1227600 | 3021 | 1245216 | 7026000 | 2747000 | 5363970 | 0 | 14943960 | 29205818.18 | 520800 | 169786312.06 | 350612275.61

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14279.71 | MW | 12:00 Hr. | Energy Generated |  |  | 350.6123 |  | MKWHr.
| Day Peak Demand |  |  | 14556.71 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.513 |  | MKWHr.
| Evening Peak Generation |  |  | 15782.36 | MW | 20:00 Hr. | Energy Demand |  |  | 358.1253 |  | MKWHr.
| Evening Peak Demand |  |  | 16100.36 | MW | 20:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 13162.78 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 979.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15782.36 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.9056 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.5545 | 0 | 14.3255 | 0 | 0 | 0.2032 | 0 | 0 | 55.0833 | Gas | 134.6463 | Gas | 480679024.3843
| Chattogram Zone |  |  | 5.3662 | 29.3527 | 15.0522 | 0 | 5.0029 | 0.14269 | 0 | 0.05712 | 54.9738 | Coal | 110.9413 | Coal | 608300972.429
| Cumilla Zone |  |  | 24.3218 | 0 | 10.9354 | 0 | 0 | 0.50579 | 0.87552 | 0 | 36.6385 | HFO | 55.9043 | HFO | 1038886976.78
| Mymensingh Zone |  |  | 0.9648 | 0 | 2.5006 | 0 | 0 | 0.2735 | 0 | 0 | 3.7389 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.3915 | Hydro | 5.0029 | Hydro | 500294
| Khulna Zone |  |  | 5.3611 | 26.5964 | 0.54362 | 0 | 0 | 0.61344 | 22.7811 | 0 | 55.8956 | Solar | 4.7487 | Solar | 71484227.1048
| Barishal Zone |  |  | 8.111 | 51.1758 | 1.766 | 0 | 0 | 0.003021 | 0 | 0 | 61.0558 | Import | 39.3116 | Import | 220488558.1
| Rajshahi Zone |  |  | 19.5755 | 0 | 6.2785 | 0 | 0 | 1.5029 | 15.655 | 0 | 43.0119 | Wind | 0.05712 | Wind | 841948.8
| Rangpur Zone |  |  | 0 | 3.8164 | 4.5025 | 0 | 0 | 1.5041 | 0 | 0 | 9.823
| Total |  |  | 134.6463 | 110.9413 | 55.9043 | 0 | 5.0029 | 4.7487 | 39.3116 | 0.05712 | 350.6123
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 480679024.3843 |  | Hydro | 500294
|  |  |  | Coal | 608300972.429 |  | Solar | 71484227.1048
|  |  |  | HFO | 1038886976.78 |  | Import | 220488558.1
|  |  |  | HSD | 0 |  | Wind | 841948.8
[5 empty] | Total: | 242,11,82,001 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8691 | Peak Hr Flow | 876.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 65281413.17 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.655 | Peak Hr Flow | 657.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2372 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.87552 | Peak Hr Flow | 38.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2734 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.3996 | Peak Hr Flow | 1571.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 22 |  | 5527
|  |  |  | Chattogram |  | 0 |  | 1522
|  |  |  | Cumilla |  | 0 |  | 1538
|  |  |  | Mymensingh |  | 75 |  | 1188
|  |  |  | Sylhet |  | 5 |  | 704
|  |  |  | Khulna |  | 80 |  | 1821
|  |  |  | Barishal |  | 0 |  | 505
|  |  |  | Rajshahi |  | 68 |  | 1531
|  |  |  | Rangpur |  | 54 |  | 1024
|  |  |  | Total |  | 304 |  | 15360
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:09 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 08:10 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 08:26 | 13:05 | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Due to
Under Construction GIS Building works.
| 08:34 |  | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to Barishal- | [7 empty] | 40.0MW load
|  |  | Bhandariya 132 KV line S/D for emergency maintenance work and from Barishal 132/33kV end | [7 empty] | interrup. Bhandaria
|  |  | Due to High temperature remedy work at different points and loop changing | [7 empty] | 132/33kV end
| 08:49 | 09:14 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance Relay | [7 empty] | and 39.0MW load
|  |  | : R phase, zone- 2,3 relays Due to Unknown and from Bhandaria 132/33kV end showing | [7 empty] | interrup. Bhandaria
|  |  | Distance relay operate zone 2,3 relays. | [7 empty] | 132/33kV end
| 09:17 | 14:19 | Madunaghat 132/33kV S/S TR-2(517T) LT Tripped showing REF-615(33KV), RET-670,RET-650 | [7 empty] | 17.0MW load
|  |  | relays Due to 33kV feeder old wasa(bpdb) is tripped, and the Y-phase loop from the bus | [7 empty] | interrup.
isolator lower point to the breaker upper point is broken down.
|  | 09:23 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT is restored.
| 09:25 | 09:40 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance, R
phase, zone 2,3 relays Due to Unknown
| 10:28 | 10:28 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance relay
DR2,3 relays.
| 10:34 | 11:08 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to transformer maintenance | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 10:35 | 11:07 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to transformer maintenance | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 10:40 | 11:54 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to 132 KV 699
number tower nest broken job.
| 10:42 |  | Meghnaghat 450 MW CCPP (MPL) Tripped with remarks:- gt & st
| 10:42 |  | Meghnaghat 450 MW CCPP (MPL) Tripped with remarks:- both
| 10:55 | 15:57 | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) Scheduled S/D Due to Maintenance
|  | 11:16 | BIPTC S/S 20DF12 is restored.
|  | 11:17 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT is restored.
| 11:24 | 13:39 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Forced S/D Due to Line DS red | [7 empty] | 2.0MW load
|  |  | hot maintenance | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 14272 MW
| 12:18 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Tripped showing Distance relay,
Lockout Relay relays Due to Directional Earth Fault
| 13:16 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-1
|  | 13:32 | Bogura-Natore 132 kV Ckt-2 is restored.
| 14:06 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 15:45 | 15:59 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing Distance
Protection Relay : Zone 2, Phase C, Lockout Relay relays. and from Naogaon 132/33kV end
showing no relays Due to None
| 15:57 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
| 16:35 | 18:11 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D Due to Piling work of G2G project
| 17:06 |  | Chowmuhani GIS–Lakshmipur 132kV Ckt-2 was charged from Chowmuhani GIS end
for the first time.
| 19:56 | 22:40 | Chowmuhani 132/33kV S/S TR1 Forced S/D Due to Y Phase Red Hot Maintenance | [7 empty] | 20.0MW load
interrup.
| 20:00 |  | Evening Peak Generation: 15782 MW.
| 21:52 |  | Chowmuhani GIS–Maijdee 132kV Ckt-2 was switched on from both ends for the first time.
| 02:45 | 03:35 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing REF-615 relays Due to 33kv Laksam REB | [7 empty] | 30.0MW load
|  |  | feeder fault C.B not trip. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 13542 MW.
| 07:09 |  | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to 33 KV L-Bus Feeder Bus DS Red Hot | [7 empty] | 40.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:10 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Forced S/D Due to Red hot maintenance work
| 07:10 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Forced S/D Due to Red hot maintenance | [7 empty] | 50.0MW load
interrup.
| 07:51 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 07:51 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 341 | 8341200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 6253300 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 308 | 7022109 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1179293 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6892267 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 778320 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 133 | 1644960 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 795875 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 796849 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 621600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 528840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 324960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 97 | 1750342 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 1332864 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2118720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2367360 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 203198 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 295200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 408 | 10895210 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 940800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2681 | 55083267
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 320814 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117855 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 933600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 209 | 5002940 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 4921196 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 2372764 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 1656074 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1139686 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 300480 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 444960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 103 | 1621440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 416509 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1149280 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 103 | 2274909 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1998491 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 150 | 868145 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 854 | 16254544 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 57120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 630 | 13098181.82 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2738.36 | 54973828.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4620000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 341 | 8509200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7850000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 103200 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 838656 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 259680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 61 | 351273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1220915 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 2664654 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 844706 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 177940 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 197 | 3076800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 38 | 875520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 584592 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 390960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 2058840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 41160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 1664640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 505791 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1659 | 36638527
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 964800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 211200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1827600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 258750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 33360 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 428400 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 136 | 3738860
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 56 | 1328880 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3697772.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715968 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1990080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4397760 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 410000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 194520 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7545500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 9395000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1242 | 30391480.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 21869090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 228480 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 315136 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 194 | 5361120 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 613440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1227 | 26596360 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2410 | 55895626
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 625 | 14943960 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1245216 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2747000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1224 | 29205818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5363970 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 520800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 7026000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3021 | -
Barishal Area Total |  |  |  |  | 2236 | 2588 | 61055785.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 339264 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 499871 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 353120 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 203 | 5005636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 5067064 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9502763 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 246397 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 337205 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 781312 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2096064 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1964544 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 657 | 15654980 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 443992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 680900 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1921 | 43011872
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 43 | 391418 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3425000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 109 | 1935926 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48200.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2566569 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 228315 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1227600 | -
Rangpur Area Total |  |  |  |  | 950 | 407 | 9823028.88
Eastern Grid Total |  |  |  |  | 17385.715 | 8456.36 | 180825963.55
Western Grid Total |  |  |  |  | 10444.16 | 7326 | 169786312.06
National Grid Total |  |  |  |  | 27829.875 | 15782.36 | 350612275.61
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-09-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10376.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4678.2 | MW
i) Dhaka area |  |  | 5504.67 |  | MW | i) Khulna area |  |  |  | 1740.6 | MW
ii) Chattogram area |  |  | 1522.2 |  | MW | ii) Barishal area |  |  |  | 505 | MW
iii) Cumilla area |  |  | 1537.69 |  | MW | iii) Rajshahi area |  |  |  | 1462.6 | MW
iv) Mymensingh area |  |  | 1113 |  | MW | iv) Rangpur area |  |  |  | 970 | MW
v) Sylhet area |  |  | 699 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15054.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 20:00 | 67 | Hathazari | 93 | 20:00 | 133 | PHP | 9 | 15:00
2 | AKSML | 112.5 | 10:00 | 68 | Ishurdi | 82 | 22:00 | 134 | Pabna | 106 | 22:00
3 | Aftabnagar | 42 | 18:00 | 69 | Jaldhaka | 77 | 22:00 | 135 | Palashbari | 139 | 19:00
4 | Agargaon | 145 | 13:00 | 70 | Jamalpur | 104 | 13:00 | 136 | Panchagarh | 56 | 18:30
5 | Agrabad | 108 | 15:00 | 71 | Jashore | 147 | 23:00 | 137 | Patiya | 12.3 | 18:30
6 | Amnura | 38 | 23:00 | 72 | Jhenaidah | 126 | 22:00 | 138 | Patuakhali | 76 | 22:00
7 | Ashuganj | 96 | 23:00 | 73 | Joydebpur | 160 | 19:00 | 139 | Payra | 36 | 22:00
8 | BSRM | 148 | 04:00 | 74 | Joypurhat | 60 | 01:00 | 140 | Postogola | 72 | 00:00
9 | Bagerhat | 89 | 21:00 | 75 | Juldah | 16.5 | 16:00 | 141 | Purbachal | 23 | 18:30
10 | Bajitpur | 106 | 18:30 | 76 | KSRM | 47 | 12:00 | 142 | Purbasadipur | 134 | 00:00
11 | Bakulia | 102 | 16:00 | 77 | Kabirpur | 259 | 11:00 | 143 | Rahanpur | 39 | 03:00
12 | Banani | 54 | 13:00 | 78 | Kachua | 96 | 19:30 | 144 | Rahim | 24 | 18:00
13 | Bangabhaban | 26 | 10:00 | 79 | Kallyanpur | 111 | 23:00 | 145 | Rajbari | 80 | 18:00
14 | Barapukuria | 69 | 02:00 | 80 | Kalurghat | 44 | 15:00 | 146 | Rajendrapur | 130 | 23:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 81 | 18:30 | 147 | Rajshahi | 110 | 00:00
16 | Barishal | 122 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 104 | 00:00
17 | Barishal-230 | 112 | 21:00 | 83 | Kasba | 38 | 19:00 | 149 | Ramganj | 120 | 21:00
18 | Baroaulia | 68 | 13:00 | 84 | Kazla | 103 | 13:00 | 150 | Rampur | 47 | 23:00
19 | Baroirhat | 71 | 18:30 | 85 | Keranigonj | 91 | 19:30 | 151 | Rangamati | 20 | 18:30
20 | Bashundhara | 211 | 13:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rangpur | 143 | 11:00
21 | BashundharaCement | 12 | 21:00 | 87 | Khulna | 92 | 13:00 | 153 | Ruppur | 7.8 | 15:00
22 | Beanibazar | 86 | 19:30 | 88 | Khulshi | 195 | 13:00 | 154 | SSM | 16 | 03:00
23 | Benapole | 72 | 12:00 | 89 | Kishoreganj | 129 | 21:00 | 155 | Saidpur | 106 | 22:00
24 | Bhaluka | 162 | 19:30 | 90 | Kodda | 282 | 21:00 | 156 | Satkhira | 139 | 22:00
25 | Bhandaria | 60 | 23:00 | 91 | Kulaura | 55 | 02:00 | 157 | Satmasjid | 104 | 12:00
26 | Bhangura | 40 | 02:00 | 92 | Kurigram | 62 | 07:00 | 158 | Savar | 224 | 11:00
27 | Bheramara(GK) | 75 | 18:30 | 93 | Kushtia | 161 | 20:00 | 159 | SevenRings | 17.83 | 01:00
28 | Bhulta | 224 | 19:30 | 94 | Laksam | 37 | 23:00 | 160 | ShahCement | 17 | 00:00
29 | Bog-Sherpur | 72 | 03:00 | 95 | Lakshmipur | 36 | 23:00 | 161 | Shahjadpur | 91 | 18:00
30 | Bogura | 173 | 22:00 | 96 | Lalbag | 61 | 11:00 | 162 | Shahjibazar | 134 | 00:00
31 | Borhanuddin | 94 | 20:00 | 97 | Lalmonirhat | 61 | 00:00 | 163 | Shahmirpur | 58 | 18:00
32 | Brahmanbaria | 142 | 21:00 | 98 | MI_Cement | 18.4 | 23:00 | 164 | Shariatpur | 86 | 00:00
33 | Cantonment | 148 | 13:00 | 99 | Madanganj | 45 | 00:00 | 165 | Sherpur | 122 | 05:00
34 | Chandina | 18.23 | 09:00 | 100 | Madaripur | 111 | 22:00 | 166 | Shikalbaha | 29 | 01:00
35 | Chandpur | 90 | 23:00 | 101 | Madartek | 102 | 23:00 | 167 | Shitalakhya | 83.7 | 16:00
36 | Chandraghona | 40 | 18:00 | 102 | Madunaghat | 60 | 18:00 | 168 | Sholosohor | 53 | 12:00
37 | Chapai | 73 | 02:00 | 103 | Magura | 66 | 18:00 | 169 | Shyampur | 96 | 00:00
38 | Charsaidpur | 29 | 00:00 | 104 | Mahasthangarh | 80 | 02:00 | 170 | Siddhirganj | 124 | 12:00
39 | Chauddagram | 78 | 19:30 | 105 | Maijdee | 24 | 23:00 | 171 | Sirajganj | 120 | 19:00
40 | Chhatak | 43 | 19:30 | 106 | Manikganj | 136 | 22:00 | 172 | Sonargaon | 160 | 18:00
41 | Chowmuhani | 204 | 19:00 | 107 | Maniknagar | 66 | 12:00 | 173 | Sreemongol | 90 | 00:00
42 | Chuadanga | 116 | 01:00 | 108 | Matarbari | 58 | 19:30 | 174 | Sreepur | 118 | 19:30
43 | Coxsbazar | 139 | 18:00 | 109 | Matuail | 74 | 09:00 | 175 | Srinagar | 52.45 | 23:00
44 | Cumilla(N) | 156 | 21:00 | 110 | Millgate | 131 | 15:00 | 176 | Sunamganj | 65 | 23:00
45 | Cumilla(S) | 153 | 15:00 | 111 | Mirpur | 130 | 18:00 | 177 | Sylhet | 61 | 01:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 13 | 15:00 | 178 | Sylhet-132 | 140 | 19:30
47 | Daudkandi | 162 | 19:30 | 113 | Mirzapur | 40 | 06:00 | 179 | TK | 29 | 22:00
48 | DhakaUniversity | 106 | 12:00 | 114 | Mithapukur | 68 | 18:00 | 180 | Tangail | 176 | 18:00
49 | Dhamrai | 134 | 21:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 00:00
50 | Dhanmondi | 147 | 12:00 | 116 | Mogbazar | 100.8 | 12:00 | 182 | Thakurgaon | 108 | 22:00
51 | Dohazari | 108 | 19:30 | 117 | Mongla | 34 | 00:00 | 183 | Tongi | 128 | 21:00
52 | Faridpur | 167 | 01:00 | 118 | Motijheel | 48 | 12:00 | 184 | Ullahpara | 35 | 10:00
53 | Fatullah | 122 | 11:00 | 119 | Muktagacha | 40 | 19:30 | 185 | Ullon | 57 | 23:00
54 | Fenchuganj | 46 | 19:00 | 120 | Munshiganj | 121 | 00:00 | 186 | Uttara | 90 | 18:00
55 | Feni | 132 | 20:00 | 121 | Muradnagar | 45 | 21:00 | 187 | UttaraNew | 65 | 18:00
56 | GPH | 9 | 19:00 | 122 | Mymensingh | 229 | 22:00 | 188 | Zigatola | 76 | 12:00
57 | Ghatail | 74 | 19:00 | 123 | Naogaon | 149 | 23:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 58 | 03:00
59 | Ghorashal-230 | 101 | 02:00 | 125 | Narinda | 68 | 12:00
60 | Goalpara | 42 | 01:00 | 126 | Narshingdi | 192 | 23:00
61 | Gollamari | 94 | 00:00 | 127 | Natore | 139 | 01:00
62 | Gopalganj | 104 | 18:30 | 128 | Nawabganj | 54.6 | 22:00
63 | Gulshan | 134 | 12:00 | 129 | Netrakona | 115 | 22:00
64 | Halishahar | 80 | 15:00 | 130 | New | 58 | 10:00
65 | HaripurSBU | 115 | 08:00 | 131 | Niamatpur | 84 | 23:00
66 | Hasnabad | 94 | 23:00 | 132 | Noapara | 46 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15016.74 | 750 |  | 15800.74
1:00 | 14819.63 | 650 |  | 15498.63
2:00 | 14585.18 | 445 |  | 15050.18
3:00 | 14322.71 | 199 |  | 14530.71
4:00 | 14032.84 | 160 |  | 14199.84
5:00 | 13789.92 | 135 |  | 13930.92
6:00 | 13314.62 | 120 |  | 13439.62
7:00 | 13239.46 | 138 |  | 13383.46
8:00 | 13162.78 | 104 |  | 13271.78
9:00 | 13434.53 | 105 |  | 13544.53
10:00 | 13682.7 | 164 |  | 13853.7
11:00 | 13851.18 | 165 |  | 14023.18
12:00 | 14279.71 | 265 |  | 14556.71
13:00 | 14173.4 | 470 |  | 14664.4
14:00 | 14296.98 | 456 |  | 14773.5
15:00 | 14586.06 | 475 |  | 15082.44
16:00 | 14445.15 | 477 |  | 14943.62
17:00 | 14352.14 | 287 |  | 14652.06
18:00 | 14702.36 | 285 |  | 15000.36
19:00 | 15355.36 | 282 |  | 15650.36
19:30 | 15700.36 | 287 |  | 16000.36
20:00 | 15782.36 | 304 |  | 16100.36
21:00 | 15735.61 | 301 |  | 16050.61
22:00 | 15767.17 | 319 |  | 16100.53
23:00 | 15571.98 | 457 |  | 16049.55
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7653.86 | 7362.88 | 15016.74 | DAILY GENERATION CURVE
00:30 | 7568.61 | 7349.575 | 14918.185
01:00 | 7483.36 | 7336.27 | 14819.63 | 29-09-2025
01:30 | 7440.86 | 7261.545 | 14702.405
02:00 | 7398.36 | 7186.82 | 14585.18
02:30 | 7280.86 | 7173.085 | 14453.945
03:00 | 7163.36 | 7159.35 | 14322.71
03:30 | 7061.36 | 7116.415 | 14177.775
04:00 | 6959.36 | 7073.48 | 14032.84
04:30 | 6899.36 | 7012.02 | 13911.38
05:00 | 6839.36 | 6950.56 | 13789.92
05:30 | 6768.705 | 6783.565 | 13552.27
06:00 | 6698.05 | 6616.57 | 13314.62
06:30 | 6697.23 | 6579.81 | 13277.04
07:00 | 6696.41 | 6543.05 | 13239.46
07:30 | 6665.55 | 6535.57 | 13201.12
08:00 | 6634.69 | 6528.09 | 13162.78
08:30 | 6684.86 | 6613.795 | 13298.655
09:00 | 6735.03 | 6699.5 | 13434.53
09:30 | 6807.155 | 6751.46 | 13558.615
10:00 | 6879.28 | 6803.42 | 13682.7
10:30 | 6941.49 | 6825.45 | 13766.94
11:00 | 7003.7 | 6847.48 | 13851.18
11:30 | 7136.615 | 6928.83 | 14065.445
12:00 | 7269.53 | 7010.18 | 14279.71
12:30 | 7218.355 | 7008.2 | 14226.555
13:00 | 7167.18 | 7006.22 | 14173.4
13:30 | 7264.415 | 6970.775 | 14235.19
14:00 | 7361.65 | 6935.33 | 14296.98
14:30 | 7506.26 | 6935.26 | 14441.52
15:00 | 7650.87 | 6935.19 | 14586.06
15:30 | 7574.17 | 6941.435 | 14515.605
16:00 | 7497.47 | 6947.68 | 14445.15
16:30 | 7516.205 | 6882.44 | 14398.645
17:00 | 7534.94 | 6817.2 | 14352.14
17:30 | 7714.15 | 6813.1 | 14527.25
18:00 | 7893.36 | 6809 | 14702.36
18:30 | 8046.86 | 6982 | 15028.86
19:00 | 8200.36 | 7155 | 15355.36
19:30 | 8442.36 | 7258 | 15700.36
20:00 | 8456.36 | 7326 | 15782.36
20:30 | 8432.36 | 7326.625 | 15758.985 |  | Executive Engineer
21:00 | 8408.36 | 7327.25 | 15735.61 |  | Network Operation Division
21:30 | 8424.86 | 7326.53 | 15751.39
22:00 | 8441.36 | 7325.81 | 15767.17
22:30 | 8347.36 | 7322.215 | 15669.575
23:00 | 8253.36 | 7318.62 | 15571.98

## En-Curve
QF-LDC-12
Date | 29-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3640 | 2009.5 | 931 | 38 | 46 | 641.68 | 208 | 4607.2 | 0 | 639 | 2256.36 | 0 | 0 | 0 | 750 | DAILY ENERGY CURVE
00:30 | 3637 | 1998.25 | 930.5 | 38 | 45 | 643.475 | 208.5 | 4602.1 | 0 | 600.5 | 2214.86 | 0 | 0 | 0 | 700 | 29-09-2025
01:00 | 3634 | 1987 | 930 | 38 | 44 | 645.27 | 209 | 4597 | 0 | 562 | 2173.36 | 0 | 0 | 0 | 650
01:30 | 3640 | 1996.5 | 930.5 | 38 | 43 | 646.045 | 209 | 4596 | 0 | 514.5 | 2088.86 | 0 | 0 | 0 | 547.5 | Energy Generated | 350.6123 |  | MKWHr
02:00 | 3646 | 2006 | 931 | 38 | 42 | 646.82 | 209 | 4595 | 0 | 467 | 2004.36 | 0 | 0 | 0 | 445 | Energy not Served | 7.513 |  | MKWHr
02:30 | 3649.5 | 1967.5 | 931 | 38 | 42 | 650.585 | 208.5 | 4591 | 0 | 454 | 1921.86 | 0 | 0 | 0 | 322 | Total Energy Requirement | 358.1253 |  | MKWHr
03:00 | 3653 | 1929 | 931 | 38 | 42 | 654.35 | 208 | 4587 | 0 | 441 | 1839.36 | 0 | 0 | 0 | 199
03:30 | 3638 | 1915 | 931 | 38 | 42 | 658.415 | 208 | 4588 | 0 | 424.5 | 1734.86 | 0 | 0 | 0 | 179.5
04:00 | 3623 | 1901 | 931 | 38 | 42 | 662.48 | 208 | 4589 | 0 | 408 | 1630.36 | 0 | 0 | 0 | 160
04:30 | 3602 | 1903 | 931 | 38 | 42 | 662.02 | 207.5 | 4583 | 0 | 408 | 1534.86 | 0 | 0 | 0 | 147.5
05:00 | 3581 | 1905 | 931 | 38 | 42 | 661.56 | 207 | 4577 | 0 | 408 | 1439.36 | 0 | 0 | 0 | 135
05:30 | 3595 | 1903.5 | 931 | 38 | 38 | 663.78 | 207 | 4557 | 2.81 | 364.5 | 1251.68 | 0 | 0 | 0 | 127.5
06:00 | 3609 | 1902 | 931 | 38 | 34 | 666 | 207 | 4537 | 5.62 | 321 | 1064 | 0 | 0 | 0 | 120
06:30 | 3617.5 | 1910.5 | 931 | 38 | 34 | 663.32 | 207 | 4456 | 68.22 | 321 | 1030.5 | 0 | 0 | 0 | 129
07:00 | 3626 | 1919 | 931 | 38 | 34 | 660.64 | 207 | 4375 | 130.82 | 321 | 997 | 0 | 0 | 0 | 138
07:30 | 3573 | 1895 | 931 | 38 | 34 | 662.75 | 207 | 4321.5 | 234.37 | 321 | 983.5 | 0 | 0 | 0 | 121
08:00 | 3520 | 1871 | 931 | 38 | 34 | 664.86 | 207 | 4268 | 337.92 | 321 | 970 | 0 | 0 | 0 | 104
08:30 | 3530 | 1886 | 931 | 38 | 34 | 664.63 | 207.5 | 4259.5 | 428.275 | 316.5 | 999.75 | 0 | 0 | 3.5 | 104.5
09:00 | 3540 | 1901 | 931 | 38 | 34 | 664.4 | 208 | 4251 | 518.63 | 312 | 1029.5 | 0 | 0 | 7 | 105
09:30 | 3551.5 | 1898.75 | 917.5 | 38 | 32 | 664.885 | 184 | 4264 | 582.98 | 311.5 | 1103.5 | 0 | 0 | 10 | 134.5
10:00 | 3563 | 1896.5 | 904 | 38 | 30 | 665.37 | 160 | 4277 | 647.33 | 311 | 1177.5 | 0 | 0 | 13 | 164
10:30 | 3604 | 1818.75 | 903.5 | 38 | 33 | 655.72 | 160 | 4276 | 646.97 | 307 | 1310.5 | 0 | 0 | 13.5 | 164.5
11:00 | 3645 | 1741 | 903 | 38 | 36 | 646.07 | 160 | 4275 | 646.61 | 303 | 1443.5 | 0 | 0 | 14 | 165
11:30 | 3656 | 1739.25 | 903 | 38 | 39 | 654.51 | 160 | 4308.5 | 658.385 | 306.5 | 1593.3 | 0 | 0 | 9 | 215
12:00 | 3667 | 1737.5 | 903 | 38 | 42 | 662.95 | 160 | 4342 | 670.16 | 310 | 1743.1 | 0 | 0 | 4 | 265
12:30 | 3599 | 1721 | 903.5 | 38 | 36 | 660.62 | 160 | 4392 | 600.705 | 301 | 1811.73 | 0 | 0 | 3 | 367.5
13:00 | 3531 | 1704.5 | 904 | 38 | 30 | 658.29 | 160 | 4442 | 531.25 | 292 | 1880.36 | 0 | 0 | 2 | 470
13:30 | 3527 | 1755.75 | 903.5 | 38 | 31 | 650.165 | 160 | 4436.5 | 526.915 | 291.5 | 1913.36 | 0 | 0 | 1.5 | 463
14:00 | 3523 | 1807 | 903 | 38 | 32 | 642.04 | 160 | 4431 | 522.58 | 291 | 1946.36 | 0 | 0 | 1 | 456
14:30 | 3582.5 | 1914.53 | 889.5 | 38 | 32 | 652.52 | 184.5 | 4438 | 481.11 | 306 | 1920.86 | 0 | 0 | 2 | 465.5
15:00 | 3642 | 2022.06 | 876 | 38 | 32 | 663 | 209 | 4445 | 439.64 | 321 | 1895.36 | 0 | 0 | 3 | 475
15:30 | 3569.5 | 2015.53 | 876.5 | 38 | 33 | 654 | 209 | 4477 | 350.715 | 355.5 | 1931.36 | 0 | 0 | 5.5 | 476
16:00 | 3497 | 2009 | 877 | 38 | 34 | 645 | 209 | 4509 | 261.79 | 390 | 1967.36 | 0 | 0 | 8 | 477
16:30 | 3537.5 | 1971 | 876.5 | 38 | 33 | 645.5 | 208 | 4503.5 | 173.785 | 412 | 1993.86 | 0 | 0 | 6 | 382
17:00 | 3578 | 1933 | 876 | 38 | 32 | 646 | 207 | 4498 | 85.78 | 434 | 2020.36 | 0 | 0 | 4 | 287
17:30 | 3587 | 1955 | 876 | 38 | 35 | 645.5 | 206.5 | 4521.5 | 42.89 | 483 | 2134.36 | 0 | 0 | 2.5 | 286
18:00 | 3596 | 1977 | 876 | 38 | 38 | 645 | 206 | 4545 | 0 | 532 | 2248.36 | 0 | 0 | 1 | 285
18:30 | 3519 | 1947 | 876.5 | 38 | 38 | 650.5 | 206 | 4732.5 | 0 | 672.5 | 2348.36 | 0 | 0 | 0.5 | 283.5
19:00 | 3442 | 1917 | 877 | 38 | 38 | 656 | 206 | 4920 | 0 | 813 | 2448.36 | 0 | 0 | 0 | 282
19:30 | 3529 | 1985 | 876 | 38 | 40 | 657 | 206 | 5010 | 0 | 819 | 2540.36 | 0 | 0 | 0 | 287
20:00 | 3564 | 2005 | 876 | 38 | 38 | 657 | 209 | 5020 | 0 | 813 | 2562.36 | 0 | 0 | 0 | 304
20:30 | 3555.5 | 1992 | 876 | 38 | 39 | 657.125 | 211 | 5019.5 | 0 | 821.5 | 2549.36 | 0 | 0 | 0 | 302.5
21:00 | 3547 | 1979 | 876 | 38 | 40 | 657.25 | 213 | 5019 | 0 | 830 | 2536.36 | 0 | 0 | 0 | 301
21:30 | 3577 | 1996.5 | 875.5 | 38 | 40 | 657.93 | 213 | 5041.6 | 0 | 816.5 | 2495.36 | 0 | 0 | 0 | 310
22:00 | 3607 | 2014 | 875 | 38 | 40 | 658.61 | 213 | 5064.2 | 0 | 803 | 2454.36 | 0 | 0 | 0 | 319
22:30 | 3620 | 2038 | 875.5 | 38 | 40 | 657.515 | 212.5 | 5026.2 | 0 | 758.5 | 2403.36 | 0 | 0 | 0 | 388
23:00 | 3633 | 2062 | 876 | 38 | 40 | 656.42 | 212 | 4988.2 | 0 | 714 | 2352.36 | 0 | 0 | 0 | 457
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 07:00 | 367 | 11:00 | Payra | 404 | 06:00 | 401 | 00:00
Ashuganj | 396 | 5:00 | 372 | 12:00 | Rahanpur | 410 | 16:00 | 403 | 02:00
Bhulta | 393 | 07:00 | 369 | 12:00 | Rampal | 396 | 17:00 | 390 | 22:00
Bibiana | 385 | 07:00 | 378 | 11:00
BIPTC | 401 | 08:00 | 390 | 00:00
Bogura | 400 | 18:30 | 391 | 02:00
Gopalganj | 386 | 07:00 | 382 | 12:00
Kaliakoir | 368 | 07:00 | 357 | 11:00
Madunaghat | 392 | 00:00 | 386 | 23:00
Meghnaghat | 378 | 05:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 216 | 12:00 | Kaliakoir | 230 | 07:00 | 221 | 11:00
AKSML | 234 | 01:00 | 229 | 09:00 | Keranigonj | 222 | 06:00 | 214 | 12:00
Aminbazar | 225 | 06:00 | 216 | 12:00 | Khulna(S) | 227 | 09:00 | 218 | 23:00
Ashuganj | 229 | 06:00 | 219 | 12:00 | Madunaghat | 233 | 00:00 | 132 | 06:00
Ashuganj-400 | 229 | 06:00 | 219 | 12:00 | Madunaghat-400 | 234 | 00:00 | 231 | 22:00
Baghabari | 231 | 17:00 | 227 | 11:00 | Maniknagar | 218 | 04:00 | 212 | 11:00
Barapukuria | 225 | 11:00 | 215 | 02:00 | Meghnaghat | 226 | 02:00 | 220 | 11:00
Barapukuria-230 | 225 | 11:00 | 215 | 02:00 | Meghnaghat-400 | 222 | 05:00 | 217 | 11:00
Barishal | 230 | 00:00 | 227 | 11:00 | Mirsorai | 234 | 19:00 | 226 | 22:00
Bheramara | 231 | 17:00 | 225 | 01:00 | Rajshahi | 230 | 17:00 | 223 | 00:00
Bhulta | 225 | 06:00 | 210 | 12:00 | Rampal | 226 | 08:00 | 220 | 01:00
Bibiana | 226 | 07:00 | 222 | 11:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 233 | 16:00 | 225 | 02:00 | Rampura | 224 | 06:00 | 206 | 12:00
Bogura | 237 | 13:00 | 231 | 02:00 | Shikalbaha | 234 | 18:00 | 230 | 19:30
Bogura-400 | 238 | 18:30 | 231 | 02:00 | Shyampur | 221 | 06:00 | 214 | 11:00
Borhanuddin | 234 | 00:00 | 232 | 05:00 | Siddhirganj | 220 | 05:00 | 214 | 11:00
BSRM | 232 | 18:30 | 226 | 22:00 | Sirajgonj | 237 | 16:00 | 235 | 01:00
Cumilla(N) | 222 | 02:00 | 218 | 11:00 | Sreepur | 224 | 06:00 | 218 | 12:00
Faridpur | 226 | 08:00 | 223 | 12:00 | Tongi | 227 | 04:00 | 213 | 11:00
Fenchuganj | 227 | 06:00 | 223 | 01:00
Ghorashal | 230 | 07:00 | 220 | 09:00
Ghorashal-230 | 225 | 06:00 | 212 | 12:00
Gopalganj | 228 | 08:00 | 225 | 11:00
GPH | 232 | 00:00 | 228 | 22:00
Haripur | 219 | 04:00 | 214 | 11:00
Hasnabad | 222 | 05:00 | 214 | 11:00
Hathazari | 232 | 18:30 | 226 | 16:00
Ishurdi | 234 | 02:00 | 226 | 01:00
Jhenaidah | 227 | 17:00 | 221 | 01:00
Kachua | 226 | 18:00 | 216 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 121 | 12:00 | Lalmonirhat | 130 | 10:00 | 117 | 01:00
Agargaon | 135 | 06:00 | 128 | 12:00 | Madanganj | 127 | 04:00 | 124 | 11:00
Agrabad | 133 | 07:00 | 130 | 10:00 | Madaripur | 134 | 18:30 | 132 | 00:00
AKS | 131 | 03:00 | 124 | 12:00 | Madartek | 134 | 06:00 | 122 | 12:00
Aminbazar | 132 | 00:00 | 126 | 12:00 | Madunaghat | 135 | 00:00 | 133 | 15:00
Amnura | 138 | 16:00 | 129 | 05:00 | Magura | 131 | 06:00 | 127 | 00:00
Ashuganj | 138 | 07:00 | 134 | 12:00 | Mahasthangarh | 133 | 18:00 | 125 | 02:00
Bagerhat | 129 | 09:00 | 119 | 23:00 | Maijdee | 129 | 18:00 | 121 | 02:00
Bajitpur | 126 | 10:00 | 122 | 12:00 | Manikganj | 126 | 06:00 | 116 | 16:00
Bakulia | 135 | 00:00 | 132 | 12:00 | Maniknagar | 132 | 04:00 | 126 | 12:00
Banani | 135 | 06:00 | 122 | 12:00 | Matarbari | 124 | 11:00 | 106 | 19:30
Bangabhaban | 132 | 05:00 | 126 | 12:00 | Matuail | 127 | 01:00 | 124 | 11:00
Barapukuria | 137 | 11:00 | 125 | 02:00 | Millgate | 130 | 05:00 | 121 | 12:00
Barguna | 136 | 10:00 | 132 | 01:00 | Mirpur | 132 | 00:00 | 125 | 11:00
Barishal | 135 | 00:00 | 130 | 05:00 | Mirzapur | 127 | 00:00 | 117 | 16:00
Barishal-230 | 133 | 00:00 | 129 | 13:00 | Mithapukur | 133 | 13:00 | 120 | 02:00
Baroaulia | 134 | 17:00 | 132 | 00:00 | MI_Cement | 128.5 | 06:00 | 125 | 11:00
Baroirhat | 129 | 18:00 | 124 | 04:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 05:00 | 121 | 11:00 | Mogbazar | 135 | 05:00 | 122 | 12:00
BashundharaCement | 127 | 04:00 | 124 | 11:00 | Mongla | 130 | 09:00 | 120 | 23:00
Beanibazar | 127 | 07:00 | 121 | 19:30 | Motijheel | 132 | 05:00 | 126 | 12:00
Benapole | 128 | 17:00 | 119 | 23:00 | Muktagacha | 125 | 07:00 | 116 | 21:00
Bhaluka | 126 | 19:00 | 118 | 15:00 | Munshiganj | 127 | 03:00 | 124 | 11:00
Bhandaria | 130 | 09:00 | 122 | 04:00 | Muradnagar | 125 | 13:00 | 120 | 19:30
Bhangura | 131 | 18:00 | 127 | 12:00 | Mymensingh | 124 | 07:00 | 111 | 20:00
Bheramara | 135 | 16:00 | 132 | 01:00 | Naogaon | 129 | 16:00 | 123 | 02:00
Bheramara(GK) | 135 | 07:00 | 132 | 01:00 | Narail | 133 | 19:00 | 126 | 23:00
Bhulta | 127 | 17:00 | 122 | 11:00 | Narinda | 132 | 04:00 | 126 | 12:00
Bog-Sherpur | 133 | 14:00 | 129 | 02:00 | Narshingdi | 130 | 08:00 | 117 | 11:00
Bogura | 135 | 16:00 | 131 | 06:00 | Natore | 133 | 16:00 | 129 | 00:00
Bogura-230 | 135 | 13:00 | 130 | 06:00 | Nawabganj | 134 | 05:00 | 128 | 12:00
Brahmanbaria | 132 | 06:00 | 126 | 00:00 | Netrakona | 118 | 04:00 | 109 | 11:00
Cantonment | 135 | 06:00 | 128 | 11:00 | New | 131 | 07:00 | 123 | 11:00
Chandina | 128 | 06:00 | 125 | 19:30 | Niamatpur | 140 | 16:00 | 136 | 23:00
Chandpur | 136 | 18:00 | 129 | 09:00 | Noapara | 131 | 09:00 | 123 | 23:00
Chandraghona | 135 | 00:00 | 133 | 19:30 | Pabna | 133 | 11:00 | 130 | 23:00
Chapai | 138 | 15:00 | 135 | 02:00 | Palashbari | 129 | 12:00 | 119 | 02:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 03:00 | 125 | 11:00 | Panchagarh | 134 | 13:00 | 122 | 02:00
Chauddagram | 128 | 18:00 | 123 | 19:30 | Patiya | 134 | 18:00 | 129 | 19:30
Chhatak | 125 | 03:00 | 119 | 19:00 | Patuakhali | 136 | 07:00 | 132 | 22:00
Chowmuhani | 130 | 18:00 | 122 | 21:00 | Payra | 136 | 03:00 | 134 | 21:00
Chuadanga | 130 | 19:00 | 124 | 00:00 | PHP | 128 | 13:00 | 124 | 04:00
Coxsbazar | 122 | 06:00 | 109 | 19:00 | Postogola | 131 | 03:00 | 127 | 11:00
Cumilla(N) | 128 | 00:00 | 125 | 19:30 | Purbachal | 134 | 04:00 | 121 | 12:00
Cumilla(S) | 133 | 05:00 | 125 | 19:30 | Purbasadipur | 131 | 11:00 | 122 | 02:00
Daganbhuiyan | 126 | 08:00 | 121 | 04:00 | Rahanpur | 140 | 11:00 | 138 | 00:00
Daudkandi | 124 | 14:00 | 116 | 19:30 | Rahanpur-400 | 141 | 11:00 | 138 | 01:00
DhakaUniversity | 134 | 06:00 | 123 | 12:00 | Rahim | 129 | 04:00 | 124 | 11:00
Dhamrai | 130 | 03:00 | 124 | 12:00 | Rajbari | 132 | 08:00 | 130 | 00:00
Dhanmondi | 134.5 | 07:00 | 125 | 11:00 | Rajendrapur | 132 | 00:00 | 120 | 14:00
Dohazari | 130 | 18:00 | 122 | 19:30 | Rajshahi | 133 | 03:00 | 128 | 12:00
Faridpur | 135 | 07:00 | 129 | 09:00 | Rajshahi-230 | 132 | 17:00 | 128 | 12:00
Fatullah | 134 | 05:00 | 129 | 11:00 | Ramganj | 132 | 18:00 | 123 | 00:00
Fenchuganj | 134 | 06:00 | 131 | 01:00 | Rampur | 133 | 00:00 | 129 | 15:00
Feni | 128 | 18:00 | 120 | 07:00 | Rampura | 134 | 05:00 | 122 | 12:00
Ghatail | 124 | 00:00 | 114 | 19:30 | Rangamati | 134 | 00:00 | 132 | 10:00
Ghorashal | 134 | 00:00 | 126 | 12:00 | Rangpur | 133 | 18:00 | 122 | 02:00
Goalpara | 134 | 09:00 | 126 | 23:00 | Ruppur | 135 | 06:00 | 133 | 00:00
Gollamari | 134 | 09:00 | 128 | 23:00 | Saidpur | 133 | 13:00 | 123 | 01:00
Gopalganj | 133 | 08:00 | 130 | 13:00 | Satkhira | 131 | 10:00 | 120 | 23:00
Gopalganj-400 | 136 | 08:00 | 134 | 00:00 | Satmasjid | 135 | 04:00 | 128 | 12:00
Gulshan | 134 | 06:00 | 122 | 12:00 | Savar | 132 | 00:00 | 125 | 11:00
Halishahar | 135 | 09:00 | 131 | 13:00 | SevenRings | 135 | 22:00 | 127 | 12:00
Haripur | 128 | 05:00 | 125 | 11:00 | ShahCement | 128 | 03:00 | 125 | 11:00
HaripurSBU | 127 | 01:00 | 125 | 11:00 | Shahjadpur | 135 | 15:00 | 133 | 00:00
Hasnabad | 131 | 03:00 | 126 | 11:00 | Shahjibazar | 132 | 07:00 | 126 | 00:00
Hathazari | 135 | 00:00 | 131 | 22:00 | Shahmirpur | 134 | 00:00 | 132 | 15:00
Ishurdi | 136 | 11:00 | 133 | 01:00 | Shariatpur | 133 | 08:00 | 130 | 13:00
Jaldhaka | 131 | 12:00 | 120 | 08:00 | Sherpur | 119 | 07:00 | 108 | 22:00
Jamalpur | 123 | 08:00 | 112 | 22:00 | Shikalbaha | 125 | 18:00 | 120 | 19:30
Jashore | 132 | 18:30 | 125 | 23:00 | Shikalbaha-230 | 136 | 18:00 | 132 | 19:30
Jhenaidah | 135 | 19:00 | 123 | 02:00 | Shitalakhya | 128.1 | 06:00 | 125 | 11:00
Jhenaidah-230 | 135 | 19:00 | 128 | 23:00 | Sholosohor | 135 | 00:00 | 133 | 12:00
Joydebpur | 135 | 00:00 | 122 | 16:00 | Shyampur | 135 | 07:00 | 129 | 11:00
Joypurhat | 126 | 16:00 | 120 | 01:00 | Shyampur-230 | 134 | 05:00 | 129 | 11:00
Juldah | 134 | 00:00 | 131 | 15:00 | Siddhirganj | 127 | 01:00 | 125 | 11:00
Kabirpur | 133 | 07:00 | 120 | 11:00 | Sirajganj | 130 | 11:00 | 127 | 00:00
Kachua | 134 | 18:00 | 127 | 03:00 | Sonargaon | 126 | 06:00 | 123 | 11:00
Kaliakoir | 133 | 00:00 | 127 | 11:00 | Sreemongol | 131 | 07:00 | 126 | 00:00
Kallyanpur | 132 | 01:00 | 126 | 11:00 | Sreepur | 129 | 06:00 | 124 | 12:00
Kalurghat | 135 | 00:00 | 133 | 19:30 | Srinagar | 134 | 03:00 | 129 | 11:00
Kamrangirchar | 135 | 06:00 | 128 | 11:00 | SSM | 134 | 00:00 | 132 | 01:00
Kaptai | 137 | 18:00 | 135 | 12:00 | Sunamganj | 122 | 06:00 | 117 | 02:00
Kasba | 125 | 07:00 | 120 | 19:30 | Sylhet | 128 | 07:00 | 123 | 20:00
Kazla | 132 | 05:00 | 126 | 12:00 | Sylhet-132 | 128 | 07:00 | 125 | 19:00
Keranigonj | 135 | 06:00 | 129 | 11:00 | Tangail | 125 | 08:00 | 117 | 14:00
Khagrachori | 133 | 00:00 | 131 | 19:00 | Taraganj | 131 | 13:00 | 123 | 01:00
Khulna | 133 | 09:00 | 125 | 23:00 | Thakurgaon | 134 | 13:00 | 122 | 02:00
Khulna(S) | 134 | 08:00 | 128 | 23:00 | TK | 135 | 18:00 | 133 | 14:00
Khulshi | 132 | 23:00 | 128 | 15:00 | Tongi | 133 | 04:00 | 124 | 15:00
Kishoreganj | 126 | 07:00 | 120 | 12:00 | Ullahpara | 132 | 14:00 | 130 | 00:00
Kodda | 132 | 18:30 | 116 | 11:00 | Ullon | 134 | 05:00 | 121 | 12:00
KSRM | 135 | 08:00 | 130 | 14:00 | Uttara | 131 | 01:00 | 124 | 11:00
Kulaura | 133 | 07:00 | 129 | 02:00 | UttaraNew | 131 | 01:00 | 125 | 12:00
Kurigram | 130 | 13:00 | 116 | 02:00 | Zigatola | 134 | 05:00 | 129 | 11:00
Kushtia | 132 | 19:00 | 128 | 00:00
Laksam | 132 | 18:00 | 124 | 05:00
Lakshmipur | 129 | 18:00 | 121 | 02:00
Lalbag | 133 | 03:00 | 128 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division