## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-03-24 | Sunday
|  | Date (day): | 2024-03-24 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11732.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13210 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-03-23 | 2024-03-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 130 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 100 | 100 | 100 | 90 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 64 | 0 | 30 | 50 | 58 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 369 | 358 | 320 | 360 | 40 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 149 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 0 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 15 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 333 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 57 | 8 | 57 | 45 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 32 | 32 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 32 | 39 | 39 |  | 41 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 95 | 45 | 195 | 105 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 50 | 17 | 51 | 98 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 50 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 52 | 54 | 54 | 50 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 0 | 54 | 108 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 17 | 38 |  | Fuel shortage
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 1700 | 2103 | 1900 | 2519 | 1421 | 801
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 20 | 30 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 196 | 214 | 216
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 43 | 67 | 32 | 66 | 32 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 68 |  | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 6 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 12 | 4 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 8 | 26 | 0 | 25 | 83 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 49 | 16 | 16 | 284 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 25 | 12 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 53 | 54 | 127 | 36 |  | Fuel shortage
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 0 | 0 | 0 | 0 | 1224 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 3 | 6 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 728 | 554 | 650 | 650
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 75 | 0 | 25 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1316 | 1206 | 1248 | 1409 | 2692 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 218 | 220 | 225 | 225 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under S/D
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 270 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 325 | 375 | 330 | 320 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 39 | 30 | 30 | 15 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 50 | 30 | 40 | 40 | 15 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 8 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 6 | 6 | 8 | 142 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 120 | 34 | 200
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 9 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 138 | 128 | 141
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 25 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 19 | 19 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 17 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 12 | 26 | 38 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 70 | 0 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1325 | 1509 | 1349 | 1775 | 765 | 228
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 158 | 80 | 120 | 82 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 19 | 0 | 18 | 182 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 45 | 47 | 95 | 20 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 191 | 228 | 178.6 | 239 | 82 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 40 | 65 | 65
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 209 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 16 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 363 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 340 | 383 | 383 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1577 | 1497 | 1607 | 1608 | 109 | 471
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 930 | 787 | 948 | 948
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 8 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 31 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 360 | 378 | 370 | 370 | 247 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1383 | 1204 | 1435 | 1455 | 1432 | 39
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 8 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 590 | 1020 | 1200 | 1200
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 54 | 96 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 230 | 150 | 150 | 157 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1029 | 1576 | 1752 | 1806 | 253 | 162
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 0 | 60 | 60 | 11 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 25 | 40 | 12 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 12 | 0 | 24 |  | 47 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 154 | 214 | 160 | 170 | 40 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 348 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 16 | 38 | 12 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 8 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 0 | 35 | 78 |  | Fuel shortage
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 0 | 35 | 78 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 879 | 931 | 1000 | 1000
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1517 | 1723 | 1854 | 2042 | 815 | 72
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 200 | 200 | 200 |  | 74 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 6 | 42 | 71 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 168 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 361 | 235 | 409 | 357 | 196 | 159
| Total |  |  |  |  | 26844 | 25809 | 10399 | 11281 | 11732.6 | 13210 | 7765 | 2262
A. |  | 2024-03-23 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11281 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7730 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11281 | MW
3 | Day peak Generation : |  |  | 10399 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10801.34 | MW
4 | Evening peak Generation : |  |  | 11281 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 239.0085 | MKWHr | By Solar | 2.9751 | MKWHr
| By Gas : | 122.2235 | MKWHr |  | By Oil: | 13.9036 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 74.6698 | MKWHr |  | By Hydro: | 0.5265 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.06432 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7765 | MW | Dhaka | 4215.04 | 4215.04 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2262 | MW | Chittagong | 1175 | 1175 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10027 | MW | Khulna | 1440.6 | 1440.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 905.98 | MMCFD |  |  | Rajshahi | 1129.2 | 1129.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 374558069.97 | ii) Oil : | Taka | 249242559.29 | Comilla | 1071 | 1071 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 498240658.6 | Total | Taka | 1122041287.86 | Mymensingh | 510.5 | 510.5 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 375 | 375 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 770 | MW (W to E) at | 19:30 | hrs | Barisal | 336 | 336 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 700 | MW at | 21:00 | hrs | Rangpur | 549 | 549 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.9°C |  |  | Total | 10801.34 | 10801.34 |  | 0
B. |  | 2024-03-24 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.9°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13210 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
4 | Reserve(Generation end) |  |  |  | 1010 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 258.4792 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7652 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7571 | MKWHr. | ii) HVDC Flow at Peak Time |  | 787 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8886 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.85 |  | (b) Today: | 80.73 |  | (c) Rule Curve: |  | 89.32
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## Generation
2024-03-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 0 |  |  |  | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 526500
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 5 | 8 | 8 | 8 | 8 | 13 |  | 25 | 25 | 25 | 25 | 0 |  | 0 | 148897
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 8 | 16 | 19 | 17 | 15 | 20 | 18 | 14 | 9 | 3 | [9 empty] | 132570
6 | Sikalbaha 225MW CCPP (Gas) | 215 | 215 | 214 | 215 | 191 | 186 | 186 | 214 | 213 | 214 | 215 | 212 | 213 | 211 | 212 | 214 | 204 | 197 |  | 186 | 196 | 197 | 196 | 197 | 212 | 214 | 4815054
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 0 | [7 empty] | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 531964
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | 0 | [6 empty] | 43 | 50 | 50 | 49 | 65 |  | 8 |  | 67 | 67 | 67 | 67 | 59 | 59 | 59 | 840672
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 17 | 17 | 17 | 18 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 235018
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [14 empty] | 10 | 27 | 29 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 308352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 250 | 250 | 280 | 280 | 230 | 230 | 280 | 280 | 280 | 280 | 330 | 328 | 325 | 326 | 328 | 330 | 333 |  | 333 | 333 | 335 | 335 | 335 | 335 | 335 | 7284730
18 | Kodda 300 MW PP Unit-2 (Summit) | [14 empty] | 25 | 47 | 47 | 57 |  | 122 | 95 | 95 | 45 | 45 | 15 | 15 | 577091
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 0 | [5 empty] | 8 | 83 | 120 | 55 | 55 | 55 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 468363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 130 | 130 | 130 | 140 | 140 | 140 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3249062
23 | Ghorasal TPP Unit-5 | [12 empty] | 10 | 25 | 25 | 40 | 65 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 819000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 31 | 32 | 31 | 31 | 5 | 5 | 5 | 5 | 31 | 31 | 34 | 36 | 36 | 35 | 35 | 35 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 38 | 40 | 721944
33 | Ashuganj 225 MW CCPP | 188 | 188 | 207 | 188 | 188 | 144 | 144 | 188 | 222 | 220 | 218 | 218 | 206 | 210 | 212 | 211 | 215 | 219 |  | 220 | 220 | 220 | 223 | 225 | 206 | 188 | 4941000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 300 | 270 | 275 | 240 | 285 | 305 | 345 | 335 | 335 | 305 | 325 | 300 | 290 | 290 | 265 | 270 |  | 270 | 270 | 270 | 270 | 270 | 310 | 270 | 7051000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 285 | 285 | 305 | 335 | 335 | 250 | 250 | 350 | 375 | 355 | 370 | 325 | 345 | 265 | 288 | 245 | 325 | 325 |  | 393 | 375 | 375 | 340 | 350 | 335 | 285 | 7630900
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 18 | 5 | 5 | 5 | 5 | 20 | 44 | 50 | 50 | 40 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 |  | 0 | 622080
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 330 | 303 | 312 | 320 | 292 | 243 | 225 | 224 | 277 | 312 | 368 | 369 | 370 | 370 | 365 | 362 | 362 | 360 |  | 359 | 358 | 357 | 352 | 342 | 341 | 347 | 7876800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 330 | 300 | 340 | 400 | 360 | 330 | 360 | 400 | 400 | 400 | 400 | 450 | 450 | 450 | 420 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 9539500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 153 | 153 | 156 | 157 | 157 | 120 | 157 | 147 | 120 | 111 | 111 | 105 | 101 | 98 | 94 | 93 | 93 | 114 |  | 115 | 158 | 159 | 154 | 150 | 144 | 142 | 3018240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 18 | 31 | 40 | 49 | 37 | 27 | 41 | 32 | 18 | 7 | 1 | [8 empty] | 315880
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 925800
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 14 | 14 | 14 | 40 | 60 | 59 | 59 | 58 | 59 | 58 | 57 | 57 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 64 | 1159488
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP | [15 empty] | 45 | 50 | 50 |  | 50 | [6 empty] | 170200
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 210 | 209 | 209 | 209 | 210 | 209 | 211 | 208 | 208 | 206 | 203 | 203 | 203 | 203 | 203 | 209 |  | 209 | 209 | 208 | 212 | 212 | 212 | 212 | 5229600
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 |  | 18 | 18 | 18 | 18 | 18 | 22 | 20 | 410000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 |  | 16 | 24 |  |  |  |  | 16 | 478968
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 290 | 295 | 300 | 285 | 305 | 280 | 300 | 310 | 310 | 315 | 310 | 305 | 290 | 310 | 305 | 295 |  | 275 | 300 | 270 | 280 | 280 | 285 | 300 | 7261000
| Bibiyana South 400 MW | 310 | 310 | 340 | 340 | 330 | 320 | 320 | 320 | 360 | 365 | 375 | 390 | 350 | 350 | 360 | 350 | 340 | 340 |  | 340 | 340 | 300 | 300 | 300 | 327 | 300 | 8001400
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 74804
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 44400
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 227184
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 112 | 110 | 112 | 114 | 108 | 94 | 88 | 106 | 100 | 122 | 122 | 130 | 128 | 142 | 146 | 134 | 128 | 142 |  | 138 | 138 | 126 | 130 | 128 | 126 | 102 | 2888640
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 9 | 4 | 12 | 10 | 10 | 7 | 10 | 10 | 2 | 7 | 14 | 25 |  | 29 | 12 | 23 | 35 | 35 | 38 | 37 | 598080
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183240
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 766200
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 11 | 11 | 15 | 15 | 15 | 15 | 18 | 15 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 404740
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 14 | 14 | 14 | 15 |  | 15 | 15 | 15 | 15 | 15 | 0 | 7 | 306720
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 0 | 0 | 33 | 633600
72 | Rupganj 33 MW PP(Summit) | 16 | 25 | 25 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 32 | 32 | 32 | 32 | 4 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 688400
73 | Ghorashal 108 MW PP (Regent) | 67 | 22 | 22 | 22 | 0 |  |  |  | 5 | 55 | 61 | 64 | 12 | 0 | [11 empty] | 0 | 377409
| Feni Lanka Power | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 34 | 34 | 17 | 17 | 17 | 17 | 25 | 258780
| Chowmuhani 113 MW | [11 empty] | 12 | 32 | 37 | 39 | 32 | 48 | 58 |  | 58 | 26 | 26 | 26 | 26 | 26 | 12 | 499800
| Manikgonj 162MW PP(MPGL) | [15 empty] | 17 | 17 | 45 |  | 54 | 54 | 54 | 17 | 0 |  | 0 | 211680
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 7 | 25 | 24 |  | 24 | [5 empty] | 0 | 74390
78 | Gazipur 52 MW PP | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 8 | 17 | 0 |  | 0 | 156480
79 | Kodda 150 MW PP |  |  | 0 | 16 | 0 |  |  | 16 | 16 | 22 | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 16 | 16 | 0 |  | 0 | 389280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [11 empty] | 8 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 32 | 25 | 25 | 25 | 328877
| Gazipur 100 MW PP | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 |  | 50 | 50 | 35 | 17 | 0 |  | 0 | 303360
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 3 | 4 | 3 | 2 | 1 | [9 empty] | 31203
| Jodiac Power | [15 empty] | 7 | 17 | 17 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 114924
| Karnaphuli Power Ltd. | [10 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 239199
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 7 | 13 |  |  |  |  | 0 | 10021
86 | Meghnaghat CCPP ( Summit) | 137 | 140 | 150 | 150 | 130 | 130 | 150 | 150 | 150 | 150 | 150 | 151 | 152 | 152 | 152 | 152 | 151 | 151 |  | 150 | 149 | 150 | 147 | 147 | 147 | 149 | 3519418
87 | Meghnaghat 100 MW(IEL) | [15 empty] | 6 | 17 | 20 | [8 empty] | 39400
| Meghnaghat 104 MW PP (OPCL) | [14 empty] | 14 | 24 | 34 | 42 |  | 48 | 52 | 52 | 50 | 50 | 53 | 53 | 421440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 6 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 12 | 0 |  | 25 | 193080
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 38 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 25 | 51 | 51 | 51 | 51 | 51 | 51 | 1024670
94 | Gagnagar 102 MW PP (Digital Power) | [14 empty] | 28 | 45 | 58 | 57 |  | 57 | 57 | 48 | 8 | 8 | 16 | 24 | 331488
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 0 | [10 empty] | 1 | 8 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 154080
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 8 | 12 | 13 | 12 | 13 | 14 | 22 |  | 26 | 26 | 26 | 26 | 13 |  | 0 | 190080
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [14 empty] | 2 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 144566
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 86126
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 120 | 120 | 120 | 120 | 163 | 3458781
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13850
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 17 | 35 | 35 | 0 |  | 0 | 90720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 |  | 19 | 19 | 19 | 19 | 19 | 8 | 8 | 103200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 22 | 0 |  |  |  | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 50 |  | 50 | 50 | 50 | 41 | 27 | 17 | 17 | 514800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 0 | [5 empty] | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 216960
116 | Chandpur 200 MW (Desh energy) | 68 | 68 | 68 | 68 | 17 | 0 |  |  |  |  | 21 | 34 | 34 | 34 | 34 | 34 | 85 | 152 |  | 155 | 120 | 120 | 100 | 68 | 68 | 71 | 1401120
117 | Ashuganj 150 MW PP (Midland) | [13 empty] | 1 | 6 | 12 | 13 | 8 |  | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 76945
118 | Bibiyana-III 400 MW CCPP | 318 | 318 | 345 | 365 | 327 | 247 | 247 | 305 | 395 | 398 | 400 | 365 | 367 | 402 | 383 | 387 | 368 | 367 |  | 363 | 363 | 365 | 363 | 364 | 387 | 361 | 8456000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 0 |  |  | 37 | 47 | 47 | 47 | 47 | 49 | 49 | 49 | 49 | 49 | 45 |  | 45 | 45 | 24 | 24 | 24 | 8 | 9 | 769200
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 0 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 49 |  | 49 | 49 | 49 | 16 | 16 | 16 | 16 | 371345
| Juldah unit-2 (Acorn) | 22 | 22 | 22 | 22 | 22 | 12 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 12 | 12 | 12 | 12 | 12 |  | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 1028160
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 0 | [5 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 321164
| Bhairob 54.5 MW | [23 empty] | 9 |  | 0 | 12600
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 12 | 20 | 27 | 31 | 33 | 32 | 28 | 22 | 13 | 5 | [9 empty] | 224085
| Chandpur 115(Doreen) | [15 empty] | 10 | 40 | 70 |  | 70 | 70 | 53 | 40 | 34 | 34 | 0 | 409920
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 27 | 17 |  | 17 | [5 empty] | 0 | 68760
| Mirsharai 150 MW (Oil) | [12 empty] | 62 | 71 | 71 | 35 | 35 | 35 |  | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 449963
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 2 | 7 | 11 | 7 | 5 | 5 |  | 7 | 6 | 6 | 2 | 5 | 2 | 0 | 64320
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 8 | 29 | 50 | 67 | 66 | 75 | 70 | 64 | 50 | 33 | 12 | 1 | [8 empty] | 524818
| Matarbari 2*600 MW (CPGCL) | 525 | 528 | 526 | 531 | 528 | 525 | 529 | 676 | 703 | 736 | 727 | 728 | 727 | 727 | 728 | 727 | 728 | 680 |  | 525 | 554 | 577 | 576 | 575 | 577 | 550 | 14989090
120 | Eastern Zone Total | 5026 | 4908 | 5095 | 5278 | 4645 | 4120 | 4311 | 4936 | 5397 | 5610 | 5828 | 6109 | 6232 | 6015 | 6034 | 6139 | 6205 | 6547 |  | 6615 | 6543 | 6297 | 6056 | 5779 | 5633 | 5502 | 135180633
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 8 | 8 | [5 empty] | 10560
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 11 | 36 | 61 | 78 | 90 | 93 | 92 | 85 | 68 | 44 | 17 | [9 empty] | 677520
131 | Rampal 1320 MW (BIFPCL) | 381 | 381 | 380 | 378 | 363 | 362 | 360 | 361 | 360 | 359 | 360 | 360 | 379 | 383 | 377 | 378 | 379 | 379 |  | 380 | 378 | 376 | 377 | 379 | 375 | 375 | 9236364
132 | United Payra Power Ltd. | [17 empty] | 2 |  | 17 | 17 | 17 |  |  |  | 0 | 45600
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 200 | 182 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4989327
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [20 empty] | 16 | 16 | 16 | 0 |  | 0 | 39168
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 150 | 150 | 150 | 150 |  | 174 | 230 | 250 | 250 | 150 | 150 | 150 | 3883600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 40 | 65 | 133000
140 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 7 | 6 | 6 | 5 | 4 | 4 | 3 | 3 | 4 | 4 | 5 | 5 | 5 | 6 | 8 |  | 8 | 8 | 8 | 8 | 4 | 9 | 9 | 131734
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [12 empty] | 4 | 5 | 5 | 6 | 10 | 18 |  | 31 | 31 | 5 |  |  |  |  | 81536
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 928 | 927 | 927 | 928 | 926 | 927 | 927 | 787 | 787 | 787 | 929 | 930 | 929 | 929 | 929 | 929 | 930 | 929 |  | 929 | 787 | 787 | 787 | 929 | 930 | 930 | 21757090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 800 | 660 | 640 | 720 | 540 | 500 | 500 | 540 | 580 | 580 | 590 | 590 | 620 | 860 | 1080 | 1000 | 990 | 990 |  | 880 | 1020 | 1040 | 1080 | 1080 | 1000 | 1040 | 20868100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4586400
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 50 | 45 | 35 | [9 empty] | 0 | 920000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 43 | 12 |  |  |  |  | 76001
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 185 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 154 | 210 | 214 | 214 | 213 | 214 | 214 |  | 190 | 214 | 214 | 214 | 214 | 205 | 190 | 4565255
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 305 | 288 | 346 | 392 | 350 | 250 | 320 | 334 | 390 | 386 | 387 | 414 | 414 | 414 | 414 | 414 | 414 | 414 |  | 320 | 348 | 308 | 347 | 316 | 347 | 408 | 8651345
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 5 | 12 | 16 |  |  |  |  | 18306
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 106290
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [17 empty] | 12 |  | 28 | 42 | 50 |  |  |  |  | 71645
168 | Santahar 50 MW Peaking PP | [17 empty] | 18 |  | 38 | 38 | 38 | 38 | 0 |  |  | 126737
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 5 | 8 | 8 | 8 | 0 |  | 0 | 22349
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 50 |  | 82 | 82 | 82 | 74 | 74 | 74 | 74 | 482496
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [26 empty] | 0
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [26 empty] | 0
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | [8 empty] | 9907
178 | Energypac Power Venture Thakurgaon Ltd. | [13 empty] | 35 |  |  |  | 17 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 186048
| Intraco Solar 30 MW | [6 empty] | 3 | 4 | 18 | 13 | 12 | 22 | 4 | 6 | 8 | 5 | 6 | 0 | [8 empty] | 97402
| Adani Power Jharkhanda Ltd | 823 | 817 | 827 | 825 | 830 | 823 | 821 | 823 | 827 | 828 | 820 | 879 | 991 | 1010 | 952 | 917 | 908 | 816 |  | 882 | 931 | 1012 | 1011 | 925 | 823 | 827 | 21106240
178 | Teesta Solar Limited | [6 empty] | 21 | 65 | 107 | 154 | 107 | 168 | 105 | 98 | 42 | 0 | 12 | 1 | [8 empty] | 912960

## YesterdayGen
2024-03-23 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 140 | 0 | 0 | 67 | 0 | 330 | 0 |  | 0 | 330 | 137 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 48 | 34 | 0 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 0 | 275 | 188 | 8 | 0 | 31 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 112 | 153 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 64 | 0 | 0 | 209 | 18 | 0 | 0 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 68 | 0 | 318 | 19 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 1 | 525 | 0 | 0 | 0 |  | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 150 | 823 | 0 | 0 |  | 5026 | 4041 | 9067 | 3296 | 928 | 1562 | 0 | 177 | 2879 | 30 | 0 | 82 | 112 | 0 | 1 | 0 | 80.87
2:00 | 0 | 0 | 140 | 0 | 0 | 22 | 0 | 303 | 0 |  | 0 | 300 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 48 | 34 | 0 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 0 | 275 | 188 | 8 | 0 | 32 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 110 | 153 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 64 | 0 | 0 | 209 | 18 | 0 | 0 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 68 | 0 | 318 | 19 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 1 | 528 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 150 | 817 | 0 | 0 |  | 4908 | 3876 | 8784 | 3249 | 927 | 1472 | 0 | 177 | 2736 | 30 | 0 | 82 | 110 | 0 | 1 | 0 | 80.87
3:00 | 0 | 0 | 140 | 0 | 0 | 22 | 0 | 312 | 0 |  | 0 | 340 | 150 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 48 | 34 | 0 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 0 | 300 | 207 | 8 | 0 | 31 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 112 | 156 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 64 | 0 | 0 | 210 | 18 | 0 | 0 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 68 | 0 | 345 | 19 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 1 | 526 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 150 | 827 | 0 | 0 |  | 5095 | 3923 | 9018 | 3381 | 927 | 1585 | 0 | 177 | 2723 | 30 | 0 | 82 | 112 | 0 | 1 | 0 | 80.86
4:00 | 0 | 0 | 140 | 0 | 0 | 22 | 0 | 320 | 0 |  | 0 | 400 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 48 | 34 | 0 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 188 | 8 | 0 | 31 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 114 | 157 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 209 | 18 | 0 | 0 | 295 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 12 | 68 | 0 | 365 | 19 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 1 | 531 | 0 | 0 | 0 |  | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 150 | 825 | 0 | 0 |  | 5278 | 4112 | 9390 | 3473 | 928 | 1760 | 0 | 182 | 2804 | 30 | 0 | 98 | 114 | 0 | 1 | 0 | 80.86
5:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 292 | 0 |  | 0 | 360 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 275 | 188 | 0 | 0 | 5 | 18 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 108 | 157 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 14 | 0 | 0 | 209 | 18 | 0 | 0 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 528 | 0 | 0 | 0 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 150 | 830 | 0 | 0 |  | 4645 | 3759 | 8404 | 3232 | 926 | 1518 | 0 | 39 | 2581 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 80.85
6:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 243 | 0 |  | 0 | 330 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 42 | 0 | 0 | 0 | 0 | 240 | 144 | 0 | 0 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 8 | 17 | 94 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 14 | 0 | 0 | 209 | 18 | 0 | 0 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 525 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 150 | 823 | 0 | 0 |  | 4120 | 3610 | 7730 | 2809 | 927 | 1358 | 0 | 12 | 2530 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 80.85
7:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 225 | 0 |  | 0 | 360 | 150 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 0 | 0 | 0 | 0 | 285 | 144 | 0 | 0 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 8 | 17 | 88 | 157 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 14 | 0 | 0 | 210 | 18 | 0 | 0 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 80 | 320 | 0 | 6 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 250 | 0 | 0 | 0 | 1 | 529 | 0 | 0 | 8 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 360 | 3 | 150 | 821 | 21 | 0 |  | 4311 | 3710 | 8021 | 2874 | 927 | 1464 | 0 | 80 | 2530 | 0 | 0 | 0 | 88 | 57 | 1 | 0 | 80.84
8:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 224 | 0 |  | 0 | 400 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 0 | 0 | 0 | 0 | 305 | 188 | 0 | 0 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 33 | 11 | 106 | 147 | 0 | 0 | 1 | 0 | 40 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 16 | 0 | 0 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 305 | 37 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 320 | 0 | 18 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 350 | 0 | 0 | 0 | 1 | 676 | 0 | 0 | 29 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 1 | 36 | 0 | 0 | 0 | 361 | 4 | 150 | 823 | 65 | 0 |  | 4936 | 3697 | 8633 | 3198 | 787 | 1487 | 0 | 142 | 2720 | 0 | 0 | 16 | 106 | 176 | 1 | 0 | 80.96
9:00 | 0 | 0 | 130 | 0 | 0 | 5 | 0 | 277 | 0 |  | 0 | 400 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 0 | 0 | 0 | 0 | 345 | 222 | 0 | 0 | 31 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 33 | 11 | 100 | 120 | 0 | 0 | 1 | 0 | 40 | 0 | 0 | 120 | 0 | 60 | 0 | 0 | 211 | 16 | 0 | 0 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 395 | 47 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 100 | 360 | 0 | 31 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 703 | 0 | 0 | 50 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 220 | 0 | 0 | 3 | 61 | 0 | 0 | 0 | 360 | 18 | 150 | 827 | 107 | 0 |  | 5397 | 3922 | 9319 | 3503 | 787 | 1616 | 0 | 167 | 2790 | 30 | 0 | 16 | 100 | 310 | 0 | 0 | 80.95
10:00 | 0 | 0 | 130 | 0 | 0 | 55 | 0 | 312 | 0 |  | 0 | 400 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 335 | 220 | 0 | 0 | 31 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 8 | 33 | 11 | 122 | 111 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 120 | 0 | 59 | 0 | 0 | 208 | 16 | 0 | 0 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 0 | 0 | 398 | 47 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 365 | 0 | 40 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 736 | 0 | 0 | 67 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 3 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 220 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 359 | 13 | 150 | 828 | 154 | 0 |  | 5610 | 3977 | 9587 | 3494 | 787 | 1712 | 0 | 189 | 2823 | 30 | 0 | 22 | 122 | 408 | 0 | 0 | 80.95
11:00 | 0 | 0 | 140 | 0 | 0 | 61 | 0 | 368 | 0 |  | 0 | 400 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 335 | 218 | 8 | 0 | 34 | 44 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 122 | 111 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 120 | 0 | 59 | 0 | 0 | 208 | 16 | 0 | 0 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 21 | 0 | 400 | 47 | 17 | 0 | 5 | 16 | 0 | 9 | 0 | 0 | 100 | 375 | 0 | 49 | 0 | 15 | 0 | 0 | 31 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 727 | 0 | 0 | 66 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 3 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 220 | 0 | 0 | 4 | 90 | 0 | 0 | 0 | 360 | 12 | 150 | 820 | 107 | 0 |  | 5828 | 4087 | 9915 | 3593 | 929 | 1764 | 0 | 255 | 2817 | 30 | 0 | 22 | 122 | 383 | 0 | 0 | 80.94
12:00 | 0 | 0 | 140 | 0 | 0 | 64 | 0 | 369 | 0 |  | 0 | 450 | 151 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 43 | 0 | 6 | 8 | 0 | 10 | 7 | 0 | 0 | 0 | 0 | 305 | 218 | 83 | 0 | 36 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 15 | 130 | 105 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 206 | 16 | 0 | 0 | 315 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 12 | 34 | 0 | 365 | 47 | 17 | 17 | 5 | 16 | 0 | 17 | 17 | 12 | 100 | 390 | 0 | 37 | 0 | 17 | 0 | 0 | 33 | 0 | 0 | 325 | 0 | 0 | 0 | 3 | 728 | 0 | 0 | 75 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 590 | 220 | 0 | 0 | 5 | 93 | 0 | 0 | 0 | 360 | 22 | 150 | 879 | 168 | 0 |  | 6109 | 4290 | 10399 | 3578 | 930 | 1972 | 0 | 353 | 2877 | 25 | 0 | 75 | 130 | 456 | 3 | 0 | 80.94
13:00 | 0 | 0 | 140 | 10 | 0 | 12 | 0 | 370 | 0 |  | 0 | 450 | 152 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 24 | 8 | 0 | 25 | 0 | 0 | 0 | 5 | 213 | 0 | 0 | 0 |  | 0 | 50 | 34 | 25 | 12 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 325 | 206 | 120 | 0 | 36 | 50 | 0 | 51 | 0 | 0 | 25 | 0 | 8 | 33 | 15 | 128 | 101 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 163 | 0 | 59 | 0 | 0 | 203 | 16 | 0 | 0 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 12 | 34 | 0 | 367 | 49 | 17 | 17 | 3 | 16 | 0 | 17 | 17 | 32 | 100 | 350 | 0 | 27 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 345 | 62 | 0 | 0 | 2 | 727 | 0 | 0 | 70 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 4 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 620 | 220 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 379 | 4 | 150 | 991 | 105 | 0 |  | 6232 | 4453 | 10685 | 3615 | 929 | 1956 | 0 | 420 | 3067 | 25 | 0 | 182 | 128 | 361 | 2 | 0 | 80.93
14:00 | 0 | 0 | 130 | 25 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 152 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 50 | 34 | 25 | 13 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 300 | 210 | 55 | 0 | 35 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 8 | 33 | 15 | 142 | 98 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 203 | 16 | 0 | 0 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 12 | 34 | 1 | 402 | 49 | 17 | 17 | 4 | 16 | 0 | 17 | 17 | 37 | 12 | 350 | 0 | 41 | 0 | 17 | 0 | 0 | 28 | 0 | 0 | 265 | 71 | 0 | 0 | 7 | 727 | 0 | 0 | 64 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 5 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 860 | 220 | 0 | 0 | 4 | 85 | 35 | 0 | 0 | 383 | 6 | 200 | 1010 | 98 | 0 |  | 6015 | 4789 | 10804 | 3536 | 929 | 1865 | 0 | 377 | 3380 | 25 | 0 | 192 | 142 | 351 | 7 | 0 | 80.94
15:00 | 0 | 0 | 130 | 25 | 0 | 0 | 0 | 365 | 0 |  | 0 | 420 | 152 | 0 | 0 | 2 | 326 | 0 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 49 | 34 | 25 | 12 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 290 | 212 | 55 | 0 | 35 | 30 | 0 | 51 | 0 | 10 | 25 | 0 | 8 | 33 | 18 | 146 | 94 | 0 | 0 | 1 | 0 | 40 | 0 | 0 | 163 | 0 | 57 | 0 | 0 | 203 | 16 | 0 | 0 | 290 | 24 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 17 | 14 | 12 | 34 | 6 | 383 | 49 | 17 | 18 | 3 | 16 | 0 | 17 | 17 | 39 | 12 | 360 | 14 | 32 | 0 | 17 | 0 | 0 | 22 | 0 | 0 | 288 | 71 | 0 | 0 | 11 | 728 | 0 | 0 | 50 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 5 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1080 | 220 | 0 | 0 | 3 | 68 | 0 | 0 | 0 | 377 | 8 | 150 | 952 | 42 | 0 |  | 6034 | 4784 | 10818 | 3554 | 929 | 1802 | 0 | 418 | 3487 | 25 | 0 | 201 | 146 | 245 | 11 | 25 | 80.8
16:00 | 0 | 0 | 130 | 40 | 0 | 0 | 0 | 362 | 0 |  | 0 | 450 | 152 | 6 | 0 | 15 | 328 | 0 | 0 | 7 | 45 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 65 | 34 | 25 | 13 | 1 | 10 | 7 | 0 | 0 | 0 | 0 | 290 | 211 | 55 | 0 | 35 | 30 | 0 | 51 | 0 | 27 | 25 | 0 | 8 | 33 | 15 | 134 | 93 | 0 | 0 | 1 | 0 | 40 | 0 | 0 | 163 | 0 | 57 | 0 | 0 | 203 | 16 | 0 | 0 | 310 | 24 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 17 | 9 | 12 | 34 | 12 | 387 | 49 | 17 | 17 | 2 | 16 | 7 | 17 | 17 | 32 | 12 | 350 | 24 | 18 | 17 | 17 | 45 | 0 | 13 | 10 | 0 | 245 | 35 | 0 | 0 | 7 | 727 | 0 | 0 | 33 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 65 | 5 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 220 | 0 | 0 | 2 | 44 | 0 | 0 | 0 | 378 | 5 | 150 | 917 | 0 | 0 |  | 6139 | 4589 | 10728 | 3550 | 929 | 1857 | 0 | 527 | 3372 | 25 | 0 | 199 | 134 | 128 | 7 | 0 | 80.8
17:00 | 0 | 0 | 130 | 65 | 0 | 0 | 0 | 362 | 0 |  | 0 | 450 | 151 | 17 | 0 | 15 | 330 | 0 | 0 | 25 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 1 | 0 | 34 | 25 | 14 | 8 | 10 | 14 | 0 | 0 | 0 | 0 | 265 | 215 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 29 | 25 | 0 | 8 | 33 | 19 | 128 | 93 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 203 | 14 | 0 | 0 | 305 | 16 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 18 | 3 | 12 | 85 | 13 | 368 | 49 | 17 | 17 | 1 | 16 | 17 | 17 | 17 | 48 | 12 | 340 | 34 | 7 | 17 | 17 | 50 | 0 | 5 | 40 | 27 | 325 | 35 | 0 | 0 | 5 | 728 | 0 | 0 | 12 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 220 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 379 | 6 | 150 | 908 | 12 | 0 |  | 6205 | 4526 | 10731 | 3549 | 930 | 1812 | 0 | 724 | 3355 | 25 | 0 | 140 | 128 | 63 | 5 | 42 | 80.79
18:00 | 0 | 0 | 130 | 90 | 0 | 0 | 0 | 360 | 0 |  | 0 | 450 | 151 | 20 | 0 | 15 | 333 | 0 | 0 | 24 | 57 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 15 | 33 | 4 | 17 | 0 | 25 | 0 | 0 | 0 | 13 | 197 | 0 | 0 | 0 |  | 6 | 8 | 34 | 25 | 22 | 19 | 10 | 25 | 0 | 0 | 0 | 0 | 270 | 219 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 142 | 114 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 209 | 14 | 0 | 0 | 295 | 16 | 0 | 0 | 57 | 0 | 0 | 19 | 0 | 50 | 0 | 12 | 152 | 8 | 367 | 45 | 50 | 17 | 0 | 49 | 17 | 17 | 34 | 58 | 12 | 340 | 42 | 1 | 45 | 17 | 50 | 0 | 0 | 70 | 17 | 325 | 35 | 0 | 0 | 5 | 680 | 0 | 0 | 1 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 18 | 0 | 65 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 12 | 0 | 18 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 220 | 0 | 2 | 0 | 0 | 17 | 0 | 0 | 379 | 0 | 150 | 816 | 1 | 0 |  | 6547 | 4517 | 11064 | 3576 | 929 | 1815 | 0 | 1101 | 3215 | 25 | 0 | 253 | 142 | 3 | 5 | 0 | 80.79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 359 | 0 |  | 0 | 450 | 150 | 0 | 0 | 15 | 333 | 0 | 0 | 24 | 57 | 32 | 7 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 15 | 33 | 32 | 17 | 0 | 25 | 0 | 0 | 0 | 25 | 186 | 0 | 0 | 0 |  | 6 | 67 | 34 | 25 | 26 | 19 | 10 | 29 | 0 | 0 | 0 | 0 | 270 | 220 | 8 | 0 | 39 | 30 | 0 | 25 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 138 | 115 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 209 | 18 | 0 | 0 | 275 | 16 | 0 | 0 | 122 | 0 | 0 | 19 | 0 | 50 | 0 | 12 | 155 | 6 | 363 | 45 | 50 | 17 | 0 | 49 | 17 | 17 | 34 | 58 | 25 | 340 | 48 | 0 | 54 | 17 | 50 | 0 | 0 | 70 | 17 | 393 | 53 | 0 | 0 | 7 | 525 | 0 | 0 | 0 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | 0 | 65 | 8 | 0 | 0 | 0 | 0 | 43 | 5 | 82 | 0 | 0 | 28 | 5 | 38 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 380 | 0 | 174 | 882 | 0 | 0 |  | 6615 | 4545 | 11160 | 3648 | 929 | 1678 | 0 | 1236 | 3041 | 25 | 0 | 458 | 138 | 0 | 7 | 0 | 80.77
19:30 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 358 | 0 |  | 0 | 450 | 149 | 0 | 0 | 15 | 333 | 0 | 0 | 0 | 57 | 32 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 15 | 33 | 32 | 17 | 0 | 25 | 0 | 0 | 0 | 25 | 196 | 0 | 0 | 0 |  | 6 | 67 | 34 | 25 | 26 | 19 | 10 | 12 | 0 | 0 | 0 | 0 | 270 | 220 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 138 | 158 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 209 | 18 | 0 | 0 | 300 | 24 | 0 | 0 | 95 | 0 | 0 | 19 | 0 | 50 | 0 | 12 | 120 | 6 | 363 | 45 | 50 | 17 | 0 | 49 | 17 | 17 | 34 | 26 | 25 | 340 | 52 | 0 | 54 | 17 | 0 | 0 | 0 | 70 | 0 | 375 | 53 | 0 | 0 | 6 | 554 | 0 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | 0 | 65 | 8 | 16 | 0 | 0 | 0 | 43 | 12 | 82 | 0 | 0 | 42 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 378 | 0 | 230 | 931 | 0 | 0 |  | 6543 | 4738 | 11281 | 3664 | 787 | 1739 | 0 | 1130 | 3313 | 25 | 0 | 479 | 138 | 0 | 6 | 0 | 0
20:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 357 | 0 |  | 0 | 450 | 150 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 25 | 197 | 0 | 0 | 0 |  | 6 | 67 | 34 | 25 | 26 | 19 | 10 | 23 | 0 | 0 | 0 | 0 | 270 | 220 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 126 | 159 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 208 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 95 | 0 | 0 | 19 | 0 | 50 | 0 | 12 | 120 | 5 | 365 | 24 | 35 | 17 | 0 | 49 | 17 | 17 | 17 | 26 | 25 | 300 | 52 | 0 | 54 | 17 | 0 | 0 | 0 | 53 | 0 | 375 | 17 | 0 | 0 | 6 | 577 | 0 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 8 | 16 | 0 | 0 | 0 | 12 | 16 | 82 | 0 | 0 | 50 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 376 | 0 | 250 | 1012 | 0 | 0 |  | 6297 | 4764 | 11061 | 3604 | 787 | 1638 | 0 | 1046 | 3455 | 25 | 0 | 374 | 126 | 0 | 6 | 0 | 80.78
21:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 147 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 17 | 15 | 33 | 32 | 17 | 0 | 25 | 0 | 0 | 0 | 25 | 196 | 0 | 0 | 0 |  | 6 | 67 | 34 | 12 | 26 | 19 | 10 | 35 | 0 | 0 | 0 | 0 | 270 | 223 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 32 | 0 | 8 | 33 | 19 | 130 | 154 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 212 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 45 | 0 | 0 | 19 | 0 | 41 | 0 | 12 | 100 | 6 | 363 | 24 | 17 | 17 | 0 | 16 | 17 | 17 | 17 | 26 | 25 | 300 | 50 | 0 | 17 | 17 | 0 | 0 | 0 | 40 | 0 | 340 | 17 | 0 | 0 | 2 | 576 | 0 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 377 | 0 | 250 | 1011 | 0 | 0 |  | 6056 | 4735 | 10791 | 3563 | 787 | 1696 | 0 | 811 | 3494 | 25 | 0 | 283 | 130 | 0 | 2 | 0 | 80.77
22:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 342 | 0 |  | 0 | 450 | 147 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 15 | 0 | 32 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 |  | 6 | 59 | 34 | 0 | 13 | 19 | 10 | 35 | 0 | 0 | 0 | 0 | 270 | 225 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 128 | 150 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 212 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 45 | 0 | 0 | 19 | 0 | 27 | 0 | 12 | 68 | 6 | 364 | 24 | 0 | 17 | 0 | 16 | 0 | 17 | 17 | 26 | 25 | 300 | 50 | 0 | 0 | 17 | 0 | 9 | 0 | 34 | 0 | 350 | 17 | 0 | 0 | 5 | 575 | 0 | 0 | 0 |  | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 379 | 0 | 150 | 925 | 0 | 0 |  | 5779 | 4596 | 10375 | 3530 | 929 | 1661 | 0 | 567 | 3309 | 25 | 0 | 221 | 128 | 0 | 5 | 0 | 80.77
23:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 341 | 0 |  | 0 | 380 | 147 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 59 | 34 | 0 | 0 | 19 | 10 | 38 | 0 | 0 | 0 | 0 | 310 | 206 | 0 | 0 | 38 | 0 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 126 | 144 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 212 | 22 | 0 | 0 | 285 | 0 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 17 | 0 | 12 | 68 | 5 | 387 | 8 | 0 | 17 | 0 | 16 | 0 | 17 | 17 | 26 | 25 | 327 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 34 | 0 | 335 | 17 | 0 | 0 | 2 | 577 | 0 | 0 | 0 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 150 | 823 | 0 | 0 |  | 5633 | 4378 | 10011 | 3549 | 930 | 1597 | 0 | 436 | 3125 | 25 | 0 | 221 | 126 | 0 | 2 | 0 | 80.76
24:00 | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 347 | 0 |  | 0 | 380 | 149 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 33 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 6 | 59 | 34 | 25 | 0 | 6 | 10 | 37 | 0 | 0 | 0 | 0 | 270 | 188 | 0 | 0 | 40 | 0 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 0 | 102 | 142 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 212 | 20 | 0 | 0 | 300 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 17 | 0 | 12 | 71 | 6 | 361 | 9 | 0 | 17 | 0 | 16 | 0 | 17 | 25 | 12 | 12 | 300 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 0 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 150 | 827 | 0 | 0 |  | 5502 | 4493 | 9995 | 3465 | 930 | 1717 | 0 | 393 | 3142 | 25 | 0 | 221 | 102 | 0 | 0 | 0 | 80.76
KWH | 0 | 0 | 3249062 | 819000 | 0 | 377409 | 0 | 7876800 | 0 |  | 0 | 9539500 | 3519418 | 39400 | 0 | 144566 | 7284730 | 0 | 0 | 74390 | 331488 | 389280 | 10021 | 0 | 0 | 0 | 90720 | 86126 | 74804 | 0 | 408000 | 306720 | 633600 | 688400 | 156480 | 0 | 526500 | 0 | 0 | 0 | 148897 | 4815054 | 0 | 0 | 0 |  | 44400 | 840672 | 531964 | 193080 | 190080 | 154080 | 227184 | 598080 | 0 | 0 | 0 | 0 | 7051000 | 4941000 | 468363 | 0 | 721944 | 622080 | 0 | 1024670 | 0 | 308352 | 328877 | 0 | 183240 | 766200 | 404740 | 2888640 | 3018240 | 0 | 0 | 13850 | 0 | 925800 | 0 | 0 | 3458781 | 0 | 1159488 | 0 | 0 | 5229600 | 410000 | 0 | 0 | 7261000 | 478968 | 0 | 0 | 577091 | 0 | 0 | 103200 | 0 | 514800 | 132570 | 216960 | 1401120 | 76945 | 8456000 | 769200 | 303360 | 235018 | 31203 | 371345 | 114924 | 239199 | 258780 | 499800 | 1028160 | 8001400 | 421440 | 315880 | 211680 | 321164 | 170200 | 12600 | 224085 | 409920 | 68760 | 7630900 | 449963 | 0 | 0 | 64320 | 14989090 | 0 | 0 | 524818 |  | 21757090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10560 | 81536 | 0 | 133000 | 131734 | 39168 | 0 | 0 | 920000 | 76001 | 18306 | 482496 | 0 | 0 | 71645 | 22349 | 126737 | 0 | 0 | 106290 | 0 | 0 | 4586400 | 0 | 0 | 4565255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8651345 | 0 | 0 | 0 | 0 | 0 | 0 | 9907 | 0 | 20868100 | 4989327 | 0 | 45600 | 34920 | 677520 | 186048 | 0 | 0 | 9236364 | 97402 | 3883600 | 21106240 | 912960 | 0 |  | 135180633 | 103827900 | 239008533 | 81581815 | 21757090 | 40641707 | 0 | 10516040 | 74669794 | 526500 | 0 | 3387512 | 2888640 | 2975115 | 64320 | 0
Fuel Cost | 0 | 0 | 13938475.98 | 3644550 | 0 | 1441702.38 | 0 | 22685184 | 0 |  | 0 | 30335610 | 12036409.56 | 778544 | 0 | 2547252.92 | 22218426.5 | 0 | 0 | 1469946.4 | 5950209.6 | 7559817.6 | 186891.65 | 0 | 0 | 0 | 1656547.2 | 1357345.76 | 1368165.16 | 0 | 306000 | 0 | 0 | 0 | 2802556.8 | 0 | 0 | 0 | 0 | 0 | 2820109.18 | 15360022.26 | 0 | 0 | 0 |  | 780996 | 14804233.92 | 9527475.24 | 3680104.8 | 3719865.6 | 2536156.8 | 845124.48 | 0 | 0 | 0 | 0 | 0 | 21576060 | 16404120 | 1569016.05 | 0 | 2432951.28 | 2724710.4 | 0 | 4108926.7 | 0 | 5522584.32 | 5939518.62 | 0 | 137430 | 2850264 | 303555 | 18949478.4 | 9386726.4 | 0 | 0 | 0 | 0 | 3453234 | 0 | 0 | 11829031.02 | 0 | 6435158.4 | 0 | 0 | 14590584 | 2697800 | 0 | 0 | 22436490 | 359226 | 0 | 0 | 11772656.4 | 0 | 0 | 1982472 | 0 | 9065628 | 0 | 3864057.6 | 24309432 | 1275748.1 | 22408400 | 14660952 | 5691033.6 | 4216222.92 | 0 | 6071490.75 | 2234122.56 | 4291230.06 | 4945285.8 | 9701118 | 18311529.6 | 21283724 | 7193980.8 | 0 | 3871627.2 | 5389131.92 | 636548 | 225162 | 0 | 7386758.4 | 1164794.4 | 22663773 | 6335479.04 | 0 | 0 | 0 | 88435631 | 0 | 0 | 0 |  | 61137422.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198633.6 | 1533692.16 | 0 | 420280 | 624419.16 | 675256.32 | 0 | 0 | 4489600 | 1361177.91 | 335915.1 | 8110757.76 | 0 | 0 | 1283161.95 | 395577.3 | 2269859.67 | 0 | 0 | 80461.53 | 0 | 0 | 38709216 | 0 | 0 | 15065341.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25261927.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135225288 | 15516806.97 | 0 | 882360 | 0 | 0 | 3227932.8 | 0 | 0 | 67425457.2 | 0 | 28932820 | 139512246.4 | 0 | 0 |  | 649452577.53 | 552675611.63 | 1202128189.16 | 246673020.33 | 61137422.9 | 127885049.64 | 0 | 190399771.02 | 498240658.6 | 0 | 0 | 58842788.27 | 18949478.4 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 64 | 0 | 369 | 0 |  | 0 | 450 | 151 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 32 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 43 | 0 | 6 | 8 | 0 | 10 | 7 | 0 | 0 | 0 | 0 | 305 | 218 | 83 | 0 | 36 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 15 | 130 | 105 | 0 | 0 | 2 | 0 | 40 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 206 | 16 | 0 | 0 | 315 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 12 | 34 | 0 | 365 | 47 | 17 | 17 | 5 | 16 | 0 | 17 | 17 | 12 | 100 | 390 | 0 | 37 | 0 | 17 | 0 | 0 | 33 | 0 | 0 | 325 | 0 | 0 | 0 | 3 | 728 | 0 | 0 | 75 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 590 | 220 | 0 | 0 | 5 | 93 | 0 | 0 | 0 | 360 | 22 | 150 | 879 | 168 | 0 |  | 10399 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 358 | 0 |  | 0 | 450 | 149 | 0 | 0 | 15 | 333 | 0 | 0 | 0 | 57 | 32 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 15 | 33 | 32 | 17 | 0 | 25 | 0 | 0 | 0 | 25 | 196 | 0 | 0 | 0 | 0 | 6 | 67 | 34 | 25 | 26 | 19 | 10 | 12 | 0 | 0 | 0 | 0 | 270 | 220 | 8 | 0 | 39 | 30 | 0 | 51 | 0 | 37 | 25 | 0 | 8 | 33 | 19 | 138 | 158 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 209 | 18 | 0 | 0 | 300 | 24 | 0 | 0 | 95 | 0 | 0 | 19 | 0 | 50 | 0 | 12 | 120 | 6 | 363 | 45 | 50 | 17 | 0 | 49 | 17 | 17 | 34 | 26 | 25 | 340 | 52 | 0 | 54 | 17 | 0 | 0 | 0 | 70 | 0 | 375 | 53 | 0 | 0 | 6 | 554 | 0 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | 0 | 65 | 8 | 16 | 0 | 0 | 0 | 43 | 12 | 82 | 0 | 0 | 42 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 378 | 0 | 230 | 931 | 0 | 0 |  | 11281 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 100 | 0 | 50 | 0 | 360 | 0 |  | 0 | 450 | 150 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 57 | 149 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 33 | 32 | 17 | 0 | 30 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 6 | 66 | 34 | 25 | 25 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 30 | 40 | 0 | 51 | 0 | 47 | 52 | 0 | 10 | 33 | 17 | 141 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 210 | 20 | 0 | 10 | 300 | 17 | 0 | 0 | 195 | 0 | 0 | 18 | 0 | 51 | 0 | 12 | 200 | 8 | 400 | 95 | 105 | 17 | 0 | 16 | 17 | 17 | 114 | 75 | 25 | 383 | 54 | 0 | 54 | 17 | 0 | 17 | 0 | 95 | 17 | 320 | 127 | 0 | 0 | 40 | 650 | 0 | 0 |  |  | 948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 65 | 7 | 110 | 0 | 0 | 60 | 40 | 24 | 90 | 28 | 42 | 50 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 42 | 0 | 0 | 35 | 1200 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 370 | 0 | 150 | 1000 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 100 | 0 | 30 | 0 | 320 | 0 | 0 | 0 | 450 | 150 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 214 |  | 0 | 0 | 0 | 0 | 32 | 34 | 25 | 0 | 6 | 10 | 4 | 0 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 30 | 40 | 0 | 51 | 0 | 47 | 25 | 0 | 9 | 33 | 19 | 128 | 80 | 0 | 0 | 1.6 | 0 | 40 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 210 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 17 | 20 | 12 | 34 | 6 | 400 | 47 | 17 | 17 | 5 | 16 | 0 | 17 | 17 | 38 | 12 | 383 | 54 | 50 | 0 | 17 | 0 | 17 | 35 | 0 | 0 | 330 | 54 | 0 | 0 | 40 | 650 | 0 | 0 | 25 |  | 948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 110 | 0 | 0 | 60 | 25 | 0 | 50 | 28 | 42 | 40 | 8 | 16 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 1200 | 220 |  | 0 | 6 | 100 | 35 | 0 |  | 370 | 30 | 150 | 1000 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 130 | 100 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 350 | 138 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 16 | 2 | 0 | 20 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 300 | 120 | 0 | 0 | 10 | 3 | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 25 | 13 | 92 | 112 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 212 | 20 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 5 | 10 | 1 | 320 | 47 | 3 | 0 | 2 | 16 | 0 | 5 | 17 | 0 | 12 | 300 | 5 | 11 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 285 | 17 | 0 | 0 | 1 | 546 | 0 | 0 | 28 | 0 | 786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 180 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 383 | 6 | 150 | 921 | 24 | 0 | 0 |  |  |  | 122223522 | 21757090 | 0 | 74669794 | 13903552 | 2888640 | 2975115 | 64320 | 526500 |  |  | 239008533
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  |  |  |  | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [12 empty] | 599468 |  |  |  | 599230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 122.2235 | 21.7571 | 0 | 74.6698 | 13.9036 | 2.8886 | 2.9751 | 0.06432 | 0.5265
| Minimum Generation |  | 7730 | 6:00
| Highest Generation |  | 11281 | 19:30 | [129 empty] | 0 | [71 empty] | 239.0085
| Day Peak Generation |  | 10399 | 12:00
| Evening Peak Generation |  | 11281 | 19:30 | [201 empty] | 202699852
| HVDC Max Flow |  | 930 | 12:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 787 | 19:30
| Load factor L.F |  | 88.28% | [167 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-03-24
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-03-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10399 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7652
Evening Peak Generation : |  |  | 11281 | MW Hour : | 19:30 | Available Max Generation : |  | 13210
E.P. Demand (at gen end) : |  |  | 11281 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12200
Maximum Generation : |  |  | 11281 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1010
Total Gen. (MKWH) : |  |  | 239.0085 | System Load Factor : | 88.28% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 700 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-03-24
Actual : |  | 80.73 | Ft.(MSL) , | Rule curve : | 89.32 | Ft.( MSL )
Gas Consumed : |  | Total = | 905.98 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 374558069.97
: |  |  | Coal : | 498240658.6 | Oil : | 249242559.29 | Total : | 1122041287.86
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4566.6177 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1254.7712 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1757.6832 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1527.7396 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1257.061 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 934.9371 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 524.0604 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 436.7424 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 854.1914 |  |  | 0 | 0%
Total |  | 0 |  | 13113.8039 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj North
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:30 | 17:58 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to 3nos 132KV LA replacement works.
8:44 | 15:08 | Pabna- Shahjadpur 132kV Ckt-1 Scheduled S/D from Pabna 132/33kV end Due to Gas leakage maintenance work in BKR.
- | 9:01 | Chapai 132/33kV S/S T-2 (415T) HT is restored.
- | 9:01 | Chapai 132/33kV S/S T-3 (425T) HT is restored.
- | 9:03 | Chapai 132/33kV S/S T-3 (425T) LT is restored.
- | 9:10 | Chapai 132/33kV S/S T-2 (415T) LT is restored.
- | 9:12 | Rahanpur 400/132kV S/S Bus Reactor 400 KV is restored.
9:14 | 17:35 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Cross Arm Painting Work.
9:45 | 16:43 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to Underground Cable Maintenance.
9:45 | 16:44 | Chandpur 132/33kV S/S 422T LT Scheduled S/D.
9:46 | 13:41 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to G2G Project works.
9:48 | 12:36 | Kishoreganj 132/33kV S/S 33 kV T3 Bus Scheduled S/D Due to 33 kv Bus-section-03 side maintenance work. |  |  |  |  | 40.0MW load interrup.
10:06 | 13:29 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to G2G project works.
- | 10:18 | Rangpur 132/33kV S/S T-1(414T) HT is restored.
- | 10:20 | Rangpur 132/33kV S/S T-1(414T) LT is restored.
10:57 | - | Savar 132/33kV S/S Main Bus Scheduled S/D Due to replacement work of 132kV Main Bus-I DS (902M) and ES (905G) of
132kV Buscoupler.
12:00 | - | Day Peak Generation : 10399 MW
- | 12:34 | Rampur 230/132/33 S/S Khulshi-1 is restored.
12:35 | 16:55 | Madanganj 132/33kV S/S Main Bus Forced S/D Due to red hot maintenance of Munshiganj-2 main bus ds.
- | 12:55 | Rampur 230/132/33 S/S Halishahar-1 is restored.
15:07 | 15:18 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance Relay operated, R,Y,B Master relay
trip relays Due to Thandaring & Rain.
15:14 | 16:46 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Project Work S/D from Cumilla(N) 230/132/33kV end Due to 230/132 KV T-03 Project work.
15:15 | 16:46 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end Due to 230/132 KV T-03 Project work.
15:17 | 16:44 | Cumilla(N) 230/132/33kV S/S 132KV TRANSFARBUS Project Work S/D Due to 230/132 KV T-03 project work.
16:09 | - | Baghabari 71 MW GTPP Shutdown.
- | 16:29 | Jashore 132/33kV S/S T-1 HT is restored.
- | 16:30 | Jashore 132/33kV S/S T-1 LT is restored.
19:30 | - | Peak generation 11281 MW
20:04 | 20:27 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance relay relays. and from
Shahjibazar 132/33kV end showing Distance Relay relays Due to Stormy Wether.
20:17 | 20:40 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance relay relays Due to Stormy Wether.
21:00 | 21:25 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Mymensingh 132/33kV end showing Distance relays.
23:10 | 23:20 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing O/C & E/F relays Due to 33 kv Nabinogor feeder fault. |  |  |  |  | 15.0MW load interrup.
1:27 | 1:38 | Ashuganj-Kishoreganj 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing DIST: Z1,R,Y,B relays Due to DIST: Z1,R,Y,B
2:00 | - | Sehri Peak Gen. 9043 MW.
2:20 | - | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing . General Trip . Dist Trip R,S,T . SOTF relays
Due to Storm and from Mirpur 132/33kV end showing Distance Protection- Zone-1 C, Auto reclose, Main Protection trip, Sync
check limit. Aminbazar-2: Zone-2, Trip Transfer relays Due to Due to heavy storm.
2:22 | 2:22 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Dead line checking after storm.
2:40 | - | Hasnabad-Shyampur 230kV Ckt-1 Tripped from Hasnabad 230/132kV end showing SIPROTEC 7SAB7 relays Due to Thundering.
2:42 | 3:06 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing PH Y, Z1, Dist. SEND (Micom P441) relays Due to Heavy
Rainfall & Thundering.
2:43 | - | Siddhirganj 335 MW CCPP Tripped with remarks:- GT
2:45 | 5:10 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing RED670 1. 86 2. LBB initiation relays Due to Rain &
Thundering and Ullon-1 trip during fault.
2:45 | 3:27 | Fatullah 132/33kV S/S 132 kV Hasnabad Tripped showing Main-1 general Trip, Dist. Zone 1 Trip. relays.
2:45 | 3:18 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Narshingdi 132/33kV end showing NA relays Due to By CB Trip from Haripur end |  |  |  |  | 74.0MW load interrup.
|  | and from Haripur 230/132kV end showing Z1. AN relays Due to Heavy Rainfall & Thundering. |  |  |  |  | Narshingdi 132/33kV end
2:45 | 3:03 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Siemens SPIROTEC 1. |  |  |  |  | 15.0MW load interrup.
|  | Zone-01 2. Ph- Y 3. Distance-2.7 km relays Due to Heavy rain & thunder during fault time. |  |  |  |  | Siddhirganj 132/33kV end
2:46 | 3:34 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Distance Relay relays Due to Unknown |  |  |  |  | 10.0MW load interrup.
4:33 | 5:03 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Chowmuhani 132/33kV end showing DISTANCE RELAY A B C, 3Phase,
Zone-2 Fault. relays Due to DISTANCE RELAY A B C, 3Phase, Zone-2 Fault.
5:31 | - | Siddhirganj 335 MW CCPP Syncronized with remarks:- GT
6:49 | - | Siddhirganj 335 MW CCPP Syncronized with remarks:- ST
7:08 | 7:39 | Keranigonj 230/132/33kV S/S TR-2 LT Tripped showing 86 relays Due to 33kV kalatiya feeder fault.
7:08 | 7:39 | Keranigonj 230/132/33kV S/S TR-1 LT Tripped showing 86 relays Due to 33kV kalatiya feeder fault.
7:22 | - | Ashuganj CCPP 225 MW Tripped with remarks:- ST
7:22 | - | Ashuganj CCPP 225 MW Syncronized with remarks:- ST tripped at 07:22
Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from
Aminbazar 400/230/132kV end.
Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled
S/D Due to General cleaning
Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled
S/D
|  | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 33 kv |  |  |  |  | 18.0MW
|  | Bus Coupler DS open from PDB (33 kv side) |  |  |  |  | load
interrup.
interrup.
|  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33 kv |  |  |  |  | 13.0MW
|  | Bus coupler T5 maintenance. work |  |  |  |  | load
interrup.
Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.
and from Bogura 230/132kV end Due to project work
Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.
and from Bogura 230/132kV end Due to project work
|  | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D |  |  |  |  | 12.0MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-03-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3249062 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 100 | 819000 | Synchronized at 12:45.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 377409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 358 | 7876800 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9539500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 39400 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 149 | 3519418 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 144566 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 10021 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 74390 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7284730
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 57 | 331488 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 90720 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 389280 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 86126 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 74804 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 32 | 714720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 633600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 688400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 156480 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 577091 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 514800 | High Voltage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 303360 | Low demand
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 52 | 421440 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 211680 | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 224085
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 68760 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2103 | 38421130
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 148897
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 132570
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 154080 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 526500 | Unit-3 under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 196 | 4815054 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 235018 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 840672 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 531964 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 193080 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 216960 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 227184 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 598080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 190080 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31203
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 371345 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 114924 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 239199 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 1028160 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 321164 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 53 | 449963 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 0 | 0 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 6 | 64320 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 554 | 14989090
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 524818
| Chattogram area Total |  |  |  | 4344 | 1206 | 26944325
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 220 | 4941000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7051000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 375 | 7630900 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 721944 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 30 | 622080 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 468363 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1024670
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 76945 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 308352 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1401120 | High Voltage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 183240 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2888640
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 766200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 328877 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 19 | 404740 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 258780 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 499800 | Low demand
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 12600 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 409920 | Low demand
| Cumilla Area Total |  |  |  | 2929 | 1509 | 29999171
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3018240 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13850
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 103200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 769200 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 315880
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44400 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 228 | 4264770
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 925800 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3458781
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1159488 | Frequency control
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 170200
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5229600 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 410000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 478968
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7261000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 363 | 8456000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8001400 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1497 | 35551237
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 787 | 21757090
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 8 | 10560 | Low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 31 | 81536 | Low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 677520
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 378 | 9236364 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1204 | 31763070
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 39168 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 8 | 131734 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 133000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 20868100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4989327
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 45600 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 230 | 3883600 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1576 | 30090529
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 920000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 76001 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 12 | 18306 | Low demand
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 71645 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4565255
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 348 | 8651345 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 126737 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 106290 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 22349 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 482496 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Fuel shortage
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 931 | 21106240 | Coal shortage
| Rajshahi Area Total |  |  |  | 3431 | 1723 | 36181584
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4586400 | Coal shortage
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 9907
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 186048 | Low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 97402
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 912960
| Rangpur Area Total |  |  |  | 950 | 235 | 5792717
| Total |  |  |  | 25809 | 11281 | 239008533
| Eastern Grid Total |  |  |  | 15926 | 6543 | 135180633
| Western Grid Total |  |  |  | 9883 | 4738 | 103827900
| National Grid Total |  |  |  | 25809 | 11281 | 239008533
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-03-23
| (a) ENTIRE EASTERN GRID : |  | 7346.54 | MW | (b) ENTIRE WESTERN GRID : |  | 3454.8 | MW
| i) Dhaka area |  | 4215.04 | MW | i) Khulna area |  | 1440.6 | MW
| ii) Chittagong area |  | 1175 | MW | ii) Rajshahi area |  | 1129.2 | MW
| iii) Comilla area |  | 1071 | MW | iii) Barisal area |  | 336 | MW
| iv) Mymensingh area |  | 510.5 | MW | iv) Rangpur area |  | 549 | MW
| v) Sylhet area |  | 375 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10801.34 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 14 | 15:00 | Chhatak | 20 | 18:00 | Kamrangirchar | 53.14 | 16:00 | Narinda | 56 | 13:00 | Sherpur | 104 | 14:00
2 | AKSML | 106 | 12:00 | Chowmuhani | 169 | 21:00 | Kaptai | N/A | N/A | Narshingdi | 156 | 19:00 | Shikalbaha | 21 | 23:00
3 | Aftabnagar | 28 | 20:00 | Chuadanga | 89 | 19:30 | Kazla | 88 | 12:00 | Natore | 117 | 20:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 58 | 18:00 | Coxsbazar | 98 | 19:00 | Keranigonj | 68 | 21:00 | Nawabganj | 36.6 | 21:00 | Shitalakhya | 85.6 | 15:00
5 | Agrabad | 64 | 19:30 | Cumilla(N) | 144 | 22:00 | Khagrachori | 28 | 18:30 | Netrakona | 107 | 03:00 | Sholosohor | 37 | 15:00
6 | Amnura | 48 | 19:00 | Cumilla(S) | 146 | 15:00 | Khulna | 74 | 18:30 | New | 19.2 | 12:00 | Shyampur | 164 | 13:00
7 | Ashuganj | 59 | 00:00 | Daudkandi | 120 | 19:00 | Khulshi | 164 | 20:00 | Niamatpur | 72 | 18:00 | Siddhirganj | 108 | 13:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 11:00 | Kishoreganj | 130 | 18:00 | Noapara | 51 | 13:00 | Sirajganj | 94 | 20:00
9 | BSRM | 101 | 17:00 | Dhamrai | 96 | 19:30 | Kodda | 263 | 10:00 | PHP | 2 | 05:00 | Sonargaon | 94 | 20:00
10 | Bagerhat | 77 | 19:00 | Dhanmondi | 108 | 13:00 | Kulaura | 30 | 17:00 | Pabna | 89 | 19:30 | Sreemongol | 53 | 18:30
11 | Bakulia | 85 | 21:00 | Dohazari | 77 | 19:00 | Kurigram | 56 | 03:00 | Palashbari | 66 | 04:00 | Sreepur | 63 | 09:00
12 | Banani | 26.6 | 19:30 | Faridpur | 124 | 19:30 | Kushtia | 110 | 19:30 | Panchagarh | 38 | 18:00 | Srinagar | 36 | 21:00
13 | Bangabhaban | 6 | 12:00 | Fatullah | 59 | 14:00 | Lalbag | 74 | 16:00 | Patuakhali | 65.5 | 21:00 | Sunamganj | 37 | 18:30
14 | Barapukuria | 42 | 12:00 | Fenchuganj | 29 | 18:30 | Lalmonirhat | 34 | 19:00 | Payra | 18 | 19:00 | Sylhet | 22 | 14:00
15 | Barguna | 16 | 20:00 | Feni | 89 | 19:00 | MI_Cement | 12.1 | 00:00 | Postogola | 44 | 13:00 | Sylhet-132 | 88 | 15:00
16 | Barishal | 93 | 22:00 | GPH | 75 | 13:00 | Madanganj | 32 | 23:00 | Purbachal | 15 | 21:00 | TK | 23.8 | 21:00
17 | Barishal-230 | 72 | 20:00 | Ghorashal | 72 | 11:00 | Madaripur | 82 | 19:00 | Purbasadipur | 85 | 13:00 | Tangail | 188 | 18:00
18 | Baroaulia | 63 | 13:00 | Goalpara | 26 | 19:00 | Madartek | 59.01 | 22:00 | Rahim | 28 | 23:00 | Thakurgaon | 68 | 19:30
19 | Baroirhat | 45 | 13:00 | Gollamari | 70 | 19:30 | Madunaghat | 41 | 19:30 | Rajbari | 56 | 19:00 | Tongi | 144 | 11:00
20 | Bashundhara | 147 | 20:00 | Gopalganj | 88 | 21:00 | Magura | 50 | 19:00 | Rajendrapur | 78 | 18:00 | Ullahpara | 23 | 01:00
21 | BashundharaCement | 6 | 07:00 | Gulshan | 66 | 12:00 | Mahasthangarh | 60 | 13:00 | Rajshahi | 121 | 21:00 | Ullon | 45 | 20:00
22 | Beanibazar | 44 | 18:30 | Halishahar | 73 | 14:00 | Manikganj | 102 | 18:30 | Rajshahi-230 | 33 | 08:00 | Uttara | 51 | 21:00
23 | Benapole | 61 | 14:00 | HaripurSBU | 150 | 12:00 | Maniknagar | 48 | 13:00 | Ramganj | 90 | 19:00 | UttaraNew | 32 | 18:00
24 | Bhaluka | 127 | 19:30 | Hasnabad | 76 | 15:00 | Matarbari | 43 | 19:00 | Rampur | 31 | 22:00 | Zigatola | 52 | 19:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 61 | 21:00 | Matuail | 64 | 11:00 | Rangamati | 35 | 03:00
26 | Bhangura | 29 | 14:00 | Ishurdi | 54 | 19:00 | Millgate | 100 | 14:00 | Rangpur | 87 | 18:00
27 | Bheramara(GK) | 44 | 19:30 | Jaldhaka | 48 | 17:00 | Mirpur | 111 | 19:30 | Ruppur | 3.4 | 11:00
28 | Bhulta | 231 | 12:00 | Jamalpur | 129 | 16:00 | Mirsorai | 6 | 15:00 | SSM | 6 | 23:00
29 | Bog-Sherpur | 52 | 03:00 | Jashore | 126 | 19:30 | Mirzapur | 46 | 18:00 | Saidpur | 72 | 10:00
30 | Bogura | 123 | 18:00 | Jhenaidah | 109 | 19:00 | Mithapukur | 41 | 03:00 | Satkhira | 108 | 19:00
31 | Borhanuddin | 60 | 21:00 | Joydebpur | 158 | 21:00 | Modern | 0 | 00:00 | Satmasjid | 87 | 21:00
32 | Brahmanbaria | 138 | 18:30 | Joypurhat | 45 | 18:00 | Mogbazar | 93.7 | 13:00 | Savar | 170 | 14:00
33 | Cantonment | 104 | 20:00 | Juldah | 13 | 04:00 | Mongla | 31 | 12:00 | SevenRings | 14.52 | 10:00
34 | Chandpur | 56 | 21:00 | KSRM | 31 | 12:00 | Motijheel | 32 | 13:00 | ShahCement | 26 | 01:00
35 | Chandraghona | 26 | 19:00 | Kabirpur | 256 | 16:00 | Munshiganj | 86 | 22:00 | Shahjadpur | 68 | 09:00
36 | Chapai | 55 | 22:00 | Kachua | 58 | 21:00 | Mymensingh | 180 | 17:00 | Shahjibazar | 98 | 19:00
37 | Charsaidpur | 44 | 23:00 | Kallyanpur | 90 | 20:00 | Naogaon | 100 | 19:30 | Shahmirpur | 43 | 00:00
38 | Chauddagram | 53 | 21:00 | Kalurghat | 32 | 12:00 | Narail | 48 | 19:00 | Shariatpur | 63 | 21:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## L-Curve
Date | 2024-03-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 920 | 5502 | 4493 | 9995 |  |  |  | QF-LDC-11
0:30 | 1100 | 5264 | 4267 | 9531 | Date: | 2024-03-23
1:00 | 1280 | 5026 | 4041 | 9067
1:30 | 1260 | 4967 | 3958.5 | 8925.5
2:00 | 1240 | 4908 | 3876 | 8784
2:30 | 1204 | 5001.5 | 3899.5 | 8901 | [5 empty] | Gen. at Eve. Peak | 11281 | 11281 MW (19:30 )
3:00 | 1168 | 5095 | 3923 | 9018 | [6 empty] | 19:30
3:30 | 1164 | 5186.5 | 4017.5 | 9204 | [5 empty] | Gen. at Day Peak | 10399 | 10399 MW (12:00 )
4:00 | 1160 | 5278 | 4112 | 9390 | [6 empty] | 12:00
4:30 | 1200 | 4961.5 | 3935.5 | 8897 | [5 empty] | Highest Generation | 11281
5:00 | 1240 | 4645 | 3759 | 8404 | [6 empty] | 19:30
5:30 | 1258 | 4382.5 | 3684.5 | 8067
6:00 | 1276 | 4120 | 3610 | 7730
6:30 | 1288 | 4215.5 | 3660 | 7875.5
7:00 | 1300 | 4311 | 3710 | 8021
7:30 | 1266 | 4623.5 | 3703.5 | 8327
8:00 | 1232 | 4936 | 3697 | 8633
8:30 | 1201 | 5166.5 | 3809.5 | 8976
9:00 | 1170 | 5397 | 3922 | 9319
9:30 | 1188 | 5503.5 | 3949.5 | 9453
10:00 | 1206 | 5610 | 3977 | 9587
10:30 | 1220 | 5719 | 4032 | 9751
11:00 | 1234 | 5828 | 4087 | 9915
11:30 | 1302 | 5968.5 | 4188.5 | 10157
12:00 | 1370 | 6109 | 4290 | 10399
12:30 | 1322 | 6170.5 | 4371.5 | 10542
13:00 | 1274 | 6232 | 4453 | 10685
13:30 | 1315 | 6123.5 | 4621 | 10744.5
14:00 | 1356 | 6015 | 4789 | 10804
14:30 | 1304 | 6024.5 | 4786.5 | 10811
15:00 | 1252 | 6034 | 4784 | 10818
15:30 | 1218 | 6086.5 | 4686.5 | 10773
16:00 | 1184 | 6139 | 4589 | 10728
16:30 | 1148 | 6172 | 4557.5 | 10729.5
17:00 | 1112 | 6205 | 4526 | 10731
17:30 | 1006 | 6376 | 4521.5 | 10897.5
18:00 | 900 | 6547 | 4517 | 11064
18:30 | 830 | 6581 | 4531 | 11112
19:00 | 760 | 6615 | 4545 | 11160
19:30 | 770 | 6543 | 4738 | 11281
20:00 | 756 | 6297 | 4764 | 11061 |  |  |  | Executive Engineer
20:30 | 728 | 6176.5 | 4749.5 | 10926 |  |  |  | Network Operation Division
21:00 | 700 | 6056 | 4735 | 10791
21:30 | 710 | 5917.5 | 4665.5 | 10583
22:00 | 720 | 5779 | 4596 | 10375 |  |  |  |  | Page 6 of 7
22:30 | 743 | 5706 | 4487 | 10193
23:00 | 766 | 5633 | 4378 | 10011
23:30 | 843 | 5567.5 | 4435.5 | 10003
24:00 | 920 | 5502 | 4493 | 9995
11281 MW (19:30 )
10399 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-03-23 |  | Energy |  | 239008533
[14 empty] | Date: | 2024-03-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3465 | 930 | 1717 | 0 | 393 | 3142 | 25 | 0 | 221 | 102 | 0 | 0 | 0
0:30 | 3380.5 | 929 | 1639.5 | 0 | 285 | 3010.5 | 27.5 | 0 | 151.5 | 107 | 0 | 0.5 | 0 |  |  | Date: | 43912
1:00 | 3296 | 928 | 1562 | 0 | 177 | 2879 | 30 | 0 | 82 | 112 | 0 | 1 | 0
1:30 | 3272.5 | 927.5 | 1517 | 0 | 177 | 2807.5 | 30 | 0 | 82 | 111 | 0 | 1 | 0 | [8 empty] | Total Energy | 239.0085 | 239.0085 | Total Energy Gen 239.009 MKWHr Energy Not Served 0.064 MKWHr Energy Requirement 239.073 MKWHr
2:00 | 3249 | 927 | 1472 | 0 | 177 | 2736 | 30 | 0 | 82 | 110 | 0 | 1 | 0 | [8 empty] | Energy not Served | 0.06432 | 0.06432
2:30 | 3315 | 927 | 1528.5 | 0 | 177 | 2729.5 | 30 | 0 | 82 | 111 | 0 | 1 | 0 | [8 empty] | Energy Requirement | 239.0729 | 239.0729
3:00 | 3381 | 927 | 1585 | 0 | 177 | 2723 | 30 | 0 | 82 | 112 | 0 | 1 | 0
3:30 | 3427 | 927.5 | 1672.5 | 0 | 179.5 | 2763.5 | 30 | 0 | 90 | 113 | 0 | 1 | 0
4:00 | 3473 | 928 | 1760 | 0 | 182 | 2804 | 30 | 0 | 98 | 114 | 0 | 1 | 0
4:30 | 3352.5 | 927 | 1639 | 0 | 110.5 | 2692.5 | 15 | 0 | 49 | 111 | 0 | 0.5 | 0
5:00 | 3232 | 926 | 1518 | 0 | 39 | 2581 | 0 | 0 | 0 | 108 | 0 | 0 | 0
5:30 | 3020.5 | 926.5 | 1438 | 0 | 25.5 | 2555.5 | 0 | 0 | 0 | 101 | 0 | 0 | 0
6:00 | 2809 | 927 | 1358 | 0 | 12 | 2530 | 0 | 0 | 0 | 94 | 0 | 0 | 0
6:30 | 2841.5 | 927 | 1411 | 0 | 46 | 2530 | 0 | 0 | 0 | 91 | 28.5 | 0.5 | 0 | [7 empty] | Coal
7:00 | 2874 | 927 | 1464 | 0 | 80 | 2530 | 0 | 0 | 0 | 88 | 57 | 1 | 0
7:30 | 3036 | 857 | 1475.5 | 0 | 111 | 2625 | 0 | 0 | 8 | 97 | 116.5 | 1 | 0 | [6 empty] | Oil
8:00 | 3198 | 787 | 1487 | 0 | 142 | 2720 | 0 | 0 | 16 | 106 | 176 | 1 | 0
8:30 | 3350.5 | 787 | 1551.5 | 0 | 154.5 | 2755 | 15 | 0 | 16 | 103 | 243 | 0.5 | 0
9:00 | 3503 | 787 | 1616 | 0 | 167 | 2790 | 30 | 0 | 16 | 100 | 310 | 0 | 0
9:30 | 3498.5 | 787 | 1664 | 0 | 178 | 2806.5 | 30 | 0 | 19 | 111 | 359 | 0 | 0
10:00 | 3494 | 787 | 1712 | 0 | 189 | 2823 | 30 | 0 | 22 | 122 | 408 | 0 | 0
10:30 | 3543.5 | 858 | 1738 | 0 | 222 | 2820 | 30 | 0 | 22 | 122 | 395.5 | 0 | 0
11:00 | 3593 | 929 | 1764 | 0 | 255 | 2817 | 30 | 0 | 22 | 122 | 383 | 0 | 0
11:30 | 3585.5 | 929.5 | 1868 | 0 | 304 | 2847 | 27.5 | 0 | 48.5 | 126 | 419.5 | 1.5 | 0
12:00 | 3578 | 930 | 1972 | 0 | 353 | 2877 | 25 | 0 | 75 | 130 | 456 | 3 | 0
12:30 | 3596.5 | 929.5 | 1964 | 0 | 386.5 | 2972 | 25 | 0 | 128.5 | 129 | 408.5 | 2.5 | 0
13:00 | 3615 | 929 | 1956 | 0 | 420 | 3067 | 25 | 0 | 182 | 128 | 361 | 2 | 0
13:30 | 3615 | 929 | 1956 | 0 | 420 | 3067 | 25 | 0 | 182 | 128 | 361 | 2 | 0
14:00 | 3615 | 929 | 1956 | 0 | 420 | 3067 | 25 | 0 | 182 | 128 | 361 | 2 | 0
14:30 | 3584.5 | 929 | 1879 | 0 | 419 | 3277 | 25 | 0 | 191.5 | 137 | 303 | 6.5 | 12.5
15:00 | 3554 | 929 | 1802 | 0 | 418 | 3487 | 25 | 0 | 201 | 146 | 245 | 11 | 25
15:30 | 3552 | 929 | 1829.5 | 0 | 472.5 | 3429.5 | 25 | 0 | 200 | 140 | 186.5 | 9 | 12.5
16:00 | 3550 | 929 | 1857 | 0 | 527 | 3372 | 25 | 0 | 199 | 134 | 128 | 7 | 0
16:30 | 3549.5 | 929.5 | 1834.5 | 0 | 625.5 | 3363.5 | 25 | 0 | 169.5 | 131 | 95.5 | 6 | 21
17:00 | 3549 | 930 | 1812 | 0 | 724 | 3355 | 25 | 0 | 140 | 128 | 63 | 5 | 42
17:30 | 3562.5 | 929.5 | 1813.5 | 0 | 912.5 | 3285 | 25 | 0 | 196.5 | 135 | 33 | 5 | 21
18:00 | 3576 | 929 | 1815 | 0 | 1101 | 3215 | 25 | 0 | 253 | 142 | 3 | 5 | 0
18:30 | 3612 | 929 | 1746.5 | 0 | 1168.5 | 3128 | 25 | 0 | 355.5 | 140 | 1.5 | 6 | 0
19:00 | 3648 | 929 | 1678 | 0 | 1236 | 3041 | 25 | 0 | 458 | 138 | 0 | 7 | 0
19:30 | 3664 | 787 | 1739 | 0 | 1130 | 3313 | 25 | 0 | 479 | 138 | 0 | 6 | 0
20:00 | 3604 | 787 | 1638 | 0 | 1046 | 3455 | 25 | 0 | 374 | 126 | 0 | 6 | 0
20:30 | 3583.5 | 787 | 1667 | 0 | 928.5 | 3474.5 | 25 | 0 | 328.5 | 128 | 0 | 4 | 0
21:00 | 3563 | 787 | 1696 | 0 | 811 | 3494 | 25 | 0 | 283 | 130 | 0 | 2 | 0
21:30 | 3546.5 | 858 | 1678.5 | 0 | 689 | 3401.5 | 25 | 0 | 252 | 129 | 0 | 3.5 | 0
22:00 | 3530 | 929 | 1661 | 0 | 567 | 3309 | 25 | 0 | 221 | 128 | 0 | 5 | 0
22:30 | 3539.5 | 929.5 | 1629 | 0 | 501.5 | 3217 | 25 | 0 | 221 | 127 | 0 | 3.5 | 0
23:00 | 3549 | 930 | 1597 | 0 | 436 | 3125 | 25 | 0 | 221 | 126 | 0 | 2 | 0
23:30 | 3507 | 930 | 1657 | 0 | 414.5 | 3133.5 | 25 | 0 | 221 | 114 | 0 | 1 | 0 |  |  | Max Temp. in Dhaka |  | 31.9°C
24:00 | 3465 | 930 | 1717 | 0 | 393 | 3142 | 25 | 0 | 221 | 102 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 239.009 MKWHr Energy Not Served 0.064 MKWHr Energy Requirement 239.073 MKWHr
Shortage
Note on W13: Author:

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-03-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 410 | 06:00 | 390 | 15:00 | Gopalganj | 413 | 06:00 | 392 | 16:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 395 | 18:00 | 374 | 15:00
| Bhulta | 403 | 18:00 | 382 | 14:00 | Madunaghat_I | 390 | 01:00 | 381 | 14:00
| Bibiana | 410 | 18:30 | 399 | 15:00 | Payra | 419 | 06:00 | 408 | 15:00
| BIPTC | 401 | 08:00 | 391 | 16:00 | Rahanpur | 415 | 06:00 | 405 | 13:00
| Bogura | 406 | 02:00 | 392 | 14:00 | Rampal | 412 | 06:00 | 395 | 14:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 18:30 | 218 | 14:00 | Haripur | 232 | 18:30 | 220 | 14:00
| AKSML | 231 | 19:00 | 222 | 11:00 | Hasnabad | 232 | 04:00 | 219 | 13:00
| Aminbazar | 233 | 18:00 | 218 | 14:00 | Hathazari | 230 | 18:30 | 221 | 14:00
| Ashuganj | 239 | 18:30 | 164 | 19:00 | Ishurdi | 235 | 06:00 | 23 | 18:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 234 | 06:00 | 219 | 12:00
| Baghabari | 234 | 06:00 | 225 | 14:00 | Kaliakoir | 235 | 18:00 | 219 | 14:00
| Barapukuria | 223 | 05:00 | 216 | 13:00 | Keranigonj | 235 | 18:30 | 218 | 14:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 236 | 06:00 | 222 | 14:00
| Barishal | 245 | 08:00 | 236 | 14:00 | Madunaghat_I | 230 | 07:00 | 222 | 14:00
| Bheramara | 234 | 06:00 | 223 | 12:00 | Maniknagar | 232 | 03:00 | 220 | 14:00
| Bhulta | 234 | 02:00 | 221 | 14:00 | Meghnaghat | 238 | 00:00 | 226 | 14:00
| Bibiana | 237 | 19:00 | 228 | 14:00 | Mirsorai | 234 | 18:30 | 222 | 10:00
| BIPTC | 235 | 06:00 | 223 | 12:00 | Rajshahi | 235 | 06:00 | 224 | 14:00
| Bogura | 233 | 06:00 | 223 | 14:00 | Rampal | 236 | 06:00 | 222 | 14:00
| Bogura-400 | 234 | 06:00 | 226 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 07:00 | 240 | 14:00 | Rampura | 234 | 06:00 | 220 | 15:00
| BSRM | 234 | 18:30 | 223 | 11:00 | Shikalbaha | 229 | 18:30 | 218 | 15:00
| Cumilla(N) | 235 | 18:00 | 222 | 14:00 | Shyampur | 235 | 18:30 | 22 | 13:00
| Fenchuganj | 240 | 18:30 | 234 | 10:00 | Siddhirganj | 233 | 03:00 | 221 | 15:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 240 | 05:00 | 232 | 14:00
| Ghorashal-230 | 233 | 03:00 | 220 | 14:00 | Sreepur | 235 | 18:30 | 224 | 14:00
| GPH | 230 | 18:30 | 220 | 14:00 | Tongi | 230 | 04:00 | 216 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 01:00 | 127 | 14:00 | Lalbag | 137 | 18:30 | 125 | 15:00
| Agargaon | 139 | 06:00 | 129 | 14:00 | Lalmonirhat | 132 | 06:00 | 125 | 09:00
| Agrabad | 132 | 18:00 | 30 | 03:00 | Madanganj | 134 | 06:00 | 125 | 14:00
| AKS | 131 | 18:00 | 126 | 10:00 | Madaripur | 137 | 07:00 | 131 | 14:00
| Aminbazar | 135 | 01:00 | 125 | 14:00 | Madartek | 135 | 01:00 | 126 | 15:00
| Amnura | 134 | 01:00 | 125 | 12:00 | Madunaghat | 135 | 19:00 | 126 | 14:00
| Ashuganj | 141 | 18:30 | 136 | 13:00 | Magura | 137 | 06:00 | 125 | 14:00
| Bagerhat | 136 | 07:00 | 123 | 21:00 | Mahasthangarh | 134 | 02:00 | 128 | 12:00
| Bakulia | 134 | 18:30 | 127 | 14:00 | Manikganj | 135 | 01:00 | 124 | 12:00
| Banani | 136 | 01:00 | 127 | 14:00 | Maniknagar | 137 | 05:00 | 128 | 14:00
| Bangabhaban | 137 | 05:00 | 128 | 14:00 | Matarbari | 124 | 06:00 | 118 | 14:00
| Barapukuria | 139 | 05:00 | 133 | 11:00 | Matuail | 137 | 18:30 | 126.2 | 14:00
| Barguna | 135 | 06:00 | 127 | 21:00 | Millgate | 138 | 18:30 | 125 | 15:00
| Barishal | 160 | 00:00 | 125 | 14:00 | Mirpur | 135 | 02:00 | 124 | 14:00
| Barishal-230 | 140 | 02:00 | 134 | 14:00 | Mirzapur | 137 | 18:30 | 128 | 15:00
| Baroaulia | 134 | 18:00 | 127 | 14:00 | Mithapukur | 133 | 02:00 | 126 | 10:00
| Baroirhat | 134 | 18:30 | 122 | 15:00 | MI_Cement | 136 | 18:30 | 126 | 14:00
| Bashundhara | 138 | 18:30 | 125 | 15:00 | Modern | 133 | 18:00 | 127 | 13:00
| BashundharaCement | 134 | 06:00 | 125 | 14:00 | Mogbazar | 138 | 04:00 | 128 | 15:00
| Beanibazar | 137 | 21:00 | 128 | 15:00 | Mongla | 136 | 05:00 | 124 | 14:00
| Benapole | 135 | 06:00 | 121 | 14:00 | Motijheel | 137 | 05:00 | 128 | 14:00
| Bhaluka | 134 | 18:30 | 123 | 14:00 | Munshiganj | 137 | 18:30 | 126 | 14:00
| Bhandaria | 135 | 01:00 | 125 | 13:00 | Mymensingh | 139 | 18:00 | 121 | 00:00
| Bhangura | 138 | 02:00 | 131 | 12:00 | Naogaon | 133 | 04:00 | 125 | 14:00
| Bheramara | 136 | 06:00 | 128 | 14:00 | Narail | 137 | 06:00 | 124 | 21:00
| Bheramara(GK) | 136 | 06:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 126 | 18:30 | 115 | 12:00 | Narshingdi | 135 | 23:00 | 119 | 15:00
| Bog-Sherpur | 135 | 02:00 | 129 | 12:00 | Natore | 135 | 06:00 | 126 | 12:00
| Bogura | 136 | 05:00 | 129 | 14:00 | Nawabganj | 137 | 06:00 | 125 | 14:00
| Bogura-230 | 136 | 06:00 | 129 | 14:00 | Netrakona | 133 | 18:30 | 120 | 14:00
| Brahmanbaria | 135 | 23:00 | 124 | 15:00 | New | 137 | 01:00 | 127 | 14:00
| Cantonment | 138 | 06:00 | 129 | 14:00 | Niamatpur | 136 | 05:00 | 131 | 12:00
| Chandpur | 139 | 18:00 | 119 | 15:00 | Noapara | 138 | 05:00 | 125 | 14:00
| Chandraghona | 135 | 18:30 | 128 | 14:00 | Pabna | 138 | 06:00 | 128 | 12:00
| Chapai | 135 | 05:00 | 130 | 14:00 | Palashbari | 132 | 05:00 | 125 | 13:00
| Charsaidpur | 137 | 18:30 | 126 | 14:00 | Panchagarh | 132 | 06:00 | 121 | 13:00
| Chauddagram | 135 | 18:00 | 122 | 14:00 | Patuakhali | 134 | 05:00 | 129 | 23:00
| Chhatak | 136 | 21:00 | 129 | 15:00 | Payra | 136 | 06:00 | 131 | 14:00
| Chowmuhani | 132 | 18:00 | 118 | 15:00 | PHP | 133 | 18:30 | 12 | 05:00
| Chuadanga | 136 | 06:00 | 120 | 14:00 | Postogola | 135 | 18:00 | 127 | 14:00
| Coxsbazar | 126 | 07:00 | 118 | 00:00 | Purbachal | 138 | 18:30 | 125 | 15:00
| Cumilla(N) | 137 | 18:00 | 128 | 14:00 | Purbasadipur | 132 | 05:00 | 122 | 13:00
| Cumilla(S) | 138 | 18:30 | 123 | 15:00 | Rahanpur | 136 | 00:00 | 133 | 13:00
| Daudkandi | 135 | 23:00 | 119 | 14:00 | Rahim | 137 | 18:30 | 128 | 14:00
| Dhaka | 136 | 02:00 | 127 | 14:00 | Rajbari | 137 | 06:00 | 129 | 12:00
| Dhamrai | 139 | 18:30 | 128 | 14:00 | Rajendrapur | 138 | 18:30 | 128 | 16:00
| Dhanmondi | 138.6 | 18:30 | 127 | 14:00 | Rajshahi | 133 | 06:00 | 125 | 12:00
| Dohazari | 131 | 07:00 | 126 | 16:00 | Rajshahi-230 | 133 | 01:00 | 124 | 12:00
| Faridpur | 137 | 05:00 | 130 | 15:00 | Ramganj | 134 | 18:00 | 117 | 14:00
| Fatullah | 137 | 18:30 | 126 | 14:00 | Rampur | 132 | 08:00 | 126 | 14:00
| Fenchuganj | 137 | 21:00 | 131 | 15:00 | Rampura | 136 | 04:00 | 127 | 14:00
| Feni | 132 | 18:30 | 121 | 15:00 | Rangamati | 133 | 17:00 | 126 | 14:00
| Ghorashal | 140 | 18:00 | 134 | 11:00 | Rangpur | 132 | 05:00 | 125 | 14:00
| Goalpara | 138 | 01:00 | 127 | 21:00 | Ruppur | 137 | 01:00 | 130 | 14:00
| Gollamari | 139 | 06:00 | 128 | 14:00 | Saidpur | 133 | 06:00 | 123 | 09:00
| Gopalganj | 138 | 06:00 | 129 | 14:00 | Satkhira | 137 | 06:00 | 123 | 21:00
| Gopalganj-400 | 138 | 06:00 | 131 | 14:00 | Satmasjid | 139 | 18:30 | 128 | 14:00
| Gulshan | 135 | 02:00 | 127 | 14:00 | Savar | 134 | 06:00 | 122 | 14:00
| Halishahar | 134 | 02:00 | 126 | 14:00 | SevenRings | 140 | 01:00 | 132 | 14:00
| Haripur | 137 | 18:30 | 128 | 14:00 | ShahCement | 137 | 18:30 | 126 | 14:00
| HaripurSBU | 137 | 18:30 | 128 | 14:00 | Shahjadpur | 141 | 02:00 | 132 | 10:00
| Hasnabad | 135 | 02:00 | 128 | 14:00 | Shahjibazar | 135 | 23:00 | 125 | 16:00
| Hathazari | 136 | 18:30 | 129 | 10:00 | Shahmirpur | 134 | 18:30 | 129 | 10:00
| Ishurdi | 139 | 06:00 | 131 | 12:00 | Shariatpur | 138 | 06:00 | 130 | 14:00
| Jaldhaka | 133 | 06:00 | 124 | 10:00 | Sherpur | 138 | 18:00 | 113 | 16:00
| Jamalpur | 139 | 18:30 | 116 | 03:00 | Shikalbaha | 124 | 07:00 | 117 | 11:00
| Jashore | 136 | 06:00 | 123 | 14:00 | Shikalbaha-230 | 135 | 08:00 | 128 | 15:00
| Jhenaidah | 138 | 06:00 | 127 | 14:00 | Shitalakhya | 136 | 18:30 | 126 | 14:00
| Jhenaidah-230 | 138 | 06:00 | 127 | 12:00 | Sholosohor | 134 | 19:30 | 126 | 14:00
| Joydebpur | 140 | 05:00 | 127 | 15:00 | Shyampur | 135 | 04:00 | 127 | 13:00
| Joypurhat | 132 | 05:00 | 124 | 14:00 | Shyampur-230 | 137 | 18:30 | 126 | 14:00
| Juldah | 136 | 18:00 | 127 | 15:00 | Siddhirganj | 138 | 18:00 | 127 | 14:00
| Kabirpur | 141 | 18:30 | 120 | 14:00 | Sirajganj | 136 | 05:00 | 128 | 12:00
| Kachua | 139 | 18:00 | 121 | 14:00 | Sonargaon | 138 | 18:00 | 124 | 14:00
| Kaliakoir | 142 | 18:00 | 131 | 14:00 | Sreemongol | 134 | 21:00 | 126 | 15:00
| Kallyanpur | 136 | 02:00 | 129 | 13:00 | Sreepur | 134 | 18:30 | 127 | 14:00
| Kalurghat | 135 | 18:30 | 127 | 14:00 | Srinagar | 136 | 05:00 | 125 | 13:00
| Kamrangirchar | 136 | 02:00 | 125 | 14:00 | SSM | 138 | 18:00 | 132 | 14:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 21:00 | 129 | 14:00
| Kazla | 136 | 06:00 | 127 | 16:00 | Sylhet | 135 | 21:00 | 130 | 14:00
| Keranigonj | 137 | 06:00 | 125 | 14:00 | Sylhet-132 | 135 | 21:00 | 131 | 15:00
| Khagrachori | 133 | 18:00 | 126 | 14:00 | Tangail | 133 | 18:00 | 124 | 16:00
| Khulna | 138 | 05:00 | 127 | 14:00 | Thakurgaon | 132 | 06:00 | 121 | 13:00
| Khulna(S) | 139 | 06:00 | 129 | 14:00 | TK | 133 | 18:00 | 128 | 15:00
| Khulshi | 133 | 18:30 | 125 | 14:00 | Tongi | 139 | 06:00 | 35 | 23:00
| Kishoreganj | 137 | 20:00 | 127 | 14:00 | Ullahpara | 138 | 05:00 | 130 | 12:00
| Kodda | 138 | 22:00 | 125 | 15:00 | Ullon | 136 | 01:00 | 127 | 14:00
| KSRM | 134 | 18:30 | 127 | 22:00 | Uttara | 135 | 02:00 | 125 | 14:00
| Kulaura | 136 | 21:00 | 131 | 15:00 | UttaraNew | 137 | 01:00 | 125 | 15:00
| Kurigram | 131 | 06:00 | 123 | 03:00 | Zigatola | 137 | 18:30 | 124 | 14:00
| Kushtia | 136 | 05:00 | 127 | 14:00