## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-28 | Tuesday
|  | Date (day): | 2024-05-28 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11003.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13704 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-27 | 2024-05-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 110 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 308 | 340 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 90 | 90 |  |  | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 80 | 80 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 15 | 60 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 85 | 90 |  |  | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 100 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 0 | 0 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 115 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 17 | 50 | 55 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 53 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 968 | 1020 | 2708 | 3279 | 794 | 829
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 20 | 30 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 0 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 100 | 150 |  | 75 | ST Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 51 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 55 | 78 | 20 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 49 | 62 | 38 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 10 | 15
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 45 | 60 | 48 |  | fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 51 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 48 | 60 | 40 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 35 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 152
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 245 | 270 | 270 | 490 |  | 734 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 53 | 51 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 164 | 162 | 250 | 250
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 27 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 514 | 483 | 1405 | 1888 | 970 | 1178
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 109 | 200 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 300 | 310 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 315 | 330 | 330
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 35 | 36 | 9
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 50 | 50
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Gas shortage due to LND S/D.
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 12 | 50 | 100 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 39 | 40
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 0 | 50 | 80 |  | 83 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 100 | 155 | 45
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 16 | 18 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 52 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 50 | 50
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 497 | 442 | 1592 | 1880 | 387 | 499
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 32 | 45 | 70 | 132 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 0 | 58 | 105 | 95 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 0 | 57 | 100 | 15 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 5 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 39 | 32 | 223.6 | 287 | 132 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 0 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 0 | 60 | 60 |  | 30 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 80 | 112 |  |  | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 10 | 0 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 177 | 204 | 204 |  | 27 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 24 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 180 | 310 | 310 | 310 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 370 | 360 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 763 | 857 | 1237 | 1669 | 0 | 449
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 350 | 209 | 355 | 452
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 20 | 85
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 32 | 32
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 53 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 15 | 100
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 8 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 0 | 0 | 100 | 350
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 358 | 209 | 755 | 1211 | 1007 | 61
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 0 | 0 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 56 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 380 | 620 | 620
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 200 | 200
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 17 | 133 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 0 | 200 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 820 | 546 | 1177 | 1394 | 133 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 |  | 12 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 14 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Machine problem
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 330 | 336 | 414 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 50 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 50 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 816 | 479 | 748 | 748 |  |  | unit-1 under maint
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1146 | 815 | 1333 | 1654 | 243 | 290
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 220 | 220 |  | 54 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 70 | 107
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 115 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 57 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 218 | 150 | 573 | 442 | 40 | 139
| Total |  |  |  |  | 27054 | 25903 | 5323 | 4554 | 11003.6 | 13704 | 3706 | 3509
A. |  | 2024-05-27 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11828 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5271 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 4554 | MW
3 | Day peak Generation : |  |  | 5323 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 4252.51 | MW
4 | Evening peak Generation : |  |  | 4554 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 150.9104 | MKWHr | By Solar | 0.66728 | MKWHr
| By Gas : | 75.397 | MKWHr |  | By Oil: | 6.3051 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 53.2474 | MKWHr |  | By Hydro: | 0.29376 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 1.189 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3706 | MW | Dhaka | 2278.41 | 2278.41 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3509 | MW | Chittagong | 638.5 | 638.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7215 | MW | Khulna | 278.5 | 278.5 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 469.42 | MMCFD |  |  | Rajshahi | 314 | 314 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 230687905.01 | ii) Oil : | Taka | 113742605.07 | Comilla | 98 | 98 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 360947211.94 | Total | Taka | 705377722.02 | Mymensingh | 56 | 56 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7693.95 | MKWHr. | Sylhet | 160 | 160 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 336 | MW (W to E) at | 21:00 | hrs | Barisal | 21.1 | 21.1 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 260 | MW at | 24:00 | hrs | Rangpur | 408 | 408 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.1°C |  |  | Total | 4252.51 | 4252.51 |  | 0
B. |  | 2024-05-28 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13704 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 1704 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 153.1049 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 3651 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.2081 | MKWHr. | ii) HVDC Flow at Peak Time |  | 209 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 0.60288 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 71.64 |  | (b) Today: | 71.75 |  | (c) Rule Curve: |  | 76.8
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 151 | 0 | 0 | 30 | 289 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 20 | 23 | 33 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 64 | 68 | 12 | 44 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 240 | 204 | 0 | 90 | 20 | 5 | 0 | 0 | 0 | 45 | 8 | 0 | 0 | 32 | 17 | 74 | 72 | 0 | 0 | 0 | 40 | 60 | 21 | 10 | 0 | 0 | 53 | 0 | 0 | 206 | 0 | 0 | 0 | 310 | 8 | 3 | 0 | 15 | 0 | 0 | 78 | 0 | 98 | 0 | 46 | 96 | 15 | 365 | 68 | 17 | 17 | 0 | 51 | 17 | 68 | 71 | 45 | 60 | 345 | 70 | 0 | 162 | 22 | 0 | 17 | 0 | 114 | 17 | 215 | 17 | 0 | 490 | 34 | 765 | 0 | 0 | 0 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 36 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 0 | 63 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 350 | 0 | 0 | 35 | 0 | 105 | 0 | 0 | 35 | 760 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 374 | 0 | 150 | 1210 | 0 | 0 |  | 7139 | 4689 | 11828 | 3382 | 636 | 1554 | 0 | 1749 | 4042 | 30 | 0 | 327 | 74 | 0 | 34 | 183.36 | 71.65
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 150 | 0 | 0 | 30 | 287 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 21 | 23 | 33 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 55 | 51 | 0 | 29 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 240 | 204 | 0 | 80 | 20 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 32 | 17 | 66 | 72 | 0 | 0 | 0 | 40 | 60 | 31 | 10 | 0 | 0 | 55 | 0 | 0 | 205 | 0 | 0 | 0 | 280 | 8 | 3 | 0 | 0 | 0 | 0 | 77 | 0 | 38 | 0 | 46 | 68 | 13 | 365 | 68 | 17 | 17 | 0 | 52 | 0 | 34 | 34 | 9 | 48 | 345 | 53 | 0 | 162 | 17 | 0 | 17 | 0 | 50 | 17 | 215 | 17 | 0 | 490 | 45 | 767 | 0 | 0 | 0 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 350 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 700 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 380 | 0 | 150 | 1199 | 0 | 0 |  | 6641 | 4309 | 10950 | 3332 | 636 | 1494 | 0 | 1175 | 3980 | 30 | 0 | 192 | 66 | 0 | 45 | 143.25 | 71.65
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 150 | 0 | 0 | 30 | 282 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 21 | 23 | 33 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 55 | 34 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 240 | 212 | 0 | 80 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 17 | 40 | 72 | 0 | 0 | 0 | 40 | 60 | 31 | 10 | 0 | 0 | 62 | 0 | 0 | 205 | 0 | 0 | 0 | 295 | 8 | 3 | 0 | 0 | 0 | 0 | 77 | 0 | 34 | 0 | 12 | 34 | 0 | 401 | 69 | 17 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 12 | 345 | 17 | 0 | 54 | 17 | 0 | 17 | 0 | 10 | 17 | 215 | 0 | 0 | 490 | 18 | 669 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 690 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 150 | 891 | 0 | 0 |  | 6008 | 3793 | 9801 | 3375 | 891 | 1509 | 0 | 650 | 3183 | 30 | 0 | 105 | 40 | 0 | 18 | 123.195 | 71.65
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 388 | 0 |  | 0 | 350 | 150 | 0 | 0 | 15 | 282 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 | 33 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 23 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 240 | 213 | 0 | 80 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 5 | 28 | 72 | 0 | 0 | 0 | 40 | 60 | 31 | 10 | 0 | 0 | 62 | 0 | 0 | 205 | 0 | 0 | 0 | 305 | 8 | 3 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 12 | 0 | 0 | 316 | 45 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 12 | 315 | 16 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 215 | 0 | 0 | 490 | 42 | 350 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 350 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 690 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 150 | 817 | 0 | 0 |  | 5136 | 3746 | 8882 | 3231 | 919 | 1419 | 0 | 383 | 2791 | 30 | 0 | 39 | 28 | 0 | 42 | 0 | 71.64
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 316 | 0 |  | 0 | 350 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 33 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 240 | 214 | 0 | 80 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 30 | 72 | 0 | 0 | 0 | 40 | 60 | 31 | 10 | 0 | 0 | 61 | 0 | 0 | 205 | 0 | 0 | 0 | 285 | 8 | 3 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 450 | 54 | 334 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 270 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 814 | 0 | 0 |  | 4645 | 3411 | 8056 | 3090 | 919 | 1319 | 0 | 52 | 2592 | 0 | 0 | 0 | 30 | 0 | 54 | 0 | 71.64
6:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 297 | 0 |  | 0 | 330 | 117 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 152 | 0 | 80 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 72 | 0 | 0 | 0 | 40 | 60 | 10 | 10 | 0 | 0 | 40 | 0 | 0 | 190 | 0 | 0 | 0 | 270 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 300 | 53 | 230 | 0 | 0 | 1 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 140 | 813 | 1 | 0 |  | 3774 | 3301 | 7075 | 2628 | 921 | 1192 | 0 | 0 | 2248 | 0 | 0 | 0 | 30 | 3 | 53 | 0 | 71.64
7:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 280 | 0 |  | 0 | 300 | 110 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 152 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 72 | 0 | 0 | 0 | 40 | 60 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 190 | 0 | 0 | 0 | 240 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 54 | 224 | 0 | 0 | 0 |  | 587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 160 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 140 | 813 | 13 | 0 |  | 3422 | 2882 | 6304 | 2358 | 587 | 1050 | 0 | 0 | 2221 | 0 | 0 | 0 | 14 | 20 | 54 | 0 | 71.63
8:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 280 | 0 |  | 0 | 200 | 110 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 151 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 190 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 270 | 53 | 186 | 0 | 0 | 2 |  | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 160 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 140 | 818 | 27 | 0 |  | 3031 | 2522 | 5553 | 2211 | 302 | 780 | 0 | 0 | 2139 | 0 | 0 | 0 | 20 | 48 | 53 | 0 | 71.63
9:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 264 | 0 |  | 0 | 220 | 110 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34 | 0 | 0 | 0 | 34 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 144 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 265 | 46 | 163 | 0 | 0 | 9 |  | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 20 | 140 | 814 | 22 | 0 |  | 2707 | 2564 | 5271 | 1754 | 452 | 820 | 0 | 0 | 2095 | 0 | 0 | 0 | 36 | 68 | 46 | 0 | 71.63
10:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 260 | 0 |  | 0 | 200 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 145 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 245 | 53 | 163 | 0 | 0 | 4 |  | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 500 | 160 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 10 | 140 | 814 | 25 | 0 |  | 2303 | 2604 | 4907 | 1355 | 482 | 832 | 0 | 0 | 2057 | 30 | 0 | 0 | 36 | 62 | 53 | 0 | 71.63
11:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 272 | 0 |  | 0 | 280 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 144 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 245 | 53 | 164 | 0 | 0 | 10 |  | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 110 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 140 | 815 | 55 | 0 |  | 2431 | 2459 | 4890 | 1393 | 350 | 960 | 0 | 0 | 2014 | 30 | 0 | 0 | 2 | 88 | 53 | 0 | 71.64
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 308 | 0 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 145 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 245 | 53 | 164 | 0 | 0 | 27 |  | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 520 | 110 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 140 | 816 | 57 | 0 |  | 2781 | 2542 | 5323 | 1636 | 350 | 1100 | 0 | 0 | 2035 | 25 | 0 | 0 | 16 | 108 | 53 | 0 | 71.64
13:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 370 | 0 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 145 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 255 | 53 | 163 | 0 | 0 | 21 |  | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 580 | 110 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 67 | 0 |  | 2958 | 2441 | 5399 | 1683 | 352 | 1180 | 0 | 0 | 1963 | 25 | 0 | 0 | 32 | 111 | 53 | 0 | 71.64
14:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 336 | 0 |  | 0 | 320 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 0 | 35 | 20 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 145 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 270 | 53 | 163 | 0 | 0 | 7 |  | 506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 110 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 9 | 0 | 818 | 57 | 0 |  | 2644 | 2465 | 5109 | 1503 | 506 | 1015 | 0 | 0 | 1921 | 25 | 0 | 0 | 6 | 80 | 53 | 0 | 71.64
15:00 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 273 | 0 |  | 0 | 230 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 35 | 20 | 0 | 0 | 20 | 0 | 20 | 0 | 0 | 144 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 250 | 53 | 160 | 0 | 0 | 7 |  | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 31 | 0 |  | 2240 | 2266 | 4506 | 1312 | 451 | 750 | 0 | 0 | 1876 | 0 | 0 | 0 | 16 | 48 | 53 | 0 | 71.65
16:00 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 231 | 0 |  | 0 | 200 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 144 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 240 | 53 | 161 | 0 | 0 | 3 |  | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 110 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 0 |  | 1995 | 1891 | 3886 | 1161 | 122 | 680 | 0 | 0 | 1854 | 0 | 0 | 0 | 8 | 8 | 53 | 0 | 71.65
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 240 | 0 |  | 0 | 200 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 234 | 54 | 162 | 0 | 0 | 1 |  | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531 | 0 | 0 |  | 1949 | 1802 | 3751 | 1102 | 307 | 696 | 0 | 0 | 1577 | 0 | 0 | 0 | 12 | 3 | 54 | 0 | 71.65
18:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 275 | 0 |  | 0 | 250 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 235 | 43 | 164 | 0 | 0 | 1 |  | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 450 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436 | 0 | 0 |  | 2142 | 1705 | 3847 | 1223 | 258 | 880 | 0 | 0 | 1435 | 0 | 0 | 0 | 6 | 2 | 43 | 0 | 71.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 300 | 0 |  | 0 | 250 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 240 | 50 | 163 | 0 | 0 | 0 |  | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 |  | 2240 | 1857 | 4097 | 1272 | 405 | 971 | 0 | 0 | 1383 | 0 | 0 | 0 | 16 | 0 | 50 | 0 | 71.69
19:30 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 300 | 0 |  | 0 | 250 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 238 | 50 | 165 | 0 | 0 | 0 |  | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 0 | 0 |  | 2368 | 1789 | 4157 | 1290 | 445 | 1107 | 0 | 0 | 1249 | 0 | 0 | 0 | 16 | 0 | 50 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 304 | 0 |  | 0 | 330 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 235 | 50 | 164 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 |  | 2588 | 1589 | 4177 | 1432 | 209 | 1217 | 0 | 0 | 1251 | 0 | 0 | 0 | 18 | 0 | 50 | 0 | 71.68
21:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 340 | 0 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 270 | 51 | 162 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 0 | 0 |  | 2834 | 1720 | 4554 | 1509 | 209 | 1326 | 0 | 0 | 1441 | 0 | 0 | 0 | 18 | 0 | 51 | 0 | 71.69
22:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 318 | 0 |  | 0 | 420 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 270 | 37 | 166 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 0 | 0 |  | 2717 | 1836 | 4553 | 1428 | 209 | 1313 | 0 | 0 | 1554 | 0 | 0 | 0 | 12 | 0 | 37 | 0 | 71.7
23:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 315 | 0 |  | 0 | 420 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 270 | 50 | 164 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 |  | 2703 | 1666 | 4369 | 1426 | 209 | 1271 | 0 | 0 | 1399 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 71.71
24:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 309 | 0 |  | 0 | 420 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 270 | 50 | 165 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 | 0 |  | 2674 | 1566 | 4240 | 1385 | 209 | 1288 | 0 | 0 | 1292 | 0 | 0 | 0 | 16 | 0 | 50 | 0 | 71.72
KWH | 0 | 0 | 0 | 3244500 | 0 | 0 | 0 | 7556400 | 0 |  | 0 | 7894000 | 3120640 | 0 | 0 | 126445 | 2404546 | 0 | 0 | 0 | 123696 | 71520 | 0 | 0 | 0 | 0 | 80640 | 197960 | 112895 | 0 | 104400 | 116000 | 302900 | 165500 | 0 | 0 | 77760 | 216000 | 0 | 0 | 0 | 1194491 | 0 | 0 | 0 |  | 59520 | 226368 | 175925 | 13680 | 73920 | 0 | 0 | 249600 | 0 | 0 | 0 | 0 | 1984000 | 3719000 | 0 | 941310 | 127224 | 31200 | 0 | 0 | 0 | 88432 | 27898 | 0 | 0 | 162900 | 65170 | 602880 | 1045440 | 0 | 0 | 0 | 607000 | 668040 | 152400 | 70632 | 45164 | 0 | 406080 | 0 | 0 | 4489090 | 0 | 0 | 0 | 5519500 | 45312 | 21168 | 0 | 82800 | 0 | 0 | 355200 | 0 | 234864 | 10260 | 115200 | 261120 | 33454 | 2964000 | 327600 | 81120 | 40982 | 0 | 215782 | 23915 | 137160 | 124260 | 82320 | 151680 | 7340900 | 191040 | 43590 | 486720 | 79036 | 0 | 83880 | 1276 | 208320 | 85680 | 5634000 | 30109 | 0 | 7510908 | 1188960 | 6407272 | 0 | 0 | 64818 |  | 13208080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474000 | 1542000 | 5954 | 0 | 0 | 0 | 0 | 53395 | 0 | 45184 | 0 | 0 | 48716 | 0 | 46904 | 0 | 0 | 0 | 642327 | 0 | 4203000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1319764 | 0 | 6779563 | 0 | 0 | 71520 | 0 | 295929 | 0 | 32726 | 43392 | 13909300 | 3357164 | 0 | 0 | 0 | 67680 | 414912 | 0 | 0 | 872727 | 54866 | 1789100 | 17912727 | 392060 | 0 |  | 83327372 | 67582990 | 150910362 | 48171135 | 13208080 | 27225817 | 0 | 5518540 | 53247361 | 293760 | 0 | 786553 | 602880 | 667276 | 1188960 | 0
Fuel Cost | 0 | 0 | 0 | 14438025 | 0 | 0 | 0 | 21762432 | 0 |  | 0 | 25102920 | 10672588.8 | 0 | 0 | 2227960.9 | 7333865.3 | 0 | 0 | 0 | 2220343.2 | 1388918.4 | 0 | 0 | 0 | 0 | 1472486.4 | 3119849.6 | 2064849.55 | 0 | 78300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3810426.29 | 0 | 0 | 0 |  | 1046956.8 | 3986340.48 | 3150816.75 | 260740.8 | 1446614.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6071040 | 12347080 | 0 | 3040431.3 | 428744.88 | 136656 | 0 | 0 | 0 | 1583817.12 | 503837.88 | 0 | 0 | 605988 | 48877.5 | 3954892.8 | 3251318.4 | 0 | 0 | 0 | 2367300 | 2491789.2 | 693420 | 321375.6 | 154460.88 | 0 | 2253744 | 0 | 0 | 12524561.1 | 0 | 0 | 0 | 17055255 | 33984 | 16087.68 | 0 | 1689120 | 0 | 0 | 6823392 | 0 | 4135955.04 | 0 | 2051712 | 4530432 | 554667.32 | 7854600 | 6244056 | 1521811.2 | 735217.08 | 0 | 3528035.7 | 464907.6 | 2460650.4 | 2374608.6 | 1597831.2 | 2701420.8 | 19526794 | 3261052.8 | 0 | 8902108.8 | 1326224.08 | 0 | 1498935.6 | 0 | 3753926.4 | 1451419.2 | 16732980 | 423934.72 | 0 | 52351028.76 | 0 | 37802904.8 | 0 | 0 | 0 |  | 37114704.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8437200 | 4872720 | 28221.96 | 0 | 0 | 0 | 0 | 956304.45 | 0 | 759543.04 | 0 | 0 | 872503.56 | 0 | 840050.64 | 0 | 0 | 0 | 7084866.81 | 0 | 35473320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4394814.12 | 0 | 19796323.96 | 0 | 0 | 1417526.4 | 0 | 5894905.68 | 0 | 0 | 860897.28 | 90132264 | 10440780.04 | 0 | 0 | 0 | 0 | 7198723.2 | 0 | 0 | 6370907.1 | 0 | 13328795 | 118403125.47 | 0 | 0 |  | 371768822.11 | 374678497.51 | 746447319.62 | 146285902.77 | 37114704.8 | 84402002.24 | 0 | 99780375.91 | 360947211.94 | 0 | 0 | 13962229.16 | 3954892.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 308 | 0 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 145 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 245 | 53 | 164 | 0 | 0 | 27 |  | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 520 | 110 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 140 | 816 | 57 | 0 |  | 5323 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 340 | 0 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 270 | 51 | 162 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 0 | 0 |  | 4554 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 300 | 90 | 80 | 55 | 330 | 0 | 0 | 90 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 78 | 85 | 70 | 60 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 310 | 220 | 0 | 80 | 36 | 50 | 0 | 0 | 0 | 40 | 52 | 0 | 0 | 32 | 20 | 151 | 70 | 0 | 0 | 0 | 42 | 60 | 50 | 42 | 112 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 310 | 24 | 5 | 0 | 300 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 155 | 50 | 400 | 100 | 50 | 51 | 0 | 52 | 35 | 110 | 114 | 75 | 60 | 360 | 72 | 0 | 162 | 53 | 0 | 50 | 0 | 115 | 35 | 330 | 152 | 0 | 490 | 40 | 250 | 0 | 0 |  |  | 452 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 42 | 60 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 25 | 90 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 113 | 100 | 107 | 0 | 0 | 113 | 620 | 200 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 350 | 0 | 307 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 90 | 80 | 55 | 100 | 0 | 0 | 85 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 100 |  | 0 | 0 | 0 | 12 | 55 | 51 | 70 | 45 | 6 | 0 | 10 | 0 | 0 | 0 | 0 | 300 | 200 | 0 | 50 | 35 | 50 | 0 | 0 | 0 | 39 | 25 | 0 | 0 | 32 | 20 | 146 | 45 | 0 | 0 | 1.6 | 42 | 60 | 50 | 42 | 80 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 310 | 24 | 5 | 0 | 300 | 0 | 0 | 58 | 0 | 115 | 20 | 49 | 100 | 12 | 0 | 57 | 17 | 51 | 5 | 52 | 35 | 51 | 52 | 36 | 48 | 360 | 53 | 50 | 162 | 35 | 0 | 50 | 35 | 115 | 17 | 330 | 54 | 0 | 270 | 40 | 250 | 0 | 0 | 70 |  | 355 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 50 | 15 | 70 | 0 | 8 | 50 | 620 | 200 |  | 17 | 6 | 100 | 115 | 0 | 0 | 100 | 30 | 200 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 450 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 9 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 335 | 0 | 0 | 255 | 50 | 165 | 0 | 0 | 9 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 110 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 11 | 0 | 443 | 60 | 0 | 0 |  |  |  | 75396952 | 13208080 | 0 | 53247361 | 6305093 | 602880 | 667276 | 1188960 | 293760 |  |  | 150910362
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 75.397 | 13.2081 | 0 | 53.2474 | 6.3051 | 0.60288 | 0.66728 | 1.189 | 0.29376
| Minimum Generation |  | 5271 | 9:00
| Highest Generation |  | 11828 | 1:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 150.9104
| Day Peak Generation |  | 5323 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 4554 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 921 | 6:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 209 | 21:00
| Load factor L.F |  | 53.16% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-28
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 5323 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 3651
Evening Peak Generation : |  |  | 4554 | MW Hour : | 21:00 | Available Max Generation : |  | 13704
E.P. Demand (at gen end) : |  |  | 4554 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 11828 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1704
Total Gen. (MKWH) : |  |  | 150.9104 | System Load Factor : | 53.16% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 260 | MW at | 24:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-28
Actual : |  | 71.75 | Ft.(MSL) , | Rule curve : | 76.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 469.42 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 230687905.01
: |  |  | Coal : | 360947211.94 | Oil : | 113742605.07 | Total : | 705377722.02
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 0 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:22 | - | Sirajgonj Unit-3 ST was shutdown due to low demand.
8:31 | - | Ashuganj South 360MW PP was shutdown due to low demand.
8:37 | - | Sirajgonj Unit-3 GT was shutdown due to low demand.
8:58 | 19:30 | Bogura 400/230kV S/S ATR-01 HT Project Work S/D Due to DFDR Commisioning work
9:11 | 9:28 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection 21/1: BN relays
Due to Strom
9:12 | - | Siddhirganj CCPP 335 MW ST was shutdown due to low demand.
9:17 | - | Siddhirganj CCPP 335 MW GT was shutdown due to low demand.
9:29 | - | Sikalbaha 225MW CCPP Tripped with remarks:- GT
9:34 | - | Bibiyana-3 400 MW ST was shutdown due to low demand.
9:36 | 18:32 | Cox'sbazar-Dohazari 132 kV Ckt-2 Forced S/D from Dohazari 132/33kV end Due to To reduce over voltage Level
9:37 | 18:37 | Dohazari-Sikalbaha 132 kV Ckt-2 Forced S/D from Dohazari 132/33kV end Due to To reduce over voltage level and from
Shikalbaha 230/132kVend.
9:50 | 10:33 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH B, Z 2. relays Due to Heavy Rainfall.
9:54 | 10:56 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing CBC Operated, Main Protection Relay Gen. Trip. relays Due to Over Voltage.
9:54 | 19:31 | Bogura 400/230kV S/S ATR-01 LT Project Work S/D Due to DFDR Commissioning Work
9:56 | 10:06 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection 21/1: BN relays Due to Strom
10:02 | 1:51 | Bashundhara-Tongi 132 kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance, B Phase relays Due to Heavy wind
10:05 | - | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end Due to Ordered By NLDC
10:05 | - | Chowmuhani-Ramganj 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end Due to Ordered By NLCD
10:07 | - | Bhola Nutan Biddyut GT-2 was shutdown due to low demand.
10:16 | 11:48 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Forced S/D
10:17 | 11:47 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Forced S/D Due to Connecting Auxiliary Transformer fuse.
- | 10:19 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
10:22 | - | Barapukuria TPP Unit-1 Shutdown
10:23 | 10:37 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF615 relays Due to 33KV kotbari & nangolkot feeder fault. |  |  |  |  | 30.0MW load interrup.
10:26 | - | Baghabari-Ishurdi 230 kV Ckt-1 Forced S/D from Baghabari 230/132kV end Due to Oder of ALDC and from Ishurdi 230/132kV
end Due to system voltage high
10:28 | - | Baghabari-Sirajganj 230 kV Ckt-1 Forced S/D from Baghabari 230/132kV end Due to Oder of ALDC and from Sirajgonj 230 end
Due to System Voltage over rated
10:32 | - | Madanganj 132/33kV S/S GT-2 LT Tripped showing O/C Blue phase relays Due to None
10:32 | 17:47 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Backup protection Trip relays Due to None
10:46 | 11:11 | Srinagar 132/33kV S/S Tr-02 LT Tripped showing Over current relay operated by 51 I>>T, 86K1 CB lockout relay-1 |  |  |  |  | 0.2MW load interrup.
operated. 86K1 CB lockout relay-2 operated. relays Due to 33KV Feeder-4 Bus Isolator Jumper Y Phase (Isolator Side) flashover
and disconnect from the clamp connector.
10:46 | 13:29 | Srinagar 132/33kV S/S Tr-01 LT Tripped showing Over current relay poerated by 51I>>T, K86-1 CB Lockout relay-1 |  |  |  |  | 0.2MW load interrup.
Operated K 86-2 CB Lockout-2 Relay operated relays Due to 33KV Feeder-4 Bus Isolator Jumper Y Phase (Isolator Side)
flashover and disconnect from the clamp connector.
10:50 | - | Bibiyana-3 400 MW GT tripped.
10:58 | 11:24 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance Relay, E/F relays Due to Cyclone Remal |  |  |  |  | 1.0MW load interrup. Barishal 132/33kV end
11:00 | - | Day peak Generation : 5323 MW
11:03 | - | Ruppur 132/11kV S/S TR-02 LT Project Work S/D Due to TR-2 of 11kv section maintenance by NESCO
11:04 | - | Ruppur 132/11kV S/S TR-02 HT Project Work S/D Due to TR-2 of 11kv section maintenance by NESCO
11:09 | 11:35 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Tripped showing CAT,CE relays Due to None
11:14 | 11:25 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing Dir O/C & E/F Relay relays Due to Trip |  |  |  |  | 5.0MW load interrup.
11:24 | 11:24 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing E/F, Distance, B phase, zone 1, 32km relays |  |  |  |  | 1.0MW load interrup. Barishal 132/33kV end
Due to Bad weather, Cyclone Rimal.
11:24 | 11:24 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance relay. E/F relays Due to Cyclone |  |  |  |  | 1.0MW load interrup. Barishal 132/33kV end
Remal. Bad weather.
11:57 | 12:45 | Madunaghat 132/33kV S/S TR-2(517T) LT Tripped showing REF:615 relays Due to 33 kV old Wasa Trip |  |  |  |  | 9.0MW load interrup.
12:09 | - | Barishal Electric 307 MW PS tripped.
- | 12:26 | Khulna (C) S/S TR-1 425T HT is restored.
- | 12:26 | Khulna (C) S/S TR-1 425T LT is restored.
12:49 | - | Kushiara 163 MW GT was sync.
12:50 | 13:13 | Chowmuhani 132/33kV S/S TR1 Forced S/D Due to 33 Kv PDB Control room station supply Transformer Read Pace Loop maintenence
13:07 | 13:31 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing MVAJ relays Due to 33 kv Anandabazar feeder loop fault |  |  |  |  | 3.0MW load interrup.
13:25 | 13:29 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection 21/1: Z1-CN relays Due to Strom
13:26 | 13:39 | Bakulia-Sikalbaha 132 kV Ckt-1 Forced S/D from Bakulia 132/33kV end Due to Removal of a long polyethene part from C.T at
Bak-Shk Ckt-01 diameter.
13:29 | 18:16 | Srinagar 132/33kV S/S Tr-01 HT Forced S/D Due to বিষয়: ৩৩ কেভি ফিডার-৪ এর বাস আইসোলেটর জাম্পার জরুরী সংরক্ষণ
কাজের জন্য ৩৩ কেভি বাস সেকশন এ সহ ১৩২/৩৩ কেভি ট্রান্সফরমার ১ সাটডাউন প্রদান
13:29 | 13:29 | Srinagar 132/33kV S/S Tr-01 LT Forced S/D Due to বিষয়: ৩৩ কেভি ফিডার-৪ এর বাস আইসোলেটর জাম্পার জরুরী সংরক্ষণ
কাজের জন্য ৩৩ কেভি বাস সেকশন এ সহ ১৩২/৩৩ কেভি ট্রান্সফরমার ১ সাটডাউন প্রদান
13:38 | 14:00 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance protection zone-1. relays Due to Distance
protection zone-1.
13:47 | - | Madaripur 132/33kV S/S T3-426T HT Tripped showing PRD relays.
13:47 | - | Madaripur 132/33kV S/S T3-426T LT Tripped showing PRD relays.
13:57 | 21:06 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Dist. Relay : zone-1, R & Y phase relays Due to Unknown
14:09 | 14:30 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection trip 21/Z1 relays
Due to Storm Remel.
14:10 | 14:32 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z 1, Dist. Send. relays Due to Heavy Rainfall.
14:14 | 18:13 | Maniknagar-Matuail 132kV Ckt-1 Tripped from Matuail 132/33kV end showing Distance relay and over current relay relays Due to Tripped
- | 14:17 | Gopalganj(N)-Madaripur 132kV Ckt-1 is restored.
14:18 | - | Candpur (Desh)- Chandpur 132kV Ckt-2 Tripped from Chandpur 132/33kV end showing Distance relay relays Due to Unknown
14:18 | 15:20 | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) Tripped showing Transformer protection relay Aux relay plug
operated relays Due to Unknown
14:20 | 15:44 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Forced S/D from Patuakhali 132/33kV end Due to Tree
14:21 | - | Candpur- Kachua 132kV Ckt-1 Tripped from Chandpur 132/33kV end showing Distance relay relays Due to Unknown
14:23 | 19:52 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance Relay: 1. zone-1 2. |  |  |  |  | 30.0MW load interrup. Siddhirganj 132/33kV end
ph-B 3. distance-12.3km relays Due to Cyclone Remal
14:30 | 14:52 | Bogura-Sirajganj 230 kV Ckt-1 Forced S/D from Sirajgonj 230 end Due to Emergency Tree Trimming
14:32 | 21:07 | Fatullah 132/33kV S/S 132 kV Hasnabad Tripped showing Main1 general trip Dist. Zone1 trip. relays Due to deu to Tropical Cyclone Remal
14:40 | 20:48 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOm P441: PH Y, Z 1, Dist. Send. relays Due to Heavy Rainfall.
14:45 | 19:06 | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing Distance relay operate relays Due to Zone 1 trip 3.7 km B-Phase Pickup SOTF trip
14:50 | 15:49 | Bogura-Sirajganj 230 kV Ckt-1 Forced S/D from Bogura 230/132kV end.
14:57 | 16:40 | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to Requested to Desh Energy power plant authority
14:58 | 7:12 | Bagerhat-Mongla 132 kV Ckt-1 Forced S/D from Mongla 132/33kV end Due to Request from ALDC
15:05 | 15:16 | Bashundhara-Rampura 132 kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance protection trip 21/1( Z1-BN) relays
Due to Storm Remel
15:05 | 17:40 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing Line distance protection, 86A/B, General trip, Over Voltage Trip relays
Due to Bad weather
15:05 | 15:10 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection trip 21/1( Z1-BN) relays
Due to Storm Remel.
15:12 | 18:12 | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing Over voltage trip relays Due to Over voltage trip |  |  |  |  | 14.0MW load interrup.
15:12 | 22:50 | Ashuganj-Kishoreganj 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end.
15:12 | 22:50 | Ashuganj-Kishoreganj 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end.
15:15 | 22:45 | Kishoreganj-Mymensingh 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing distance relay relays Due to O/V
15:18 | 22:59 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Satkhira 132/33kV end showing no relays Due to ঘূর্ণিঝড় রিমাল এর কারনে ভোল্টেজ
কন্ট্রোল করার জন্য এলডিসি খুলনার নির্দেশে ট্রিপ করিয়ে রাখা হয়। and from Khulna(S) 230/132kV end Due to According to ALDC
instruction ( For high Voltage).
15:22 | 1:43 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance protection trip 21/1( Z1-CN) relays
Due to Storm Remel.
15:22 | 16:31 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Tripped showing Multilin relays Due to Over voltage
15:22 | 16:32 | Siddhirganj 230/132kV S/S 335MW EGCB 2 Tripped showing Multilin relays Due to Over Voltage
15:23 | 7:16 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Forced S/D from BIPTC end Due to As per ALDC instruction. and from
Jhenaidah 230/132kV end Due to For reducing the voltage.
15:24 | 7:20 | Jhenaidah-Khulna 230kV Ckt-1 Forced S/D from Jhenaidah 230/132kV end Due to For Reducing the Voltage and from
Khulna(S) 230/132kV end Due to According to ALDC instruction ( For high Voltage).
15:32 | 15:55 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D
15:35 | 7:23 | Bheramara 230/132kV S/S Transformer-1 LT Forced S/D Due to voltage risen
15:35 | 7:24 | Bheramara 230/132kV S/S Transformer-1 HT Forced S/D Due to voltage risen
15:40 | 17:01 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kv Anandabazar feeder raiser loop change under T2 bus section
15:40 | 17:01 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to 33 kv Anandabazar feeder raiser loop change under T2 bus section
15:44 | 17:20 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing distance relay relays Due to O/V
15:44 | 17:07 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance Protection Relay Operated, Zone-2,
Distance 19.3km. relays Due to Distance Protection Relay Operated, Zone-2, Distance 19.3km.
- | 15:44 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt is restored.
15:45 | - | Aminbazar-Meghnaghat 400kV Ckt-1 Forced S/D from Meghnaghat 400/230kV end.
15:48 | - | Madunaghat-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end. |  |  |  |  | 23.0MW load interrup. Meghnaghat 400/230kV end
15:53 | 16:03 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance relay zone ABC relays Due to Cyclone Remal
- | 15:55 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
15:55 | 7:12 | Bagerhat-Mongla 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Recommend of ALDC Khulna
15:58 | - | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Forced S/D from Bogura 230/132kV end Due to Only CB Open .
16:01 | 16:09 | Bagerhat-Goalpara 132 kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to Instraction of aldc and from Bagerhat 132/33kV
end Due to Recommend of ALDC Khulna.
16:07 | 16:14 | Goalpara-Labanchura 132kV Ckt-2 Forced S/D from Goalpara 132/33kV end Due to Instraction of ALDC
16:09 | 17:06 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Didtance relay zone :ABC relays Due to Cyclone Remal
16:11 | - | HVDC Bheramera- Rajshahi 230kV Ckt-1 Forced S/D from BIPTC end Due to instructed by NLDC
16:11 | - | HVDC Bheramera- Rajshahi 230kV Ckt-2 Forced S/D from BIPTC end Due to Instructed by NLDC.
16:12 | 7:06 | Bagerhat-Labanchura 132 kV Ckt-2 Forced S/D from Bagerhat 132/33kV end Due to Recommend of ALDC Khulna
16:12 | 19:34 | Sirajganj-Ullahpara 132KV Ckt-1 Tripped from Ullahpara 132/33kV end showing REL 650, REL 670 relays. and from
Sirajganj 132/33kV end showing RP Signal:1. 21 Distance Relay C-phase, 2. SOTF, 3. 79 A/R relays Due to the cyclone Romal,
a tree fell on the line from a distance.
16:17 | - | Haripur-Meghnaghat 230kV Ckt-2 Forced S/D from Haripur 230/132kV end Due to Line DS (B phase) shaft displacement.
16:20 | 19:35 | Sirajganj-Ullahpara 132KV Ckt-2 Forced S/D from Ullahpara 132/33kV end Due to Removal of trees Sirajganj Line 1
16:21 | 16:42 | Chowmuhani-Ramganj 132 kV Ckt-1 Tripped from Chowmuhani 132/33kV end showing Distance Relay A,B&C Distance
Relay3Ph relays Due to Tripped.
16:43 | 17:08 | Baroaulia-KSRM 132 kV Ckt-1 Tripped from KSRM 132/33kV end showing k34 & k35 relays Due to Earth Fault & Over current
16:46 | 17:54 | Chowmuhani-Ramganj 132 kV Ckt-1 Tripped from Chowmuhani 132/33kV end showing Distance Relay A,B&C Distance
Relay3Ph relays Due to Tripped.
16:48 | 19:31 | Sirajganj-Ullahpara 132KV Ckt-2 Forced S/D from Sirajganj 132/33kV end Due to cyclone Romal, a tree fell on the line from a
distance to Ullahpara ckt-1 for tree trimming clearance Ullahpara ckt-2 has taken shutdown.
17:19 | 21:06 | Fatullah-Shyampur(New) 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing Main1 general trip Comm. Distance
Carrier send Dist. Zone1 trip. relays Due to Due to Tropical Cyclone Remal
17:27 | 18:07 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing distance relay relays Due to O/V
17:27 | 23:08 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance trip , Z-1, Phase: ABC 0.5 KM Distance. |  |  |  |  | 13.0MW load interrup. Siddhirganj 132/33kV end

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 3244500 | Bad weather
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 340 | 7556400 | Bad weather
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 7894000 | Bad weather
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Bad weather
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3120640 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Bad weather
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 126445 | Bad weather
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Bad weather
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0 | Bad weather
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2404546 | Bad weather
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 123696 | Bad weather
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 80640 | Bad weather
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 71520 | Bad weather
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 197960 | Bad weather
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 112895 | Bad weather
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 0 | 220400 | Bad weather
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 302900 | Bad weather
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 165500 | Bad weather
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 82800 | Bad weather
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 234864 | Bad weather
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 81120 | Bad weather
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 191040 | Bad weather
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 486720 | Bad weather
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 1276
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 85680 | Bad weather
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Bad weather
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | Bad weather
| Dhaka area Total |  |  |  | 5332 | 1020 | 26785542
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Bad weather
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Bad weather
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 10260
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Bad weather
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 0 | 293760 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 1194491 | Bad weather
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 40982 | Bad weather
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 226368 | Bad weather
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 175925 | Bad weather
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 13680 | Bad weather
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 115200 | Bad weather
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Bad weather
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 249600 | Bad weather
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 73920 | Bad weather
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 0
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 215782 | Bad weather
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 23915 | Bad weather
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 137160 | Bad weather
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 151680 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 79036 | Bad weather
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 30109 | Bad weather
60 | SS Power I |  | SS Power | 2*612 | 1224 | 270 | 7510908 | Bad weather
| Cox's Bazar Wind |  | IPP | 66 | 60 | 51 | 1188960 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 162 | 6407272 | Bad weather
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 64818
| Chattogram area Total |  |  |  | 4404 | 483 | 18203826
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 109 | 3719000 | Bad weather
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 1984000 | Bad weather
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 315 | 5634000 | Bad weather
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 127224 | Bad weather
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 31200 | Bad weather
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Bad weather
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Bad weather
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 33454 | Bad weather
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 88432 | Bad weather
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 941310 | Bad weather
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 261120 | Bad weather
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Bad weather
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 18 | 602880
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 162900 | Bad weather
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 27898 | Bad weather
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 65170 | Bad weather
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 124260 | Bad weather
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 82320 | Bad weather
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 83880 | Bad weather
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 208320 | Bad weather
| Cumilla Area Total |  |  |  | 2929 | 442 | 14177368
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 1045440 | Bad weather
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 0
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 355200 | Bad weather
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 327600 | Bad weather
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 43590
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 59520 | Bad weather
| Mymensingh Area Total |  |  |  | 592 | 32 | 1831350
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 607000 | Bad weather
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 668040 | Bad weather
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 45164 | Bad weather
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 152400 | Bad weather
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 70632 | Bad weather
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 21168 | Bad weather
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 406080
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Bad weather
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4489090 | Bad weather
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 45312 | Bad weather
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 5519500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 2964000 | Bad weather
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 370 | 7340900 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 857 | 22329286
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Bad weather
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 209 | 13208080 | Bad weather
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Bad weather
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Bad weather
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Bad weather
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Bad weather
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 474000 | Bad weather
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Bad weather
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Bad weather
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 67680
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 0 | 872727
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 209 | 14622487
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Bad weather
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 0 | 5954
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 56 | 1542000 | Bad weather
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 380 | 13909300 | Bad weather
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 3357164 | Bad weather
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Bad weather
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 1789100 | Bad weather
| Barisal Area Total |  |  |  | 2235 | 546 | 20603518
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 53395 | Bad weather
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Bad weather
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Bad weather
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 48716 | Bad weather
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 1319764 | Bad weather
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 336 | 6779563 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 46904 | Bad weather
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Bad weather
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 45184 | Bad weather
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 71520 | Bad weather
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 43392 | Bad weather
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 0
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 479 | 17912727 | Bad weather
| Rajshahi Area Total |  |  |  | 3431 | 815 | 26321165
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 642327
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 4203000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 295929 | Bad weather
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32726
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 414912 | Bad weather
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 54866
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 392060
| Rangpur Area Total |  |  |  | 950 | 150 | 6035820
| Total |  |  |  | 25903 | 4554 | 150910362
| Eastern Grid Total |  |  |  | 15588 | 2834 | 83327372
| Western Grid Total |  |  |  | 10315 | 1720 | 67582990
| National Grid Total |  |  |  | 25903 | 4554 | 150910362
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-27
| (a) ENTIRE EASTERN GRID : |  | 3230.91 | MW | (b) ENTIRE WESTERN GRID : |  | 1021.6 | MW
| i) Dhaka area |  | 2278.41 | MW | i) Khulna area |  | 278.5 | MW
| ii) Chittagong area |  | 638.5 | MW | ii) Rajshahi area |  | 314 | MW
| iii) Comilla area |  | 98 | MW | iii) Barisal area |  | 21.1 | MW
| iv) Mymensingh area |  | 56 | MW | iv) Rangpur area |  | 408 | MW
| v) Sylhet area |  | 160 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 4252.51 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 16 | 13:00 | Chhatak | 27 | 02:00 | Kalurghat | 28 | 00:00 | Narail | 7 | 00:00 | Shariatpur | 32 | 00:00
2 | AKSML | 10 | 07:00 | Chowmuhani | 141 | 00:00 | Kamrangirchar | 53.2 | 12:00 | Narinda | 34 | 12:00 | Sherpur | 100 | 03:00
3 | Aftabnagar | 38 | 00:00 | Chuadanga | 97 | 00:00 | Kaptai | N/A | N/A | Narshingdi | 151 | 01:00 | Shikalbaha | 23 | 00:00
4 | Agargaon | 97 | 12:00 | Coxsbazar | 88 | 21:00 | Kazla | 102 | 00:00 | Natore | 142 | 00:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 76 | 14:00 | Cumilla(N) | 158 | 01:00 | Keranigonj | 73 | 00:00 | Nawabganj | 42.6 | 00:00 | Shitalakhya | 81.6 | 00:00
6 | Amnura | 65 | 02:00 | Cumilla(S) | 153 | 01:00 | Khagrachori | 26 | 00:00 | Netrakona | 121 | 00:00 | Sholosohor | 33 | 00:00
7 | Ashuganj | 84 | 00:00 | Daudkandi | 118 | 00:00 | Khulna | 73 | 13:00 | New | 53.8 | 12:00 | Shyampur | 156 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 42 | 13:00 | Khulshi | 168 | 00:00 | Niamatpur | 66 | 01:00 | Siddhirganj | 110 | 00:00
9 | BSRM | 184 | 18:00 | Dhamrai | 118 | 00:00 | Kishoreganj | 134 | 01:00 | Noapara | 13 | 17:00 | Sirajganj | 92 | 00:00
10 | Bagerhat | 2.5 | 19:30 | Dhanmondi | 135.8 | 13:00 | Kodda | 256 | 00:00 | PHP | 6 | 03:00 | Sonargaon | 73 | 01:00
11 | Bakulia | 94 | 19:30 | Dohazari | 78 | 00:00 | Kulaura | 42 | 00:00 | Pabna | 119 | 00:00 | Sreemongol | 67 | 00:00
12 | Banani | 34 | 13:00 | Faridpur | 103 | 00:00 | Kurigram | 50 | 01:00 | Palashbari | 116 | 01:00 | Sreepur | 59 | 00:00
13 | Bangabhaban | 14 | 10:00 | Fatullah | 62 | 00:00 | Kushtia | 122 | 00:00 | Panchagarh | 60 | 00:00 | Srinagar | 40 | 00:00
14 | Barapukuria | 69 | 00:00 | Fenchuganj | 40 | 00:00 | Lalbag | 91 | 12:00 | Patuakhali | 4 | 22:00 | Sunamganj | 37 | 02:00
15 | Barguna | 0 | 00:00 | Feni | 98 | 00:00 | Lalmonirhat | 43 | 01:00 | Payra | 6 | 00:00 | Sylhet | 42 | 01:00
16 | Barishal | 46 | 00:00 | GPH | 10 | 10:00 | MI_Cement | 10.4 | 00:00 | Postogola | 51 | 00:00 | Sylhet-132 | 114 | 01:00
17 | Barishal-230 | 0 | 00:00 | Ghatail | 32 | 01:00 | Madanganj | 25 | 00:00 | Purbachal | 20 | 00:00 | TK | 27.5 | 00:00
18 | Baroaulia | 63 | 02:00 | Ghorashal | 34 | 01:00 | Madaripur | 42 | 00:00 | Purbasadipur | 154 | 00:00 | Tangail | 161 | 00:00
19 | Baroirhat | 53 | 00:00 | Goalpara | 15 | 05:00 | Madartek | 78.02 | 01:00 | Rahim | 42 | 00:00 | Thakurgaon | 122 | 00:00
20 | Bashundhara | 172 | 00:00 | Gollamari | 20 | 19:30 | Madunaghat | 46 | 00:00 | Rajbari | 60 | 00:00 | Tongi | 122 | 00:00
21 | BashundharaCement | 0 | 00:00 | Gopalganj | 7.6 | 01:00 | Magura | 38 | 00:00 | Rajendrapur | 106 | 00:00 | Ullahpara | 32 | 00:00
22 | Beanibazar | 50 | 02:00 | Gulshan | 108 | 12:00 | Mahasthangarh | 82 | 01:00 | Rajshahi | 140 | 00:00 | Ullon | 59 | 00:00
23 | Benapole | 12 | 18:30 | Halishahar | 68 | 19:00 | Manikganj | 113 | 00:00 | Rajshahi-230 | 65 | 00:00 | Uttara | 62 | 12:00
24 | Bhaluka | 124 | 00:00 | HaripurSBU | 149 | 01:00 | Maniknagar | 66 | 13:00 | Ramganj | 90 | 00:00 | UttaraNew | 31 | 00:00
25 | Bhandaria | 0 | 00:00 | Hasnabad | 91 | 00:00 | Matarbari | 28 | 00:00 | Rampur | 37 | 00:00 | Zigatola | 78 | 00:00
26 | Bhangura | 32 | 00:00 | Hathazari | 76 | 00:00 | Matuail | 68 | 00:00 | Rangamati | 11 | 00:00
27 | Bheramara(GK) | 59 | 00:00 | Ishurdi | 70 | 00:00 | Millgate | 107 | 09:00 | Rangpur | 145 | 00:00
28 | Bhulta | 226 | 02:00 | Jaldhaka | 52 | 01:00 | Mirpur | 131 | 00:00 | Ruppur | 5.2 | 10:00
29 | Bog-Sherpur | 60 | 03:00 | Jamalpur | 100 | 04:00 | Mirsorai | 3 | 00:00 | SSM | 3 | 13:00
30 | Bogura | 136 | 04:00 | Jashore | 52 | 14:00 | Mirzapur | 42 | 00:00 | Saidpur | 87 | 03:00
31 | Borhanuddin | 4 | 00:00 | Jhenaidah | 82 | 00:00 | Mithapukur | 60 | 02:00 | Satkhira | 20 | 23:00
32 | Brahmanbaria | 169 | 00:00 | Joydebpur | 177 | 01:00 | Modern | 0 | 00:00 | Satmasjid | 101 | 00:00
33 | Cantonment | 130 | 00:00 | Joypurhat | 64 | 00:00 | Mogbazar | 106.2 | 12:00 | Savar | 175 | 00:00
34 | Chandpur | 62 | 00:00 | Juldah | 21 | 00:00 | Mongla | 3 | 21:00 | SevenRings | 6.87 | 15:00
35 | Chandraghona | 33 | 00:00 | KSRM | 52 | 22:00 | Motijheel | 39 | 12:00 | ShahCement | 22 | 01:00
36 | Chapai | 58 | 22:00 | Kabirpur | 271 | 00:00 | Munshiganj | 94 | 00:00 | Shahjadpur | 67 | 00:00
37 | Charsaidpur | 38 | 00:00 | Kachua | 70 | 00:00 | Mymensingh | 218 | 02:00 | Shahjibazar | 132 | 00:00
38 | Chauddagram | 74 | 00:00 | Kallyanpur | 111 | 00:00 | Naogaon | 128 | 01:00 | Shahmirpur | 45 | 00:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 416 | 16:00 | 371 | 00:00 | Kaliakoir | 375 | 04:00 | 364 | 00:00
| Ashuganj | 425.9 | 19:21 | 385.3 | 0:47 | Madunaghat_I | 408 | 10:00 | 397 | 07:00
| Bhulta | 418 | 15:00 | 382 | 00:00 | Meghnaghat | 401 | 16:00 | 364 | 00:00
| Bibiana | 419 | 18:30 | 390 | 00:00 | Payra | 419 | 16:00 | 404 | 00:00
| BIPTC | 412 | 09:00 | 398 | 04:00 | Rahanpur | 415 | 07:00 | 393 | 00:00
| Bogura | 411 | 17:00 | 383 | 00:00 | Rampal | 417 | 15:00 | 388 | 03:00
| Gopalganj | 418 | 16:00 | 387 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 245 | 16:00 | 219 | 00:00 | Hasnabad | 247 | 16:00 | 221 | 00:00
| AKSML | 240 | 22:00 | 224 | 02:00 | Hathazari | 240 | 09:00 | 230 | 00:00
| Aminbazar | 242 | 15:00 | 220 | 00:00 | Ishurdi | 248 | 16:00 | 228 | 03:00
| Ashuganj | 247 | 16:00 | 225 | 00:00 | Jhenaidah | 246 | 16:00 | 225 | 00:00
| Ashuganj-400 | 247 | 16:00 | 225 | 00:00 | Kaliakoir | 227 | 04:00 | 220 | 00:00
| Baghabari | 243 | 15:00 | 225 | 00:00 | Keranigonj | 245 | 16:00 | 219 | 00:00
| Barapukuria | 225 | 16:00 | 212 | 00:00 | Khulna(S) | 245 | 16:00 | 227 | 00:00
| Barapukuria-230 | 225 | 16:00 | 212 | 00:00 | Madunaghat_I | 240 | 09:00 | 230 | 03:00
| Barishal | 242 | 17:00 | 232 | 00:00 | Maniknagar | 245 | 16:00 | 219 | 00:00
| Bheramara | 248 | 16:00 | 226 | 03:00 | Meghnaghat | 250 | 16:00 | 230 | 00:00
| Bhulta | 245 | 16:00 | 220 | 00:00 | Meghnaghat-400 | 247 | 16:00 | 224 | 00:00
| Bibiana | 239 | 17:00 | 222 | 00:00 | Mirsorai | 244 | 17:00 | 225 | 00:00
| BIPTC | 249 | 15:00 | 228 | 03:00 | Rajshahi | 249 | 16:00 | 227 | 03:00
| Bogura | 236 | 16:00 | 220 | 00:00 | Rampal | 241 | 15:00 | 224 | 03:00
| Bogura-400 | 237 | 16:00 | 221 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 14:00 | 236 | 00:00 | Rampura | 242 | 16:00 | 218 | 00:00
| BSRM | 239 | 12:00 | 225 | 03:00 | Shikalbaha | 238 | 10:00 | 226 | 19:00
| Cumilla(N) | 245 | 16:00 | 224 | 00:00 | Shyampur | 246 | 16:00 | 137 | 14:00
| Fenchuganj | 243 | 17:00 | 225 | 00:00 | Siddhirganj | 247 | 16:00 | 222 | 00:00
| Ghorashal | 248 | 15:00 | 230 | 00:00 | Sirajgonj | 246 | 16:00 | 232 | 00:00
| Ghorashal-230 | 246 | 16:00 | 220 | 00:00 | Sreepur | 245 | 16:00 | 222 | 00:00
| GPH | 239 | 10:00 | 227 | 03:00 | Tongi | 243 | 16:00 | 215 | 00:00
| Haripur | 244 | 15:00 | 220 | 00:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 141 | 07:00 | 131 | 00:00 | Kushtia | 143 | 07:00 | 130 | 00:00
| Agargaon | 143 | 16:00 | 130 | 13:00 | Lalbag | 140 | 05:00 | 131 | 20:00
| Agrabad | 142 | 09:00 | 132 | 00:00 | Lalmonirhat | 138 | 16:00 | 120 | 00:00
| AKS | 137 | 13:00 | 130 | 00:00 | Madanganj | 144 | 16:00 | 127 | 00:00
| Aminbazar | 145 | 07:00 | 124 | 00:00 | Madaripur | 138 | 16:00 | 126 | 00:00
| Amnura | 144 | 16:00 | 126 | 00:00 | Madartek | 141 | 16:00 | 130 | 00:00
| Ashuganj | 146 | 16:00 | 133 | 00:00 | Madunaghat | 142 | 09:00 | 132 | 03:00
| Bagerhat | 146 | 07:00 | 135 | 00:00 | Magura | 147 | 07:00 | 134 | 00:00
| Bakulia | 142 | 09:00 | 132 | 18:30 | Mahasthangarh | 141 | 16:00 | 127 | 03:00
| Banani | 142 | 16:00 | 130 | 00:00 | Manikganj | 141 | 15:00 | 118 | 00:00
| Bangabhaban | 145 | 16:00 | 127 | 00:00 | Maniknagar | 145 | 16:00 | 127 | 00:00
| Barapukuria | 141 | 16:00 | 130 | 00:00 | Matarbari | 139 | 17:00 | 126 | 00:00
| Barguna | 140 | 13:00 | 134 | 00:00 | Matuail | 146 | 16:00 | 125.3 | 00:00
| Barishal | 142 | 16:00 | 130 | 00:00 | Millgate | 144 | 16:00 | 125 | 00:00
| Barishal-230 | 140 | 16:00 | 132 | 00:00 | Mirpur | 139 | 16:00 | 130 | 12:00
| Baroaulia | 140 | 10:00 | 133 | 00:00 | Mirzapur | 140 | 09:00 | 124 | 00:00
| Baroirhat | 141 | 09:00 | 130 | 01:00 | Mithapukur | 139 | 16:00 | 124 | 02:00
| Bashundhara | 144 | 16:00 | 126 | 00:00 | MI_Cement | 145 | 16:00 | 127 | 00:00
| BashundharaCement | 144 | 16:00 | 127 | 00:00 | Modern | 142 | 09:00 | 132 | 01:00
| Beanibazar | 135 | 22:00 | 124 | 00:00 | Mogbazar | 142 | 16:00 | 130 | 00:00
| Benapole | 143 | 07:00 | 134 | 00:00 | Mongla | 141 | 06:00 | 136 | 00:00
| Bhaluka | 141 | 17:00 | 119 | 00:00 | Motijheel | 145 | 16:00 | 127 | 00:00
| Bhandaria | 140 | 09:00 | 135 | 01:00 | Munshiganj | 145 | 16:00 | 128 | 00:00
| Bhangura | 145 | 18:00 | 131 | 00:00 | Mymensingh | 143 | 15:00 | 116 | 00:00
| Bheramara | 144 | 16:00 | 131 | 00:00 | Naogaon | 142 | 16:00 | 126 | 00:00
| Bheramara(GK) | 142 | 16:00 | 14 | 17:00 | Narail | 145 | 07:00 | 133 | 00:00
| Bhulta | 140 | 15:00 | 120 | 00:00 | Narinda | 145 | 16:00 | 127 | 00:00
| Bog-Sherpur | 144 | 16:00 | 130 | 03:00 | Narshingdi | 145 | 16:00 | 118 | 00:00
| Bogura | 143 | 16:00 | 131 | 02:00 | Natore | 143 | 10:00 | 129 | 00:00
| Bogura-230 | 143 | 10:00 | 132 | 00:00 | Nawabganj | 140 | 05:00 | 130 | 21:00
| Brahmanbaria | 143 | 23:00 | 120 | 00:00 | Netrakona | 143 | 15:00 | 129 | 00:00
| Cantonment | 142 | 16:00 | 131 | 00:00 | New | 146 | 16:00 | 127 | 00:00
| Chandpur | 145 | 16:00 | 134 | 03:00 | Niamatpur | 140 | 08:00 | 130 | 00:00
| Chandraghona | 142 | 09:00 | 132 | 15:00 | Noapara | 145 | 07:00 | 135 | 00:00
| Chapai | 140 | 08:00 | 127 | 02:00 | Pabna | 145 | 16:00 | 5 | 07:00
| Charsaidpur | 145 | 16:00 | 127 | 00:00 | Palashbari | 139 | 16:00 | 123 | 00:00
| Chauddagram | 143 | 17:00 | 130 | 00:00 | Panchagarh | 140 | 14:00 | 117 | 22:00
| Chhatak | 137 | 22:00 | 125 | 00:00 | Patuakhali | 137 | 13:00 | 8 | 08:00
| Chowmuhani | 142 | 23:00 | 129 | 01:00 | Payra | 138 | 16:00 | 134 | 00:00
| Chuadanga | 147 | 07:00 | 126 | 00:00 | PHP | 142 | 17:00 | 129 | 00:00
| Coxsbazar | 133 | 09:00 | 122 | 18:00 | Postogola | 145 | 15:00 | 128 | 00:00
| Cumilla(N) | 145 | 17:00 | 131 | 00:00 | Purbachal | 144 | 16:00 | 126 | 00:00
| Cumilla(S) | 144 | 19:00 | 131 | 00:00 | Purbasadipur | 134 | 14:00 | 121 | 03:00
| Daudkandi | 145 | 16:00 | 120 | 00:00 | Rahanpur | 141 | 07:00 | 133 | 00:00
| Dhaka | 141 | 16:00 | 131 | 00:00 | Rahim | 145 | 15:00 | 128 | 00:00
| Dhamrai | 142 | 16:00 | 125 | 00:00 | Rajbari | 142 | 16:00 | 126 | 00:00
| Dhanmondi | 142 | 16:00 | 127.7 | 00:00 | Rajendrapur | 142 | 16:00 | 121 | 00:00
| Dohazari | 140 | 09:00 | 130 | 00:00 | Rajshahi | 144 | 10:00 | 130 | 00:00
| Faridpur | 139 | 08:00 | 126 | 00:00 | Rajshahi-230 | 142 | 16:00 | 122 | 01:00
| Fatullah | 145 | 16:00 | 127 | 00:00 | Ramganj | 143 | 16:00 | 131 | 00:00
| Fenchuganj | 140 | 23:00 | 128 | 00:00 | Rampur | 140 | 09:00 | 131 | 00:00
| Feni | 140 | 10:00 | 127 | 01:00 | Rampura | 140 | 16:00 | 130 | 00:00
| Ghatail | 143 | 15:00 | 127 | 02:00 | Rangamati | 140 | 09:00 | 132 | 00:00
| Ghorashal | 147 | 15:00 | 130 | 00:00 | Rangpur | 138 | 14:00 | 123 | 03:00
| Goalpara | 147 | 07:00 | 137 | 00:00 | Ruppur | 143 | 10:00 | 132 | 00:00
| Gollamari | 143 | 16:00 | 135 | 00:00 | Saidpur | 135 | 14:00 | 124 | 00:00
| Gopalganj | 139 | 15:00 | 130 | 00:00 | Satkhira | 145 | 07:00 | 136 | 12:00
| Gopalganj-400 | 137 | 16:00 | 126 | 00:00 | Satmasjid | 143 | 07:00 | 132 | 00:00
| Gulshan | 141 | 16:00 | 130 | 00:00 | Savar | 143 | 07:00 | 128 | 12:00
| Halishahar | 141 | 09:00 | 133 | 00:00 | SevenRings | 150 | 16:00 | 132 | 01:00
| Haripur | 145 | 15:00 | 128 | 00:00 | ShahCement | 145 | 16:00 | 127 | 00:00
| HaripurSBU | 145 | 15:00 | 128 | 00:00 | Shahjadpur | 146 | 16:00 | 135 | 00:00
| Hasnabad | 142 | 15:00 | 128 | 00:00 | Shahjibazar | 140 | 18:00 | 119 | 00:00
| Hathazari | 141 | 12:00 | 132 | 14:00 | Shahmirpur | 141 | 09:00 | 133 | 15:00
| Ishurdi | 145 | 16:00 | 133 | 00:00 | Shariatpur | 139 | 16:00 | 126 | 00:00
| Jaldhaka | 136 | 14:00 | 121 | 05:00 | Sherpur | 144 | 15:00 | 124 | 04:00
| Jamalpur | 144 | 16:00 | 125 | 04:00 | Shikalbaha | 129 | 09:00 | 121 | 18:30
| Jashore | 145 | 07:00 | 133 | 00:00 | Shikalbaha-230 | 141 | 10:00 | 131 | 18:30
| Jhenaidah | 146 | 07:00 | 134 | 00:00 | Shitalakhya | 145 | 16:00 | 127 | 00:00
| Jhenaidah-230 | 146 | 07:00 | 134 | 00:00 | Sholosohor | 141 | 09:00 | 132 | 00:00
| Joydebpur | 148 | 16:00 | 125 | 00:00 | Shyampur | 144 | 16:00 | 128 | 00:00
| Joypurhat | 141 | 16:00 | 123 | 00:00 | Shyampur-230 | 146 | 16:00 | 127 | 00:00
| Juldah | 140 | 08:00 | 132 | 15:00 | Siddhirganj | 144 | 16:00 | 128 | 00:00
| Kabirpur | 142 | 16:00 | 122 | 00:00 | Sirajganj | 145 | 10:00 | 130 | 00:00
| Kachua | 146 | 16:00 | 132 | 01:00 | Sonargaon | 144 | 16:00 | 125 | 00:00
| Kaliakoir | 134 | 04:00 | 127 | 00:00 | Sreemongol | 139 | 23:00 | 121 | 00:00
| Kallyanpur | 141 | 16:00 | 122 | 00:00 | Sreepur | 141 | 16:00 | 124 | 00:00
| Kalurghat | 142 | 09:00 | 132 | 01:00 | Srinagar | 142 | 07:00 | 131 | 21:00
| Kamrangirchar | 141 | 07:00 | 122 | 00:00 | SSM | 142 | 13:00 | 138 | 00:00
| Kaptai | 142 | 23:00 | 135 | 1:00 | Sunamganj | 138 | 23:00 | 124 | 01:00
| Kazla | 144 | 18:30 | 128 | 00:00 | Sylhet | 136 | 20:00 | 125 | 00:00
| Keranigonj | 140 | 07:00 | 131 | 21:00 | Sylhet-132 | 136 | 23:00 | 128 | 00:00
| Khagrachori | 141 | 09:00 | 132 | 00:00 | Tangail | 142 | 15:00 | 122 | 00:00
| Khulna | 145 | 07:00 | 136 | 00:00 | Thakurgaon | 137 | 14:00 | 117 | 05:00
| Khulna(S) | 145 | 07:00 | 135 | 00:00 | TK | 140 | 09:00 | 132 | 00:00
| Khulshi | 141 | 09:00 | 131 | 00:00 | Tongi | 146 | 16:00 | 127 | 00:00
| Kishoreganj | 145 | 16:00 | 122 | 00:00 | Ullahpara | 146 | 16:00 | 132 | 00:00
| Kodda | 148 | 16:00 | 120 | 01:00 | Ullon | 140 | 18:00 | 130 | 00:00
| KSRM | 143 | 09:00 | 132 | 00:00 | Uttara | 145 | 07:00 | 129 | 13:00
| Kulaura | 138 | 21:00 | 127 | 00:00 | UttaraNew | 144 | 07:00 | 130 | 12:00
| Kurigram | 138 | 15:00 | 121 | 00:00 | Zigatola | 140 | 07:00 | 131 | 21:00

## L-Curve
Date | 2024-05-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 260 | 2674 | 1566 | 4240 |  |  |  | QF-LDC-11
0:30 | 561 | 4906.5 | 3127.5 | 8034 | Date: | 2024-05-27
1:00 | 862 | 7139 | 4689 | 11828
1:30 | 864 | 6890 | 4499 | 11389
2:00 | 866 | 6641 | 4309 | 10950
2:30 | 815 | 6324.5 | 4051 | 10375.5 | [5 empty] | Gen. at Eve. Peak | 4554 | 4554 MW (21:00 )
3:00 | 764 | 6008 | 3793 | 9801 | [6 empty] | 21:00
3:30 | 904 | 5572 | 3769.5 | 9341.5 | [5 empty] | Gen. at Day Peak | 5323 | 5323 MW (12:00 )
4:00 | 1044 | 5136 | 3746 | 8882 | [6 empty] | 12:00
4:30 | 1049 | 4890.5 | 3578.5 | 8469 | [5 empty] | Highest Generation | 11828
5:00 | 1054 | 4645 | 3411 | 8056 | [6 empty] | 1:00
5:30 | 1182 | 4209.5 | 3356 | 7565.5
6:00 | 1310 | 3774 | 3301 | 7075
6:30 | 1189 | 3598 | 3091.5 | 6689.5
7:00 | 1068 | 3422 | 2882 | 6304
7:30 | 1013 | 3226.5 | 2702 | 5928.5
8:00 | 958 | 3031 | 2522 | 5553
8:30 | 1053 | 2869 | 2543 | 5412
9:00 | 1148 | 2707 | 2564 | 5271
9:30 | 1150 | 2505 | 2584 | 5089
10:00 | 1152 | 2303 | 2604 | 4907
10:30 | 1124 | 2367 | 2531.5 | 4898.5
11:00 | 1096 | 2431 | 2459 | 4890
11:30 | 1109 | 2606 | 2500.5 | 5106.5
12:00 | 1122 | 2781 | 2542 | 5323
12:30 | 1135 | 2869.5 | 2491.5 | 5361
13:00 | 1148 | 2958 | 2441 | 5399
13:30 | 1222 | 2801 | 2453 | 5254
14:00 | 1296 | 2644 | 2465 | 5109
14:30 | 1211 | 2442 | 2365.5 | 4807.5
15:00 | 1126 | 2240 | 2266 | 4506
15:30 | 953 | 2117.5 | 2078.5 | 4196
16:00 | 780 | 1995 | 1891 | 3886
16:30 | 738 | 1972 | 1846.5 | 3818.5
17:00 | 696 | 1949 | 1802 | 3751
17:30 | 592 | 2045.5 | 1753.5 | 3799
18:00 | 488 | 2142 | 1705 | 3847
18:30 | 537 | 2191 | 1781 | 3972
19:00 | 586 | 2240 | 1857 | 4097
19:30 | 596 | 2368 | 1789 | 4157
20:00 | 340 | 2588 | 1589 | 4177 |  |  |  | Executive Engineer
20:30 | 338 | 2711 | 1654.5 | 4365.5 |  |  |  | Network Operation Division
21:00 | 336 | 2834 | 1720 | 4554
21:30 | 348 | 2775.5 | 1778 | 4553.5
22:00 | 360 | 2717 | 1836 | 4553 |  |  |  |  | Page 6 of 7
22:30 | 318 | 2710 | 1751 | 4461
23:00 | 276 | 2703 | 1666 | 4369
23:30 | 268 | 2688.5 | 1616 | 4304.5
24:00 | 260 | 2674 | 1566 | 4240
4554 MW (21:00 )
5323 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-27 |  | Energy |  | 150910362
[14 empty] | Date: | 2024-05-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 1385 | 209 | 1288 | 0 | 0 | 1292 | 0 | 0 | 0 | 16 | 0 | 50 | 0
0:30 | 2383.5 | 422.5 | 1421 | 0 | 874.5 | 2667 | 15 | 0 | 163.5 | 45 | 0 | 42 | 91.68 |  |  | Date: | 43977
1:00 | 3382 | 636 | 1554 | 0 | 1749 | 4042 | 30 | 0 | 327 | 74 | 0 | 34 | 183.36
1:30 | 3357 | 636 | 1524 | 0 | 1462 | 4011 | 30 | 0 | 259.5 | 70 | 0 | 39.5 | 163.305 | [8 empty] | Total Energy | 150.9104 | 150.9104 | Total Energy Gen 150.910 MKWHr Energy Not Served 0.432 MKWHr Energy Requirement 151.342 MKWHr
2:00 | 3332 | 636 | 1494 | 0 | 1175 | 3980 | 30 | 0 | 192 | 66 | 0 | 45 | 143.25 | [8 empty] | Energy not Served | 0.43181 | 0.43181
2:30 | 3353.5 | 763.5 | 1501.5 | 0 | 912.5 | 3581.5 | 30 | 0 | 148.5 | 53 | 0 | 31.5 | 133.2225 | [8 empty] | Energy Requirement | 151.3422 | 151.3422
3:00 | 3375 | 891 | 1509 | 0 | 650 | 3183 | 30 | 0 | 105 | 40 | 0 | 18 | 123.195
3:30 | 3303 | 905 | 1464 | 0 | 516.5 | 2987 | 30 | 0 | 72 | 34 | 0 | 30 | 61.5975
4:00 | 3231 | 919 | 1419 | 0 | 383 | 2791 | 30 | 0 | 39 | 28 | 0 | 42 | 0
4:30 | 3160.5 | 919 | 1369 | 0 | 217.5 | 2691.5 | 15 | 0 | 19.5 | 29 | 0 | 48 | 0
5:00 | 3090 | 919 | 1319 | 0 | 52 | 2592 | 0 | 0 | 0 | 30 | 0 | 54 | 0
5:30 | 2859 | 920 | 1255.5 | 0 | 26 | 2420 | 0 | 0 | 0 | 30 | 1.5 | 53.5 | 0
6:00 | 2628 | 921 | 1192 | 0 | 0 | 2248 | 0 | 0 | 0 | 30 | 3 | 53 | 0
6:30 | 2493 | 754 | 1121 | 0 | 0 | 2234.5 | 0 | 0 | 0 | 22 | 11.5 | 53.5 | 0 | [7 empty] | Coal
7:00 | 2358 | 587 | 1050 | 0 | 0 | 2221 | 0 | 0 | 0 | 14 | 20 | 54 | 0
7:30 | 2284.5 | 444.5 | 915 | 0 | 0 | 2180 | 0 | 0 | 0 | 17 | 34 | 53.5 | 0 | [6 empty] | Oil
8:00 | 2211 | 302 | 780 | 0 | 0 | 2139 | 0 | 0 | 0 | 20 | 48 | 53 | 0
8:30 | 1982.5 | 377 | 800 | 0 | 0 | 2117 | 0 | 0 | 0 | 28 | 58 | 49.5 | 0
9:00 | 1754 | 452 | 820 | 0 | 0 | 2095 | 0 | 0 | 0 | 36 | 68 | 46 | 0
9:30 | 1554.5 | 467 | 826 | 0 | 0 | 2076 | 15 | 0 | 0 | 36 | 65 | 49.5 | 0
10:00 | 1355 | 482 | 832 | 0 | 0 | 2057 | 30 | 0 | 0 | 36 | 62 | 53 | 0
10:30 | 1374 | 416 | 896 | 0 | 0 | 2035.5 | 30 | 0 | 0 | 19 | 75 | 53 | 0
11:00 | 1393 | 350 | 960 | 0 | 0 | 2014 | 30 | 0 | 0 | 2 | 88 | 53 | 0
11:30 | 1514.5 | 350 | 1030 | 0 | 0 | 2024.5 | 27.5 | 0 | 0 | 9 | 98 | 53 | 0
12:00 | 1636 | 350 | 1100 | 0 | 0 | 2035 | 25 | 0 | 0 | 16 | 108 | 53 | 0
12:30 | 1659.5 | 351 | 1140 | 0 | 0 | 1999 | 25 | 0 | 0 | 24 | 109.5 | 53 | 0
13:00 | 1683 | 352 | 1180 | 0 | 0 | 1963 | 25 | 0 | 0 | 32 | 111 | 53 | 0
13:30 | 1683 | 352 | 1180 | 0 | 0 | 1963 | 25 | 0 | 0 | 32 | 111 | 53 | 0
14:00 | 1683 | 352 | 1180 | 0 | 0 | 1963 | 25 | 0 | 0 | 32 | 111 | 53 | 0
14:30 | 1497.5 | 401.5 | 965 | 0 | 0 | 1919.5 | 12.5 | 0 | 0 | 24 | 79.5 | 53 | 0
15:00 | 1312 | 451 | 750 | 0 | 0 | 1876 | 0 | 0 | 0 | 16 | 48 | 53 | 0
15:30 | 1236.5 | 286.5 | 715 | 0 | 0 | 1865 | 0 | 0 | 0 | 12 | 28 | 53 | 0
16:00 | 1161 | 122 | 680 | 0 | 0 | 1854 | 0 | 0 | 0 | 8 | 8 | 53 | 0
16:30 | 1131.5 | 214.5 | 688 | 0 | 0 | 1715.5 | 0 | 0 | 0 | 10 | 5.5 | 53.5 | 0
17:00 | 1102 | 307 | 696 | 0 | 0 | 1577 | 0 | 0 | 0 | 12 | 3 | 54 | 0
17:30 | 1162.5 | 282.5 | 788 | 0 | 0 | 1506 | 0 | 0 | 0 | 9 | 2.5 | 48.5 | 0
18:00 | 1223 | 258 | 880 | 0 | 0 | 1435 | 0 | 0 | 0 | 6 | 2 | 43 | 0
18:30 | 1247.5 | 331.5 | 925.5 | 0 | 0 | 1409 | 0 | 0 | 0 | 11 | 1 | 46.5 | 0
19:00 | 1272 | 405 | 971 | 0 | 0 | 1383 | 0 | 0 | 0 | 16 | 0 | 50 | 0
19:30 | 1290 | 445 | 1107 | 0 | 0 | 1249 | 0 | 0 | 0 | 16 | 0 | 50 | 0
20:00 | 1432 | 209 | 1217 | 0 | 0 | 1251 | 0 | 0 | 0 | 18 | 0 | 50 | 0
20:30 | 1470.5 | 209 | 1271.5 | 0 | 0 | 1346 | 0 | 0 | 0 | 18 | 0 | 50.5 | 0
21:00 | 1509 | 209 | 1326 | 0 | 0 | 1441 | 0 | 0 | 0 | 18 | 0 | 51 | 0
21:30 | 1468.5 | 209 | 1319.5 | 0 | 0 | 1497.5 | 0 | 0 | 0 | 15 | 0 | 44 | 0
22:00 | 1428 | 209 | 1313 | 0 | 0 | 1554 | 0 | 0 | 0 | 12 | 0 | 37 | 0
22:30 | 1427 | 209 | 1292 | 0 | 0 | 1476.5 | 0 | 0 | 0 | 13 | 0 | 43.5 | 0
23:00 | 1426 | 209 | 1271 | 0 | 0 | 1399 | 0 | 0 | 0 | 14 | 0 | 50 | 0
23:30 | 1405.5 | 209 | 1279.5 | 0 | 0 | 1345.5 | 0 | 0 | 0 | 15 | 0 | 50 | 0 |  |  | Max Temp. in Dhaka |  | 27.1°C
24:00 | 1385 | 209 | 1288 | 0 | 0 | 1292 | 0 | 0 | 0 | 16 | 0 | 50 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 150.910 MKWHr Energy Not Served 0.432 MKWHr Energy Requirement 151.342 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [11 empty] | 25 | 25 | 25 | 0 | [11 empty] | 77760
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 0 |  |  |  |  | 30 | 30 | [15 empty] | 216000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 1 | 1 | [5 empty] | 2 | 1 | [10 empty] | 10260
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 151 | 151 | 100 | 71 | 71 | 67 | [16 empty] | 0 | 1194491
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 51 | 34 | [22 empty] | 0 | 175925
12 | Hathazari 100 MW peaking PP | 64 | 55 | 55 | 23 | [22 empty] | 226368
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | [23 empty] | 0 | 40982
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 45 | [24 empty] | 0 | 88432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 289 | 287 | 282 | 282 | 280 | 217 | 170 | 160 | 158 | [16 empty] | 0 | 2404546
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | [24 empty] | 0 | 82800
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 100 | 100 | 100 | 100 | 100 | 100 | 180 | 160 | 160 | 150 | 150 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3244500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 490 | 490 | 490 | 450 | 300 | 300 | 270 | 265 | 245 | 245 | 245 | 255 | 270 | 250 | 240 | 234 | 235 |  | 240 | 238 | 235 | 270 | 270 | 270 | 270 | 7510908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | [20 empty] | 0 | 127224
33 | Ashuganj 225 MW CCPP | 204 | 204 | 212 | 213 | 214 | 152 | 152 | 151 | 151 | 135 | 185 | 201 | 200 | 140 | 118 | 110 | 109 | 109 |  | 110 | 110 | 109 | 109 | 109 | 109 | 109 | 3719000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 220 | 145 | [17 empty] | 0 | 1984000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 215 | 215 | 215 | 215 | 215 | 245 | 230 | 230 | 205 | 200 | 200 | 230 | 250 | 230 | 200 | 185 | 185 | 190 |  | 220 | 250 | 330 | 315 | 285 | 285 | 285 | 5634000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | [19 empty] | 0 | 31200
36 | Chandpur 150 MW CCPP | 90 | 80 | 80 | 80 | 80 | 80 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [11 empty] | 0 | 941310
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 407 | 404 | 388 | 316 | 297 | 280 | 280 | 264 | 260 | 272 | 308 | 370 | 336 | 273 | 231 | 240 | 275 |  | 300 | 300 | 304 | 340 | 318 | 315 | 309 | 7556400
| Meghnaghat Unique power | [25 empty] | 0 | 0
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 350 | 350 | 330 | 300 | 200 | 220 | 200 | 280 | 330 | 380 | 320 | 230 | 200 | 200 | 250 |  | 250 | 250 | 330 | 420 | 420 | 420 | 420 | 7894000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 32 | 34 | 34 | 34 | 34 | 50 | 34 | 32 | 32 | 32 | 32 |  | 32 | 21 | 32 | 32 | 33 | 35 | 30 | 1045440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 3 | 3 | 5 | 4 | 5 | 6 | 2 | [12 empty] | 43590
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 34 | 38 | 38 | 38 | 38 | 35 | 35 | 0 | [10 empty] | 607000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [10 empty] | 668040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 53 | 55 | 62 | 62 | 61 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | [9 empty] | 0 | 406080
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 206 | 205 | 205 | 205 | 205 | 190 | 190 | 190 | 144 | 145 | 144 | 145 | 145 | 145 | 144 | 144 | 144 | 147 |  | 146 | 145 | 145 | 177 | 177 | 176 | 176 | 4489090
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [18 empty] | 0 | 21168
55 | Fenchugonj 51 MW PP (Barakatullah) | 21 | 31 | 31 | 31 | 31 | 10 | [19 empty] | 0 | 152400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | [19 empty] | 0 | 45312
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 280 | 295 | 305 | 285 | 270 | 240 | 150 | 150 | 150 | 170 | 180 | 220 | 210 | 130 | 110 | 115 | 155 |  | 190 | 300 | 300 | 310 | 295 | 280 | 280 | 5519500
| Bibiyana South 400 MW | 345 | 345 | 345 | 315 | 310 | 280 | 250 | 285 | 220 | 255 | 290 | 370 | 340 | 285 | 270 | 232 | 230 | 310 |  | 300 | 300 | 346 | 370 | 340 | 340 | 310 | 7340900
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 17 | [22 empty] | 0 | 112895
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | [21 empty] | 0 | 59520
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 74 | 66 | 40 | 28 | 30 | 30 | 14 | 20 | 36 | 36 | 2 | 16 | 32 | 6 | 16 | 8 | 12 | 6 |  | 16 | 16 | 18 | 18 | 12 | 14 | 16 | 602880
64 | Malancha, Ctg. EPZ (United) | 37 | 38 | 38 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 7 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249600
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | [20 empty] | 0 | 162900
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 5 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | [12 empty] | 0 | 65170
69 | Summit Ashulia | 20 | 21 | 21 | 20 | 0 | 0 | [19 empty] | 0 | 104400
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 0 | 0 |  |  | 0 |  | 0 | [14 empty] | 116000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 0 | 0 | 0 | 0 | 0 | 13 | [11 empty] | 0 | 302900
72 | Rupganj 33 MW PP(Summit) | 22 | 30 | 30 | 30 | 12 | 14 | [19 empty] | 0 | 165500
73 | Ghorashal 108 MW PP (Regent) | [25 empty] | 0 | 0
| Feni Lanka Power | 71 | 34 | [23 empty] | 0 | 124260
| Chowmuhani 113 MW | 45 | 9 | [23 empty] | 0 | 82320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 54 | [22 empty] | 0 | 486720
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | [21 empty] | 0 | 71520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | [24 empty] | 27898
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | [21 empty] | 0 | 81120
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 |  |  |  | 0
| Jodiac Power | 17 | [24 empty] | 0 | 23915
| Karnaphuli Power Ltd. | 68 | 34 | [23 empty] | 0 | 137160
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 151 | 150 | 150 | 150 | 150 | 117 | 110 | 110 | 110 | 112 | 130 | 150 | 150 | 115 | 110 | 110 | 114 | 113 |  | 113 | 113 | 115 | 150 | 145 | 135 | 144 | 3120640
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 70 | 53 | 17 | 16 | [21 empty] | 0 | 191040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | [24 empty] | 0 | 13680
92 | Fenchuganj 44 MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | [19 empty] | 0 | 70632
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 64 | 24 | 8 | [22 empty] | 0 | 123696
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | 44 | 29 | [8 empty] | 0 | [14 empty] | 0 | 73920
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 15 | [21 empty] | 0 | 126445
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | [22 empty] | 0 | 197960
101 | Kushiara 163 MW CCPP (KP) | [12 empty] | 20 | 20 | 20 | [10 empty] | 0 | 45164
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | [23 empty] | 0 | 80640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 77 | 77 | 45 | 24 | [20 empty] | 0 | 355200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 98 | 38 | 34 | 34 | [21 empty] | 0 | 234864
115 | Juldah 100 MW PP Unit-3 (Acorn) | 46 | 46 | 12 | 12 | [21 empty] | 0 | 115200
116 | Chandpur 200 MW (Desh energy) | 96 | 68 | 34 | [22 empty] | 0 | 261120
117 | Ashuganj 150 MW PP (Midland) | 15 | 13 | [23 empty] | 0 | 33454
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 401 | 316 | 305 | 247 | 247 | 247 | 247 | 58 | [15 empty] | 0 | 2964000
| Jamalpur 115 MW PP (United) | 68 | 68 | 69 | 45 | 24 | [20 empty] | 0 | 327600
| Anwara 300 MW PP (United) | 51 | 52 | 52 | 16 | [21 empty] | 0 | 215782
| Juldah unit-2 (Acorn) | 60 | 48 | 12 | 12 | [21 empty] | 0 | 151680
| Anlima Energy Ltd. | 22 | 17 | 17 | 17 | [21 empty] | 0 | 79036
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | [21 empty] | 0 | 83880
| Spectra Solar Plant Ltd. | [26 empty] | 1276
| Chandpur 115(Doreen) | 114 | 50 | 10 | [22 empty] | 0 | 208320
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | [21 empty] | 0 | 85680
| Mirsharai 150 MW (Oil) | 17 | 17 | [23 empty] | 0 | 30109
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 34 | 45 | 18 | 42 | 54 | 53 | 54 | 53 | 46 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 54 | 43 |  | 50 | 50 | 50 | 51 | 37 | 50 | 50 | 1188960
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 0 | 2 | 9 | 4 | 10 | 27 | 21 | 7 | 7 | 3 | 1 | 1 | [8 empty] | 64818
| Matarbari 2*600 MW (CPGCL) | 765 | 767 | 669 | 350 | 334 | 230 | 224 | 186 | 163 | 163 | 164 | 164 | 163 | 163 | 160 | 161 | 162 | 164 |  | 163 | 165 | 164 | 162 | 166 | 164 | 165 | 6407272
120 | Eastern Zone Total | 7139 | 6641 | 6008 | 5136 | 4645 | 3774 | 3422 | 3031 | 2707 | 2303 | 2431 | 2781 | 2958 | 2644 | 2240 | 1995 | 1949 | 2142 |  | 2240 | 2368 | 2588 | 2834 | 2717 | 2703 | 2674 | 83327372
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 4 | 2 | 8 | 12 | 7 | 8 | 14 | 5 | 8 | 1 | [10 empty] | 67680
131 | Rampal 1320 MW (BIFPCL) | 374 | 380 | [24 empty] | 872727
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 160 | 160 | 160 | 160 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 3357164
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | [14 empty] | 1789100
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 80 | 80 | 80 | 80 | 80 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 50 |  | 54 | 54 | 56 | 56 | 56 | 56 | 56 | 1542000
140 | Bhola 33 MW PP (Venture) | [25 empty] | 0 | 5954
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 474000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 636 | 636 | 891 | 919 | 919 | 921 | 587 | 302 | 452 | 482 | 350 | 350 | 352 | 506 | 451 | 122 | 307 | 258 |  | 405 | 445 | 209 | 209 | 209 | 209 | 209 | 13208080
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 760 | 700 | 690 | 690 | 560 | 500 | 500 | 500 | 500 | 500 | 500 | 520 | 580 | 520 | 500 | 500 | 500 | 450 |  | 400 | 270 | 270 | 380 | 430 | 350 | 280 | 13909300
149
150 | Barapukuria TPP Unit-1 | 63 | 64 | 63 | 64 | 64 | 65 | 64 | 65 | 63 | 45 | [15 empty] | 0 | 642327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 200 | 180 | 160 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4203000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 31 | 31 | [23 empty] | 0 | 53395
Sirajgonj 6.55 MW Solar
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 159 | 159 | 159 | 158 | 150 | 130 | 130 | 125 | [17 empty] | 0 | 1319764
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 350 | 350 | 270 | 270 | 240 | 160 | 180 | 210 | 270 | 330 | 300 | 240 | 150 | 150 | 150 | 250 |  | 308 | 334 | 362 | 336 | 343 | 326 | 344 | 6779563
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit)
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | [25 empty] | 48716
168 | Santahar 50 MW Peaking PP | 22 | 22 | [24 empty] | 46904
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | 36 | [24 empty] | 0 | 45184
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [24 empty] | 0 | 71520
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [24 empty] | 0 | 43392
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 105 | 53 | 34 | 33 | 4 | [20 empty] | 0 | 295929
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 | 5 | 4 | 3 |  |  | 3 | 2 | 1 | [8 empty] | 32726
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 75 | 75 | 75 | [21 empty] | 0 | 414912
| Intraco Solar 30 MW | [7 empty] | 10 | 20 | 10 | 7 | 7 |  | 9 | [12 empty] | 54866
| Adani Power Jharkhanda Ltd | 1210 | 1199 | 891 | 817 | 814 | 813 | 813 | 818 | 814 | 814 | 815 | 816 | 815 | 818 | 816 | 803 | 531 | 436 |  | 430 | 426 | 432 | 479 | 538 | 465 | 427 | 17912727
178 | Teesta Solar Limited | [5 empty] | 1 | 13 | 27 | 22 | 25 | 55 | 57 | 67 | 57 | 31 | 0 | 0 | 0 | [8 empty] | 392060