## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-09-2025 | [28 empty] | Date: | 30-09-2025 | [28 empty] | Date: | 30-09-2025 | [28 empty] | Date: | 30-09-2025 | [28 empty] | Date: | 30-09-2025 | [14 empty] | Date: | 30-09-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 381 | 17 | 17 | 48 | 123 | 146 | 55 | 35 | 162 | 0 | 300 | 283 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 92 | 16 | 104 | 0 | 1 | 50 | 67 | 54.36 | 12 | 0 | 0 | 212 | 85 | 28 | 650 | 17 | 0 | 39 | 17 | 105 | 213 | 0 | 0 | 0 | 630 | 0 | 51 | 120 | 81 | 0 | 349 | 330 | 27 | 187 | 35 | 54 | 93 | 198 | 0 | 20 | 107 | 40 | 34 | 0 | 35 | 310 | 0 | 362 | 30 | 57 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 164 | 17 | 78 | 9 | 47 | 0 | 0 | 0 | 7898.36 | 876 | 175 | 0 | 35 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 653.59 | 0 | 39 | 0 | 113 | 113 | 0 | 93 | 35 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 399 | 0 | 0 | 139 | 45 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 625 | 1232 | 17 | 7331.79 | 15230.15 | 108.06
01:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 381 | 17 | 0 | 32 | 123 | 146 | 55 | 35 | 162 | 0 | 300 | 280 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 85 | 16 | 98 | 0 | 4 | 40 | 67 | 54.36 | 12 | 0 | 0 | 212 | 84 | 28 | 650 | 17 | 0 | 39 | 17 | 96 | 212 | 0 | 0 | 0 | 600 | 0 | 51 | 123 | 95 | 0 | 352 | 330 | 38 | 180 | 36 | 73 | 93 | 89 | 0 | 20 | 98 | 38 | 34 | 0 | 35 | 305 | 0 | 350 | 30 | 57 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 76 | 9 | 49 | 0 | 0 | 0 | 7720.36 | 875 | 174 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 652.48 | 0 | 39 | 0 | 113 | 113 | 0 | 93 | 28 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 188 | 0 | 0 | 0 | 390 | 0 | 0 | 139 | 44 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 626 | 1222 | 17 | 7285.48 | 15005.84 | 108.06
02:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 392 | 17 | 0 | 32 | 123 | 32 | 55 | 35 | 152 | 0 | 300 | 283 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 84 | 16 | 98 | 0 | 0 | 50 | 67 | 54.36 | 12 | 0 | 0 | 213 | 97 | 30 | 650 | 17 | 0 | 39 | 17 | 101 | 212 | 0 | 0 | 0 | 600 | 0 | 51 | 127 | 130 | 0 | 351 | 330 | 40 | 189 | 36 | 89 | 93 | 51 | 0 | 20 | 98 | 36 | 34 | 0 | 27 | 300 | 0 | 366 | 30 | 57 | 140 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 76 | 9 | 49 | 0 | 0 | 0 | 7669.36 | 876 | 174 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 652.04 | 0 | 39 | 0 | 113 | 113 | 0 | 0 | 21 | 43 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 188 | 0 | 0 | 0 | 336 | 0 | 0 | 137 | 43 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 622 | 1222 | 17 | 7119.04 | 14788.4 | 108.06
03:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 386 | 17 | 0 | 32 | 123 | 32 | 55 | 35 | 145 | 0 | 300 | 283 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 28 | 22 | 0 | 0 | 82 | 16 | 96 | 0 | 0 | 50 | 60 | 54.36 | 12 | 0 | 0 | 213 | 95 | 35 | 650 | 17 | 0 | 39 | 17 | 91 | 212 | 0 | 0 | 0 | 600 | 0 | 51 | 120 | 130 | 0 | 352 | 330 | 42 | 185 | 36 | 90 | 93 | 52 | 0 | 20 | 96 | 26 | 34 | 0 | 27 | 305 | 0 | 366 | 30 | 57 | 137 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 76 | 9 | 49 | 0 | 0 | 0 | 7617.36 | 875 | 180 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 648.2 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 21 | 43 | 0 | 0 | 20 | 0 | 0 | 203 | 0 | 191 | 0 | 0 | 0 | 332 | 0 | 0 | 142 | 43 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 622 | 1222 | 17 | 7123.2 | 14740.56 | 108.05
04:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 397 | 17 | 0 | 32 | 90 | 32 | 55 | 0 | 142 | 0 | 300 | 288 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 26 | 22 | 0 | 0 | 81 | 16 | 82 | 0 | 1 | 50 | 60 | 54.36 | 12 | 0 | 0 | 212 | 94 | 35 | 650 | 17 | 0 | 39 | 17 | 89 | 212 | 0 | 0 | 0 | 600 | 0 | 51 | 122 | 61 | 0 | 351 | 330 | 42 | 187 | 36 | 91 | 94 | 52 | 0 | 20 | 48 | 36 | 34 | 0 | 27 | 300 | 0 | 379 | 30 | 57 | 136 | 8 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 49 | 0 | 0 | 0 | 7428.36 | 876 | 180 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1201 | 0 | 652.64 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 0 | 43 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 191 | 0 | 0 | 0 | 343 | 0 | 0 | 139 | 43 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 622 | 1120 | 17 | 6974.64 | 14403 | 108.05
05:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 403 | 17 | 0 | 32 | 90 | 32 | 55 | 0 | 72 | 0 | 300 | 290 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 26 | 22 | 0 | 0 | 85 | 16 | 50 | 0 | 0 | 50 | 53 | 54.36 | 12 | 0 | 0 | 211 | 99 | 37 | 650 | 17 | 0 | 39 | 17 | 95 | 214 | 0 | 0 | 0 | 600 | 0 | 51 | 123 | 63 | 0 | 350 | 330 | 42 | 186 | 36 | 90 | 95 | 52 | 0 | 20 | 46 | 42 | 34 | 0 | 27 | 310 | 0 | 387 | 30 | 57 | 140 | 8 | 0 | 84 | 30 | 0 | 18 | 163 | 0 | 76 | 9 | 50 | 0 | 0 | 0 | 7384.36 | 876 | 180 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 651.59 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 204 | 0 | 191 | 0 | 0 | 0 | 353 | 0 | 0 | 139 | 42 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 624 | 1100 | 17 | 6824.59 | 14208.95 | 108.05
06:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 383 | 17 | 0 | 34 | 90 | 32 | 15 | 0 | 72 | 0 | 300 | 283 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 90 | 16 | 46 | 0 | 0 | 50 | 53 | 17 | 12 | 0 | 0.02 | 210 | 100 | 38 | 645 | 17 | 0 | 27 | 17 | 94 | 213 | 0 | 0 | 0 | 600 | 0 | 51 | 127 | 8 | 0 | 354 | 330 | 43 | 198 | 36 | 90 | 95 | 52 | 0 | 20 | 15 | 40 | 34 | 0 | 28 | 310 | 0 | 360 | 30 | 57 | 141 | 8 | 0 | 84 | 30 | 0 | 18 | 163 | 0 | 76 | 9 | 50 | 0 | 0.42 | 0 | 7116.44 | 876 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 656.28 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.39 | 205 | 0 | 191 | 0 | 0 | 0 | 340 | 0 | 0.03 | 138 | 45 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 271 | 115 | 220 | 0 | 623 | 1100 | 17 | 6645.9 | 13762.34 | 108.04
07:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 392 | 17.5 | 0 | 34 | 123 | 15 | 15 | 0 | 35 | 0 | 300 | 287 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 17 | 26.6 | 22 | 0 | 0 | 15 | 16 | 13 | 0 | 0 | 50 | 23 | 17 | 12 | 0 | 0.29 | 210 | 99 | 38 | 650 | 17 | 0 | 6 | 17 | 95 | 213 | 0 | 0 | 0 | 602 | 1 | 51 | 70 | 8 | 0 | 353 | 330 | 43 | 210 | 36 | 90 | 94 | 52 | 0 | 20 | 15 | 38 | 34 | 16 | 28 | 310 | 0 | 370 | 30 | 57 | 141 | 8 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 76 | 9 | 50 | 0 | 10.11 | 0 | 6937.5 | 876 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 1215 | 0 | 669.95 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 9.81 | 15 | 0 | 0 | 10.7 | 205 | 0 | 193 | 0 | 0 | 0 | 348 | 0 | 0.89 | 137 | 42 | 115 | 5 | 49 | 0 | 0 | 0 | 1.1 | 32 | 0.09 | 0 | 275 | 115 | 220 | 0 | 623 | 1100 | 17 | 6609.54 | 13547.04 | 108.04
08:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 409 | 17.5 | 0 | 34 | 123 | 15 | 15 | 0 | 35 | 0 | 300 | 286 | 0 | 0 | 0 | 250 | 0 | 0 | 15 | 17 | 21.6 | 22 | 0 | 0 | 13 | 16 | 12 | 0 | 0 | 50 | 23 | 17 | 12 | 0 | 0.49 | 209 | 99 | 2 | 650 | 0 | 0 | 17 | 17 | 92 | 213 | 0 | 0 | 0 | 605 | 9 | 51 | 70 | 8 | 0 | 347 | 330 | 43 | 191 | 36 | 90 | 93 | 52 | 0 | 12 | 0 | 34 | 34 | 37 | 28 | 310 | 0 | 385 | 30 | 57 | 138 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 49 | 1 | 24.03 | 0 | 6876.62 | 876 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1213 | 0 | 665 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 26.35 | 45 | 0 | 0 | 29.23 | 205 | 0 | 197 | 0 | 0 | 0 | 346 | 0 | 2.51 | 136 | 41 | 115 | 15 | 49 | 0 | 0 | 0 | 3.1 | 89 | 0.27 | 0 | 274 | 115 | 220 | 0 | 623 | 1094 | 17 | 6694.46 | 13571.08 | 108.03
09:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 432 | 17.5 | 0 | 35 | 123 | 15 | 15 | 17 | 35 | 0 | 300 | 301 | 0 | 0 | 0 | 250 | 0 | 0 | 23 | 26 | 0 | 22 | 0 | 0 | 16 | 16 | 12 | 0 | 0 | 50 | 23 | 17 | 12 | 0 | 2.59 | 216 | 104 | 2 | 650 | 0 | 0 | 0 | 17 | 100 | 212 | 0 | 0 | 0 | 601 | 12 | 51 | 70 | 8 | 0 | 335 | 330 | 40 | 205 | 36 | 66 | 92 | 51 | 0 | 12 | 0 | 34 | 34 | 55 | 27 | 320 | 0 | 390 | 30 | 30 | 155 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 44 | 2 | 34.41 | 0 | 6964.5 | 876 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1230 | 0 | 658 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 42.58 | 74 | 0 | 0 | 44.45 | 203 | 0 | 195 | 0 | 0 | 0 | 394 | 0 | 3.87 | 135 | 47 | 115 | 24 | 49 | 0 | 0 | 0 | 4.9 | 138 | 0.47 | 0 | 281 | 115 | 220 | 0 | 622 | 1102 | 17 | 6911.27 | 13875.77 | 108.03
10:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 415 | 17.5 | 0 | 35 | 108 | 15 | 19 | 35 | 72 | 0 | 300 | 300 | 0 | 0 | 17 | 250 | 0 | 0 | 16 | 52 | 0 | 22 | 0 | 0 | 16 | 16 | 19 | 0 | 0 | 50 | 38 | 17 | 12 | 0 | 1.9 | 216 | 106 | 4 | 650 | 17 | 0 | 0 | 17 | 102 | 212 | 0 | 0 | 0 | 648 | 13 | 51 | 88 | 8 | 0 | 335 | 330 | 39 | 200 | 35 | 51 | 91 | 73 | 0 | 12 | 6 | 40 | 34 | 65 | 27 | 320 | 0 | 388 | 30 | 30 | 156 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 76 | 9 | 44 | 2 | 45.64 | 0 | 7182.04 | 877 | 178 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 1224 | 0 | 652 | 0 | 0 | 0 | 25 | 35 | 0 | 0 | 0 | 0 | 30.37 | 65 | 0 | 0 | 59.2 | 205 | 0 | 191 | 0 | 0 | 0 | 380 | 0 | 5.13 | 122 | 47 | 115 | 31 | 54 | 0 | 0 | 0 | 6.2 | 173 | 0.17 | 0 | 277 | 115 | 220 | 0 | 622 | 1110 | 17 | 6959.07 | 14141.11 | 108.02
11:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 383 | 0 | 15 | 35 | 120 | 75 | 55 | 35 | 72 | 0 | 300 | 290 | 0 | 0 | 35 | 250 | 0 | 0 | 34 | 52 | 20 | 22 | 0 | 0 | 37 | 16 | 65 | 0 | 0 | 25 | 52 | 17 | 12 | 0 | 3.67 | 216 | 101 | 2 | 650 | 54 | 0 | 35 | 17 | 93 | 212 | 0 | 0 | 0 | 710 | 10 | 51 | 102 | 0 | 63 | 337 | 330 | 37 | 191 | 33 | 51 | 91 | 98 | 0 | 15 | 45 | 38 | 34 | 73 | 27 | 315 | 0 | 388 | 30 | 30 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 13 | 76 | 9 | 44 | 2 | 48.19 | 3 | 7597.86 | 876 | 175 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.99 | 1212 | 0 | 642 | 0 | 0 | 0 | 35 | 58 | 0 | 0 | 0 | 8 | 34.58 | 99 | 0 | 0 | 64.8 | 205 | 0 | 189 | 0 | 0 | 0 | 353 | 0 | 5.64 | 121 | 42 | 115 | 16 | 85 | 0 | 0 | 0 | 6.9 | 172 | 0.17 | 0 | 276 | 115 | 220 | 0 | 623 | 1095 | 17 | 6982.08 | 14579.94 | 108.02
12:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 426 | 0 | 17 | 35 | 120 | 80 | 55 | 35 | 72 | 0 | 300 | 296 | 0 | 0 | 35 | 250 | 0 | 0 | 34 | 142 | 20 | 22 | 0 | 0 | 62 | 16 | 75 | 0 | 0 | 34 | 50 | 31 | 12 | 0 | 3.4 | 216 | 104 | 2 | 650 | 54 | 0 | 49 | 17 | 102 | 211 | 0 | 0 | 0 | 717 | 11 | 51 | 90 | 0 | 100 | 300 | 305 | 36 | 202 | 33 | 51 | 90 | 103 | 0 | 15 | 114 | 34 | 34 | 46 | 34 | 320 | 0 | 379 | 30 | 30 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 163 | 17 | 76 | 9 | 30 | 2 | 39.47 | 7 | 7827.87 | 876 | 170 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 1222 | 0 | 651 | 0 | 0 | 0 | 100 | 80 | 0 | 0 | 0 | 8 | 55.12 | 55 | 26 | 0 | 66.43 | 205 | 0 | 185 | 0 | 0 | 0 | 389 | 0 | 5.88 | 137 | 44 | 115 | 35 | 94 | 0 | 0 | 0 | 7.1 | 132 | 0.48 | 0 | 279 | 115 | 220 | 0 | 623 | 1102 | 17 | 7138.01 | 14965.88 | 108.01
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 398 | 0 | 17 | 34 | 120 | 80 | 55 | 35 | 72 | 0 | 300 | 287 | 0 | 0 | 35 | 250 | 0 | 0 | 24 | 142 | 19.5 | 22 | 0 | 0 | 90 | 16 | 76 | 0 | 0 | 50 | 48 | 54.36 | 12 | 0 | 0.83 | 216 | 110 | 12 | 650 | 54 | 0 | 50 | 17 | 104 | 210 | 0 | 0 | 0 | 712 | 18 | 51 | 66 | 0 | 129 | 280 | 280 | 14 | 184 | 33 | 50 | 90 | 100 | 0 | 17 | 100 | 38 | 34 | 65 | 33 | 325 | 0 | 378 | 30 | 30 | 151 | 0 | 0 | 83 | 30 | 0 | 18 | 163 | 17 | 76 | 9 | 31 | 2 | 43.41 | 0 | 7779.1 | 876 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1228 | 0 | 653 | 0 | 0 | 0 | 113 | 113 | 0 | 22 | 0 | 8 | 56.66 | 91 | 25 | 0 | 63.11 | 204 | 0 | 181 | 0 | 0 | 0 | 401 | 0 | 5.3 | 137 | 43 | 115 | 34 | 92 | 0 | 0 | 0 | 6.2 | 125 | 0.67 | 0 | 276 | 115 | 220 | 0 | 623 | 1110 | 17 | 7229.94 | 15009.04 | 108.01
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 405 | 0 | 17 | 34 | 121 | 80 | 55 | 35 | 72 | 0 | 300 | 295 | 0 | 0 | 35 | 250 | 0 | 0 | 24 | 142 | 18.5 | 22 | 0 | 0 | 95 | 16 | 76 | 0 | 0 | 50 | 50 | 54.36 | 12 | 0 | 3.19 | 215 | 109 | 6 | 650 | 54 | 0 | 50 | 17 | 102 | 210 | 0 | 0 | 0 | 706 | 18 | 51 | 65 | 0 | 0 | 330 | 330 | 6 | 201 | 30 | 50 | 0 | 104 | 0 | 17 | 101 | 38 | 34 | 53 | 26 | 320 | 0 | 378 | 30 | 30 | 151 | 0 | 0 | 83 | 30 | 0 | 18 | 163 | 17 | 75 | 9 | 31 | 2 | 24.35 | 0 | 7634.4 | 876 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 1227 | 0 | 652.59 | 0 | 0 | 0 | 113 | 113 | 0 | 22 | 0 | 8 | 39.38 | 11 | 25 | 0 | 55.21 | 199 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 4.92 | 137 | 45 | 115 | 29 | 106 | 0 | 0 | 0 | 6.2 | 154 | 0.59 | 0 | 276 | 115 | 220 | 0 | 624 | 1111 | 17 | 7166.89 | 14801.29 | 108
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 390 | 54 | 17 | 43 | 122 | 80 | 55 | 35 | 72 | 0 | 300 | 283 | 0 | 0 | 35 | 250 | 0 | 0 | 22 | 142 | 18.8 | 22 | 0 | 0 | 90 | 16 | 69 | 0 | 3 | 42 | 51 | 54.36 | 12 | 0 | 2.13 | 215 | 106 | 3 | 650 | 17 | 0 | 50 | 17 | 101 | 209 | 0 | 0 | 0 | 707 | 0 | 51 | 66 | 11 | 0 | 334 | 330 | 18 | 194 | 33 | 48 | 0 | 103 | 0 | 14 | 100 | 38 | 34 | 44 | 26 | 315 | 0 | 345 | 30 | 30 | 150 | 8 | 0 | 82 | 30 | 0 | 15 | 164 | 17 | 82 | 9 | 31 | 2 | 4.76 | 0 | 7545.05 | 876 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63 | 1228 | 0 | 662.13 | 0 | 0 | 0 | 113 | 113 | 0 | 22 | 0 | 8 | 44.74 | 9 | 25 | 0 | 38.58 | 190 | 0 | 175 | 0 | 0 | 0 | 394 | 0 | 3.84 | 131 | 46 | 115 | 23 | 106 | 0 | 0 | 0 | 4.7 | 127 | 0.26 | 1 | 272 | 115 | 220 | 0 | 624 | 1125 | 17 | 7090.25 | 14635.3 | 108
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 390 | 54 | 16 | 53 | 122 | 80 | 55 | 35 | 72 | 0 | 300 | 283 | 0 | 0 | 35 | 250 | 0 | 0 | 3 | 142 | 20 | 22 | 0 | 0 | 92 | 16 | 72 | 0 | 23 | 32 | 65 | 54.36 | 12 | 0 | 0.83 | 214 | 96 | 2 | 650 | 17 | 0 | 50 | 17 | 92 | 209 | 0 | 0 | 0 | 708 | 0 | 51 | 70 | 16 | 0 | 336 | 330 | 30 | 194 | 33 | 48 | 0 | 103 | 0 | 17 | 97 | 38 | 34 | 24 | 26 | 310 | 0 | 345 | 30 | 30 | 151 | 8 | 0 | 82 | 30 | 0 | 15 | 163 | 17 | 83 | 9 | 31 | 1 | 3.79 | 0 | 7526.98 | 876 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 1220 | 0 | 658.49 | 0 | 0 | 0 | 113 | 113 | 0 | 22 | 8 | 8 | 4.17 | 0 | 25 | 0 | 24.02 | 188 | 0 | 174 | 0 | 0 | 0 | 353 | 0 | 1.55 | 123 | 46 | 115 | 13 | 106 | 0 | 0 | 0 | 1.7 | 77 | 0.31 | 16 | 272 | 115 | 220 | 0 | 571 | 1180 | 17 | 6897.24 | 14424.22 | 107.99
17:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 385 | 54 | 17 | 53 | 121 | 80 | 55 | 55 | 72 | 0 | 300 | 277 | 0 | 0 | 55 | 250 | 0 | 0 | 1 | 142 | 20 | 22 | 0 | 0 | 86 | 16 | 77 | 0 | 14 | 50 | 66 | 54.36 | 12 | 0 | 0.08 | 214 | 98 | 10 | 650 | 17 | 0 | 50 | 17 | 94 | 199 | 0 | 0 | 0 | 703 | 1 | 51 | 75 | 16 | 0 | 300 | 300 | 32 | 180 | 33 | 49 | 0 | 109 | 5 | 5 | 94 | 36 | 34 | 5 | 27 | 305 | 0 | 301 | 30 | 30 | 149 | 8 | 0 | 83 | 30 | 0 | 15 | 163 | 17 | 75 | 9 | 31 | 0 | 1.2 | 1 | 7426.64 | 876 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 1183 | 0 | 652.43 | 0 | 0 | 0 | 113 | 113 | 0 | 22 | 17 | 8 | 1.3 | 0 | 25 | 0 | 0.94 | 187 | 0 | 140 | 0 | 0 | 0 | 333 | 0 | 0.08 | 141 | 46 | 115 | 3 | 106 | 0 | 0 | 0 | 0.7 | 20 | 0.11 | 49 | 240 | 115 | 220 | 0 | 524 | 1185 | 17 | 6666.56 | 14093.2 | 107.99
18:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 408 | 54 | 35 | 88 | 121 | 277 | 55 | 55 | 90 | 0 | 280 | 290 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 25.8 | 22 | 0 | 0 | 82 | 16 | 82 | 0 | 12 | 50 | 66 | 54.36 | 12 | 0 | 0 | 214 | 95 | 4 | 645 | 160 | 0 | 50 | 17 | 89 | 201 | 0 | 0 | 0 | 791 | 0 | 51 | 88 | 16 | 0 | 334 | 330 | 34 | 201 | 33 | 74 | 0 | 166 | 8 | 5 | 94 | 40 | 34 | 0 | 27 | 295 | 0 | 383 | 30 | 30 | 137 | 8 | 0 | 83 | 30 | 0 | 15 | 163 | 17 | 84 | 9 | 31 | 0 | 0 | 0 | 8217.16 | 876 | 151 | 0 | 11 | 61 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 655.95 | 0 | 24 | 0 | 113 | 113 | 0 | 93 | 36 | 8 | 0 | 0 | 25 | 0 | 0 | 149 | 0 | 150 | 0 | 0 | 0 | 364 | 0 | 0 | 139 | 46 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 279 | 115 | 180 | 0 | 520 | 1185 | 17 | 6759.95 | 14977.11 | 107.99
19:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 380 | 54 | 35 | 115 | 136 | 295 | 55 | 55 | 108 | 0 | 300 | 278 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 25.8 | 22 | 0 | 0 | 87 | 32 | 99 | 0 | 13 | 50 | 58 | 54.36 | 12 | 0 | 0 | 214 | 96 | 17 | 650 | 138 | 0 | 50 | 17 | 92 | 212 | 0 | 0 | 0 | 888 | 0 | 51 | 100 | 51 | 0 | 342 | 330 | 36 | 187 | 33 | 90 | 0 | 168 | 9 | 5 | 100 | 42 | 34 | 0 | 35 | 310 | 0 | 363 | 30 | 30 | 141 | 8 | 0 | 84 | 30 | 0 | 15 | 163 | 17 | 76 | 9 | 32 | 0 | 0 | 0 | 8490.16 | 876 | 151 | 0 | 28 | 49 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 0 | 659.86 | 0 | 24 | 0 | 113 | 113 | 0 | 93 | 36 | 8 | 0 | 0 | 25 | 0 | 0 | 182 | 0 | 173 | 0 | 0 | 0 | 333 | 0 | 0 | 130 | 46 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 266 | 115 | 220 | 0 | 624 | 1200 | 17 | 7019.86 | 15510.02 | 107.99
19:30 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 380 | 54 | 35 | 115 | 138 | 295 | 55 | 55 | 108 | 0 | 300 | 282 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 25.8 | 22 | 0 | 0 | 83 | 32 | 100 | 0 | 14 | 50 | 59 | 54.36 | 12 | 0 | 0 | 214 | 96 | 20 | 631 | 140 | 0 | 50 | 17 | 88 | 212 | 0 | 0 | 0 | 910 | 0 | 51 | 105 | 38 | 0 | 341 | 330 | 36 | 189 | 33 | 90 | 0 | 168 | 8 | 15 | 95 | 42 | 34 | 0 | 35 | 310 | 0 | 363 | 30 | 30 | 137 | 10 | 0 | 84 | 30 | 0 | 15 | 163 | 17 | 77 | 9 | 32 | 0 | 0 | 0 | 8500.16 | 876 | 151 | 0 | 35 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1199 | 0 | 657.43 | 0 | 47 | 0 | 113 | 113 | 0 | 93 | 36 | 8 | 0 | 0 | 25 | 0 | 0 | 185 | 0 | 172 | 0 | 0 | 0 | 338 | 0 | 0 | 156 | 47 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 269 | 115 | 220 | 0 | 626 | 1222 | 17 | 7138.43 | 15638.59
20:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 385 | 54 | 17 | 115 | 142 | 295 | 55 | 55 | 108 | 0 | 300 | 285 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 25.8 | 22 | 0 | 0 | 85 | 32 | 103 | 0 | 19 | 50 | 59 | 54.36 | 12 | 0 | 0 | 213 | 95 | 25 | 650 | 135 | 0 | 50 | 17 | 92 | 213 | 0 | 0 | 0 | 910 | 0 | 51 | 107 | 35 | 0 | 341 | 330 | 39 | 191 | 34 | 89 | 0 | 164 | 8 | 17 | 96 | 42 | 34 | 0 | 35 | 300 | 0 | 356 | 30 | 30 | 138 | 10 | 0 | 84 | 30 | 0 | 18 | 163 | 17 | 77 | 9 | 32 | 0 | 0 | 0 | 8521.16 | 876 | 150 | 0 | 30 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 660 | 0 | 47 | 0 | 113 | 113 | 0 | 93 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 185 | 0 | 172 | 0 | 0 | 0 | 341 | 0 | 0 | 153 | 46 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 274 | 115 | 220 | 0 | 625 | 1222 | 17 | 7158 | 15679.16 | 107.98
21:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 408 | 54 | 17 | 115 | 141 | 295 | 55 | 55 | 126 | 0 | 300 | 293 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 26.8 | 22 | 0 | 0 | 82 | 16 | 100 | 0 | 14 | 50 | 59 | 54.36 | 12 | 0 | 0 | 213 | 93 | 31 | 646 | 142 | 0 | 40 | 17 | 89 | 212 | 0 | 0 | 0 | 917 | 0 | 51 | 117 | 0 | 0 | 343 | 330 | 29 | 169 | 35 | 87 | 0 | 167 | 9 | 17 | 96 | 42 | 34 | 0 | 35 | 305 | 0 | 387 | 30 | 30 | 139 | 0 | 0 | 84 | 30 | 0 | 18 | 162 | 17 | 76 | 22 | 33 | 0 | 0 | 0 | 8528.16 | 876 | 142 | 0 | 30 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 664.35 | 0 | 47 | 0 | 113 | 113 | 0 | 93 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 186 | 0 | 166 | 0 | 0 | 0 | 355 | 0 | 0 | 154 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 275 | 115 | 180 | 0 | 504 | 1222 | 17 | 6985.35 | 15513.51 | 107.98
22:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 407 | 54 | 17 | 124 | 141 | 295 | 55 | 55 | 126 | 0 | 300 | 299 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 27 | 22 | 0 | 0 | 92 | 16 | 95 | 0 | 12 | 50 | 59 | 54.36 | 12 | 0 | 0 | 213 | 102 | 24 | 650 | 150 | 0 | 39 | 17 | 96 | 212 | 0 | 0 | 0 | 916 | 0 | 51 | 122 | 0 | 0 | 320 | 300 | 0 | 197 | 35 | 52 | 0 | 175 | 0 | 17 | 102 | 42 | 34 | 0 | 35 | 310 | 0 | 387 | 30 | 30 | 153 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 76 | 101 | 33 | 0 | 0 | 0 | 8609.36 | 876 | 132 | 0 | 30 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 661.49 | 0 | 47 | 0 | 113 | 113 | 0 | 93 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 185 | 0 | 164 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 547 | 1222 | 17 | 7059.49 | 15668.85 | 107.98
23:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 436 | 54 | 17 | 133 | 140 | 295 | 55 | 35 | 155 | 0 | 300 | 300 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 52 | 27 | 22 | 0 | 0 | 97 | 16 | 96 | 0 | 17 | 50 | 59 | 54.36 | 12 | 0 | 0 | 214 | 106 | 28 | 650 | 17 | 0 | 39 | 17 | 102 | 215 | 0 | 0 | 0 | 838 | 0 | 51 | 123 | 0 | 0 | 320 | 300 | 0 | 206 | 36 | 51 | 0 | 180 | 0 | 17 | 110 | 44 | 34 | 0 | 35 | 310 | 0 | 390 | 30 | 30 | 160 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 76 | 100 | 32 | 0 | 0 | 0 | 8429.36 | 876 | 127 | 0 | 30 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 666.04 | 0 | 47 | 0 | 113 | 113 | 0 | 93 | 38 | 8 | 0 | 0 | 26 | 0 | 0 | 180 | 0 | 140 | 0 | 0 | 0 | 408 | 0 | 0 | 154 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 287 | 115 | 220 | 0 | 615 | 1224 | 17 | 7118.04 | 15547.4 | 107.96
Total KWH | 0 | 2087040 | 450720 | 0 | 0 | 0 | 0 | 0 | 8308800 | 0 | 9614300 | 689076 | 297360 | 1478736 | 2926560 | 2811436 | 1173016 | 799949 | 2335680 | 0 | 7578000 | 6970589 | 0 | 0 | 795228 | 6513812 | 0 | 0 | 182960 | 1980000 | 542400 | 527040 | 0 | 0 | 1772673 | 426545 | 1728960 | 0 | 138240 | 1116051 | 1280448 | 1127284 | 303360 | 0 | 22199 | 5024078 | 2425454 | 438720 | 15643636.36 | 1150836 | 0 | 931200 | 390479.4 | 2341818 | 4916029 | 0 | 0 | 0 | 17001816 | 88020 | 1202984 | 2418763 | 702545 | 320800 | 8382000 | 7786000 | 733440 | 4719000 | 808344 | 1674240 | 1239660 | 2505600 | 43680 | 366400 | 1853640 | 916800 | 832272 | 464809 | 718848 | 7545000 | 0 | 9297000 | 717000 | 961983 | 3534054.55 | 150192 | 0 | 1984320 | 712704 | 0 | 411000 | 3375380 | 298440 | 1826400 | 484800 | 888960 | 14300 | 273750 | 15120 | 186510777.31 | 21208727 | 4093632 | 0 | 342720 | 446464 | 912000 | 0 | 0 | 0 | 0 | 0 | 585360 | 28821820 | 0 | 15671745.53 | 0 | 565816 | 0 | 2205216 | 2370240 | 0 | 817328 | 324788 | 306984 | 327980 | 532770 | 410523 | 0 | 446256 | 4679455 | 0 | 4508173 | 0 | 0 | 0 | 8850400 | 0 | 39600 | 3427000 | 1033745 | 2753278 | 238828 | 2375664 | 0 | 0 | 0 | 48194.88 | 1257840 | 4128 | 1363584 | 6763000 | 2736000 | 5347230 | 0 | 14500368 | 28218181.82 | 434400 | 168969439.23 | 355480216.54

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-09-2025 | during | 01-10-2025 | during | 01-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 348 | 335 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 340 | 340 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 285 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 49 | 49 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 120 | 142 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 25.8 | 33 | 33 | 28 | 28 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 80 | 295 | 300 | 300 | 81 | 300 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 115 | 149 | 149 | 51 | 102 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 87 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 426 | 385 | 718 | 718 | 600 | 600 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 144 | 144 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2381 | 2799.8 | 5819.2 | 5789.2 | 3447.31 | 3763.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 49 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 213 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 213 | 195 | 200 | 195 | 200 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 102 | 92 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 50 | 59 | 64 | 75 | 64 | 75 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 34 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 25 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 75 | 103 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.4 | 0 | 3.73 | 0 | 3.73 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 32 | 300 | 300 | 16 | 30 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 31 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 104 | 95 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 62 | 85 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 54 | 135 | 159.86 | 159.86 | 54 | 36 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 717 | 910 | 1224 | 1224 | 1224 | 1224 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 19 | 25 | 46 | 25 | 46 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 840 | 840 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2416.4 | 2814.36 | 3670.45 | 3708.72 | 3242.09 | 3276.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 191 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 341 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 305 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 100 | 0 | 270 | 270 | 270 | 270 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 34 | 46.7 | 46.7 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 39 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 35 | 195 | 195 | 130 | 130 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 90 | 107 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 34 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 0 | 163 | 163 | 95 | 95 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 164 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 42 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 34 | 43.5 | 43.5 | 34 | 34 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 17 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 96 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 89 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 46 | 0 | 75 | 0 | 75 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1638 | 1613 | 2555.86 | 2480.86 | 2182.16 | 2116.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-09-2025 | during | 01-10-2025 | during | 01-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 32 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 76 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.47 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 7 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 180.47 | 135 | 371.7 | 320.5 | 210.7 | 159.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 138 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 163 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 10 | 25 | 25 | 12 | 12 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 379 | 356 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1212 | 1159 | 1298 | 1298 | 1205 | 1205
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 170 | 150 | 410 | 410 | 248 | 248 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 96 | 0 | 96 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1222 | 1222 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | None
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2391 | 2356 | 3642.2 | 3546.2 | 3285.2 | 3189.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 623 | 625 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1102 | 1222 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 279 | 274 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2356.48 | 2583 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.12 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 205 | 185 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 172 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 389 | 341 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 26 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 43 | 43 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 80 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 100 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.88 | 0 | 5.58 | 0 | 5.58 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 651 | 660 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.43 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 55 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1826.43 | 1795 | 2492.57 | 2325.99 | 2409.99 | 2243.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 44 | 46 | 45 | 45 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 137 | 153 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 94 | 110 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 132 | 0 | 129.07 | 0 | 129.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 564.1 | 424 | 608.07 | 443 | 563.07 | 398
System Total |  |  |  |  | 28823.2 | 27743.955 | 14965.88 | 15679.16 | 22605.05 | 22058.47 | 18509.52 | 18313.94
Forecast Scenario (01-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15410 |  | 0 |  | 15410
|  |  |  | 1:00 | 15000 |  | 0 |  | 15000
|  |  |  | 2:00 | 14550 |  | 0 |  | 14550
|  |  |  | 3:00 | 14290 |  | 0 |  | 14290
|  |  |  | 4:00 | 13910 |  | 0 |  | 13910
|  |  |  | 5:00 | 13700 |  | 0 |  | 13700
|  |  |  | 6:00 | 13040 |  | 0 |  | 13040
|  |  |  | 7:00 | 12670 |  | 0 |  | 12670
|  |  |  | 8:00 | 12490 |  | 0 |  | 12490
|  |  |  | 9:00 | 12330 |  | 0 |  | 12330
|  |  |  | 10:00 | 12320 |  | 0 |  | 12320
|  |  |  | 11:00 | 12450 |  | 0 |  | 12450
|  |  |  | 12:00 | 13060 |  | 0 |  | 13060
|  |  |  | 13:00 | 13810 |  | 0 |  | 13810
|  |  |  | 14:00 | 13420 |  | 0 |  | 13420
|  |  |  | 15:00 | 13470 |  | 0 |  | 13470
|  |  |  | 16:00 | 13100 |  | 0 |  | 13100
|  |  |  | 17:00 | 12670 |  | 0 |  | 12670
|  |  |  | 18:00 | 13000 |  | 0 |  | 13000
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 15050 |  | 0 |  | 15050
|  |  |  | 19:30 | 15230 |  | 0 |  | 15230
|  |  |  | 20:00 | 15240 |  | 0 |  | 15240
|  |  |  | 21:00 | 15260 |  | 0 |  | 15260
|  |  |  | 22:00 | 15250 |  | 0 |  | 15250
|  |  |  | 23:00 | 15350 |  | 0 |  | 15350
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 13060.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15260.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15260.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 330.84 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:17 hrs on 01-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-09-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14965.88 | MW | 12:00 Hr. | Energy Generated |  |  | 355.4802 |  | MKWHr.
| Day Peak Demand |  |  | 15102.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.942 |  | MKWHr.
| Evening Peak Generation |  |  | 15679.16 | MW | 20:00 Hr. | Energy Demand |  |  | 360.4222 |  | MKWHr.
| Evening Peak Demand |  |  | 15771.16 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13547.04 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 944.38 |  | MMCFD
| Maximum Generation of the Day |  |  | 15679.16 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.1072 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.0549 | 0 | 17.8248 | 0 | 0 | 0.18296 | 0 | 0 | 58.0627 | Gas | 131.4633 | Gas | 472212258.6505
| Chattogram Zone |  |  | 5.3547 | 32.6455 | 14.9951 | 0 | 5.0241 | 0.11022 | 0 | 0.13824 | 58.2678 | Coal | 115.4096 | Coal | 640662738.4846
| Cumilla Zone |  |  | 26.2612 | 0 | 10.047 | 0 | 0 | 0.46481 | 0.9168 | 0 | 37.6898 | HFO | 60.2087 | HFO | 1124572759.002
| Mymensingh Zone |  |  | 0.88896 | 0 | 2.6248 | 0 | 0 | 0.28805 | 0 | 0 | 3.8018 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6886 | Hydro | 5.0241 | Hydro | 502407.8
| Khulna Zone |  |  | 4.0936 | 28.8218 | 0.78918 | 0 | 0 | 0.58536 | 22.1207 | 0 | 56.4107 | Solar | 4.527 | Solar | 68624517.3648
| Barishal Zone |  |  | 8.0832 | 49.4815 | 1.798 | 0 | 0 | 0.004128 | 0 | 0 | 59.3669 | Import | 38.7093 | Import | 217869154.4809
| Rajshahi Zone |  |  | 18.038 | 0 | 7.0009 | 0 | 0 | 1.3466 | 15.6717 | 0 | 42.0573 | Wind | 0.13824 | Wind | 2037657.6
| Rangpur Zone |  |  | 0 | 4.4607 | 5.1289 | 0 | 0 | 1.5449 | 0 | 0 | 11.1345
| Total |  |  | 131.4633 | 115.4096 | 60.2087 | 0 | 5.0241 | 4.527 | 38.7093 | 0.13824 | 355.4802
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 472212258.6505 |  | Hydro | 502407.8
|  |  |  | Coal | 640662738.4846 |  | Solar | 68624517.3648
|  |  |  | HFO | 1124572759.002 |  | Import | 217869154.4809
|  |  |  | HSD | 0 |  | Wind | 2037657.6
[5 empty] | Total: | 252,64,81,493 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2087 | Peak Hr Flow | 876.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 30340192.07 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.6717 | Peak Hr Flow | 660.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1918 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9168 | Peak Hr Flow | 42.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2666 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.7973 | Peak Hr Flow | 1578.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5397
|  |  |  | Chattogram |  | 0 |  | 1583
|  |  |  | Cumilla |  | 0 |  | 1580
|  |  |  | Mymensingh |  | 88 |  | 1196
|  |  |  | Sylhet |  | 0 |  | 495
|  |  |  | Khulna |  | 0 |  | 1822
|  |  |  | Barishal |  | 0 |  | 508
|  |  |  | Rajshahi |  | 0 |  | 1600
|  |  |  | Rangpur |  | 0 |  | 993
|  |  |  | Total |  | 88 |  | 15174
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:35 | 10:28 | Kachua 230/132/33kV S/S TR-1 LT Forced S/D Due to 33 kV Source DS maintenance of PBS | [7 empty] | 30.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 08:43 | 13:45 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to Due to under Construction GIS
Building Works.
|  | 09:07 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 09:08 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT is restored.
|  | 09:24 | Chowmuhani 132/33kV S/S TR2 is restored.
|  | 09:38 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT is restored.
|  | 09:38 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT is restored.
| 09:52 |  | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D Due to Pilling Work
| 09:59 |  | Ashuganj 420 MW CCPP (East) GT was sync.
| 10:09 | 11:30 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to ALDC Khulna
Instraction
| 10:09 | 11:30 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to ALDC Khulna
Instraction
| 10:12 | 11:29 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to temperature
reduce and from Khulna(S) 230/132kV end Due to Emergency Maintenance work at central ckt
end.
| 12:00 |  | Day Peak Generation is 14963 MW.
| 12:31 |  | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing Distance relay, Zone-01, Blue-Phase relays.
| 12:31 | 12:58 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing Master relay Operated (86).
relays Due to Due to Ullon Circuit-1 Tripped.
| 12:32 |  | Ullon-Siddhirganj 132kV ckt tripped at 12:32 hours showing distance relay. At that time,
Siddhirganj-EGCB 240MW line also tripped.
| 12:41 | 15:01 | Fenchuganj-Kulaura 132 kV Ckt-2 Tripped from Fenchuganj 230/132/33kV end showing
REL670, REC650 relays Due to L2-L3 Fault and from Kulaura 132/33kV end showing Distance
Relay & Overcurrent Relay. relays.
| 12:46 |  | Bogura (W)- Kaliyakoir 400 KV ckt syn.
|  | 12:46 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
| 13:03 |  | Chandpur CCPP was shutdown for lube oil leakage at the generator compartment.
| 13:33 |  | Fenchuganj-Kulaura 132kV ckt-2 tripped showing distance & overcurrent relay.
| 13:41 | 16:28 | Thakurgaon 132/33kV S/S T-3(432T) LT Forced S/D Due to Circuit Sheild Relay ফল্টে পুড়ে
যাওয়ায় টি-৩ ইনকামিং শাটডাউনে রয়েছে। উল্লেখ্য যে টি-১ ও টি-২ দিয়ে পাওয়ার স্বাভাবিক আছে।
কোনো লোডশেড নাই।
| 13:47 |  | Ashuganj 420 MW CCPP (East) was shutdown due to gas shortage.
| 16:04 | 16:11 | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
| 16:11 | 16:21 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 18:20 | 18:38 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing Differential Y-phase,
relays Due to 33kv feeder fauilt due to strom.
| 19:15 | 00:50 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing Differential Y-phase,
relays.
| 20:00 |  | Evening peak Generation is 15678 MW
| 02:14 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- ST
| 02:16 | 04:27 | Keraniganj-Nawabganj 132kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | and 23.0MW load
|  |  | Siprotec 7SA52 relays Due to Storm and heavy rain and from Nawabganj 132/33kV end showing | [7 empty] | interrup. Nawabganj
|  |  | Distance Relay relays Due to Line 02 trip at the Keraniganj source S/S, R phase, O/C, | [7 empty] | 132/33kV end
Zone 01, Fault location 12.45 km.
| 02:16 | 04:27 | Keraniganj-Nawabganj 132kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | and 23.0MW load
|  |  | Siprotec 7SA52 relays Due to Storm and heavy rain and from Nawabganj 132/33kV end showing | [7 empty] | interrup. Nawabganj
|  |  | Distance Relay relays Due to Line 02 trip at the Keraniganj source S/S, R phase, O/C, | [7 empty] | 132/33kV end
Zone 01, Fault location 12.45 km.
| 02:16 | 04:27 | Keraniganj-Nawabganj 132kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | and 23.0MW load
|  |  | Siprotec 7SA52 relays Due to Storm and heavy rain and from Nawabganj 132/33kV end showing | [7 empty] | interrup. Nawabganj
|  |  | Distance Relay relays Due to Line 02 trip at the Keraniganj source S/S, R phase, O/C, | [7 empty] | 132/33kV end
Zone 01, Fault location 12.45 km.
| 02:16 | 04:23 | Keraniganj-Nawabganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | and 23.0MW load
|  |  | Siprotec 7SA52 relays Due to Storm and heavy rain and from Nawabganj 132/33kV end showing | [7 empty] | interrup. Nawabganj
|  |  | Distance Relay relays Due to Line 01 trip at Keraniganj source S/S B-phase, O/C, Zone 1, | [7 empty] | 132/33kV end
Fault Location -12.45 km.
| 02:16 | 02:55 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens 7sa87
relays.
| 02:30 |  | Ashuganj 450 MW CCPP(South) Synchronized
| 07:00 |  | Minimum Generation: 10046 MW.
| 07:09 |  | Ishwardi-Natore 132kV Ckt-1 Tripped from Ishurdi 132/33kV end showing Lz32 relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-09-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 335 | 8308800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7578000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 6970589 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1173016 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6513812 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 689076 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 2926560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 799949 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 795228 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25.8 | 542400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 450720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 2811436 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1478736 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2087040 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 2335680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 182960 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 297360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 385 | 9614300 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1980000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2799.8 | 58062702
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 390479.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 88020 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 931200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 213 | 5024078 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 4916029 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 2341818 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 1280448 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1116051 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 303360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 438720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 103 | 1728960 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 426545 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1127284 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 95 | 2425454 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 85 | 1772673 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 135 | 1150836 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 910 | 17001816 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 19 | 138240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15643636.36 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2814.36 | 58267846.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 191 | 4719000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 341 | 8382000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7786000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 320800 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 808344 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 39 | 733440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 35 | 702545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1202984 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 107 | 2418763 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 718848 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1239660 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 164 | 2505600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 42 | 916800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 832272 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 366400 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 1853640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 43680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1674240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 464809 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1613 | 37689825
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 32 | 888960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 484800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1826400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 273750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 15120 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 298440 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 135 | 3801770
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 961983 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3534054.55 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 712704 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1984320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 3375380 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 411000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 150192 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7545000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 9297000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1159 | 28688633.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 21208727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 342720 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 446464 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 150 | 4093632 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 585360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1222 | 28821820 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2356 | 56410723
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 625 | 14500368 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1363584 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2736000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 28218181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5347230 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 434400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 6763000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4128 | -
Barishal Area Total |  |  |  |  | 2236 | 2583 | 59366891.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 327980 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 565816 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 324788 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 4679455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4508173 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 341 | 8850400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 410523 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 306984 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 817328 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2370240 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 2205216 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 660 | 15671745.53 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 446256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 532770 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1795 | 42057274.53
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1033745 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3427000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 2375664 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48194.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2753278 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 238828 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1257840 | -
Rangpur Area Total |  |  |  |  | 950 | 424 | 11134549.88
Eastern Grid Total |  |  |  |  | 17385.715 | 8521.16 | 186510777.31
Western Grid Total |  |  |  |  | 10358.24 | 7158 | 168969439.23
National Grid Total |  |  |  |  | 27743.955 | 15679.16 | 355480216.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-09-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10163.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4923 | MW
i) Dhaka area |  |  | 5397.43 |  | MW | i) Khulna area |  |  |  | 1822 | MW
ii) Chattogram area |  |  | 1583.15 |  | MW | ii) Barishal area |  |  |  | 508 | MW
iii) Cumilla area |  |  | 1579.73 |  | MW | iii) Rajshahi area |  |  |  | 1600 | MW
iv) Mymensingh area |  |  | 1108 |  | MW | iv) Rangpur area |  |  |  | 993 | MW
v) Sylhet area |  |  | 495 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15086.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 06:00 | 67 | Hathazari | 95 | 20:00 | 133 | PHP | 5 | 03:00
2 | AKSML | 116.3 | 13:00 | 68 | Ishurdi | 84 | 19:00 | 134 | Pabna | 105 | 00:00
3 | Aftabnagar | 42 | 13:00 | 69 | Jaldhaka | 96 | 19:00 | 135 | Palashbari | 139 | 00:00
4 | Agargaon | 149 | 13:00 | 70 | Jamalpur | 127 | 22:00 | 136 | Panchagarh | 65 | 19:30
5 | Agrabad | 108 | 15:00 | 71 | Jashore | 162 | 03:00 | 137 | Patiya | 13 | 00:00
6 | Amnura | 38 | 13:00 | 72 | Jhenaidah | 126 | 03:00 | 138 | Patuakhali | 74.8 | 22:00
7 | Ashuganj | 99 | 00:00 | 73 | Joydebpur | 158 | 18:30 | 139 | Payra | 36 | 00:00
8 | BSRM | 154 | 05:00 | 74 | Joypurhat | 72 | 23:00 | 140 | Postogola | 70 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 19 | 13:00 | 141 | Purbachal | 22 | 00:00
10 | Bajitpur | 94 | 18:00 | 76 | KSRM | 43 | 10:00 | 142 | Purbasadipur | 123 | 01:00
11 | Bakulia | 102 | 16:00 | 77 | Kabirpur | 259 | 09:00 | 143 | Rahanpur | 43 | 22:00
12 | Banani | 58 | 12:00 | 78 | Kachua | 106 | 18:00 | 144 | Rahim | 28 | 16:00
13 | Bangabhaban | 26 | 10:00 | 79 | Kallyanpur | 111 | 00:00 | 145 | Rajbari | 85 | 22:00
14 | Barapukuria | 67 | 20:00 | 80 | Kalurghat | 42 | 11:00 | 146 | Rajendrapur | 133 | 19:30
15 | Barguna | 22 | 02:00 | 81 | Kamrangirchar | 81 | 13:00 | 147 | Rajshahi | 111 | 00:00
16 | Barishal | 129 | 20:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 108 | 13:00
17 | Barishal-230 | 112 | 22:00 | 83 | Kasba | 41 | 21:00 | 149 | Ramganj | 118 | 20:00
18 | Baroaulia | 68 | 11:00 | 84 | Kazla | 105 | 13:00 | 150 | Rampur | 47 | 00:00
19 | Baroirhat | 73 | 20:00 | 85 | Keranigonj | 92 | 18:30 | 151 | Rangamati | 20 | 18:30
20 | Bashundhara | 221 | 15:00 | 86 | Khagrachori | 36 | 18:00 | 152 | Rangpur | 152 | 18:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 72 | 16:00 | 153 | Ruppur | 7.8 | 10:00
22 | Beanibazar | 90 | 18:00 | 88 | Khulshi | 197 | 12:00 | 154 | SSM | 8 | 02:00
23 | Benapole | 66 | 00:00 | 89 | Kishoreganj | 146 | 20:00 | 155 | Saidpur | 107 | 19:30
24 | Bhaluka | 161 | 18:00 | 90 | Kodda | 309 | 19:30 | 156 | Satkhira | 137 | 00:00
25 | Bhandaria | 60 | 04:00 | 91 | Kulaura | 59 | 18:00 | 157 | Satmasjid | 104 | 14:00
26 | Bhangura | 40 | 21:00 | 92 | Kurigram | 66 | 07:00 | 158 | Savar | 218 | 11:00
27 | Bheramara(GK) | 69 | 00:00 | 93 | Kushtia | 155 | 13:00 | 159 | SevenRings | 13.38 | 16:00
28 | Bhulta | 219 | 00:00 | 94 | Laksam | 37 | 23:00 | 160 | ShahCement | 18 | 00:00
29 | Bog-Sherpur | 78 | 19:00 | 95 | Lakshmipur | 36 | 01:00 | 161 | Shahjadpur | 93 | 19:00
30 | Bogura | 177 | 14:00 | 96 | Lalbag | 62 | 12:00 | 162 | Shahjibazar | 133 | 18:30
31 | Borhanuddin | 95 | 04:00 | 97 | Lalmonirhat | 64 | 03:00 | 163 | Shahmirpur | 59 | 18:00
32 | Brahmanbaria | 144 | 20:00 | 98 | MI_Cement | 19 | 10:00 | 164 | Shariatpur | 102 | 22:00
33 | Cantonment | 154 | 13:00 | 99 | Madanganj | 41 | 18:30 | 165 | Sherpur | 142 | 23:00
34 | Chandina | 28.12 | 18:30 | 100 | Madaripur | 122 | 22:00 | 166 | Shikalbaha | 25.5 | 18:30
35 | Chandpur | 92 | 20:00 | 101 | Madartek | 103 | 00:00 | 167 | Shitalakhya | 80.6 | 11:00
36 | Chandraghona | 40 | 18:30 | 102 | Madunaghat | 57 | 10:00 | 168 | Sholosohor | 50 | 12:00
37 | Chapai | 76 | 22:00 | 103 | Magura | 65 | 19:00 | 169 | Shyampur | 90 | 04:00
38 | Charsaidpur | 32 | 04:00 | 104 | Mahasthangarh | 90 | 23:00 | 170 | Siddhirganj | 126 | 16:00
39 | Chauddagram | 84 | 18:00 | 105 | Maijdee | 24 | 21:00 | 171 | Sirajganj | 120 | 20:00
40 | Chhatak | 44 | 19:30 | 106 | Manikganj | 136 | 22:00 | 172 | Sonargaon | 145 | 07:00
41 | Chowmuhani | 197 | 18:00 | 107 | Maniknagar | 72 | 13:00 | 173 | Sreemongol | 90 | 18:30
42 | Chuadanga | 116 | 00:00 | 108 | Matarbari | 54 | 22:00 | 174 | Sreepur | 109 | 20:00
43 | Coxsbazar | 151 | 14:00 | 109 | Matuail | 73 | 12:00 | 175 | Srinagar | 52.85 | 22:00
44 | Cumilla(N) | 156 | 19:30 | 110 | Millgate | 136 | 15:00 | 176 | Sunamganj | 66 | 19:30
45 | Cumilla(S) | 159 | 18:30 | 111 | Mirpur | 134 | 15:00 | 177 | Sylhet | 62 | 19:30
46 | Daganbhuiyan | 0 | 08:00 | 112 | Mirsorai | 13 | 18:00 | 178 | Sylhet-132 | 145 | 18:00
47 | Daudkandi | 156 | 19:30 | 113 | Mirzapur | 48 | 11:00 | 179 | TK | 29 | 00:00
48 | DhakaUniversity | 106 | 13:00 | 114 | Mithapukur | 74 | 04:00 | 180 | Tangail | 188 | 23:00
49 | Dhamrai | 134 | 18:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 25 | 18:00
50 | Dhanmondi | 127.4 | 13:00 | 116 | Mogbazar | 105.2 | 13:00 | 182 | Thakurgaon | 114 | 19:30
51 | Dohazari | 110 | 18:30 | 117 | Mongla | 44 | 11:00 | 183 | Tongi | 135 | 15:00
52 | Faridpur | 186 | 02:00 | 118 | Motijheel | 50 | 13:00 | 184 | Ullahpara | 40 | 18:30
53 | Fatullah | 110 | 09:00 | 119 | Muktagacha | 33 | 22:00 | 185 | Ullon | 55 | 00:00
54 | Fenchuganj | 49 | 18:00 | 120 | Munshiganj | 124 | 23:00 | 186 | Uttara | 93 | 13:00
55 | Feni | 132 | 18:30 | 121 | Muradnagar | 46 | 20:00 | 187 | UttaraNew | 66 | 15:00
56 | GPH | 78 | 20:00 | 122 | Mymensingh | 221 | 21:00 | 188 | Zigatola | 78 | 15:00
57 | Ghatail | 76 | 11:00 | 123 | Naogaon | 147 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 62 | 03:00
59 | Ghorashal-230 | 107 | 20:00 | 125 | Narinda | 70 | 13:00
60 | Goalpara | 42 | 01:00 | 126 | Narshingdi | 198 | 21:00
61 | Gollamari | 108 | 13:00 | 127 | Natore | 157 | 21:00
62 | Gopalganj | 113 | 21:00 | 128 | Nawabganj | 54 | 22:00
63 | Gulshan | 140 | 13:00 | 129 | Netrakona | 163 | 18:30
64 | Halishahar | 78 | 15:00 | 130 | New | 57 | 11:00
65 | HaripurSBU | 135 | 17:00 | 131 | Niamatpur | 84 | 22:00
66 | Hasnabad | 94 | 00:00 | 132 | Noapara | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-09-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15230.15 | 641 |  | 15900
1:00 | 15005.84 | 568 |  | 15599.4
2:00 | 14788.4 | 441 |  | 15249.25
3:00 | 14740.56 | 248 |  | 14999.72
4:00 | 14403 | 141 |  | 14550.35
5:00 | 14208.95 | 136 |  | 14351.07
6:00 | 13762.34 | 114 |  | 13881.47
7:00 | 13547.04 | 103 |  | 13654.68
8:00 | 13571.08 | 126 |  | 13702.75
9:00 | 13875.77 | 123 |  | 14004.31
10:00 | 14141.11 | 107 |  | 14252.93
11:00 | 14579.94 | 91 |  | 14675.04
12:00 | 14965.88 | 131 |  | 15102.78
13:00 | 15009.04 | 186 |  | 15203.04
14:00 | 14801.29 | 261 |  | 15074.29
15:00 | 14635.3 | 353 |  | 15004.3
16:00 | 14424.22 | 344 |  | 14783.22
17:00 | 14093.2 | 267 |  | 14372.2
18:00 | 14977.11 | 0 |  | 14977.11
19:00 | 15510.02 | 117 |  | 15632.02
19:30 | 15638.59 | 89 |  | 15731.59
20:00 | 15679.16 | 88 |  | 15771.16
21:00 | 15513.51 | 84 |  | 15601.51
22:00 | 15668.85 | 78 |  | 15750.36
23:00 | 15547.4 | 194 |  | 15750.13
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-09-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7898.36 | 7331.79 | 15230.15 | DAILY GENERATION CURVE
00:30 | 7809.36 | 7308.635 | 15117.995
01:00 | 7720.36 | 7285.48 | 15005.84 | 30-09-2025
01:30 | 7694.86 | 7202.26 | 14897.12
02:00 | 7669.36 | 7119.04 | 14788.4
02:30 | 7643.36 | 7121.12 | 14764.48
03:00 | 7617.36 | 7123.2 | 14740.56
03:30 | 7522.86 | 7048.92 | 14571.78
04:00 | 7428.36 | 6974.64 | 14403
04:30 | 7406.36 | 6899.615 | 14305.975
05:00 | 7384.36 | 6824.59 | 14208.95
05:30 | 7250.4 | 6735.245 | 13985.645
06:00 | 7116.44 | 6645.9 | 13762.34
06:30 | 7026.97 | 6627.72 | 13654.69
07:00 | 6937.5 | 6609.54 | 13547.04
07:30 | 6907.06 | 6652 | 13559.06
08:00 | 6876.62 | 6694.46 | 13571.08
08:30 | 6920.56 | 6802.865 | 13723.425
09:00 | 6964.5 | 6911.27 | 13875.77
09:30 | 7073.27 | 6935.17 | 14008.44
10:00 | 7182.04 | 6959.07 | 14141.11
10:30 | 7389.95 | 6970.575 | 14360.525
11:00 | 7597.86 | 6982.08 | 14579.94
11:30 | 7712.865 | 7060.045 | 14772.91
12:00 | 7827.87 | 7138.01 | 14965.88
12:30 | 7803.485 | 7183.975 | 14987.46
13:00 | 7779.1 | 7229.94 | 15009.04
13:30 | 7706.75 | 7198.415 | 14905.165
14:00 | 7634.4 | 7166.89 | 14801.29
14:30 | 7589.725 | 7128.57 | 14718.295
15:00 | 7545.05 | 7090.25 | 14635.3
15:30 | 7536.015 | 6993.745 | 14529.76
16:00 | 7526.98 | 6897.24 | 14424.22
16:30 | 7476.81 | 6781.9 | 14258.71
17:00 | 7426.64 | 6666.56 | 14093.2
17:30 | 7821.9 | 6713.255 | 14535.155
18:00 | 8217.16 | 6759.95 | 14977.11
18:30 | 8353.66 | 6889.905 | 15243.565
19:00 | 8490.16 | 7019.86 | 15510.02
19:30 | 8500.16 | 7138.43 | 15638.59
20:00 | 8521.16 | 7158 | 15679.16
20:30 | 8524.66 | 7071.675 | 15596.335 |  | Executive Engineer
21:00 | 8528.16 | 6985.35 | 15513.51 |  | Network Operation Division
21:30 | 8568.76 | 7022.42 | 15591.18
22:00 | 8609.36 | 7059.49 | 15668.85
22:30 | 8519.36 | 7088.765 | 15608.125
23:00 | 8429.36 | 7118.04 | 15547.4

## En-Curve
QF-LDC-12
Date | 30-09-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3616 | 1998 | 876 | 38 | 40 | 653.59 | 212 | 4862.2 | 0 | 675 | 2258.36 | 0 | 0 | 1 | 641 | DAILY ENERGY CURVE
00:30 | 3598 | 2005 | 875.5 | 38 | 39 | 653.035 | 212 | 4834.6 | 0 | 661.5 | 2198.86 | 0 | 0 | 2.5 | 604.5 | 30-09-2025
01:00 | 3580 | 2012 | 875 | 38 | 38 | 652.48 | 212 | 4807 | 0 | 648 | 2139.36 | 0 | 0 | 4 | 568
01:30 | 3564 | 2030 | 875.5 | 38 | 37 | 652.26 | 212.5 | 4800 | 0 | 599 | 2086.86 | 0 | 0 | 2 | 504.5 | Energy Generated | 355.4802 |  | MKWHr
02:00 | 3548 | 2048 | 876 | 38 | 36 | 652.04 | 213 | 4793 | 0 | 550 | 2034.36 | 0 | 0 | 0 | 441 | Energy not Served | 4.942 |  | MKWHr
02:30 | 3546 | 2049.5 | 875.5 | 38 | 31 | 650.12 | 213 | 4795 | 0 | 547 | 2019.36 | 0 | 0 | 0 | 344.5 | Total Energy Requirement | 360.4222 |  | MKWHr
03:00 | 3544 | 2051 | 875 | 38 | 26 | 648.2 | 213 | 4797 | 0 | 544 | 2004.36 | 0 | 0 | 0 | 248
03:30 | 3556.5 | 2020.5 | 875.5 | 38 | 31 | 650.42 | 212.5 | 4724 | 0 | 517 | 1945.86 | 0 | 0 | 0.5 | 194.5
04:00 | 3569 | 1990 | 876 | 38 | 36 | 652.64 | 212 | 4651 | 0 | 490 | 1887.36 | 0 | 0 | 1 | 141
04:30 | 3585 | 2003 | 876 | 38 | 39 | 652.115 | 211.5 | 4648.5 | 0 | 486.5 | 1765.86 | 0 | 0 | 0.5 | 138.5
05:00 | 3601 | 2016 | 876 | 38 | 42 | 651.59 | 211 | 4646 | 0 | 483 | 1644.36 | 0 | 0 | 0 | 136
05:30 | 3591 | 1976 | 876 | 38 | 41 | 653.935 | 210.5 | 4639 | 1.53 | 437 | 1521.68 | 0 | 0 | 0 | 125
06:00 | 3581 | 1936 | 876 | 38 | 40 | 656.28 | 210 | 4632 | 3.06 | 391 | 1399 | 0 | 0 | 0 | 114
06:30 | 3597 | 1943.3 | 876 | 38 | 39 | 663.115 | 210 | 4638 | 60.525 | 380 | 1209.75 | 0 | 0 | 0 | 108.5
07:00 | 3613 | 1950.6 | 876 | 38 | 38 | 669.95 | 210 | 4644 | 117.99 | 369 | 1020.5 | 0 | 0 | 0 | 103
07:30 | 3591 | 1931.1 | 876 | 38 | 36 | 667.475 | 209.5 | 4640 | 227.485 | 353 | 989.5 | 0 | 0 | 0 | 114.5
08:00 | 3569 | 1911.6 | 876 | 38 | 34 | 665 | 209 | 4636 | 336.98 | 337 | 958.5 | 0 | 0 | 0 | 126
08:30 | 3585.5 | 1931.8 | 876 | 38 | 34 | 661.5 | 212.5 | 4652 | 432.625 | 345 | 954.5 | 0 | 0 | 0 | 124.5
09:00 | 3602 | 1952 | 876 | 38 | 34 | 658 | 216 | 4668 | 528.27 | 353 | 950.5 | 0 | 0 | 0 | 123
09:30 | 3591.5 | 1944 | 876.5 | 38 | 37 | 655 | 216 | 4684 | 563.44 | 370 | 1033 | 0 | 0 | 0 | 115
10:00 | 3581 | 1936 | 877 | 38 | 40 | 652 | 216 | 4700 | 598.61 | 387 | 1115.5 | 0 | 0 | 0 | 107
10:30 | 3583 | 1916.5 | 876.5 | 38 | 39 | 647 | 216 | 4714.5 | 625.775 | 387.5 | 1316.75 | 0 | 0 | 0 | 99
11:00 | 3585 | 1897 | 876 | 38 | 38 | 642 | 216 | 4729 | 652.94 | 388 | 1518 | 0 | 0 | 0 | 91
11:30 | 3583 | 1924.5 | 876 | 38 | 36 | 646.5 | 216 | 4751.5 | 615.41 | 444 | 1642 | 0 | 0 | 0 | 111
12:00 | 3581 | 1952 | 876 | 38 | 34 | 651 | 216 | 4774 | 577.88 | 500 | 1766 | 0 | 0 | 0 | 131
12:30 | 3574.5 | 1925.75 | 876 | 38 | 36 | 652 | 216 | 4776.5 | 591.03 | 508 | 1793.68 | 0 | 0 | 0 | 158.5
13:00 | 3568 | 1899.5 | 876 | 38 | 38 | 653 | 216 | 4779 | 604.18 | 516 | 1821.36 | 0 | 0 | 0 | 186
13:30 | 3512.5 | 1897 | 876 | 38 | 38 | 652.795 | 215.5 | 4777.5 | 553.01 | 514 | 1830.86 | 0 | 0 | 0 | 223.5
14:00 | 3457 | 1894.5 | 876 | 38 | 38 | 652.59 | 215 | 4776 | 501.84 | 512 | 1840.36 | 0 | 0 | 0 | 261
14:30 | 3420.5 | 1890.15 | 876 | 38 | 38 | 657.36 | 215 | 4779.5 | 445.425 | 509 | 1847.86 | 0 | 0 | 1.5 | 307
15:00 | 3384 | 1885.8 | 876 | 38 | 38 | 662.13 | 215 | 4783 | 389.01 | 506 | 1855.36 | 0 | 0 | 3 | 353
15:30 | 3355.5 | 1893.9 | 876 | 38 | 38 | 660.31 | 214.5 | 4776.5 | 290.69 | 512 | 1861.36 | 0 | 0 | 13 | 348.5
16:00 | 3327 | 1902 | 876 | 38 | 38 | 658.49 | 214 | 4770 | 192.37 | 518 | 1867.36 | 0 | 0 | 23 | 344
16:30 | 3235 | 1892.5 | 876 | 38 | 37 | 655.46 | 214 | 4721 | 120.89 | 541 | 1909.36 | 0 | 0 | 18.5 | 305.5
17:00 | 3143 | 1883 | 876 | 38 | 36 | 652.43 | 214 | 4672 | 49.41 | 564 | 1951.36 | 0 | 0 | 14 | 267
17:30 | 3244 | 1860.9 | 876 | 38 | 38 | 654.19 | 214 | 4689.5 | 24.705 | 657 | 2225.86 | 0 | 0 | 13 | 133.5
18:00 | 3345 | 1838.8 | 876 | 38 | 40 | 655.95 | 214 | 4707 | 0 | 750 | 2500.36 | 0 | 0 | 12 | 0
18:30 | 3335.5 | 1883.8 | 876 | 38 | 41 | 657.905 | 214 | 4837 | 0 | 777.5 | 2570.36 | 0 | 0 | 12.5 | 58.5
19:00 | 3326 | 1928.8 | 876 | 38 | 42 | 659.86 | 214 | 4967 | 0 | 805 | 2640.36 | 0 | 0 | 13 | 117
19:30 | 3339 | 1930.8 | 876 | 38 | 42 | 657.43 | 214 | 5060 | 0 | 832 | 2635.36 | 0 | 0 | 14 | 89
20:00 | 3346 | 1936.8 | 876 | 38 | 42 | 660 | 213 | 5102 | 0 | 830 | 2616.36 | 0 | 0 | 19 | 88
20:30 | 3351 | 1911.3 | 876 | 38 | 42 | 662.175 | 213 | 5033 | 0 | 829.5 | 2623.86 | 0 | 0 | 16.5 | 86
21:00 | 3356 | 1885.8 | 876 | 38 | 42 | 664.35 | 213 | 4964 | 0 | 829 | 2631.36 | 0 | 0 | 14 | 84
21:30 | 3389.5 | 1899.9 | 876 | 38 | 42 | 662.92 | 213 | 4963.5 | 0 | 826.5 | 2666.86 | 0 | 0 | 13 | 81
22:00 | 3423 | 1914 | 876 | 38 | 42 | 661.49 | 213 | 4963 | 0 | 824 | 2702.36 | 0 | 0 | 12 | 78
22:30 | 3416.5 | 1934.5 | 876 | 38 | 43 | 663.765 | 213.5 | 4971 | 0 | 778.5 | 2658.86 | 0 | 0 | 14.5 | 136
23:00 | 3410 | 1955 | 876 | 38 | 44 | 666.04 | 214 | 4979 | 0 | 733 | 2615.36 | 0 | 0 | 17 | 194
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-09-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 04:00 | 365 | 12:00 | Payra | 407 | 17:00 | 402 | 12:00
Ashuganj | 398 | 6:00 | 373 | 14:00 | Rahanpur | 414 | 17:00 | 402 | 22:00
Bhulta | 394 | 06:00 | 366 | 12:00 | Rampal | 399 | 18:00 | 389 | 12:00
Bibiana | 384 | 06:00 | 377 | 12:00
BIPTC | 402 | 08:00 | 393 | 00:00
Bogura | 405 | 18:00 | 391 | 23:00
Gopalganj | 389 | 18:00 | 380 | 12:00
Kaliakoir | 368 | 03:00 | 354 | 12:00
Madunaghat | 392 | 18:00 | 389 | 00:00
Meghnaghat | 379 | 06:00 | 371 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 03:00 | 215 | 12:00 | Kaliakoir | 230 | 03:00 | 219 | 12:00
AKSML | 234 | 17:00 | 228 | 09:00 | Keranigonj | 222 | 03:00 | 213 | 12:00
Aminbazar | 224 | 05:00 | 216 | 12:00 | Khulna(S) | 228 | 17:00 | 217 | 23:00
Ashuganj | 229 | 03:00 | 219 | 12:00 | Madunaghat | 234 | 17:00 | 230 | 07:00
Ashuganj-400 | 229 | 03:00 | 219 | 12:00 | Madunaghat-400 | 234 | 01:00 | 231 | 09:00
Baghabari | 234 | 17:00 | 226 | 12:00 | Maniknagar | 218 | 04:00 | 211 | 12:00
Barapukuria | 226 | 14:00 | 218 | 20:00 | Meghnaghat | 226 | 02:00 | 221 | 09:00
Barapukuria-230 | 226 | 14:00 | 218 | 20:00 | Meghnaghat-400 | 222 | 03:00 | 216 | 12:00
Barishal | 232 | 17:00 | 225 | 15:00 | Mirsorai | 234 | 18:30 | 225 | 10:00
Bheramara | 233 | 17:00 | 223 | 23:00 | Rajshahi | 232 | 17:00 | 222 | 12:00
Bhulta | 226 | 03:00 | 207 | 12:00 | Rampal | 228 | 18:00 | 218 | 23:00
Bibiana | 227 | 07:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 236 | 17:00 | 223 | 23:00 | Rampura | 225 | 05:00 | 206 | 12:00
Bogura | 241 | 17:00 | 232 | 09:00 | Shikalbaha | 234 | 17:00 | 230 | 10:00
Bogura-400 | 240 | 17:00 | 232 | 09:00 | Shyampur | 221 | 01:00 | 214 | 12:00
Borhanuddin | 235 | 17:00 | 230 | 12:00 | Siddhirganj | 222 | 23:00 | 216 | 15:00
BSRM | 230 | 18:00 | 225 | 10:00 | Sirajgonj | 240 | 12:00 | 234 | 19:30
Cumilla(N) | 223 | 01:00 | 216 | 11:00 | Sreepur | 227 | 17:00 | 219 | 12:00
Faridpur | 228 | 18:30 | 221 | 12:00 | Tongi | 225 | 04:00 | 212 | 13:00
Fenchuganj | 228 | 21:00 | 223 | 18:00
Ghorashal | 220 | 00:00 | 220 | 00:00
Ghorashal-230 | 225 | 01:00 | 211 | 12:00
Gopalganj | 229 | 17:00 | 224 | 11:00
GPH | 232 | 19:00 | 228 | 09:00
Haripur | 219 | 03:00 | 213 | 12:00
Hasnabad | 221 | 01:00 | 213 | 12:00
Hathazari | 231 | 04:00 | 225 | 12:00
Ishurdi | 236 | 17:00 | 225 | 12:00
Jhenaidah | 231 | 17:00 | 217 | 01:00
Kachua | 225 | 17:00 | 208 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 124 | 11:00 | Lalmonirhat | 129 | 14:00 | 119 | 22:00
Agargaon | 135 | 03:00 | 127 | 12:00 | Madanganj | 127 | 01:00 | 122 | 12:00
Agrabad | 133 | 00:00 | 129 | 09:00 | Madaripur | 135 | 17:00 | 130 | 16:00
AKS | 130 | 00:00 | 127 | 09:00 | Madartek | 134 | 06:00 | 123 | 11:00
Aminbazar | 132 | 00:00 | 126 | 12:00 | Madunaghat | 135 | 04:00 | 132 | 07:00
Amnura | 140 | 17:00 | 128 | 12:00 | Magura | 136 | 17:00 | 125 | 13:00
Ashuganj | 138 | 07:00 | 133 | 13:00 | Mahasthangarh | 135 | 17:00 | 126 | 20:00
Bagerhat | 130 | 17:00 | 118 | 23:00 | Maijdee | 128 | 17:00 | 116 | 21:00
Bajitpur | 128 | 17:00 | 120 | 14:00 | Manikganj | 125 | 05:00 | 117 | 12:00
Bakulia | 134 | 00:00 | 131 | 11:00 | Maniknagar | 132 | 03:00 | 126 | 12:00
Banani | 135 | 00:00 | 123 | 11:00 | Matarbari | 123 | 17:00 | 111 | 23:00
Bangabhaban | 132 | 03:00 | 126 | 12:00 | Matuail | 127.5 | 03:00 | 124 | 10:00
Barapukuria | 138 | 14:00 | 128 | 20:00 | Millgate | 131 | 03:00 | 120 | 12:00
Barguna | 135 | 06:00 | 132 | 00:00 | Mirpur | 132 | 03:00 | 124 | 12:00
Barishal | 137 | 18:00 | 128 | 12:00 | Mirzapur | 129 | 21:00 | 121 | 12:00
Barishal-230 | 135 | 17:00 | 128 | 14:00 | Mithapukur | 132 | 14:00 | 124 | 20:00
Baroaulia | 134 | 00:00 | 132 | 08:00 | MI_Cement | 129 | 05:00 | 123 | 12:00
Baroirhat | 132 | 17:00 | 124 | 10:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 22:00 | 121 | 12:00 | Mogbazar | 135 | 00:00 | 124 | 12:00
BashundharaCement | 127 | 01:00 | 122 | 12:00 | Mongla | 130 | 17:00 | 120 | 00:00
Beanibazar | 129 | 20:00 | 120 | 18:00 | Motijheel | 132 | 03:00 | 124 | 14:00
Benapole | 131 | 17:00 | 119 | 11:00 | Muktagacha | 130 | 21:00 | 116 | 12:00
Bhaluka | 129 | 17:00 | 121 | 09:00 | Munshiganj | 128 | 19:00 | 123 | 09:00
Bhandaria | 130 | 00:00 | 121 | 13:00 | Muradnagar | 127 | 17:00 | 120 | 23:00
Bhangura | 133 | 18:00 | 127 | 13:00 | Mymensingh | 128 | 21:00 | 110 | 13:00
Bheramara | 136 | 16:00 | 131 | 23:00 | Naogaon | 131 | 17:00 | 122 | 22:00
Bheramara(GK) | 137 | 17:00 | 131 | 23:00 | Narail | 136 | 17:00 | 124 | 12:00
Bhulta | 124 | 01:00 | 120 | 12:00 | Narinda | 132 | 03:00 | 126 | 12:00
Bog-Sherpur | 134 | 17:00 | 128 | 20:00 | Narshingdi | 129 | 07:00 | 117 | 11:00
Bogura | 137 | 17:00 | 130 | 09:00 | Natore | 134 | 17:00 | 127 | 23:00
Bogura-230 | 137 | 17:00 | 130 | 09:00 | Nawabganj | 134 | 06:00 | 128 | 12:00
Brahmanbaria | 130 | 05:00 | 125 | 23:00 | Netrakona | 120 | 17:00 | 108 | 12:00
Cantonment | 135 | 03:00 | 127 | 12:00 | New | 131 | 05:00 | 122 | 13:00
Chandina | 129 | 17:00 | 124 | 12:00 | Niamatpur | 141 | 17:00 | 136 | 13:00
Chandpur | 136 | 17:00 | 125 | 21:00 | Noapara | 134 | 17:00 | 125 | 00:00
Chandraghona | 135 | 01:00 | 133 | 09:00 | Pabna | 135 | 17:00 | 129 | 12:00
Chapai | 140 | 17:00 | 134 | 22:00 | Palashbari | 129 | 14:00 | 121 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 03:00 | 124 | 09:00 | Panchagarh | 136 | 14:00 | 121 | 19:00
Chauddagram | 129 | 17:00 | 122 | 18:00 | Patiya | 133 | 19:30 | 130 | 12:00
Chhatak | 129 | 21:00 | 118 | 18:00 | Patuakhali | 136 | 07:00 | 133 | 23:00
Chowmuhani | 127 | 17:00 | 117 | 23:00 | Payra | 137 | 06:00 | 135 | 00:00
Chuadanga | 134 | 17:00 | 122 | 13:00 | PHP | 131 | 17:00 | 123 | 10:00
Coxsbazar | 119 | 02:00 | 114 | 12:00 | Postogola | 131 | 06:00 | 126 | 03:00
Cumilla(N) | 129 | 17:00 | 125 | 10:00 | Purbachal | 135 | 00:00 | 124 | 11:00
Cumilla(S) | 133 | 03:00 | 124 | 12:00 | Purbasadipur | 134 | 17:00 | 122 | 20:00
Daganbhuiyan | 126 | 16:00 | 121 | 08:00 | Rahanpur | 141 | 17:00 | 137 | 21:00
Daudkandi | 125 | 17:00 | 118 | 09:00 | Rahanpur-400 | 141 | 15:00 | 138 | 00:00
DhakaUniversity | 136 | 04:00 | 124 | 11:00 | Rahim | 128 | 00:00 | 123 | 12:00
Dhamrai | 130 | 19:00 | 122 | 12:00 | Rajbari | 133 | 18:00 | 129 | 12:00
Dhanmondi | 135 | 00:00 | 124 | 11:00 | Rajendrapur | 133 | 22:00 | 117 | 12:00
Dohazari | 130 | 17:00 | 125 | 23:00 | Rajshahi | 134 | 17:00 | 127 | 12:00
Faridpur | 134 | 05:00 | 130 | 12:00 | Rajshahi-230 | 133 | 17:00 | 127 | 12:00
Fatullah | 134 | 03:00 | 129 | 12:00 | Ramganj | 130 | 17:00 | 119 | 21:00
Fenchuganj | 135 | 21:00 | 130 | 18:00 | Rampur | 133 | 03:00 | 129 | 09:00
Feni | 126 | 00:00 | 119 | 21:00 | Rampura | 135 | 00:00 | 124 | 11:00
Ghatail | 125 | 16:00 | 115 | 12:00 | Rangamati | 134 | 03:00 | 131 | 09:00
Ghorashal | 135 | 19:00 | 128 | 12:00 | Rangpur | 132 | 13:00 | 125 | 20:00
Goalpara | 135 | 17:00 | 127 | 00:00 | Ruppur | 136 | 16:00 | 132 | 21:00
Gollamari | 136 | 17:00 | 127 | 13:00 | Saidpur | 133 | 17:00 | 123 | 22:00
Gopalganj | 135 | 17:00 | 129 | 12:00 | Satkhira | 132 | 17:00 | 120 | 23:00
Gopalganj-400 | 137 | 18:00 | 133 | 12:00 | Satmasjid | 135 | 03:00 | 127 | 12:00
Gulshan | 135 | 05:00 | 125 | 09:00 | Savar | 133 | 02:00 | 125 | 09:00
Halishahar | 134 | 00:00 | 129 | 09:00 | SevenRings | 136 | 06:00 | 127 | 13:00
Haripur | 128 | 07:00 | 124 | 12:00 | ShahCement | 128 | 02:00 | 123 | 12:00
HaripurSBU | 128 | 18:00 | 124 | 13:00 | Shahjadpur | 137 | 05:00 | 132 | 12:00
Hasnabad | 131 | 03:00 | 126 | 12:00 | Shahjibazar | 131 | 06:00 | 126 | 18:00
Hathazari | 135 | 14:00 | 132 | 02:00 | Shahmirpur | 134 | 00:00 | 131 | 09:00
Ishurdi | 138 | 17:00 | 132 | 22:00 | Shariatpur | 134 | 18:00 | 129 | 12:00
Jaldhaka | 131 | 14:00 | 119 | 20:00 | Sherpur | 125 | 21:00 | 110 | 12:00
Jamalpur | 129 | 21:00 | 114 | 00:00 | Shikalbaha | 124 | 00:00 | 120 | 09:00
Jashore | 136 | 16:00 | 120 | 11:00 | Shikalbaha-230 | 136 | 02:00 | 133 | 07:00
Jhenaidah | 138 | 17:00 | 122 | 12:00 | Shitalakhya | 129 | 05:00 | 123 | 12:00
Jhenaidah-230 | 138 | 17:00 | 128 | 01:00 | Sholosohor | 135 | 17:00 | 132 | 09:00
Joydebpur | 132 | 22:00 | 120 | 12:00 | Shyampur | 135 | 07:00 | 130 | 11:00
Joypurhat | 128 | 17:00 | 118 | 23:00 | Shyampur-230 | 134 | 04:00 | 129 | 12:00
Juldah | 134 | 00:00 | 130 | 09:00 | Siddhirganj | 128 | 02:00 | 123 | 12:00
Kabirpur | 134 | 21:00 | 119 | 12:00 | Sirajganj | 131 | 14:00 | 125 | 19:30
Kachua | 136 | 17:00 | 125 | 21:00 | Sonargaon | 127 | 19:00 | 122 | 10:00
Kaliakoir | 134 | 21:00 | 125 | 12:00 | Sreemongol | 131 | 08:00 | 126 | 14:00
Kallyanpur | 133 | 01:00 | 127 | 08:00 | Sreepur | 132 | 17:00 | 126 | 12:00
Kalurghat | 135 | 00:00 | 133 | 09:00 | Srinagar | 135 | 03:00 | 128 | 12:00
Kamrangirchar | 134 | 05:00 | 127 | 12:00 | SSM | 138 | 19:00 | 132 | 00:00
Kaptai | 137 | 22:00 | 135 | 3:00 | Sunamganj | 126 | 21:00 | 117 | 12:00
Kasba | 126 | 17:00 | 119 | 12:00 | Sylhet | 130 | 21:00 | 123 | 18:30
Kazla | 132 | 04:00 | 126 | 12:00 | Sylhet-132 | 129 | 21:00 | 123 | 13:00
Keranigonj | 135 | 03:00 | 128 | 13:00 | Tangail | 126 | 21:00 | 115 | 12:00
Khagrachori | 133 | 01:00 | 130 | 10:00 | Taraganj | 132 | 14:00 | 121 | 22:00
Khulna | 134 | 17:00 | 125 | 22:00 | Thakurgaon | 136 | 14:00 | 123 | 20:00
Khulna(S) | 136 | 17:00 | 128 | 21:00 | TK | 135 | 00:00 | 133 | 01:00
Khulshi | 132 | 00:00 | 129 | 09:00 | Tongi | 133 | 04:00 | 124 | 13:00
Kishoreganj | 126 | 17:00 | 118 | 12:00 | Ullahpara | 133 | 17:00 | 127 | 21:00
Kodda | 133 | 03:00 | 119 | 12:00 | Ullon | 135 | 00:00 | 124 | 11:00
KSRM | 135 | 17:00 | 130 | 00:00 | Uttara | 132 | 02:00 | 124 | 12:00
Kulaura | 134 | 21:00 | 128 | 18:00 | UttaraNew | 133 | 03:00 | 124 | 12:00
Kurigram | 130 | 14:00 | 119 | 21:00 | Zigatola | 135 | 06:00 | 128 | 12:00
Kushtia | 134 | 17:00 | 126 | 23:00
Laksam | 134 | 17:00 | 124 | 21:00
Lakshmipur | 127 | 17:00 | 116 | 21:00
Lalbag | 134 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division