## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-10-2025 | [28 empty] | Date: | 02-10-2025 | [28 empty] | Date: | 02-10-2025 | [28 empty] | Date: | 02-10-2025 | [28 empty] | Date: | 02-10-2025 | [14 empty] | Date: | 02-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 397 | 46.3 | 35 | 101 | 30 | 60 | 15 | 22 | 142 | 0 | 300 | 292 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 50 | 42 | 0 | 0 | 0 | 0 | 218 | 100 | 31 | 650 | 0 | 0 | 19 | 0 | 94 | 214 | 0 | 0 | 0 | 640 | 0 | 51 | 127 | 0 | 0 | 356 | 330 | 5 | 186 | 10 | 93 | 0 | 95 | 0 | 17 | 34 | 46 | 0 | 0 | 0 | 315 | 0 | 371 | 30 | 30 | 154 | 6 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 85 | 73 | 0 | 0 | 11 | 7301.3 | 847 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 653.98 | 0 | 47 | 0 | 0 | 50 | 0 | 95 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 202 | 0 | 210 | 0 | 0 | 0 | 406 | 0 | 0 | 140 | 49 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 304 | 1155 | 17 | 6446.98 | 13748.28 | 107.91
01:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 408 | 45.3 | 0 | 101 | 15 | 0 | 15 | 35 | 144 | 0 | 300 | 295 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 14 | 18 | 0 | 0 | 0 | 0 | 219 | 95 | 32 | 650 | 0 | 0 | 19 | 0 | 93 | 214 | 0 | 0 | 0 | 640 | 0 | 51 | 50 | 0 | 0 | 359 | 330 | 5 | 198 | 10 | 88 | 0 | 100 | 0 | 17 | 17 | 44 | 0 | 0 | 0 | 305 | 0 | 384 | 30 | 30 | 145 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 17 | 77 | 85 | 73 | 0 | 0 | 12 | 6991.3 | 847 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 644.29 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 210 | 0 | 0 | 0 | 409 | 0 | 0 | 140 | 49 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 304 | 1230 | 17 | 6242.29 | 13233.59 | 107.91
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 408 | 46.6 | 0 | 71 | 0 | 0 | 0 | 35 | 148 | 0 | 300 | 291 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 3 | 0 | 0 | 0 | 0 | 0 | 218 | 68 | 32 | 650 | 0 | 0 | 19 | 0 | 94 | 214 | 0 | 0 | 0 | 642 | 0 | 51 | 0 | 0 | 0 | 360 | 330 | 5 | 191 | 10 | 90 | 0 | 100 | 0 | 17 | 17 | 42 | 0 | 0 | 0 | 310 | 0 | 358 | 30 | 30 | 154 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 85 | 94 | 0 | 0 | 6 | 6731.6 | 847 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 637.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 208 | 0 | 0 | 0 | 349 | 0 | 0 | 139 | 49 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 304 | 1232 | 0 | 6095.85 | 12827.45 | 107.91
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 409 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 90 | 0 | 300 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 33 | 34 | 650 | 0 | 0 | 0 | 0 | 51 | 214 | 0 | 0 | 0 | 645 | 0 | 51 | 0 | 0 | 0 | 359 | 330 | 5 | 191 | 10 | 84 | 0 | 100 | 0 | 17 | 17 | 40 | 0 | 0 | 0 | 310 | 0 | 360 | 30 | 30 | 143 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 85 | 92 | 0 | 0 | 6 | 6428 | 847 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 640.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 207 | 0 | 0 | 0 | 339 | 0 | 0 | 139 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 305 | 1180 | 0 | 6004.65 | 12432.65 | 107.91
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 409 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 640 | 0 | 51 | 0 | 0 | 0 | 360 | 330 | 5 | 196 | 10 | 51 | 0 | 100 | 0 | 17 | 17 | 40 | 0 | 0 | 0 | 305 | 0 | 370 | 30 | 30 | 143 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 8 | 92 | 0 | 0 | 6 | 6097 | 847 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 0 | 636.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 207 | 0 | 0 | 0 | 349 | 0 | 0 | 139 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 115 | 220 | 0 | 303 | 1110 | 0 | 5880.83 | 11977.83 | 107.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 408 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 642 | 0 | 51 | 0 | 0 | 0 | 359 | 330 | 5 | 194 | 10 | 36 | 0 | 100 | 0 | 17 | 17 | 38 | 0 | 0 | 0 | 315 | 0 | 335 | 30 | 30 | 144 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 8 | 92 | 0 | 0 | 6 | 6056 | 847 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 638.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 207 | 0 | 0 | 0 | 350 | 0 | 0 | 140 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 115 | 220 | 0 | 303 | 1102 | 0 | 5696.88 | 11752.88 | 107.91
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 411 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 287 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0.03 | 218 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 643 | 0 | 51 | 0 | 0 | 0 | 360 | 295 | 5 | 180 | 10 | 34 | 0 | 100 | 0 | 17 | 17 | 36 | 0 | 1 | 0 | 305 | 0 | 312 | 30 | 30 | 143 | 4 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 77 | 8 | 91 | 0 | 0 | 6 | 5959.03 | 847 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 0 | 640.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 190 | 0 | 0 | 0 | 330 | 0 | 0 | 138 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 115 | 220 | 0 | 303 | 950 | 0 | 5352.92 | 11311.95 | 107.91
07:00 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 410 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 34 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0.4 | 218 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 648 | 4 | 51 | 0 | 0 | 0 | 280 | 280 | 5 | 203 | 10 | 34 | 0 | 100 | 0 | 17 | 17 | 34 | 0 | 7 | 0 | 315 | 0 | 335 | 30 | 30 | 148 | 4 | 0 | 84 | 20 | 0 | 18 | 165 | 0 | 77 | 8 | 88 | 0 | 1.33 | 6 | 5904.73 | 847 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 933 | 0 | 631.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 3 | 0 | 0 | 4.91 | 150 | 0 | 150 | 0 | 0 | 0 | 371 | 0 | 0.51 | 138 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 7 | 0.01 | 0 | 172 | 115 | 180 | 0 | 304 | 810 | 0 | 5158.36 | 11063.09 | 107.91
08:00 | 0 | 17 | 9 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 407 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 34 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0.48 | 218 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 640 | 2 | 51 | 0 | 0 | 0 | 280 | 280 | 5 | 201 | 10 | 34 | 0 | 68 | 0 | 17 | 17 | 34 | 0 | 21 | 0 | 315 | 0 | 335 | 30 | 30 | 151 | 4 | 0 | 81 | 20 | 0 | 18 | 165 | 0 | 77 | 8 | 88 | 0 | 9.71 | 3 | 5914.19 | 847 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 905 | 0 | 626.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 11 | 0 | 0 | 5.06 | 150 | 0 | 150 | 0 | 0 | 0 | 362 | 0 | 0.54 | 138 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 4.5 | 10 | 0.01 | 0 | 169 | 115 | 180 | 0 | 306 | 790 | 0 | 5116.56 | 11030.75 | 107.91
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 397 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 289 | 0 | 0 | 0 | 250 | 0 | 0 | 7 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 1.31 | 217 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 642 | 1 | 51 | 0 | 0 | 0 | 280 | 280 | 5 | 189 | 10 | 34 | 0 | 34 | 0 | 17 | 0 | 32 | 0 | 8 | 0 | 305 | 0 | 314 | 30 | 30 | 144 | 0 | 0 | 84 | 20 | 0 | 18 | 166 | 0 | 77 | 8 | 84 | 1 | 24.12 | 5 | 5761.43 | 846 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 888 | 0 | 739.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.04 | 27 | 0 | 0 | 20.17 | 159 | 0 | 163 | 0 | 0 | 0 | 338 | 0 | 3.3 | 140 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 4.7 | 41 | 0 | 0 | 168 | 115 | 180 | 0 | 303 | 788 | 0 | 5276.38 | 11037.81 | 107.91
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 400 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 286 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 1.36 | 221 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 642 | 1 | 10 | 0 | 0 | 4 | 280 | 280 | 5 | 192 | 10 | 34 | 0 | 32 | 0 | 17 | 0 | 32 | 0 | 4 | 0 | 310 | 0 | 330 | 30 | 30 | 139 | 0 | 0 | 40 | 20 | 0 | 18 | 166 | 0 | 55 | 8 | 72 | 1 | 10.5 | 6 | 5672.86 | 846 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 777 | 0 | 866.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.19 | 71 | 0 | 0 | 9.85 | 160 | 0 | 164 | 0 | 0 | 0 | 343 | 0 | 1.01 | 140 | 49 | 0 | 14 | 0 | 0 | 0 | 0 | 5.1 | 93 | 0.02 | 0 | 169 | 115 | 180 | 0 | 300 | 705 | 0 | 5318.46 | 10991.32 | 107.9
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 421 | 0 | 12 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 240 | 0 | 0 | 5 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 1.4 | 218 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 643 | 0 | 10 | 0 | 0 | 4 | 330 | 327 | 5 | 200 | 10 | 16 | 0 | 17 | 0 | 17 | 0 | 34 | 0 | 6 | 0 | 315 | 0 | 386 | 30 | 30 | 150 | 0 | 0 | 21 | 20 | 0 | 18 | 166 | 0 | 55 | 8 | 72 | 0 | 13.26 | 6 | 5815.66 | 847 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 772 | 0 | 813.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.53 | 78 | 0 | 0 | 38.54 | 168 | 0 | 172 | 0 | 0 | 0 | 364 | 0 | 3.12 | 140 | 49 | 0 | 13 | 0 | 0 | 0 | 0 | 1.8 | 28 | 0.03 | 0 | 140 | 100 | 220 | 0 | 303 | 655 | 0 | 5230.58 | 11046.24 | 107.9
12:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 441 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 240 | 0 | 0 | 8 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0.29 | 218 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 642 | 1 | 10 | 0 | 0 | 25 | 345 | 330 | 5 | 207 | 10 | 0 | 0 | 0 | 0 | 17 | 0 | 30 | 0 | 3 | 0 | 320 | 0 | 398 | 30 | 30 | 162 | 0 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 55 | 8 | 72 | 1 | 26.68 | 6 | 6008.97 | 847 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 772 | 0 | 869.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.04 | 39 | 0 | 0 | 34.9 | 182 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 2.53 | 140 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 4.4 | 37 | 0.04 | 0 | 153 | 115 | 220 | 0 | 304 | 668 | 0 | 5346.92 | 11355.89 | 107.9
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 401 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 640 | 1 | 25 | 0 | 0 | 25 | 352 | 280 | 5 | 194 | 10 | 0 | 0 | 0 | 0 | 17 | 0 | 32 | 0 | 5 | 0 | 315 | 0 | 379 | 30 | 30 | 160 | 0 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 76 | 8 | 73 | 1 | 5.1 | 6 | 5898.1 | 847 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 754 | 0 | 876.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.29 | 65 | 0 | 0 | 25.09 | 198 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 1.98 | 140 | 49 | 0 | 12 | 0 | 0 | 0 | 0 | 7.5 | 105 | 0.07 | 0 | 170 | 115 | 220 | 0 | 302 | 824 | 0 | 5635.69 | 11533.79 | 107.9
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 412 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 240 | 0 | 0 | 5 | 52 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 640 | 2 | 51 | 0 | 0 | 15 | 280 | 280 | 5 | 196 | 10 | 0 | 0 | 0 | 0 | 5 | 0 | 38 | 0 | 7 | 0 | 310 | 0 | 330 | 30 | 30 | 143 | 0 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 77 | 8 | 72 | 2 | 3.14 | 6 | 5761.14 | 847 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 746 | 0 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.98 | 100 | 0 | 0 | 28.28 | 181 | 0 | 176 | 0 | 0 | 0 | 356 | 0 | 2.09 | 140 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 1.9 | 58 | 0.06 | 0 | 173 | 115 | 180 | 0 | 304 | 898 | 0 | 5551.31 | 11312.45 | 107.9
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 411 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 0 | 0 | 0 | 240 | 0 | 0 | 3 | 52 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.58 | 220 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 640 | 1 | 51 | 0 | 0 | 18 | 280 | 280 | 5 | 195 | 10 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 0 | 7 | 0 | 315 | 0 | 326 | 30 | 30 | 145 | 6 | 0 | 84 | 30 | 0 | 16 | 166 | 0 | 77 | 8 | 72 | 1 | 16.12 | 6 | 5766.7 | 847 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 756 | 0 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.34 | 27 | 0 | 0 | 6.41 | 176 | 0 | 170 | 0 | 0 | 0 | 355 | 0 | 0.61 | 140 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 1.9 | 101 | 0.06 | 0 | 170 | 115 | 180 | 0 | 302 | 900 | 0 | 5470.32 | 11237.02 | 107.9
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 422 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0.48 | 220 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 640 | 2 | 10 | 0 | 0 | 20 | 280 | 280 | 5 | 200 | 10 | 0 | 0 | 0 | 0 | 19 | 0 | 32 | 0 | 5 | 0 | 305 | 0 | 333 | 30 | 30 | 140 | 5 | 0 | 22 | 30 | 0 | 16 | 166 | 0 | 77 | 16 | 72 | 1 | 3.22 | 6 | 5654.7 | 846 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 750 | 0 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.36 | 18 | 0 | 0 | 5.06 | 172 | 0 | 167 | 0 | 0 | 0 | 370 | 0 | 0.52 | 140 | 48 | 0 | 6 | 0 | 0 | 0 | 0 | 1.1 | 8 | 0.07 | 0 | 171 | 100 | 180 | 0 | 304 | 800 | 0 | 5254.11 | 10908.81 | 107.9
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 431 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 303 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.14 | 220 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 640 | 1 | 10 | 0 | 0 | 23 | 280 | 280 | 5 | 204 | 10 | 0 | 0 | 0 | 5 | 19 | 0 | 34 | 0 | 2 | 0 | 315 | 0 | 334 | 30 | 30 | 150 | 5 | 0 | 22 | 30 | 0 | 16 | 166 | 0 | 55 | 16 | 72 | 0 | 1.22 | 6 | 5680.36 | 847 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 757 | 0 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 3 | 0 | 0 | 2.68 | 179 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0.25 | 137 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0.03 | 0 | 172 | 115 | 220 | 0 | 304 | 760 | 0 | 5295.46 | 10975.82 | 107.9
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 423 | 16 | 0 | 58 | 83 | 0 | 0 | 9 | 15 | 0 | 300 | 305 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 132 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 36 | 650 | 0 | 0 | 5 | 0 | 0 | 182 | 0 | 0 | 0 | 640 | 0 | 25 | 0 | 0 | 19 | 305 | 305 | 5 | 204 | 10 | 5 | 0 | 22 | 8 | 19 | 52 | 40 | 4 | 0 | 0 | 300 | 0 | 385 | 30 | 30 | 142 | 7 | 0 | 70 | 30 | 0 | 16 | 166 | 0 | 77 | 38 | 74 | 0 | 0 | 6 | 6332 | 846 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 0 | 1052 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 166 | 0 | 0 | 0 | 402 | 0 | 0 | 138 | 49 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 115 | 220 | 0 | 326 | 832 | 0 | 5870 | 12202 | 107.9
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 391 | 29 | 0 | 76 | 45 | 0 | 0 | 30 | 44 | 0 | 300 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 50 | 0 | 0 | 0 | 0 | 0 | 221 | 4 | 34 | 650 | 0 | 0 | 9 | 0 | 7 | 182 | 0 | 0 | 0 | 643 | 0 | 51 | 0 | 0 | 21 | 360 | 330 | 5 | 183 | 10 | 54 | 0 | 61 | 9 | 20 | 44 | 38 | 8 | 0 | 0 | 300 | 0 | 350 | 30 | 30 | 151 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 74 | 0 | 0 | 6 | 6486 | 847 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1034 | 0 | 1205 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 185 | 0 | 0 | 0 | 333 | 0 | 0 | 139 | 49 | 50 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 115 | 180 | 0 | 402 | 1050 | 0 | 6428 | 12914 | 107.9
19:30 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 391 | 15 | 0 | 52 | 45 | 0 | 0 | 17 | 17 | 0 | 300 | 292 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 8 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 641 | 0 | 51 | 0 | 0 | 21 | 359 | 330 | 5 | 191 | 10 | 60 | 0 | 60 | 9 | 20 | 47 | 40 | 8 | 0 | 0 | 310 | 0 | 362 | 30 | 30 | 149 | 7 | 0 | 84 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 74 | 0 | 0 | 6 | 6400 | 847 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 0 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 166 | 0 | 0 | 0 | 340 | 0 | 0 | 137 | 49 | 50 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 180 | 0 | 401 | 1080 | 0 | 6421 | 12821
20:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 410 | 18.3 | 0 | 49 | 45 | 0 | 0 | 24 | 17 | 0 | 300 | 295 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 641 | 0 | 51 | 0 | 0 | 19 | 359 | 330 | 5 | 197 | 10 | 58 | 0 | 60 | 3 | 17 | 47 | 40 | 8 | 0 | 0 | 310 | 0 | 386 | 30 | 30 | 151 | 7 | 0 | 83 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 74 | 0 | 0 | 6 | 6403.3 | 846 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 168 | 0 | 0 | 0 | 348 | 0 | 0 | 136 | 49 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 180 | 0 | 402 | 1085 | 0 | 6457 | 12860.3 | 107.91
21:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 420 | 0 | 0 | 33 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 641 | 0 | 51 | 0 | 0 | 16 | 359 | 330 | 5 | 200 | 10 | 63 | 0 | 65 | 9 | 17 | 48 | 40 | 8 | 0 | 0 | 310 | 0 | 386 | 30 | 30 | 155 | 7 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 84 | 0 | 0 | 6 | 6348 | 846 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 173 | 0 | 0 | 0 | 359 | 0 | 0 | 139 | 49 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 403 | 1100 | 0 | 6539 | 12887 | 107.92
22:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 415 | 0 | 0 | 33 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 640 | 0 | 51 | 0 | 0 | 28.6 | 359 | 330 | 5 | 200 | 10 | 65 | 0 | 65 | 0 | 20 | 49 | 40 | 8 | 0 | 0 | 310 | 0 | 386 | 30 | 30 | 159 | 7 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 84 | 0 | 0 | 6 | 6350.6 | 847 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 176 | 0 | 0 | 0 | 362 | 0 | 0 | 138 | 49 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 402 | 1100 | 0 | 6550 | 12900.6 | 107.93
23:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 410 | 0 | 0 | 33 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 640 | 0 | 51 | 0 | 0 | 34.26 | 359 | 330 | 5 | 199 | 10 | 63 | 0 | 64 | 0 | 20 | 45 | 42 | 8 | 0 | 0 | 310 | 0 | 376 | 30 | 30 | 155 | 7 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 78 | 65 | 81 | 0 | 0 | 6 | 6330.26 | 847 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 172 | 0 | 0 | 0 | 349 | 0 | 0 | 140 | 49 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 401 | 1100 | 0 | 6520 | 12850.26 | 107.94
Total KWH | 0 | 912000 | 373440 | 0 | 0 | 0 | 0 | 0 | 8481600 | 0 | 9845310 | 158760 | 91440 | 922032 | 355680 | 43658 | 19547 | 153651 | 544320 | 0 | 7589500 | 7107084 | 0 | 0 | 62574 | 6251403 | 0 | 0 | 61547 | 1866000 | 455400 | 466920 | 0 | 0 | 0 | 0 | 0 | 0 | 844320 | 142910 | 78528 | 0 | 0 | 0 | 7719 | 5267302 | 286500 | 204036 | 15992727.27 | 0 | 0 | 26400 | 0 | 314473 | 4722014 | 0 | 0 | 0 | 15436362 | 13095 | 1089816 | 95345 | 0 | 234700 | 8217600 | 7498000 | 136320 | 4778000 | 266616 | 934080 | 15950 | 1345920 | 36960 | 407050 | 475380 | 880320 | 56198 | 74645 | 0 | 7535000 | 0 | 8889000 | 717000 | 718744 | 3584864 | 112800 | 0 | 1725120 | 658464 | 0 | 432000 | 4419510 | 19440 | 1754400 | 902400 | 1844160 | 7450 | 115380 | 151200 | 149228084.27 | 20506181 | 5837184 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 95760 | 23025460 | 0 | 20851883 | 0 | 28138 | 0 | 0 | 26880 | 0 | 148176 | 12621 | 0 | 105062 | 385740 | 20319 | 0 | 182256 | 4340727 | 0 | 4548918 | 0 | 0 | 0 | 8842036 | 0 | 16140 | 3421000 | 1144145 | 426555 | 119875 | 493353 | 0 | 0 | 0 | 34639.56 | 513360 | 406 | 0 | 5193000 | 2713000 | 5233020 | 0 | 7854545 | 23524363.64 | 19200 | 140575943.2 | 289804027.47

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-10-2025 | during | 03-10-2025 | during | 03-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 366 | 320 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 285 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 29 | 53.97 | 53.97 | 49 | 49 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 45 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 30 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 17 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 81 | 300 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 76 | 149 | 149 | 100 | 100 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 105 | 105 | 87 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 44 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 441 | 391 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 144 | 144 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 1833 | 2064 | 5807.2 | 5789.2 | 5275.04 | 5552.04
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 9 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 200 | 182 | 195 | 195 | 195 | 195 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 7 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 64 | 75 | 64 | 75 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 42 | 34 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.29 | 0 | 3.71 | 0 | 3.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 30 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 4 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 54 | 159.86 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 642 | 643 | 1224 | 1224 | 1224 | 1224 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 36 | 39 | 28 | 30 | 28 | 30 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 840 | 840 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1789.29 | 1839 | 3668.43 | 3674.72 | 3240.07 | 3366.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 207 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 25 | 21 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 10 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 61 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 38 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 43.5 | 43.5 | 34 | 34 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 44 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 54 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 3 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 982 | 1194 | 2633.86 | 2603.86 | 2408.36 | 2387.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-10-2025 | during | 03-10-2025 | during | 03-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 72 | 74 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 65 | 150 | 150 | 150 | 150 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 78 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 26.68 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 168.68 | 223 | 500.9 | 461 | 447.4 | 407.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 151 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 7 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 398 | 350 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1236 | 1166 | 1296 | 1296 | 1234 | 1234
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 847 | 847 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 249 | 240 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 6 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 772 | 1034 | 0 | 0 | 1148 | 1148 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1912 | 2159 | 2384 | 2312 | 3337 | 3265
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 402 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 668 | 1050 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 153 | 268 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.04 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1460.04 | 2015 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 14.04 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 168 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 185 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 333 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 93 | 93 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.53 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 869.01 | 1205 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.9 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 39 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1735.48 | 1941 | 3185.46 | 3018.87 | 3097.88 | 2931.29
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 44 | 46 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 140 | 139 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 75 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 22 | 0 | 22 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 37 | 0 | 85.94 | 0 | 85.94 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 239.4 | 313 | 561.94 | 448 | 555.94 | 444
System Total |  |  |  |  | 28823.2 | 28365.955 | 11355.89 | 12914 | 22184.79 | 21749.65 | 21559.69 | 21550.41
Forecast Scenario (03-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12840 |  | 0 |  | 12840
|  |  |  | 1:00 | 12330 |  | 0 |  | 12330
|  |  |  | 2:00 | 11920 |  | 0 |  | 11920
|  |  |  | 3:00 | 11530 |  | 0 |  | 11530
|  |  |  | 4:00 | 11070 |  | 0 |  | 11070
|  |  |  | 5:00 | 10850 |  | 0 |  | 10850
|  |  |  | 6:00 | 10410 |  | 0 |  | 10410
|  |  |  | 7:00 | 10160 |  | 0 |  | 10160
|  |  |  | 8:00 | 10130 |  | 0 |  | 10130
|  |  |  | 9:00 | 10230 |  | 0 |  | 10230
|  |  |  | 10:00 | 10590 |  | 0 |  | 10590
|  |  |  | 11:00 | 10940 |  | 0 |  | 10940
|  |  |  | 12:00 | 11500 |  | 0 |  | 11500
|  |  |  | 13:00 | 12000 |  | 0 |  | 12000
|  |  |  | 14:00 | 11400 |  | 0 |  | 11400
|  |  |  | 15:00 | 11100 |  | 0 |  | 11100
|  |  |  | 16:00 | 10800 |  | 0 |  | 10800
|  |  |  | 17:00 | 10770 |  | 0 |  | 10770
|  |  |  | 18:00 | 11600 |  | 0 |  | 11600
|  |  |  | 18:30 | 11900 |  | 0 |  | 11900
|  |  |  | 19:00 | 12410 |  | 0 |  | 12410
|  |  |  | 19:30 | 12320 |  | 0 |  | 12320
|  |  |  | 20:00 | 12260 |  | 0 |  | 12260
|  |  |  | 21:00 | 12280 |  | 0 |  | 12280
|  |  |  | 22:00 | 12100 |  | 0 |  | 12100
|  |  |  | 23:00 | 12150 |  | 0 |  | 12150
Probable Maximum Temperature: |  |  | 30.10°C
Probable Maximum Demand at Day Peak: |  |  | 11500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12410.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12410.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 273.37 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:29 hrs on 03-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11355.89 | MW | 12:00 Hr. | Energy Generated |  |  | 289.804 |  | MKWHr.
| Day Peak Demand |  |  | 11355.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12914 | MW | 19:00 Hr. | Energy Demand |  |  | 289.804 |  | MKWHr.
| Evening Peak Demand |  |  | 12914 | MW | 19:00 Hr. | Maximum Temperature |  |  | 29.1 |  | °C
| Minimum Generation of the Day |  |  | 10908.81 | MW | 16:00 Hr. | Total Gas Supplied |  |  | 943.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 13748.28 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.3407 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.1972 | 0 | 5.5031 | 0 | 0 | 0.061547 | 0 | 0 | 45.7619 | Gas | 129.9189 | Gas | 462727810.56
| Chattogram Zone |  |  | 4.9261 | 31.4291 | 0.84881 | 0 | 5.2673 | 0.020814 | 0 | 0.84432 | 43.3364 | Coal | 95.5916 | Coal | 554041626.6852
| Cumilla Zone |  |  | 22.6441 | 0 | 2.9439 | 0 | 0 | 0.074645 | 0.88032 | 0 | 26.5429 | HFO | 13.2985 | HFO | 243003580.74
| Mymensingh Zone |  |  | 1.8442 | 0 | 2.8274 | 0 | 0 | 0.12283 | 0 | 0 | 4.7944 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7925 | Hydro | 5.2673 | Hydro | 526730.2
| Khulna Zone |  |  | 5.8372 | 23.0255 | 0 | 0 | 0 | 0.09576 | 21.4182 | 0 | 50.3766 | Solar | 1.7331 | Solar | 26972861.3476
| Barishal Zone |  |  | 7.946 | 36.5719 | 0.0192 | 0 | 0 | 0.000406 | 0 | 0 | 44.5375 | Import | 43.1504 | Import | 248049385.3
| Rajshahi Zone |  |  | 17.7317 | 0 | 0.23613 | 0 | 0 | 0.6892 | 20.8519 | 0 | 39.5089 | Wind | 0.84432 | Wind | 12445276.8
| Rangpur Zone |  |  | 0 | 4.5651 | 0.91991 | 0 | 0 | 0.66787 | 0 | 0 | 6.1529
| Total |  |  | 129.9189 | 95.5916 | 13.2985 | 0 | 5.2673 | 1.7331 | 43.1504 | 0.84432 | 289.804
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 462727810.56 |  | Hydro | 526730.2
|  |  |  | Coal | 554041626.6852 |  | Solar | 26972861.3476
|  |  |  | HFO | 243003580.74 |  | Import | 248049385.3
|  |  |  | HSD | 0 |  | Wind | 12445276.8
[5 empty] | Total: | 154,77,67,271 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.5062 | Peak Hr Flow | 847.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45891970.96 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.8519 | Peak Hr Flow | 1205.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2360 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88032 | Peak Hr Flow | 38.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2482 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.2384 | Peak Hr Flow | 2090.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4597
|  |  |  | Chattogram |  | 0 |  | 1168
|  |  |  | Cumilla |  | 0 |  | 1135
|  |  |  | Mymensingh |  | 0 |  | 1066
|  |  |  | Sylhet |  | 0 |  | 482
|  |  |  | Khulna |  | 0 |  | 1509
|  |  |  | Barishal |  | 0 |  | 377
|  |  |  | Rajshahi |  | 0 |  | 1247
|  |  |  | Rangpur |  | 0 |  | 740
|  |  |  | Total |  | 0 |  | 12321
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 |  | Adani Power Jharkhand Ltd. unit-1 was sync.
| 08:46 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 09:36 |  | Ashuganj 420 MW CCPP (East) GT was sync.
| 10:20 | 17:35 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to Opgw conductor work
| 12:00 |  | Day Peak Generation: 11353 MW.
| 12:10 | 13:21 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH R, PH Y, Z1,
Dist Send. relays Due to None
| 19:00 |  | Evening Peak Generation is 12914 MW.
| 21:30 | 23:21 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Atrai 33kv feeder jamper maintenance which
is connected T3(132/33kv) 33kv Bus.All loadshed purpose of the feeder .
| 21:30 | 23:20 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Atrai 33kv feeder jamper maintenance which
is connected under T3(132/33kv) 33kv Bus.All loadshed purpose of the feeder .
| 23:09 | 23:29 | Patuakhali 132/33kV S/S 415T (T-2) LT Tripped showing O/C relays Due to Due to Amtoli | [7 empty] | 23.0MW load
|  |  | 33kv O/C, E/F with heavy flashing at the underground cable tip. | [7 empty] | interrup.
| 23:09 | 23:29 | Patuakhali 132/33kV S/S 425T (T-3) LT Tripped showing O/C relays Due to Due to Amtoli | [7 empty] | 23.0MW load
|  |  | 33kv O/C, E/F with heavy flashing at the underground cable tip. | [7 empty] | interrup.
| 02:41 |  | Rahanpur 400/132kV S/S AT-02 HT Tripped showing SIEMENS relays Due to 87 Trip,R PH
Trip,GEN Trip
| 02:41 |  | Rahanpur 400/132kV S/S AT-02 LT Tripped showing SIEMENS relays Due to 87 Trip,R PH
Trip,GEN Trip
| 05:54 | 06:45 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Manikganj 132/33kV end showing Distrance | [7 empty] | 72.0MW load
|  |  | relays Due to Zone-2 | [7 empty] | interrup. Manikganj
132/33kV end
| 05:54 | 06:52 | Kabirpur - Manikganj 132kV Ckt-2 Tripped from Manikganj 132/33kV end showing Distrance | [7 empty] | 18.0MW load
|  |  | relays Due to Zone-2 | [7 empty] | interrup. Manikganj
132/33kV end
| 07:00 |  | MInimum Generation: 10168 MW.
| 07:24 |  | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to
Hathazari main bus section work at hathazari side.
| 07:24 |  | Baroaulia-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroaulia 132/33kV end Due to
Hathazari main BUS section work at Hathazari side.
| 07:24 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- One GT shutdown given on accordance
with NLDC demand.
| 07:24 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 07:44 |  | Bogura 132/33kV S/S Transformer-3 LT Tripped showing Int. O/C & E/F Trip. relays Due to | [7 empty] | 54.0MW load
|  |  | 33 kv PBS Bogura-2 Feeder O/C & E/F Trip. | [7 empty] | interrup.
| 07:44 |  | Bogura 132/33kV S/S Transformer-4 LT Tripped showing Inst. O/C & E/F Trip. relays Due to | [7 empty] | 54.0MW load
|  |  | 33 kv PBS Bogura-2 Feeder O/C & E/F Trip. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 320 | 8481600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7589500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 7107084 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 19547 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6251403 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 29 | 158760 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 45 | 355680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 30 | 153651 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 62574 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 455400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 466920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 373440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 43658 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 76 | 922032 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 912000 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 44 | 544320 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 61547 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 91440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 391 | 9845310 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1866000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2064 | 45761866
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 13095 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 9 | 26400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5267302 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 182 | 4722014 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 7 | 314473 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 78528 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 142910 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 204036 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 7719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 4 | 286500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 643 | 15436362 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 39 | 844320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15992727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 1839 | 43336386.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 183 | 4778000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8217600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7498000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 21 | 234700 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 266616 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 136320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1089816 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 95345 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 15950 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 61 | 1345920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 38 | 880320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 56198 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 407050 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 44 | 475380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 36960 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 934080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 74645 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1194 | 26542900
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 74 | 1844160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 902400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1754400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 115380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 151200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 19440 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 223 | 4794430
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 718744 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3584864 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 658464 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1725120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 4419510 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 112800 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7535000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8889000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1166 | 28792502
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 847 | 20506181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 240 | 5837184 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 95760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1034 | 23025460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2159 | 50376585
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 402 | 7854545 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2713000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 23524363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5233020 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 19200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5193000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 406 | -
Barishal Area Total |  |  |  |  | 2858 | 2015 | 44537534.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 105062 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 28138 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 12621 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 4340727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4548918 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 333 | 8842036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 20319 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 148176 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 26880 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16140 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1205 | 20851883 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 182256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 385740 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1941 | 39508896
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1144145 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 139 | 3421000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 75 | 493353 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34639.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 426555 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 119875 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 513360 | -
Rangpur Area Total |  |  |  |  | 950 | 313 | 6152927.56
Eastern Grid Total |  |  |  |  | 17385.715 | 6486 | 149228084.27
Western Grid Total |  |  |  |  | 10980.24 | 6428 | 140575943.2
National Grid Total |  |  |  |  | 28365.955 | 12914 | 289804027.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8448.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3873.2 | MW
i) Dhaka area |  |  | 4596.98 |  | MW | i) Khulna area |  |  |  | 1509 | MW
ii) Chattogram area |  |  | 1168.5 |  | MW | ii) Barishal area |  |  |  | 377 | MW
iii) Cumilla area |  |  | 1135.13 |  | MW | iii) Rajshahi area |  |  |  | 1247.2 | MW
iv) Mymensingh area |  |  | 1066 |  | MW | iv) Rangpur area |  |  |  | 740 | MW
v) Sylhet area |  |  | 482 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12321.81 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 11:00 | 67 | Hathazari | 79 | 00:00 | 133 | PHP | 2 | 01:00
2 | AKSML | 143 | 13:00 | 68 | Ishurdi | 69 | 01:00 | 134 | Pabna | 87 | 20:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jaldhaka | 64 | 00:00 | 135 | Palashbari | 98 | 00:00
4 | Agargaon | 99 | 13:00 | 70 | Jamalpur | 110 | 20:00 | 136 | Panchagarh | 55 | 18:30
5 | Agrabad | 82 | 00:00 | 71 | Jashore | 125 | 00:00 | 137 | Patiya | 11 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jhenaidah | 117 | 19:00 | 138 | Patuakhali | 58.5 | 22:00
7 | Ashuganj | 80 | 01:00 | 73 | Joydebpur | 124 | 00:00 | 139 | Payra | 32 | 01:00
8 | BSRM | 116 | 01:00 | 74 | Joypurhat | 56 | 00:00 | 140 | Postogola | 64 | 12:00
9 | Bagerhat | 80 | 00:00 | 75 | Juldah | 16.5 | 00:00 | 141 | Purbachal | 20 | 00:00
10 | Bajitpur | 89 | 00:00 | 76 | KSRM | 23 | 07:00 | 142 | Purbasadipur | 91 | 00:00
11 | Bakulia | 82 | 00:00 | 77 | Kabirpur | 215 | 09:00 | 143 | Rahanpur | 36 | 00:00
12 | Banani | 30 | 13:00 | 78 | Kachua | 86 | 00:00 | 144 | Rahim | 26 | 09:00
13 | Bangabhaban | 5 | 11:00 | 79 | Kallyanpur | 99 | 00:00 | 145 | Rajbari | 75 | 00:00
14 | Barapukuria | 53 | 18:30 | 80 | Kalurghat | 30 | 00:00 | 146 | Rajendrapur | 120 | 00:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 71 | 13:00 | 147 | Rajshahi | 92 | 00:00
16 | Barishal | 96 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 84 | 13:00
17 | Barishal-230 | 82 | 00:00 | 83 | Kasba | 32 | 21:00 | 149 | Ramganj | 106 | 01:00
18 | Baroaulia | 58 | 07:00 | 84 | Kazla | 92 | 12:00 | 150 | Rampur | 45 | 00:00
19 | Baroirhat | 57 | 00:00 | 85 | Keranigonj | 74 | 00:00 | 151 | Rangamati | 16 | 18:30
20 | Bashundhara | 161 | 13:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rangpur | 124 | 18:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 60 | 00:00 | 153 | Ruppur | 7.2 | 11:00
22 | Beanibazar | 70 | 00:00 | 88 | Khulshi | 155 | 01:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 58 | 00:00 | 89 | Kishoreganj | 116 | 19:00 | 155 | Saidpur | 75 | 18:30
24 | Bhaluka | 142 | 18:00 | 90 | Kodda | 289 | 18:30 | 156 | Satkhira | 122 | 00:00
25 | Bhandaria | 52 | 00:00 | 91 | Kulaura | 42 | 00:00 | 157 | Satmasjid | 91 | 13:00
26 | Bhangura | 33 | 00:00 | 92 | Kurigram | 55 | 18:30 | 158 | Savar | 182 | 15:00
27 | Bheramara(GK) | 62 | 00:00 | 93 | Kushtia | 133 | 00:00 | 159 | SevenRings | 6.14 | 10:00
28 | Bhulta | 204 | 20:00 | 94 | Laksam | 35 | 04:00 | 160 | ShahCement | 22 | 09:00
29 | Bog-Sherpur | 62 | 02:00 | 95 | Lakshmipur | 32 | 00:00 | 161 | Shahjadpur | 74 | 19:30
30 | Bogura | 142 | 01:00 | 96 | Lalbag | 60 | 13:00 | 162 | Shahjibazar | 114 | 00:00
31 | Borhanuddin | 94 | 23:00 | 97 | Lalmonirhat | 70 | 21:00 | 163 | Shahmirpur | 44 | 00:00
32 | Brahmanbaria | 128 | 00:00 | 98 | MI_Cement | 18 | 17:00 | 164 | Shariatpur | 77 | 00:00
33 | Cantonment | 114 | 13:00 | 99 | Madanganj | 32 | 00:00 | 165 | Sherpur | 134 | 00:00
34 | Chandina | 14.14 | 15:00 | 100 | Madaripur | 106 | 00:00 | 166 | Shikalbaha | 26 | 18:30
35 | Chandpur | 78 | 01:00 | 101 | Madartek | 80 | 01:00 | 167 | Shitalakhya | 71.4 | 13:00
36 | Chandraghona | 33 | 19:00 | 102 | Madunaghat | 53 | 00:00 | 168 | Sholosohor | 38 | 00:00
37 | Chapai | 64 | 00:00 | 103 | Magura | 56 | 00:00 | 169 | Shyampur | 96 | 12:00
38 | Charsaidpur | 17 | 00:00 | 104 | Mahasthangarh | 72 | 00:00 | 170 | Siddhirganj | 104 | 15:00
39 | Chauddagram | 64 | 00:00 | 105 | Maijdee | 23 | 17:00 | 171 | Sirajganj | 96 | 18:30
40 | Chhatak | 33 | 22:00 | 106 | Manikganj | 117 | 21:00 | 172 | Sonargaon | 127 | 03:00
41 | Chowmuhani | 161 | 00:00 | 107 | Maniknagar | 54 | 00:00 | 173 | Sreemongol | 68 | 01:00
42 | Chuadanga | 104 | 00:00 | 108 | Matarbari | 47 | 00:00 | 174 | Sreepur | 101 | 18:00
43 | Coxsbazar | 124 | 01:00 | 109 | Matuail | 70 | 10:00 | 175 | Srinagar | 43.2 | 00:00
44 | Cumilla(N) | 124 | 00:00 | 110 | Millgate | 104 | 12:00 | 176 | Sunamganj | 50 | 22:00
45 | Cumilla(S) | 125 | 00:00 | 111 | Mirpur | 106 | 13:00 | 177 | Sylhet | 48 | 02:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 10 | 00:00 | 178 | Sylhet-132 | 105 | 18:00
47 | Daudkandi | 115 | 00:00 | 113 | Mirzapur | 45 | 00:00 | 179 | TK | 24.5 | 00:00
48 | DhakaUniversity | 46 | 13:00 | 114 | Mithapukur | 58 | 00:00 | 180 | Tangail | 146 | 18:30
49 | Dhamrai | 122 | 18:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 18 | 00:00
50 | Dhanmondi | 92.3 | 13:00 | 116 | Mogbazar | 72.8 | 01:00 | 182 | Thakurgaon | 86 | 19:00
51 | Dohazari | 92 | 18:00 | 117 | Mongla | 31 | 00:00 | 183 | Tongi | 104 | 11:00
52 | Faridpur | 162 | 00:00 | 118 | Motijheel | 31 | 00:00 | 184 | Ullahpara | 34 | 19:00
53 | Fatullah | 102 | 10:00 | 119 | Muktagacha | 33 | 18:00 | 185 | Ullon | 45 | 00:00
54 | Fenchuganj | 37 | 01:00 | 120 | Munshiganj | 110 | 00:00 | 186 | Uttara | 68 | 13:00
55 | Feni | 102 | 00:00 | 121 | Muradnagar | 37 | 00:00 | 187 | UttaraNew | 54 | 00:00
56 | GPH | 77 | 00:00 | 122 | Mymensingh | 184 | 00:00 | 188 | Zigatola | 62 | 00:00
57 | Ghatail | 82 | 18:30 | 123 | Naogaon | 114 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 51 | 00:00
59 | Ghorashal-230 | 96 | 00:00 | 125 | Narinda | 42 | 13:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 174 | 00:00
61 | Gollamari | 82 | 00:00 | 127 | Natore | 131 | 00:00
62 | Gopalganj | 96 | 00:00 | 128 | Nawabganj | 44.8 | 00:00
63 | Gulshan | 78 | 13:00 | 129 | Netrakona | 125 | 18:30
64 | Halishahar | 51.5 | 13:00 | 130 | New | 46.6 | 11:00
65 | HaripurSBU | 130 | 16:00 | 131 | Niamatpur | 68 | 00:00
66 | Hasnabad | 89 | 00:00 | 132 | Noapara | 38 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13748.28 | 0 |  | 13748.28
1:00 | 13233.59 | 0 |  | 13233.59
2:00 | 12827.45 | 0 |  | 12827.45
3:00 | 12432.65 | 0 |  | 12432.65
4:00 | 11977.83 | 0 |  | 11977.83
5:00 | 11752.88 | 0 |  | 11752.88
6:00 | 11311.95 | 0 |  | 11311.95
7:00 | 11063.09 | 0 |  | 11063.09
8:00 | 11030.75 | 0 |  | 11030.75
9:00 | 11037.81 | 0 |  | 11037.81
10:00 | 10991.32 | 0 |  | 10991.32
11:00 | 11046.24 | 0 |  | 11046.24
12:00 | 11355.89 | 0 |  | 11355.89
13:00 | 11533.79 | 0 |  | 11533.79
14:00 | 11312.45 | 0 |  | 11312.45
15:00 | 11237.02 | 0 |  | 11237.02
16:00 | 10908.81 | 0 |  | 10908.81
17:00 | 10975.82 | 0 |  | 10975.82
18:00 | 12202 | 0 |  | 12202
19:00 | 12914 | 0 |  | 12914
19:30 | 12821 | 0 |  | 12821
20:00 | 12860.3 | 0 |  | 12860.3
21:00 | 12887 | 0 |  | 12887
22:00 | 12900.6 | 0 |  | 12900.6
23:00 | 12850.26 | 0 |  | 12850.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7301.3 | 6446.98 | 13748.28 | DAILY GENERATION CURVE
00:30 | 7146.3 | 6344.635 | 13490.935
01:00 | 6991.3 | 6242.29 | 13233.59 | 02-10-2025
01:30 | 6861.45 | 6169.07 | 13030.52
02:00 | 6731.6 | 6095.85 | 12827.45
02:30 | 6579.8 | 6050.25 | 12630.05
03:00 | 6428 | 6004.65 | 12432.65
03:30 | 6262.5 | 5942.74 | 12205.24
04:00 | 6097 | 5880.83 | 11977.83
04:30 | 6076.5 | 5788.855 | 11865.355
05:00 | 6056 | 5696.88 | 11752.88
05:30 | 6007.515 | 5524.9 | 11532.415
06:00 | 5959.03 | 5352.92 | 11311.95
06:30 | 5931.88 | 5255.64 | 11187.52
07:00 | 5904.73 | 5158.36 | 11063.09
07:30 | 5909.46 | 5137.46 | 11046.92
08:00 | 5914.19 | 5116.56 | 11030.75
08:30 | 5837.81 | 5196.47 | 11034.28
09:00 | 5761.43 | 5276.38 | 11037.81
09:30 | 5717.145 | 5297.42 | 11014.565
10:00 | 5672.86 | 5318.46 | 10991.32
10:30 | 5744.26 | 5274.52 | 11018.78
11:00 | 5815.66 | 5230.58 | 11046.24
11:30 | 5912.315 | 5288.75 | 11201.065
12:00 | 6008.97 | 5346.92 | 11355.89
12:30 | 5953.535 | 5491.305 | 11444.84
13:00 | 5898.1 | 5635.69 | 11533.79
13:30 | 5829.62 | 5593.5 | 11423.12
14:00 | 5761.14 | 5551.31 | 11312.45
14:30 | 5763.92 | 5510.815 | 11274.735
15:00 | 5766.7 | 5470.32 | 11237.02
15:30 | 5710.7 | 5362.215 | 11072.915
16:00 | 5654.7 | 5254.11 | 10908.81
16:30 | 5667.53 | 5274.785 | 10942.315
17:00 | 5680.36 | 5295.46 | 10975.82
17:30 | 6006.18 | 5582.73 | 11588.91
18:00 | 6332 | 5870 | 12202
18:30 | 6409 | 6149 | 12558
19:00 | 6486 | 6428 | 12914
19:30 | 6400 | 6421 | 12821
20:00 | 6403.3 | 6457 | 12860.3
20:30 | 6375.65 | 6498 | 12873.65 |  | Executive Engineer
21:00 | 6348 | 6539 | 12887 |  | Network Operation Division
21:30 | 6349.3 | 6544.5 | 12893.8
22:00 | 6350.6 | 6550 | 12900.6
22:30 | 6340.43 | 6535 | 12875.43
23:00 | 6330.26 | 6520 | 12850.26

## En-Curve
QF-LDC-12
Date | 02-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3591 | 1914 | 847 | 38 | 46 | 653.98 | 218 | 4441 | 0 | 556 | 1414.3 | 0 | 0 | 29 | 0 | DAILY ENERGY CURVE
00:30 | 3603.5 | 1911 | 847 | 38 | 45 | 649.135 | 218.5 | 4474.5 | 0 | 418 | 1254.8 | 0 | 0 | 31.5 | 0 | 02-10-2025
01:00 | 3616 | 1908 | 847 | 38 | 44 | 644.29 | 219 | 4508 | 0 | 280 | 1095.3 | 0 | 0 | 34 | 0
01:30 | 3583.5 | 1913 | 847 | 38 | 43 | 641.07 | 218.5 | 4511.5 | 0 | 190.5 | 1001.95 | 0 | 0 | 42.5 | 0 | Energy Generated | 289.804 |  | MKWHr
02:00 | 3551 | 1918 | 847 | 38 | 42 | 637.85 | 218 | 4515 | 0 | 101 | 908.6 | 0 | 0 | 51 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3546.5 | 1913 | 847 | 38 | 41 | 639.25 | 218 | 4491 | 0 | 99.5 | 744.3 | 0 | 0 | 52.5 | 0 | Total Energy Requirement | 289.804 |  | MKWHr
03:00 | 3542 | 1908 | 847 | 38 | 40 | 640.65 | 218 | 4467 | 0 | 98 | 580 | 0 | 0 | 54 | 0
03:30 | 3557 | 1907.5 | 847 | 38 | 40 | 638.74 | 218 | 4397 | 0 | 84 | 428 | 0 | 0 | 50 | 0
04:00 | 3572 | 1907 | 847 | 38 | 40 | 636.83 | 218 | 4327 | 0 | 70 | 276 | 0 | 0 | 46 | 0
04:30 | 3556.5 | 1913.5 | 847 | 38 | 39 | 637.855 | 218 | 4233.5 | 0 | 70 | 268.5 | 0 | 0 | 43.5 | 0
05:00 | 3541 | 1920 | 847 | 38 | 38 | 638.88 | 218 | 4140 | 0 | 70 | 261 | 0 | 0 | 41 | 0
05:30 | 3457 | 1913 | 847 | 38 | 37 | 639.9 | 218 | 4011.5 | 0.515 | 70 | 260 | 0 | 0 | 40.5 | 0
06:00 | 3373 | 1906 | 847 | 38 | 36 | 640.92 | 218 | 3883 | 1.03 | 70 | 259 | 0 | 0 | 40 | 0
06:30 | 3352 | 1894 | 847 | 38 | 35 | 636.455 | 218 | 3794 | 23.065 | 54.5 | 259 | 0 | 0 | 36.5 | 0
07:00 | 3331 | 1882 | 847 | 38 | 34 | 631.99 | 218 | 3705 | 45.1 | 39 | 259 | 0 | 0 | 33 | 0
07:30 | 3328.5 | 1881.5 | 847 | 38 | 34 | 629.215 | 218 | 3676.5 | 66.705 | 49.5 | 241.5 | 0 | 0 | 36.5 | 0
08:00 | 3326 | 1881 | 847 | 38 | 34 | 626.44 | 218 | 3648 | 88.31 | 60 | 224 | 0 | 0 | 40 | 0
08:30 | 3289 | 1859 | 846.5 | 38 | 33 | 682.805 | 217.5 | 3638.5 | 123.975 | 68.5 | 199.5 | 0 | 0 | 38 | 0
09:00 | 3252 | 1837 | 846 | 38 | 32 | 739.17 | 217 | 3629 | 159.64 | 77 | 175 | 0 | 0 | 36 | 0
09:30 | 3249 | 1800.5 | 846 | 38 | 32 | 802.73 | 219 | 3530.5 | 204.835 | 77 | 169.5 | 0 | 0 | 45.5 | 0
10:00 | 3246 | 1764 | 846 | 38 | 32 | 866.29 | 221 | 3432 | 250.03 | 77 | 164 | 0 | 0 | 55 | 0
10:30 | 3331.5 | 1800 | 846.5 | 38 | 33 | 839.925 | 219.5 | 3392 | 239.855 | 77 | 156 | 0 | 0 | 45.5 | 0
11:00 | 3417 | 1836 | 847 | 38 | 34 | 813.56 | 218 | 3352 | 229.68 | 77 | 148 | 0 | 0 | 36 | 0
11:30 | 3511 | 1884.5 | 847 | 38 | 32 | 841.285 | 218 | 3365 | 208.28 | 86 | 134 | 0 | 0 | 36 | 0
12:00 | 3605 | 1933 | 847 | 38 | 30 | 869.01 | 218 | 3378 | 186.88 | 95 | 120 | 0 | 0 | 36 | 0
12:30 | 3578 | 1911.5 | 847 | 38 | 31 | 872.885 | 219 | 3453.5 | 227.955 | 103.5 | 130.5 | 0 | 0 | 32 | 0
13:00 | 3551 | 1890 | 847 | 38 | 32 | 876.76 | 220 | 3529 | 269.03 | 112 | 141 | 0 | 0 | 28 | 0
13:30 | 3420.5 | 1874 | 847 | 38 | 35 | 876.38 | 220 | 3564.5 | 260.24 | 120.5 | 141.5 | 0 | 0 | 25.5 | 0
14:00 | 3290 | 1858 | 847 | 38 | 38 | 876 | 220 | 3600 | 251.45 | 129 | 142 | 0 | 0 | 23 | 0
14:30 | 3282.5 | 1860.5 | 847 | 38 | 35 | 877.5 | 220 | 3603.5 | 219.235 | 129 | 142 | 0 | 0 | 20.5 | 0
15:00 | 3275 | 1863 | 847 | 38 | 32 | 879 | 220 | 3607 | 187.02 | 129 | 142 | 0 | 0 | 18 | 0
15:30 | 3276.5 | 1822.5 | 846.5 | 38 | 32 | 878 | 220 | 3555 | 126.915 | 120.5 | 137.5 | 0 | 0 | 19.5 | 0
16:00 | 3278 | 1782 | 846 | 38 | 32 | 877 | 220 | 3503 | 66.81 | 112 | 133 | 0 | 0 | 21 | 0
16:30 | 3325.5 | 1818.5 | 846.5 | 38 | 33 | 877 | 220 | 3486.5 | 42.815 | 112 | 124.5 | 0 | 0 | 18 | 0
17:00 | 3373 | 1855 | 847 | 38 | 34 | 877 | 220 | 3470 | 18.82 | 112 | 116 | 0 | 0 | 15 | 0
17:30 | 3425.5 | 1873 | 846.5 | 38 | 37 | 964.5 | 220.5 | 3600 | 9.41 | 278.5 | 280.5 | 0 | 0 | 15.5 | 0
18:00 | 3478 | 1891 | 846 | 38 | 40 | 1052 | 221 | 3730 | 0 | 445 | 445 | 0 | 0 | 16 | 0
18:30 | 3436.5 | 1865 | 846.5 | 38 | 39 | 1128.5 | 221 | 3982.5 | 0 | 426.5 | 547 | 0 | 0 | 27.5 | 0
19:00 | 3395 | 1839 | 847 | 38 | 38 | 1205 | 221 | 4235 | 0 | 408 | 649 | 0 | 0 | 39 | 0
19:30 | 3416 | 1855 | 847 | 38 | 40 | 1209 | 221 | 4287 | 0 | 298 | 564 | 0 | 0 | 46 | 0
20:00 | 3459 | 1882 | 846 | 38 | 40 | 1219 | 221 | 4305 | 0 | 244 | 553.3 | 0 | 0 | 53 | 0
20:30 | 3482 | 1906 | 846 | 38 | 40 | 1220.5 | 221 | 4320 | 0 | 236 | 516.65 | 0 | 0 | 47.5 | 0
21:00 | 3505 | 1930 | 846 | 38 | 40 | 1222 | 221 | 4335 | 0 | 228 | 480 | 0 | 0 | 42 | 0
21:30 | 3518.3 | 1935.5 | 846.5 | 38 | 40 | 1218 | 220.5 | 4338 | 0 | 228 | 477 | 0 | 0 | 34 | 0
22:00 | 3531.6 | 1941 | 847 | 38 | 40 | 1214 | 220 | 4341 | 0 | 228 | 474 | 0 | 0 | 26 | 0
22:30 | 3516.93 | 1935.5 | 847 | 38 | 41 | 1208.5 | 220 | 4340 | 0 | 228 | 470.5 | 0 | 0 | 30 | 0
23:00 | 3502.26 | 1930 | 847 | 38 | 42 | 1203 | 220 | 4339 | 0 | 228 | 467 | 0 | 0 | 34 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 07:00 | 374 | 22:00 | Payra | 413 | 10:00 | 407 | 01:00
Ashuganj | 404 | 6:00 | 392 | 13:00 | Rahanpur | 414 | 09:00 | 401 | 20:00
Bhulta | 400 | 06:00 | 389 | 13:00 | Rampal | 405 | 09:00 | 393 | 00:00
Bibiana | 388 | 06:00 | 384 | 03:00
BIPTC | 407 | 09:00 | 399 | 01:00
Bogura | 404 | 09:00 | 390 | 21:00
Gopalganj | 397 | 08:00 | 387 | 01:00
Kaliakoir | 377 | 14:00 | 368 | 11:00
Madunaghat | 390 | 10:00 | 387 | 00:00
Meghnaghat | 384 | 06:00 | 378 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 223 | 12:00 | Kaliakoir | 234 | 07:00 | 228 | 12:00
AKSML | 232 | 11:00 | 226 | 23:00 | Keranigonj | 227 | 06:00 | 221 | 12:00
Aminbazar | 230 | 07:00 | 222 | 17:00 | Khulna(S) | 231 | 10:00 | 218 | 00:00
Ashuganj | 231 | 06:00 | 227 | 18:00 | Madunaghat | 232 | 11:00 | 228 | 05:00
Ashuganj-400 | 231 | 06:00 | 227 | 18:00 | Madunaghat-400 | 233 | 12:00 | 229 | 04:00
Baghabari | 234 | 07:00 | 227 | 01:00 | Maniknagar | 223 | 06:00 | 219 | 01:00
Barapukuria | 225 | 10:00 | 220 | 01:00 | Meghnaghat | 230 | 05:00 | 226 | 12:00
Barapukuria-230 | 225 | 10:00 | 220 | 01:00 | Meghnaghat-400 | 226 | 06:00 | 221 | 11:00
Barishal | 235 | 10:00 | 226 | 00:00 | Mirsorai | 231 | 06:00 | 226 | 23:00
Bheramara | 232 | 09:00 | 222 | 00:00 | Rajshahi | 231 | 09:00 | 222 | 00:00
Bhulta | 231 | 06:00 | 218 | 02:00 | Rampal | 232 | 09:00 | 219 | 00:00
Bibiana | 230 | 07:00 | 225 | 18:30 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 09:00 | 222 | 01:00 | Rampura | 230 | 06:00 | 222 | 11:00
Bogura | 239 | 09:00 | 232 | 01:00 | Shikalbaha | 230 | 00:00 | 227 | 05:00
Bogura-400 | 239 | 09:00 | 232 | 21:00 | Shyampur | 225 | 06:00 | 221 | 12:00
Borhanuddin | 237 | 09:00 | 231 | 00:00 | Siddhirganj | 224 | 05:00 | 220 | 11:00
BSRM | 231 | 07:00 | 225 | 23:00 | Sirajgonj | 240 | 06:00 | 236 | 01:00
Cumilla(N) | 227 | 07:00 | 222 | 12:00 | Sreepur | 228 | 06:00 | 223 | 02:00
Faridpur | 232 | 10:00 | 223 | 00:00 | Tongi | 230 | 07:00 | 222 | 09:00
Fenchuganj | 231 | 09:00 | 228 | 01:00
Ghorashal | 230 | 09:00 | 220 | 00:00
Ghorashal-230 | 229 | 06:00 | 221 | 12:00
Gopalganj | 233 | 08:00 | 226 | 00:00
GPH | 232 | 11:00 | 227 | 23:00
Haripur | 224 | 07:00 | 220 | 11:00
Hasnabad | 226 | 04:00 | 221 | 12:00
Hathazari | 230 | 00:00 | 223 | 23:00
Ishurdi | 235 | 09:00 | 225 | 01:00
Jhenaidah | 230 | 10:00 | 216 | 00:00
Kachua | 218 | 06:00 | 209 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 06:00 | 130 | 12:00 | Lalmonirhat | 129 | 18:00 | 124 | 09:00
Agargaon | 139 | 06:00 | 135 | 11:00 | Madanganj | 129 | 07:00 | 126 | 01:00
Agrabad | 132 | 07:00 | 129 | 04:00 | Madaripur | 135 | 10:00 | 130 | 00:00
AKS | 130 | 00:00 | 128 | 23:00 | Madartek | 134 | 06:00 | 129 | 12:00
Aminbazar | 135 | 00:00 | 130 | 12:00 | Madunaghat | 134 | 06:00 | 132 | 03:00
Amnura | 140 | 10:00 | 127 | 21:00 | Magura | 134 | 17:00 | 122 | 00:00
Ashuganj | 140 | 06:00 | 138 | 00:00 | Mahasthangarh | 133 | 09:00 | 126 | 03:00
Bagerhat | 135 | 09:00 | 118 | 00:00 | Maijdee | 129 | 07:00 | 121 | 00:00
Bajitpur | 131 | 13:00 | 125 | 01:00 | Manikganj | 130 | 07:00 | 125 | 21:00
Bakulia | 134 | 03:00 | 130 | 21:00 | Maniknagar | 135 | 05:00 | 133 | 00:00
Banani | 134 | 06:00 | 128 | 13:00 | Matarbari | 123 | 11:00 | 113 | 23:00
Bangabhaban | 135 | 05:00 | 132 | 12:00 | Matuail | 130 | 06:00 | 127 | 12:00
Barapukuria | 138 | 18:00 | 129 | 01:00 | Millgate | 134 | 06:00 | 129 | 11:00
Barguna | 137 | 08:00 | 133 | 00:00 | Mirpur | 134 | 00:00 | 129 | 12:00
Barishal | 135 | 10:00 | 128 | 00:00 | Mirzapur | 130 | 04:00 | 126 | 12:00
Barishal-230 | 135 | 10:00 | 128 | 00:00 | Mithapukur | 132 | 11:00 | 125 | 01:00
Baroaulia | 133 | 12:00 | 130 | 20:00 | MI_Cement | 131 | 06:00 | 127 | 00:00
Baroirhat | 133 | 12:00 | 129 | 23:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 134 | 04:00 | 128 | 12:00 | Mogbazar | 135 | 05:00 | 130 | 12:00
BashundharaCement | 129 | 08:00 | 126 | 01:00 | Mongla | 135 | 10:00 | 123 | 00:00
Beanibazar | 129 | 14:00 | 126 | 00:00 | Motijheel | 135 | 05:00 | 132 | 12:00
Benapole | 134 | 16:00 | 120 | 00:00 | Muktagacha | 134 | 09:00 | 127 | 13:00
Bhaluka | 131 | 06:00 | 124 | 22:00 | Munshiganj | 129 | 02:00 | 126 | 00:00
Bhandaria | 134 | 11:00 | 120 | 00:00 | Muradnagar | 129 | 06:00 | 125 | 00:00
Bhangura | 134 | 15:00 | 128 | 02:00 | Mymensingh | 136 | 09:00 | 117 | 00:00
Bheramara | 137 | 09:00 | 132 | 00:00 | Naogaon | 132 | 14:00 | 124 | 01:00
Bheramara(GK) | 137 | 08:00 | 132 | 00:00 | Narail | 133 | 17:00 | 120 | 00:00
Bhulta | 126 | 09:00 | 124 | 02:00 | Narinda | 135 | 05:00 | 133 | 00:00
Bog-Sherpur | 134 | 09:00 | 129 | 01:00 | Narshingdi | 133 | 07:00 | 122 | 00:00
Bogura | 135 | 09:00 | 131 | 21:00 | Natore | 134 | 09:00 | 127 | 01:00
Bogura-230 | 135 | 09:00 | 130 | 01:00 | Nawabganj | 134 | 06:00 | 130 | 12:00
Brahmanbaria | 135 | 14:00 | 130 | 12:00 | Netrakona | 123 | 05:00 | 115 | 00:00
Cantonment | 138 | 06:00 | 134 | 12:00 | New | 134 | 02:00 | 130 | 12:00
Chandina | 133 | 07:00 | 129 | 00:00 | Niamatpur | 141 | 09:00 | 135 | 21:00
Chandpur | 136 | 07:00 | 126 | 15:00 | Noapara | 136 | 09:00 | 124 | 00:00
Chandraghona | 135 | 07:00 | 132 | 22:00 | Pabna | 134 | 06:00 | 130 | 00:00
Chapai | 140 | 06:00 | 134 | 19:00 | Palashbari | 131 | 10:00 | 124 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 05:00 | 127 | 00:00 | Panchagarh | 135 | 19:30 | 124 | 03:00
Chauddagram | 131 | 06:00 | 126 | 00:00 | Patiya | 132 | 10:00 | 128 | 21:00
Chhatak | 130 | 15:00 | 123 | 02:00 | Patuakhali | 137 | 07:00 | 132 | 15:00
Chowmuhani | 130 | 07:00 | 122 | 00:00 | Payra | 137 | 07:00 | 135 | 00:00
Chuadanga | 132 | 09:00 | 121 | 00:00 | PHP | 133 | 12:00 | 128 | 04:00
Coxsbazar | 122 | 11:00 | 115 | 00:00 | Postogola | 135 | 01:00 | 130 | 12:00
Cumilla(N) | 132 | 07:00 | 128 | 03:00 | Purbachal | 135 | 06:00 | 129 | 12:00
Cumilla(S) | 132 | 05:00 | 127 | 23:00 | Purbasadipur | 132 | 19:30 | 124 | 03:00
Daganbhuiyan | 129 | 13:00 | 120 | 02:00 | Rahanpur | 142 | 11:00 | 137 | 21:00
Daudkandi | 127 | 06:00 | 123 | 00:00 | Rahanpur-400 | 143 | 09:00 | 137 | 21:00
DhakaUniversity | 135 | 05:00 | 130 | 12:00 | Rahim | 130 | 05:00 | 127 | 12:00
Dhamrai | 134 | 07:00 | 130 | 11:00 | Rajbari | 135 | 07:00 | 129 | 00:00
Dhanmondi | 135 | 06:00 | 130 | 12:00 | Rajendrapur | 136 | 00:00 | 126 | 02:00
Dohazari | 130 | 11:00 | 123 | 23:00 | Rajshahi | 133 | 08:00 | 128 | 00:00
Faridpur | 137 | 10:00 | 132 | 00:00 | Rajshahi-230 | 133 | 09:00 | 127 | 21:00
Fatullah | 137 | 07:00 | 134 | 16:00 | Ramganj | 131 | 06:00 | 123 | 23:00
Fenchuganj | 136 | 07:00 | 134 | 00:00 | Rampur | 133 | 00:00 | 129 | 22:00
Feni | 127 | 13:00 | 119 | 00:00 | Rampura | 135 | 06:00 | 129 | 12:00
Ghatail | 130 | 01:00 | 125 | 13:00 | Rangamati | 134 | 02:00 | 132 | 18:00
Ghorashal | 137 | 00:00 | 134 | 01:00 | Rangpur | 133 | 18:00 | 128 | 03:00
Goalpara | 138 | 10:00 | 126 | 00:00 | Ruppur | 137 | 09:00 | 132 | 00:00
Gollamari | 138 | 16:00 | 127 | 01:00 | Saidpur | 133 | 03:00 | 127 | 13:00
Gopalganj | 136 | 10:00 | 128 | 00:00 | Satkhira | 136 | 15:00 | 121 | 00:00
Gopalganj-400 | 136 | 06:00 | 132 | 00:00 | Satmasjid | 138 | 07:00 | 134 | 06:00
Gulshan | 135 | 06:00 | 129 | 12:00 | Savar | 136 | 00:00 | 128 | 12:00
Halishahar | 134 | 11:00 | 129 | 22:00 | SevenRings | 138 | 17:00 | 133 | 11:00
Haripur | 131 | 06:00 | 128 | 00:00 | ShahCement | 130 | 05:00 | 127 | 00:00
HaripurSBU | 131 | 07:00 | 128 | 01:00 | Shahjadpur | 136 | 07:00 | 134 | 00:00
Hasnabad | 135 | 00:00 | 130 | 11:00 | Shahjibazar | 135 | 07:00 | 130 | 03:00
Hathazari | 135 | 00:00 | 131 | 21:00 | Shahmirpur | 133 | 10:00 | 129 | 22:00
Ishurdi | 138 | 09:00 | 132 | 01:00 | Shariatpur | 134 | 07:00 | 127 | 00:00
Jaldhaka | 132 | 18:00 | 124 | 01:00 | Sherpur | 135 | 02:00 | 124 | 13:00
Jamalpur | 138 | 03:00 | 126 | 13:00 | Shikalbaha | 124 | 11:00 | 119 | 22:00
Jashore | 132 | 17:00 | 120 | 00:00 | Shikalbaha-230 | 135 | 11:00 | 131 | 21:00
Jhenaidah | 135 | 09:00 | 124 | 00:00 | Shitalakhya | 131 | 06:00 | 127 | 00:00
Jhenaidah-230 | 136 | 10:00 | 126 | 00:00 | Sholosohor | 134 | 11:00 | 131 | 02:00
Joydebpur | 140 | 00:00 | 127 | 11:00 | Shyampur | 137 | 06:00 | 134 | 13:00
Joypurhat | 130 | 09:00 | 122 | 01:00 | Shyampur-230 | 137 | 06:00 | 134 | 10:00
Juldah | 132 | 10:00 | 130 | 21:00 | Siddhirganj | 131 | 07:00 | 128 | 12:00
Kabirpur | 133 | 18:30 | 126 | 11:00 | Sirajganj | 132 | 06:00 | 127 | 21:00
Kachua | 137 | 06:00 | 130 | 23:00 | Sonargaon | 128 | 07:00 | 125 | 00:00
Kaliakoir | 136 | 07:00 | 130 | 11:00 | Sreemongol | 134 | 07:00 | 130 | 00:00
Kallyanpur | 136 | 01:00 | 130 | 12:00 | Sreepur | 132 | 06:00 | 128 | 02:00
Kalurghat | 135 | 11:00 | 132 | 04:00 | Srinagar | 135 | 06:00 | 130 | 12:00
Kamrangirchar | 135 | 06:00 | 129 | 12:00 | SSM | 139 | 12:00 | 136 | 00:00
Kaptai | 137 | 8:00 | 134 | 11:00 | Sunamganj | 128 | 15:00 | 121 | 22:00
Kasba | 129 | 07:00 | 124 | 00:00 | Sylhet | 130 | 07:00 | 127 | 00:00
Kazla | 135 | 08:00 | 132 | 12:00 | Sylhet-132 | 129 | 07:00 | 128 | 00:00
Keranigonj | 135 | 06:00 | 130 | 13:00 | Tangail | 129 | 07:00 | 124 | 13:00
Khagrachori | 133 | 07:00 | 130 | 20:00 | Taraganj | 130 | 09:00 | 127 | 01:00
Khulna | 137 | 16:00 | 126 | 00:00 | Thakurgaon | 133 | 18:00 | 121 | 03:00
Khulna(S) | 138 | 10:00 | 127 | 00:00 | TK | 134 | 07:00 | 132 | 21:00
Khulshi | 132 | 11:00 | 128 | 22:00 | Tongi | 137 | 07:00 | 131 | 19:30
Kishoreganj | 130 | 15:00 | 125 | 00:00 | Ullahpara | 134 | 09:00 | 129 | 01:00
Kodda | 135 | 00:00 | 124 | 02:00 | Ullon | 135 | 06:00 | 129 | 12:00
KSRM | 133 | 09:00 | 131 | 00:00 | Uttara | 135 | 01:00 | 129 | 12:00
Kulaura | 135 | 07:00 | 133 | 00:00 | UttaraNew | 135 | 01:00 | 129 | 12:00
Kurigram | 128 | 10:00 | 124 | 00:00 | Zigatola | 135 | 07:00 | 130 | 12:00
Kushtia | 135 | 10:00 | 127 | 00:00
Laksam | 134 | 10:00 | 129 | 02:00
Lakshmipur | 130 | 13:00 | 122 | 00:00
Lalbag | 134 | 05:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division