## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-10-2025 | during | 05-10-2025 | during | 05-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 370 | 332 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 147 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 6.8 | 45.5 | 53.97 | 53.97 | 35 | 35 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 45 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 26.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 20 | 15 | 300 | 300 | 81 | 300 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 80 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 99 | 105 | 105 | 106 | 106 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 98 | 143 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 439 | 466 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 125 | 160 | 160 | 144 | 144 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2080.8 | 2390 | 5834.4 | 5804.4 | 5264.44 | 5511.44
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 3 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 201 | 210 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 34 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 70 | 64 | 75 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 17 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 87 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.34 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 30 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 54 | 159.86 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 705 | 985 | 1224 | 1224 | 1224 | 1224 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 2 | 1 | 2 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 275 | 275 | 280 | 280 | 840 | 840 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1475.34 | 1958 | 3043.47 | 3053.72 | 2992.11 | 3119.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 181 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 250 | 224 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 394 | 385 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 15 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 94 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 78 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 48 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 43.5 | 43.5 | 34 | 34 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 16 | 59 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 85 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 29 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1395 | 1483 | 2673.86 | 2603.86 | 2448.36 | 2387.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-10-2025 | during | 05-10-2025 | during | 05-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 105 | 105 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 5 | 60 | 150 | 150 | 150 | 150 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 73 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.66 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 224.66 | 267 | 500.9 | 461 | 447.4 | 407.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 57 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 144 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 313 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1233 | 1149 | 1293 | 1293 | 1215 | 1215
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 844 | 845 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 392 | 350 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1030 | 1066 | 370 | 370 | 1148 | 1148 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2373 | 2299 | 2788 | 2688 | 3371 | 3271
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 301 | 602 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 885 | 1093 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 202 | 274 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1723.31 | 2304 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 15.19 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 185 | 187 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 188 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 340 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.72 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 845 | 1309 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.85 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1826.76 | 2024 | 3187.46 | 3020.87 | 3054.48 | 2887.89
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 49 | 50 | 50 | 44 | 46 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 141 | 141 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 44 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 156.91 | 0 | 156.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 352.6 | 284 | 635.91 | 448 | 629.91 | 444
System Total |  |  |  |  | 28823.2 | 28365.955 | 12684.47 | 14158 | 22104 | 21518.85 | 21386.7 | 21206.41
Forecast Scenario (05-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14040 |  | 0 |  | 14040
|  |  |  | 1:00 | 13520 |  | 0 |  | 13520
|  |  |  | 2:00 | 13100 |  | 0 |  | 13100
|  |  |  | 3:00 | 12620 |  | 0 |  | 12620
|  |  |  | 4:00 | 12270 |  | 0 |  | 12270
|  |  |  | 5:00 | 11890 |  | 0 |  | 11890
|  |  |  | 6:00 | 11490 |  | 0 |  | 11490
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11170 |  | 0 |  | 11170
|  |  |  | 9:00 | 11360 |  | 0 |  | 11360
|  |  |  | 10:00 | 11700 |  | 0 |  | 11700
|  |  |  | 11:00 | 11930 |  | 0 |  | 11930
|  |  |  | 12:00 | 12280 |  | 0 |  | 12280
|  |  |  | 13:00 | 12650 |  | 0 |  | 12650
|  |  |  | 14:00 | 12670 |  | 0 |  | 12670
|  |  |  | 15:00 | 12670 |  | 0 |  | 12670
|  |  |  | 16:00 | 12510 |  | 0 |  | 12510
|  |  |  | 17:00 | 12190 |  | 0 |  | 12190
|  |  |  | 18:00 | 13040 |  | 0 |  | 13040
|  |  |  | 18:30 | 13250 |  | 0 |  | 13250
|  |  |  | 19:00 | 13590 |  | 0 |  | 13590
|  |  |  | 19:30 | 13990 |  | 0 |  | 13990
|  |  |  | 20:00 | 14150 |  | 0 |  | 14150
|  |  |  | 21:00 | 14150 |  | 0 |  | 14150
|  |  |  | 22:00 | 14250 |  | 0 |  | 14250
|  |  |  | 23:00 | 14150 |  | 0 |  | 14150
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12280.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 304.79 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:04 hrs on 05-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-10-2025 | [28 empty] | Date: | 04-10-2025 | [28 empty] | Date: | 04-10-2025 | [28 empty] | Date: | 04-10-2025 | [28 empty] | Date: | 04-10-2025 | [14 empty] | Date: | 04-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 405 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 49 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 40 | 275 | 0 | 0 | 19 | 0 | 0 | 200 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 197 | 10 | 48 | 97 | 16 | 0 | 20 | 30 | 48 | 0 | 0 | 0 | 315 | 0 | 387 | 30 | 30 | 158 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 8 | 144 | 0 | 0 | 12 | 6058.8 | 849 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 844 | 0 | 1362.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 137 | 48 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 115 | 220 | 0 | 562 | 1222 | 0 | 6891.64 | 12950.44 | 108.05
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 153 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 40 | 277 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 201 | 10 | 47 | 96 | 16 | 0 | 20 | 30 | 44 | 0 | 0 | 0 | 305 | 0 | 390 | 30 | 30 | 157 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 8 | 147 | 0 | 0 | 6 | 5995 | 849 | 379 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 0 | 1354.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 138 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 115 | 220 | 0 | 452 | 1140 | 0 | 6679.09 | 12674.09 | 108.05
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 148 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 192 | 10 | 48 | 97 | 15 | 0 | 20 | 30 | 44 | 0 | 0 | 0 | 310 | 0 | 378 | 30 | 30 | 156 | 8 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 45 | 8 | 152 | 0 | 0 | 0 | 5937 | 849 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 844 | 0 | 1158.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 115 | 220 | 0 | 401 | 1108 | 0 | 6394.2 | 12331.2 | 108.05
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 41 | 275 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 194 | 10 | 26 | 97 | 15 | 0 | 20 | 29 | 42 | 0 | 0 | 0 | 305 | 0 | 361 | 30 | 30 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 35 | 0 | 157 | 0 | 0 | 0 | 5849 | 849 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 0 | 1150.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 0 | 138 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 115 | 220 | 0 | 301 | 960 | 0 | 6013.33 | 11862.33 | 108.05
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 146 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 41 | 275 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 189 | 10 | 0 | 97 | 15 | 0 | 20 | 28 | 40 | 0 | 0 | 0 | 310 | 0 | 365 | 30 | 30 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 35 | 0 | 157 | 0 | 0 | 0 | 5791 | 849 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 845 | 0 | 1016.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 0 | 136 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 115 | 220 | 0 | 301 | 900 | 0 | 5815.22 | 11606.22 | 108.05
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 147 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 41 | 275 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 710 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 194 | 10 | 0 | 97 | 14 | 0 | 20 | 29 | 38 | 0 | 0 | 0 | 300 | 0 | 384 | 30 | 30 | 150 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 35 | 0 | 157 | 0 | 0 | 0 | 5814 | 849 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 0 | 910.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 300 | 820 | 0 | 5620.68 | 11434.68 | 108.05
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 145 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 12 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.03 | 218 | 0 | 38 | 275 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 710 | 0 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 188 | 10 | 0 | 97 | 15 | 0 | 0 | 15 | 38 | 0 | 0 | 0 | 300 | 0 | 362 | 30 | 30 | 150 | 8 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 35 | 0 | 158 | 0 | 0.16 | 0 | 5739.19 | 848 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 829 | 0 | 861.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 185 | 0 | 188 | 0 | 0 | 0 | 347 | 0 | 0 | 136 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 300 | 720 | 0 | 5401.07 | 11140.26 | 108.05
07:00 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 410 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.67 | 218 | 0 | 38 | 275 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 705 | 5 | 51 | 0 | 8 | 345 | 300 | 280 | 5 | 198 | 10 | 0 | 97 | 0 | 0 | 20 | 0 | 36 | 0 | 3 | 0 | 310 | 0 | 387 | 30 | 30 | 154 | 6 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 55 | 0 | 157 | 0 | 8.33 | 0 | 5797 | 849 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 782 | 0 | 851.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.76 | 14 | 0 | 0 | 3.42 | 191 | 0 | 194 | 0 | 0 | 0 | 369 | 0 | 0.55 | 136 | 48 | 0 | 2 | 0 | 0 | 0 | 0 | 0.1 | 16 | 0.1 | 0 | 172 | 115 | 220 | 0 | 301 | 700 | 0 | 5429.6 | 11226.6 | 108.05
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 414 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 149 | 0 | 0 | 0 | 280 | 0 | 0 | 15 | 17 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.91 | 218 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 700 | 11 | 51 | 0 | 0 | 345 | 280 | 280 | 5 | 198 | 10 | 0 | 94 | 0 | 0 | 20 | 0 | 34 | 0 | 22 | 0 | 305 | 0 | 336 | 30 | 30 | 152 | 6 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 55 | 0 | 142 | 1 | 18.72 | 0 | 5733.63 | 849 | 401 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 773 | 0 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.36 | 20 | 0 | 0 | 23.99 | 193 | 0 | 195 | 0 | 0 | 0 | 370 | 0 | 2.29 | 135 | 48 | 0 | 8 | 0 | 0 | 0 | 0 | 0.5 | 70 | 0.26 | 0 | 172 | 115 | 180 | 0 | 300 | 695 | 0 | 5519.4 | 11253.03 | 108.05
09:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 413 | 0 | 0 | 17 | 0 | 0 | 0 | 3 | 0 | 0 | 320 | 151 | 0 | 0 | 0 | 280 | 0 | 0 | 25 | 35 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 220 | 0 | 0 | 275 | 0 | 0 | 1 | 0 | 0 | 201 | 0 | 0 | 0 | 710 | 14 | 51 | 0 | 0 | 345 | 340 | 280 | 5 | 199 | 10 | 0 | 94 | 0 | 0 | 20 | 0 | 32 | 0 | 44 | 0 | 320 | 0 | 336 | 30 | 30 | 151 | 6 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 35 | 0 | 142 | 1 | 26.15 | 0 | 5887.87 | 844 | 402 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 784 | 0 | 854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.88 | 73 | 0 | 0 | 16.76 | 199 | 0 | 202 | 0 | 0 | 0 | 372 | 0 | 2.01 | 135 | 48 | 0 | 19 | 0 | 0 | 0 | 0 | 1.7 | 83 | 0.5 | 0 | 171 | 115 | 180 | 0 | 301 | 700 | 0 | 5635.85 | 11523.72 | 108.05
10:00 | 0 | 35 | 6 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 400 | 0 | 0 | 23 | 0 | 0 | 0 | 24 | 0 | 0 | 320 | 152 | 0 | 0 | 0 | 280 | 0 | 0 | 15 | 35 | 20 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1.92 | 220 | 0 | 10 | 275 | 0 | 0 | 18 | 0 | 0 | 201 | 0 | 0 | 0 | 710 | 17 | 51 | 0 | 0 | 380 | 349 | 280 | 5 | 195 | 10 | 0 | 94 | 0 | 0 | 20 | 0 | 34 | 0 | 43 | 0 | 310 | 0 | 336 | 30 | 30 | 146 | 6 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 0 | 128 | 1 | 43.26 | 0 | 5971.18 | 844 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 88 | 778 | 0 | 854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.44 | 72 | 0 | 0 | 60.03 | 196 | 0 | 189 | 0 | 0 | 0 | 370 | 0 | 1.66 | 138 | 48 | 0 | 15 | 0 | 0 | 0 | 0 | 2.3 | 163 | 0.44 | 0 | 172 | 115 | 180 | 0 | 301 | 700 | 0 | 5757.87 | 11729.05 | 108.04
11:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 431 | 0 | 17 | 33 | 8 | 0 | 0 | 35 | 40 | 0 | 320 | 149 | 0 | 0 | 0 | 327 | 0 | 0 | 36 | 35 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1.74 | 220 | 0 | 4 | 275 | 0 | 0 | 21 | 0 | 0 | 201 | 0 | 0 | 0 | 710 | 17 | 51 | 0 | 0 | 394 | 280 | 280 | 5 | 198 | 10 | 1 | 94 | 0 | 0 | 20 | 2 | 36 | 0 | 75 | 0 | 320 | 0 | 336 | 30 | 50 | 153 | 12 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 0 | 104 | 1 | 49.16 | 0 | 6163.9 | 844 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 839 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.28 | 59 | 0 | 0 | 39.37 | 200 | 0 | 184 | 0 | 0 | 0 | 380 | 0 | 3.31 | 140 | 48 | 0 | 15 | 0 | 0 | 0 | 0 | 2.2 | 153 | 0.73 | 0 | 181 | 115 | 220 | 0 | 300 | 737 | 0 | 5874.89 | 12038.79 | 108.04
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 439 | 6.8 | 35 | 33 | 30 | 20 | 0 | 35 | 98 | 0 | 320 | 151 | 0 | 0 | 0 | 326 | 0 | 0 | 30 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.34 | 220 | 0 | 4 | 275 | 0 | 0 | 39 | 0 | 5 | 201 | 0 | 0 | 0 | 705 | 14 | 51 | 0 | 0 | 394 | 280 | 250 | 5 | 181 | 10 | 17 | 97 | 0 | 7 | 20 | 16 | 38 | 0 | 29 | 0 | 315 | 0 | 380 | 30 | 50 | 154 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 65 | 5 | 105 | 1 | 48.66 | 0 | 6408.8 | 844 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1030 | 0 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.19 | 110 | 0 | 0 | 66.85 | 185 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 5.72 | 141 | 48 | 0 | 17 | 0 | 0 | 0 | 0 | 0.6 | 146 | 0.31 | 0 | 202 | 115 | 220 | 0 | 301 | 885 | 0 | 6275.67 | 12684.47 | 108.04
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 404 | 31 | 35 | 51 | 30 | 95 | 0 | 35 | 102 | 0 | 320 | 145 | 0 | 0 | 0 | 325 | 0 | 0 | 29 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 2.66 | 220 | 0 | 14 | 275 | 0 | 0 | 39 | 0 | 41 | 201 | 0 | 0 | 0 | 703 | 16 | 51 | 0 | 0 | 399 | 280 | 230 | 5 | 160 | 0 | 37 | 97 | 28 | 8 | 19 | 29 | 42 | 0 | 59 | 0 | 310 | 0 | 380 | 30 | 50 | 158 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 66 | 24 | 105 | 2 | 36.53 | 0 | 6619.19 | 844 | 386 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 1135 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.21 | 80 | 0 | 0 | 16.76 | 175 | 0 | 176 | 0 | 0 | 0 | 355 | 0 | 1.5 | 140 | 48 | 0 | 16 | 0 | 0 | 0 | 0 | 2.3 | 181 | 0.33 | 0 | 199 | 115 | 180 | 0 | 301 | 940 | 0 | 6278.1 | 12897.29 | 108.04
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 436 | 32 | 35 | 51 | 30 | 60 | 0 | 35 | 97 | 0 | 320 | 149 | 0 | 0 | 0 | 327 | 0 | 0 | 8 | 70 | 0 | 22 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1.15 | 220 | 0 | 12 | 275 | 0 | 0 | 39 | 0 | 16 | 214 | 0 | 0 | 0 | 701 | 11 | 51 | 0 | 0 | 400 | 280 | 224 | 5 | 150 | 0 | 47 | 94 | 32 | 9 | 17 | 29 | 42 | 0 | 65 | 0 | 310 | 0 | 364 | 30 | 50 | 153 | 13 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 66 | 24 | 105 | 0 | 8.98 | 0 | 6505.13 | 844 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1100 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 9 | 0 | 0 | 9.16 | 175 | 0 | 174 | 0 | 0 | 0 | 340 | 0 | 0.94 | 140 | 47 | 0 | 6 | 0 | 0 | 0 | 0 | 2.9 | 93 | 0.03 | 0 | 193 | 115 | 180 | 0 | 301 | 940 | 0 | 6044.1 | 12549.23 | 108.04
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 437 | 30.8 | 35 | 51 | 15 | 15 | 0 | 35 | 98 | 0 | 320 | 151 | 0 | 0 | 0 | 329 | 0 | 0 | 1 | 70 | 19 | 22 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 2.3 | 220 | 0 | 6 | 275 | 0 | 0 | 39 | 0 | 15 | 215 | 0 | 0 | 0 | 708 | 10 | 0 | 0 | 0 | 405 | 280 | 224 | 5 | 150 | 0 | 40 | 94 | 34 | 9 | 2.5 | 29 | 44 | 0 | 38 | 0 | 310 | 0 | 386 | 30 | 57 | 151 | 13 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 65 | 24 | 105 | 1 | 32.39 | 0 | 6437.99 | 844 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 1078 | 0 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 7 | 0 | 0 | 16.32 | 176 | 0 | 176 | 0 | 0 | 0 | 361 | 0 | 1.51 | 136 | 47 | 0 | 9 | 0 | 0 | 0 | 0 | 3 | 46 | 0.11 | 0 | 197 | 115 | 180 | 0 | 301 | 950 | 0 | 5987.66 | 12425.65 | 108.04
16:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 432 | 31.4 | 35 | 51 | 14 | 15 | 0 | 35 | 99 | 0 | 320 | 149 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 70 | 22 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 16 | 33 | 0 | 0 | 0 | 0 | 0.04 | 221 | 0 | 6 | 275 | 0 | 0 | 39 | 0 | 14 | 214 | 0 | 0 | 0 | 700 | 4 | 0 | 0 | 0 | 415 | 280 | 224 | 5 | 150 | 0 | 17 | 94 | 16 | 9 | 5 | 30 | 42 | 0 | 24 | 0 | 310 | 0 | 382 | 30 | 57 | 141 | 13 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 65 | 24 | 106 | 0 | 7.35 | 0 | 6351.79 | 844 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1084 | 0 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 6 | 0 | 0 | 3.23 | 176 | 0 | 176 | 0 | 0 | 0 | 347 | 0 | 0.24 | 144 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 0.93 | 0 | 200 | 115 | 180 | 0 | 301 | 949 | 0 | 5910.41 | 12262.2 | 108.04
17:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 428 | 30.4 | 38 | 51 | 14 | 15 | 0 | 35 | 95 | 0 | 320 | 148 | 0 | 0 | 0 | 310 | 0 | 0 | 1 | 70 | 26 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0.07 | 221 | 0 | 13 | 275 | 0 | 0 | 2 | 0 | 15 | 214 | 0 | 0 | 0 | 700 | 1 | 0 | 0 | 0 | 415 | 280 | 224 | 5 | 150 | 0 | 17 | 94 | 15 | 0 | 8 | 30 | 40 | 0 | 6 | 0 | 305 | 0 | 386 | 30 | 57 | 138 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 24 | 16 | 106 | 0 | 0.75 | 0 | 6187.22 | 844 | 328 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 1048 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 5 | 0 | 0 | 2.13 | 174 | 0 | 173 | 0 | 0 | 0 | 352 | 0 | 0.2 | 144 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0.23 | 0 | 198 | 115 | 180 | 0 | 301 | 950 | 0 | 5837.61 | 12024.83 | 108.04
18:00 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 455 | 40.5 | 54 | 51 | 20 | 140 | 5 | 42 | 140 | 0 | 320 | 153 | 0 | 0 | 45 | 280 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 10 | 0 | 49 | 0 | 0 | 33 | 37 | 0 | 0 | 0 | 0 | 221 | 8 | 15 | 275 | 50 | 0 | 23 | 0 | 38 | 214 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 410 | 280 | 224 | 5 | 150 | 0 | 42 | 94 | 31 | 0 | 14 | 58 | 46 | 0 | 0 | 4 | 310 | 0 | 390 | 30 | 57 | 143 | 8 | 0 | 81 | 30 | 0 | 18 | 165 | 11 | 73 | 24 | 105 | 0 | 0 | 5 | 7006.5 | 844 | 330 | 0 | 11 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 1099 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 15 | 0 | 0 | 0 | 25 | 0 | 0 | 176 | 0 | 178 | 0 | 0 | 0 | 405 | 0 | 0 | 140 | 49 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 115 | 220 | 0 | 416 | 975 | 12 | 6543 | 13549.5 | 108.03
19:00 | 0 | 99 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 466 | 45.5 | 54 | 80 | 45 | 15 | 0 | 55 | 143 | 0 | 320 | 147 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26.5 | 22 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 221 | 16 | 17 | 275 | 0 | 0 | 44 | 3 | 34 | 210 | 0 | 0 | 0 | 985 | 0 | 0 | 0 | 0 | 385 | 280 | 224 | 5 | 190 | 0 | 85 | 94 | 78 | 0 | 20 | 59 | 48 | 0 | 0 | 15 | 305 | 0 | 313 | 30 | 57 | 144 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 73 | 60 | 105 | 0 | 0 | 12 | 7247 | 845 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 188 | 0 | 0 | 0 | 340 | 0 | 0 | 141 | 49 | 50 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 602 | 1093 | 0 | 6911 | 14158 | 108.03
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 482 | 46.5 | 54 | 68 | 15 | 0 | 0 | 55 | 146 | 0 | 320 | 149 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 125 | 26.5 | 22 | 0 | 0 | 0 | 0 | 106 | 0 | 1 | 66 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 21 | 275 | 0 | 0 | 50 | 8 | 15 | 210 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 385 | 280 | 224 | 5 | 196 | 0 | 90 | 94 | 46 | 0 | 20 | 64 | 46 | 0 | 0 | 18 | 310 | 0 | 331 | 30 | 57 | 136 | 4 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 73 | 55 | 107 | 0 | 0 | 12 | 7219 | 834 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 1311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 188 | 0 | 0 | 0 | 346 | 0 | 0 | 143 | 49 | 35 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 602 | 1100 | 0 | 6904 | 14123
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 471 | 45.2 | 54 | 78 | 15 | 0 | 0 | 54 | 147 | 0 | 320 | 148 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 26.5 | 22 | 0 | 0 | 0 | 0 | 106 | 0 | 5 | 66 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 23 | 275 | 0 | 0 | 50 | 8 | 16 | 210 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 385 | 280 | 224 | 5 | 193 | 0 | 85 | 94 | 51 | 0 | 20 | 60 | 48 | 0 | 0 | 34 | 305 | 0 | 326 | 30 | 57 | 138 | 4 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 77 | 55 | 106 | 0 | 0 | 12 | 7187.7 | 834 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 190 | 0 | 0 | 0 | 343 | 0 | 0 | 145 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 602 | 1100 | 0 | 6922 | 14109.7 | 108.03
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 482 | 46.2 | 22 | 66 | 15 | 0 | 0 | 36 | 145 | 0 | 320 | 148 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 105 | 0 | 1 | 66 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 16 | 274 | 0 | 0 | 50 | 8 | 14 | 204 | 0 | 0 | 0 | 995 | 0 | 15 | 0 | 0 | 380 | 280 | 224 | 5 | 195 | 0 | 87 | 96 | 47 | 0 | 20 | 60 | 48 | 0 | 0 | 34 | 305 | 0 | 327 | 30 | 57 | 141 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 77 | 55 | 108 | 0 | 0 | 12 | 7129.2 | 833 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1319.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 193 | 0 | 0 | 0 | 347 | 0 | 0 | 143 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 602 | 1110 | 0 | 6949.75 | 14078.95 | 108.02
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 226 | 46.7 | 17 | 68 | 15 | 0 | 0 | 35 | 149 | 0 | 320 | 149 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 106 | 0 | 3 | 66 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 12 | 280 | 0 | 0 | 50 | 8 | 15 | 203 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 5 | 195 | 0 | 86 | 97 | 47 | 0 | 20 | 60 | 50 | 0 | 0 | 36 | 310 | 0 | 333 | 30 | 57 | 144 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 77 | 55 | 103 | 0 | 0 | 12 | 7006.7 | 833 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 0 | 1320.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 195 | 0 | 0 | 0 | 347 | 0 | 0 | 145 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 602 | 1110 | 0 | 7033.34 | 14040.04 | 108.02
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 230 | 45.2 | 17 | 68 | 15 | 0 | 0 | 17 | 146 | 0 | 320 | 153 | 60 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 105 | 0 | 12 | 66 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 14 | 280 | 0 | 0 | 50 | 8 | 14 | 203 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 5 | 200 | 0 | 86 | 96 | 47 | 0 | 18 | 65 | 50 | 0 | 0 | 36 | 305 | 0 | 333 | 30 | 57 | 142 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 78 | 55 | 98 | 0 | 0 | 10 | 7057.2 | 834 | 344 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 1307.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 194 | 0 | 0 | 0 | 355 | 0 | 0 | 144 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 603 | 1110 | 0 | 6981.62 | 14038.82 | 108.02
Total KWH | 0 | 1107360 | 344640 | 0 | 0 | 0 | 0 | 0 | 8485200 | 0 | 9782400 | 490680 | 479880 | 877392 | 265920 | 379124 | 17979 | 530125 | 1586880 | 0 | 8012000 | 3566924 | 9553 | 0 | 119697 | 7373803 | 0 | 0 | 156334 | 1699200 | 419400 | 487080 | 0 | 0 | 30109 | 0 | 890880 | 0 | 137280 | 615860 | 38784 | 0 | 0 | 0 | 17160 | 5296038 | 43500 | 483840 | 6647272.73 | 31782 | 0 | 545280 | 47075.4 | 323673 | 4868857 | 0 | 0 | 0 | 18954543 | 117720 | 914564 | 0 | 66909 | 8954800 | 7342300 | 6162000 | 130560 | 4511000 | 141336 | 877440 | 2118710 | 599520 | 47040 | 377920 | 767220 | 995520 | 0 | 372182 | 179696 | 7531000 | 0 | 8984000 | 717000 | 1027920 | 3588627 | 207672 | 0 | 1950160 | 719904 | 0 | 418000 | 4403130 | 118800 | 1346400 | 530400 | 2904000 | 9950 | 279590 | 84240 | 154660735.13 | 20422545 | 9058752 | 0 | 16320 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 455760 | 22967280 | 0 | 25133455 | 0 | 0 | 0 | 0 | 0 | 0 | 76608 | 13036 | 0 | 215940 | 483780 | 23566 | 0 | 270752 | 4749973 | 0 | 4739436 | 0 | 0 | 0 | 9059490 | 0 | 23700 | 3445000 | 1124072 | 358157 | 110150 | 341904 | 0 | 0 | 0 | 16022.04 | 992160 | 3175 | 35040 | 5150000 | 2773000 | 5277200 | 0 | 9388152 | 23301818.18 | 27600 | 150965843.22 | 305626578.35

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12684.47 | MW | 12:00 Hr. | Energy Generated |  |  | 305.6266 |  | MKWHr.
| Day Peak Demand |  |  | 12684.47 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14158 | MW | 19:00 Hr. | Energy Demand |  |  | 305.6266 |  | MKWHr.
| Evening Peak Demand |  |  | 14158 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11140.26 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1016.88 |  | MMCFD
| Maximum Generation of the Day |  |  | 14158 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.4205 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.1364 | 0 | 7.8989 | 0 | 0 | 0.15633 | 0 | 0 | 46.1916 | Gas | 142.3184 | Gas | 507168012.46
| Chattogram Zone |  |  | 5.3527 | 25.6018 | 2.5669 | 0 | 5.296 | 0.13488 | 0 | 0.13728 | 39.0897 | Coal | 90.9781 | Coal | 524175443.9922
| Cumilla Zone |  |  | 30.7201 | 0 | 2.4709 | 0 | 0 | 0.37218 | 0.99552 | 0 | 34.5587 | HFO | 15.9088 | HFO | 291768332.112
| Mymensingh Zone |  |  | 2.904 | 0 | 2.0798 | 0 | 0 | 0.28954 | 0 | 0 | 5.2734 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5474 | Hydro | 5.296 | Hydro | 529603.8
| Khulna Zone |  |  | 9.0588 | 22.9673 | 0.01632 | 0 | 0 | 0.45576 | 21.3345 | 0 | 53.8327 | Solar | 3.5244 | Solar | 54311358.1684
| Barishal Zone |  |  | 8.0502 | 37.84 | 0.06264 | 0 | 0 | 0.003175 | 0 | 0 | 45.956 | Import | 47.4635 | Import | 276678572.9
| Rajshahi Zone |  |  | 18.5489 | 0 | 0.11321 | 0 | 0 | 0.99417 | 25.1335 | 0 | 44.7897 | Wind | 0.13728 | Wind | 2023507.2
| Rangpur Zone |  |  | 0 | 4.5691 | 0.70006 | 0 | 0 | 1.1183 | 0 | 0 | 6.3875
| Total |  |  | 142.3184 | 90.9781 | 15.9088 | 0 | 5.296 | 3.5244 | 47.4635 | 0.13728 | 305.6266
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 507168012.46 |  | Hydro | 529603.8
|  |  |  | Coal | 524175443.9922 |  | Solar | 54311358.1684
|  |  |  | HFO | 291768332.112 |  | Import | 276678572.9
|  |  |  | HSD | 0 |  | Wind | 2023507.2
[5 empty] | Total: | 165,66,54,830 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4225 | Peak Hr Flow | 845.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52965752.79 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.1335 | Peak Hr Flow | 1309.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2624 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.99552 | Peak Hr Flow | 48.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2843 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.5515 | Peak Hr Flow | 2202.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5095
|  |  |  | Chattogram |  | 0 |  | 1476
|  |  |  | Cumilla |  | 0 |  | 1373
|  |  |  | Mymensingh |  | 0 |  | 1077
|  |  |  | Sylhet |  | 0 |  | 577
|  |  |  | Khulna |  | 0 |  | 1672
|  |  |  | Barishal |  | 0 |  | 431
|  |  |  | Rajshahi |  | 0 |  | 1228
|  |  |  | Rangpur |  | 0 |  | 750
|  |  |  | Total |  | 0 |  | 13679
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 17:59 | Jaldhaka 132/33kV S/S 406T-1 LT Scheduled S/D Due to Annual maintenance work.
| 08:25 | 17:57 | Jaldhaka 132/33kV S/S 406T-1 HT Scheduled S/D Due to Annual maintenance work.
|  | 09:26 | Tangail 132/33kV S/S Tr-3 HT is restored.
| 09:31 | 19:22 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to 132 KV Lalmonirhat | [7 empty] | 8.0MW load
|  |  | - Kurigram change Earth o OPGW | [7 empty] | interrup.
| 09:37 | 11:32 | Bogura 132/33kV S/S Transformer-4 LT Forced S/D Due to Red hot maintenance 33 kv side in
CT
| 09:37 | 11:32 | Bogura 132/33kV S/S Transformer-4 HT Forced S/D Due to Red hot maintenance 33 kv side in
CT
| 09:45 | 17:52 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
Annual maintenance and from Chandraghona 132/33kV end Due to Annual maintenance
| 09:59 |  | Aftabnagar-Rampura 132kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Emergency
work in AIS end (BPDB).
| 10:04 |  | Hathazari-Kaptai 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
|  | 10:07 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT is restored.
|  | 10:13 | Keranigonj 230/132/33kV S/S ATR-1 LT is restored.
|  | 10:13 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 HT is restored.
|  | 10:13 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 LT is restored.
|  | 10:13 | Keranigonj 230/132/33kV S/S ATR-1 HT is restored.
| 11:46 | 13:03 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Red
hot Maintenance at Kulaura End
| 11:57 | 12:58 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to
Fen-kul-line-2(line DS Redhot maintenance)
| 11:57 | 12:59 | Kulaura 132/33kV S/S 132 kV Bus-B Scheduled S/D Due to Fen-kul-line-2(line DS Redhot
maintenance
| 12:12 | 14:17 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to For project work
| 12:48 | 13:50 | Chapainawabganj-Rahanpur 132kV Ckt-1 Tripped from Chapai 132/33kV end showing Siemens
relays Due to Thunderstorm
|  | 13:20 | Tangail 132/33kV S/S Tr-3 LT is restored.
| 13:22 | 13:46 | Kushtia 132/33kV S/S T2 LT Tripped showing 50/51 trip, O/C DMT -1 relays Due to Poradah
feeder trip
| 14:26 | 17:36 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to 33 kv pbs feeder redhot
| 14:26 | 17:35 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to 33 kv pbs feeder redhot
| 14:43 | 16:52 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Hotspot Maintenance by | [7 empty] | 60.0MW load
|  |  | WZPDCO. | [7 empty] | interrup.
| 14:43 | 16:52 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Hotspot Maintenance by | [7 empty] | 60.0MW load
|  |  | WZPDCO. | [7 empty] | interrup.
| 14:47 | 17:45 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to By the
instruction of ALDC, Khulna
| 14:56 | 17:20 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Goalpara
Sub station 132 kv BUS insulation resistance test
| 20:01 | 21:14 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to Red hot maintenance | [7 empty] | 18.0MW load
|  |  | work | [7 empty] | interrup.
| 20:02 | 21:12 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to Red hot maintenance | [7 empty] | 18.0MW load
|  |  | work | [7 empty] | interrup.
| 20:39 | 22:25 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Forced S/D Due to 33/11 kv T4 Red hot | [7 empty] | 25.0MW load
interrup.
| 20:40 | 22:25 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D Due to 33/11 kv T4 Red hot
| 21:56 |  | ERA Meghnaghat Power Limited 718 MW CCPP GT12 was shutdown.
| 22:11 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 22:11 |  | Summit Meghnaghat-2 589 MW CCPP GT was sync.
| 23:52 |  | Summit Meghnaghat-2 589 MW CCPP ST was sync.
| 23:52 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 00:03 |  | Rampal 1320 MW (BIFPCL) unit-2 was shutdown due to coal shortage.
| 00:03 |  | Rampal 1320 MW (BIFPCL) unit-2 was shutdown due to coal shortage.
| 00:03 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 00:04 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-1 (False )
| 00:04 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-1 (False )
| 00:04 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-1 (False )
| 03:18 |  | Sikalbaha 225 MW ST tripped.
| 04:58 | 05:21 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Tripped showing Distance relays Due to 923B and | [7 empty] | 12.0MW load
|  |  | 920B Trip by Z2 Alarm (47.9km) during heavy thundering. | [7 empty] | interrup.
| 04:58 | 05:22 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Thakurgaon 132/33kV end showing Distance | [7 empty] | 12.0MW load
|  |  | relays Due to 905B and 920B Trip by Z2 Alarm (47.9km) during heavy thundering. and from | [7 empty] | interrup.
|  |  | Panchagarh 132/33kV end showing MiCOM P442 (DISTANCE PROTECTION RELAY) relays. | [7 empty] | Thakurgaon 132/33kV
end and 25.0MW load
interrup.
Panchagarh 132/33kV
end
| 06:37 |  | Baroaulia-KSRM 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to SF6 Breaker
change purpose.
| 06:38 |  | Chowmuhani-Feni 132 kV Ckt-1 Forced S/D from Daganbhuiyan 132/33kV end Due to Shoutdown
by Feni 132/33KV Grid Substation
| 06:40 |  | KSRM 132/33kV S/S Baraulia Main Scheduled S/D Due to Change SF6 breaker from Baraulia S/S
| 06:41 |  | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Change sf6 breaker form Barauia
S/S
| 06:42 |  | KSRM 132/33kV S/S Transformer-02 LT Scheduled S/D Due to Change SF6 breaker from Baraulia
S/S
| 06:43 |  | KSRM 132/33kV S/S Transformer-03 LT Scheduled S/D Due to Change SF6 breaker from Baraulia
S/S
| 06:50 | 07:19 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Tripped from Purbasadipur 132/33kV end showing
ALSTOM, EPAC 3000, Distance relay relays Due to Heavy rain and thundering.
| 06:57 | 07:23 | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Purbasadipur 132/33kV end showing
QUADRAMHO SHMP 101 relays Due to Heavy rain and thundering
| 07:00 |  | Minimum Generation is 11573 MW.
| 07:22 |  | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Due to temperature rise of Y-ph
33 KB incomer breaker -1.
| 07:24 |  | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Chowmuhani 132/33kV end Due to 230kv
Feni GIS Grid LILO connection and commissioning work,
| 07:40 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Lilo taping open
direct connected to feni 230 kV S/S EEGBPS Project Work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 332 | 8485200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8012000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 147 | 3566924 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 17979 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7373803 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45.5 | 490680 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 45 | 265920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 530125 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 119697 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.5 | 419400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 487080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 344640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 379124 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 80 | 877392 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 99 | 1107360 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 143 | 1586880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 156334 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 479880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 9553 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 466 | 9782400 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1699200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2390 | 46191571
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 3 | 47075.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117720 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 545280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5296038 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 210 | 4868857 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 323673 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 38784 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 615860 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 483840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 890880 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 43500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 30109 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 31782 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 985 | 18954543 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 137280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 275 | 6647272.73 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 1958 | 39089654.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4511000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7342300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 224 | 6162000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 385 | 8954800 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 141336 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 130560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 66909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 914564 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 179696 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 2118710 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 78 | 599520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 48 | 995520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 377920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 59 | 767220 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 47040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 85 | 877440 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 372182 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1483 | 34558717
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 105 | 2904000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 60 | 530400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 73 | 1346400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 279590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 84240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 118800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 267 | 5273380
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1027920 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 144 | 3588627 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719904 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1950160 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4403130 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 418000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 207672 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7531000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 313 | 8984000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1149 | 29547413
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 845 | 20422545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 16320 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 350 | 9058752 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 455760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1066 | 22967280 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2299 | 53832657
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 602 | 9388152 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 35040 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2773000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1093 | 23301818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5277200 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 27600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5150000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3175 | -
Barishal Area Total |  |  |  |  | 2858 | 2304 | 45955985.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 215940 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 13036 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 187 | 4749973 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4739436 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 340 | 9059490 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 23566 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 76608 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1309 | 25133455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 270752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 483780 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2024 | 44789736
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1124072 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 141 | 3445000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 44 | 341904 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 16022.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 358157 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 110150 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 992160 | -
Rangpur Area Total |  |  |  |  | 950 | 284 | 6387465.04
Eastern Grid Total |  |  |  |  | 17385.715 | 7247 | 154660735.13
Western Grid Total |  |  |  |  | 10980.24 | 6911 | 150965843.22
National Grid Total |  |  |  |  | 28365.955 | 14158 | 305626578.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9598.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4080.9 | MW
i) Dhaka area |  |  | 5094.85 |  | MW | i) Khulna area |  |  |  | 1671.5 | MW
ii) Chattogram area |  |  | 1476 |  | MW | ii) Barishal area |  |  |  | 431 | MW
iii) Cumilla area |  |  | 1373.18 |  | MW | iii) Rajshahi area |  |  |  | 1228.4 | MW
iv) Mymensingh area |  |  | 1077 |  | MW | iv) Rangpur area |  |  |  | 750 | MW
v) Sylhet area |  |  | 577 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13678.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 17:00 | 67 | Hathazari | 80 | 18:00 | 133 | PHP | 3 | 13:00
2 | AKSML | 130 | 23:00 | 68 | Ishurdi | 76 | 18:30 | 134 | Pabna | 91 | 18:30
3 | Aftabnagar | 36 | 18:00 | 69 | Jaldhaka | 66 | 00:00 | 135 | Palashbari | 104 | 18:00
4 | Agargaon | 113 | 13:00 | 70 | Jamalpur | 117 | 22:00 | 136 | Panchagarh | 47 | 18:00
5 | Agrabad | 80 | 18:00 | 71 | Jashore | 142 | 18:30 | 137 | Patiya | 10.4 | 00:00
6 | Amnura | 24 | 00:00 | 72 | Jhenaidah | 122 | 18:00 | 138 | Patuakhali | 70 | 22:00
7 | Ashuganj | 76 | 23:00 | 73 | Joydebpur | 149 | 18:30 | 139 | Payra | 32 | 00:00
8 | BSRM | 115 | 02:00 | 74 | Joypurhat | 53 | 00:00 | 140 | Postogola | 65 | 13:00
9 | Bagerhat | 83 | 19:30 | 75 | Juldah | 18.5 | 15:00 | 141 | Purbachal | 19 | 13:00
10 | Bajitpur | 97 | 21:00 | 76 | KSRM | 40 | 04:00 | 142 | Purbasadipur | 92 | 18:30
11 | Bakulia | 92 | 20:00 | 77 | Kabirpur | 270 | 18:00 | 143 | Rahanpur | 31 | 00:00
12 | Banani | 39.2 | 13:00 | 78 | Kachua | 84 | 00:00 | 144 | Rahim | 25 | 12:00
13 | Bangabhaban | 9 | 12:00 | 79 | Kallyanpur | 102 | 13:00 | 145 | Rajbari | 73 | 18:30
14 | Barapukuria | 51 | 13:00 | 80 | Kalurghat | 38 | 15:00 | 146 | Rajendrapur | 127 | 18:30
15 | Barguna | 22 | 14:00 | 81 | Kamrangirchar | 65 | 12:00 | 147 | Rajshahi | 92 | 22:00
16 | Barishal | 108 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 91 | 13:00
17 | Barishal-230 | 100 | 00:00 | 83 | Kasba | 36 | 20:00 | 149 | Ramganj | 116 | 21:00
18 | Baroaulia | 63 | 14:00 | 84 | Kazla | 98 | 18:00 | 150 | Rampur | 40 | 14:00
19 | Baroirhat | 64 | 18:00 | 85 | Keranigonj | 87 | 23:00 | 151 | Rangamati | 17 | 18:00
20 | Bashundhara | 183 | 14:00 | 86 | Khagrachori | 32 | 18:00 | 152 | Rangpur | 127 | 13:00
21 | BashundharaCement | 9 | 20:00 | 87 | Khulna | 69 | 13:00 | 153 | Ruppur | 5.4 | 12:00
22 | Beanibazar | 80 | 18:00 | 88 | Khulshi | 199 | 18:30 | 154 | SSM | 0 | 00:00
23 | Benapole | 57 | 22:00 | 89 | Kishoreganj | 112 | 00:00 | 155 | Saidpur | 93 | 12:00
24 | Bhaluka | 151 | 19:00 | 90 | Kodda | 296 | 12:00 | 156 | Satkhira | 121 | 22:00
25 | Bhandaria | 56 | 22:00 | 91 | Kulaura | 53 | 18:30 | 157 | Satmasjid | 99 | 13:00
26 | Bhangura | 34 | 19:30 | 92 | Kurigram | 66 | 18:00 | 158 | Savar | 222 | 12:00
27 | Bheramara(GK) | 63 | 19:30 | 93 | Kushtia | 143 | 18:30 | 159 | SevenRings | 14.89 | 21:00
28 | Bhulta | 227 | 12:00 | 94 | Laksam | 32 | 20:00 | 160 | ShahCement | 27 | 22:00
29 | Bog-Sherpur | 68 | 18:30 | 95 | Lakshmipur | 34 | 20:00 | 161 | Shahjadpur | 78 | 18:30
30 | Bogura | 149 | 23:00 | 96 | Lalbag | 60 | 13:00 | 162 | Shahjibazar | 117 | 20:00
31 | Borhanuddin | 94 | 22:00 | 97 | Lalmonirhat | 55 | 18:00 | 163 | Shahmirpur | 55 | 23:00
32 | Brahmanbaria | 138 | 22:00 | 98 | MI_Cement | 17.8 | 07:00 | 164 | Shariatpur | 84 | 22:00
33 | Cantonment | 128 | 13:00 | 99 | Madanganj | 41 | 19:00 | 165 | Sherpur | 136 | 23:00
34 | Chandina | 25.03 | 18:00 | 100 | Madaripur | 108 | 22:00 | 166 | Shikalbaha | 23 | 18:00
35 | Chandpur | 92 | 18:30 | 101 | Madartek | 82 | 23:00 | 167 | Shitalakhya | 83.5 | 12:00
36 | Chandraghona | 34 | 18:00 | 102 | Madunaghat | 55 | 18:00 | 168 | Sholosohor | 47 | 18:00
37 | Chapai | 59 | 00:00 | 103 | Magura | 61 | 18:30 | 169 | Shyampur | 98 | 07:00
38 | Charsaidpur | 28 | 02:00 | 104 | Mahasthangarh | 68 | 00:00 | 170 | Siddhirganj | 120 | 12:00
39 | Chauddagram | 75 | 05:00 | 105 | Maijdee | 22 | 23:00 | 171 | Sirajganj | 100 | 19:30
40 | Chhatak | 38 | 18:30 | 106 | Manikganj | 118 | 18:30 | 172 | Sonargaon | 120 | 21:00
41 | Chowmuhani | 181 | 20:00 | 107 | Maniknagar | 60 | 13:00 | 173 | Sreemongol | 74 | 00:00
42 | Chuadanga | 108 | 18:30 | 108 | Matarbari | 51 | 19:00 | 174 | Sreepur | 97 | 22:00
43 | Coxsbazar | 137 | 18:30 | 109 | Matuail | 74 | 12:00 | 175 | Srinagar | 45.4 | 21:00
44 | Cumilla(N) | 148 | 22:00 | 110 | Millgate | 121 | 14:00 | 176 | Sunamganj | 64 | 23:00
45 | Cumilla(S) | 152 | 19:30 | 111 | Mirpur | 120 | 18:30 | 177 | Sylhet | 56 | 18:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Mirsorai | 11 | 15:00 | 178 | Sylhet-132 | 127 | 18:00
47 | Daudkandi | 134 | 21:00 | 113 | Mirzapur | 46 | 20:00 | 179 | TK | 24.5 | 18:00
48 | DhakaUniversity | 70 | 13:00 | 114 | Mithapukur | 62 | 18:00 | 180 | Tangail | 164 | 18:30
49 | Dhamrai | 132 | 18:30 | 115 | Modern | N/A | N/A | 181 | Taraganj | 18.5 | 00:00
50 | Dhanmondi | 125 | 13:00 | 116 | Mogbazar | 85.9 | 15:00 | 182 | Thakurgaon | 88 | 18:30
51 | Dohazari | 101 | 19:00 | 117 | Mongla | 44 | 14:00 | 183 | Tongi | 116 | 15:00
52 | Faridpur | 166 | 21:00 | 118 | Motijheel | 45 | 13:00 | 184 | Ullahpara | 33 | 18:30
53 | Fatullah | 110 | 15:00 | 119 | Muktagacha | 40 | 18:00 | 185 | Ullon | 48 | 13:00
54 | Fenchuganj | 46 | 21:00 | 120 | Munshiganj | 107 | 22:00 | 186 | Uttara | 77 | 13:00
55 | Feni | 115 | 19:30 | 121 | Muradnagar | 39 | 20:00 | 187 | UttaraNew | 57 | 14:00
56 | GPH | 77 | 07:00 | 122 | Mymensingh | 191 | 18:30 | 188 | Zigatola | 69 | 14:00
57 | Ghatail | 80 | 18:00 | 123 | Naogaon | 112 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 54 | 20:00
59 | Ghorashal-230 | 96 | 18:30 | 125 | Narinda | 56 | 18:00
60 | Goalpara | 39 | 13:00 | 126 | Narshingdi | 179 | 21:00
61 | Gollamari | 80 | 18:30 | 127 | Natore | 137 | 20:00
62 | Gopalganj | 101 | 18:30 | 128 | Nawabganj | 47.2 | 22:00
63 | Gulshan | 100 | 13:00 | 129 | Netrakona | 137 | 18:00
64 | Halishahar | 75 | 09:00 | 130 | New | 54.2 | 18:00
65 | HaripurSBU | 137 | 11:00 | 131 | Niamatpur | 63 | 00:00
66 | Hasnabad | 92 | 19:30 | 132 | Noapara | 42 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12950.44 | 0 |  | 12950.44
1:00 | 12674.09 | 0 |  | 12674.09
2:00 | 12331.2 | 0 |  | 12331.2
3:00 | 11862.33 | 0 |  | 11862.33
4:00 | 11606.22 | 0 |  | 11606.22
5:00 | 11434.68 | 0 |  | 11434.68
6:00 | 11140.26 | 0 |  | 11140.26
7:00 | 11226.6 | 0 |  | 11226.6
8:00 | 11253.03 | 0 |  | 11253.03
9:00 | 11523.72 | 0 |  | 11523.72
10:00 | 11729.05 | 0 |  | 11729.05
11:00 | 12038.79 | 0 |  | 12038.79
12:00 | 12684.47 | 0 |  | 12684.47
13:00 | 12897.29 | 0 |  | 12897.29
14:00 | 12549.23 | 0 |  | 12549.23
15:00 | 12425.65 | 0 |  | 12425.65
16:00 | 12262.2 | 0 |  | 12262.2
17:00 | 12024.83 | 0 |  | 12024.83
18:00 | 13549.5 | 0 |  | 13549.5
19:00 | 14158 | 0 |  | 14158
19:30 | 14123 | 0 |  | 14123
20:00 | 14109.7 | 0 |  | 14109.7
21:00 | 14078.95 | 0 |  | 14078.95
22:00 | 14040.04 | 0 |  | 14040.04
23:00 | 14038.82 | 0 |  | 14038.82
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6058.8 | 6891.64 | 12950.44 | DAILY GENERATION CURVE
00:30 | 6026.9 | 6785.365 | 12812.265
01:00 | 5995 | 6679.09 | 12674.09 | 04-10-2025
01:30 | 5966 | 6536.645 | 12502.645
02:00 | 5937 | 6394.2 | 12331.2
02:30 | 5893 | 6203.765 | 12096.765
03:00 | 5849 | 6013.33 | 11862.33
03:30 | 5820 | 5914.275 | 11734.275
04:00 | 5791 | 5815.22 | 11606.22
04:30 | 5802.5 | 5717.95 | 11520.45
05:00 | 5814 | 5620.68 | 11434.68
05:30 | 5776.595 | 5510.875 | 11287.47
06:00 | 5739.19 | 5401.07 | 11140.26
06:30 | 5768.095 | 5415.335 | 11183.43
07:00 | 5797 | 5429.6 | 11226.6
07:30 | 5765.315 | 5474.5 | 11239.815
08:00 | 5733.63 | 5519.4 | 11253.03
08:30 | 5810.75 | 5577.625 | 11388.375
09:00 | 5887.87 | 5635.85 | 11523.72
09:30 | 5929.525 | 5696.86 | 11626.385
10:00 | 5971.18 | 5757.87 | 11729.05
10:30 | 6067.54 | 5816.38 | 11883.92
11:00 | 6163.9 | 5874.89 | 12038.79
11:30 | 6286.35 | 6075.28 | 12361.63
12:00 | 6408.8 | 6275.67 | 12684.47
12:30 | 6513.995 | 6276.885 | 12790.88
13:00 | 6619.19 | 6278.1 | 12897.29
13:30 | 6562.16 | 6161.1 | 12723.26
14:00 | 6505.13 | 6044.1 | 12549.23
14:30 | 6471.56 | 6015.88 | 12487.44
15:00 | 6437.99 | 5987.66 | 12425.65
15:30 | 6394.89 | 5949.035 | 12343.925
16:00 | 6351.79 | 5910.41 | 12262.2
16:30 | 6269.505 | 5874.01 | 12143.515
17:00 | 6187.22 | 5837.61 | 12024.83
17:30 | 6596.86 | 6190.305 | 12787.165
18:00 | 7006.5 | 6543 | 13549.5
18:30 | 7126.75 | 6727 | 13853.75
19:00 | 7247 | 6911 | 14158
19:30 | 7219 | 6904 | 14123
20:00 | 7187.7 | 6922 | 14109.7
20:30 | 7158.45 | 6935.875 | 14094.325 |  | Executive Engineer
21:00 | 7129.2 | 6949.75 | 14078.95 |  | Network Operation Division
21:30 | 7067.95 | 6991.545 | 14059.495
22:00 | 7006.7 | 7033.34 | 14040.04
22:30 | 7031.95 | 7007.48 | 14039.43
23:00 | 7057.2 | 6981.62 | 14038.82

## En-Curve
QF-LDC-12
Date | 04-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4164 | 1845 | 849 | 38 | 48 | 1362.64 | 219 | 4015 | 0 | 118 | 277.8 | 0 | 0 | 14 | 0 | DAILY ENERGY CURVE
00:30 | 4166.5 | 1846 | 849 | 38 | 46 | 1358.365 | 218.5 | 3922 | 0 | 109.5 | 249.4 | 0 | 0 | 9 | 0 | 04-10-2025
01:00 | 4169 | 1847 | 849 | 38 | 44 | 1354.09 | 218 | 3829 | 0 | 101 | 221 | 0 | 0 | 4 | 0
01:30 | 4157.5 | 1832.5 | 849 | 38 | 44 | 1256.145 | 218 | 3786 | 0 | 101 | 218 | 0 | 0 | 2.5 | 0 | Energy Generated | 305.6266 |  | MKWHr
02:00 | 4146 | 1818 | 849 | 38 | 44 | 1158.2 | 218 | 3743 | 0 | 101 | 215 | 0 | 0 | 1 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 4142 | 1818 | 849 | 38 | 43 | 1154.265 | 218 | 3588.5 | 0 | 84.5 | 160 | 0 | 0 | 1.5 | 0 | Total Energy Requirement | 305.6266 |  | MKWHr
03:00 | 4138 | 1818 | 849 | 38 | 42 | 1150.33 | 218 | 3434 | 0 | 68 | 105 | 0 | 0 | 2 | 0
03:30 | 4135 | 1812.5 | 849 | 38 | 41 | 1083.275 | 218 | 3403.5 | 0 | 60 | 91.5 | 0 | 0 | 2.5 | 0
04:00 | 4132 | 1807 | 849 | 38 | 40 | 1016.22 | 218 | 3373 | 0 | 52 | 78 | 0 | 0 | 3 | 0
04:30 | 4139.5 | 1807 | 849 | 38 | 39 | 963.45 | 218 | 3333.5 | 0 | 52 | 78 | 0 | 0 | 3 | 0
05:00 | 4147 | 1807 | 849 | 38 | 38 | 910.68 | 218 | 3294 | 0 | 52 | 78 | 0 | 0 | 3 | 0
05:30 | 4103 | 1793 | 848.5 | 38 | 38 | 886.315 | 218 | 3239.5 | 0.155 | 43.5 | 71.5 | 0 | 0 | 8 | 0
06:00 | 4059 | 1779 | 848 | 38 | 38 | 861.95 | 218 | 3185 | 0.31 | 35 | 65 | 0 | 0 | 13 | 0
06:30 | 4099.5 | 1793 | 848.5 | 38 | 37 | 856.81 | 218 | 3152 | 43.62 | 27.5 | 60.5 | 0 | 0 | 9 | 0
07:00 | 4140 | 1807 | 849 | 38 | 36 | 851.67 | 218 | 3119 | 86.93 | 20 | 56 | 0 | 0 | 5 | 0
07:30 | 4101 | 1763 | 849 | 38 | 35 | 854.335 | 218 | 3108.5 | 176.98 | 27 | 64 | 0 | 0 | 5 | 0
08:00 | 4062 | 1719 | 849 | 38 | 34 | 857 | 218 | 3098 | 267.03 | 34 | 72 | 0 | 0 | 5 | 0
08:30 | 4105.5 | 1726.5 | 846.5 | 38 | 33 | 855.5 | 219 | 3111 | 334.875 | 52 | 64 | 0 | 0 | 2.5 | 0
09:00 | 4149 | 1734 | 844 | 38 | 32 | 854 | 220 | 3124 | 402.72 | 70 | 56 | 0 | 0 | 0 | 0
09:30 | 4148.5 | 1726.5 | 844 | 38 | 33 | 854 | 220 | 3123 | 480.885 | 73 | 83 | 0 | 0 | 2.5 | 0
10:00 | 4148 | 1719 | 844 | 38 | 34 | 854 | 220 | 3122 | 559.05 | 76 | 110 | 0 | 0 | 5 | 0
10:30 | 4153 | 1753.5 | 844 | 38 | 35 | 851 | 220 | 3176 | 571.92 | 85 | 152 | 0 | 0 | 4.5 | 0
11:00 | 4158 | 1788 | 844 | 38 | 36 | 848 | 220 | 3230 | 584.79 | 94 | 194 | 0 | 0 | 4 | 0
11:30 | 4167 | 1801 | 844 | 38 | 37 | 846.5 | 220 | 3408.5 | 570.23 | 134.5 | 292.9 | 0 | 0 | 2 | 0
12:00 | 4176 | 1814 | 844 | 38 | 38 | 845 | 220 | 3587 | 555.67 | 175 | 391.8 | 0 | 0 | 0 | 0
12:30 | 4100 | 1776.5 | 844 | 38 | 40 | 876 | 220 | 3664 | 519.98 | 175 | 526.4 | 0 | 0 | 11 | 0
13:00 | 4024 | 1739 | 844 | 38 | 42 | 907 | 220 | 3741 | 484.29 | 175 | 661 | 0 | 0 | 22 | 0
13:30 | 3986.5 | 1744 | 844 | 38 | 42 | 911 | 220 | 3719 | 385.26 | 175 | 638 | 0 | 0 | 20.5 | 0
14:00 | 3949 | 1749 | 844 | 38 | 42 | 915 | 220 | 3697 | 286.23 | 175 | 615 | 0 | 0 | 19 | 0
14:30 | 3981 | 1723.25 | 844 | 38 | 43 | 916.5 | 220 | 3694.5 | 245.79 | 171.5 | 588.9 | 0 | 0 | 21 | 0
15:00 | 4013 | 1697.5 | 844 | 38 | 44 | 918 | 220 | 3692 | 205.35 | 168 | 562.8 | 0 | 0 | 23 | 0
15:30 | 4009.5 | 1691.75 | 844 | 38 | 43 | 914.5 | 220.5 | 3696 | 145.075 | 180 | 542.1 | 0 | 0 | 19.5 | 0
16:00 | 4006 | 1686 | 844 | 38 | 42 | 911 | 221 | 3700 | 84.8 | 192 | 521.4 | 0 | 0 | 16 | 0
16:30 | 3984.5 | 1684 | 844 | 38 | 41 | 918.5 | 221 | 3681.5 | 56.615 | 192 | 474.4 | 0 | 0 | 8 | 0
17:00 | 3963 | 1682 | 844 | 38 | 40 | 926 | 221 | 3663 | 28.43 | 192 | 427.4 | 0 | 0 | 0 | 0
17:30 | 3998 | 1727 | 844 | 38 | 43 | 1012.5 | 221 | 3849 | 14.215 | 301 | 739.45 | 0 | 0 | 0 | 0
18:00 | 4033 | 1772 | 844 | 38 | 46 | 1099 | 221 | 4035 | 0 | 410 | 1051.5 | 0 | 0 | 0 | 0
18:30 | 3989.5 | 1776.75 | 844.5 | 38 | 47 | 1204 | 221 | 4260 | 0 | 392.5 | 1080.5 | 0 | 0 | 0 | 0
19:00 | 3946 | 1781.5 | 845 | 38 | 48 | 1309 | 221 | 4485 | 0 | 375 | 1109.5 | 0 | 0 | 0 | 0
19:30 | 3990 | 1796.5 | 834 | 38 | 46 | 1311 | 221 | 4515 | 0 | 354 | 1016.5 | 0 | 0 | 1 | 0
20:00 | 3977 | 1783.5 | 834 | 38 | 48 | 1315 | 221 | 4534 | 0 | 370 | 984.2 | 0 | 0 | 5 | 0
20:30 | 3986 | 1790.75 | 833.5 | 38 | 48 | 1317.375 | 221 | 4536.5 | 0 | 370 | 950.2 | 0 | 0 | 3 | 0
21:00 | 3995 | 1798 | 833 | 38 | 48 | 1319.75 | 221 | 4539 | 0 | 370 | 916.2 | 0 | 0 | 1 | 0
21:30 | 3977 | 1690.5 | 833 | 38 | 49 | 1320.045 | 221.5 | 4640.5 | 0 | 371 | 916.95 | 0 | 0 | 2 | 0
22:00 | 3959 | 1583 | 833 | 38 | 50 | 1320.34 | 222 | 4742 | 0 | 372 | 917.7 | 0 | 0 | 3 | 0
22:30 | 3962 | 1616.5 | 833.5 | 38 | 50 | 1313.98 | 221 | 4717.5 | 0 | 372 | 907.45 | 0 | 0 | 7.5 | 0
23:00 | 3965 | 1650 | 834 | 38 | 50 | 1307.62 | 220 | 4693 | 0 | 372 | 897.2 | 0 | 0 | 12 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 06:00 | 369 | 22:00 | Payra | 412 | 05:00 | 403 | 00:00
Ashuganj | 410 | 6:00 | 391 | 11:00 | Rahanpur | 409 | 06:00 | 395 | 00:00
Bhulta | 405 | 06:00 | 383 | 11:00 | Rampal | 404 | 06:00 | 390 | 18:30
Bibiana | 388 | 06:00 | 380 | 11:00
BIPTC | 402 | 06:00 | 392 | 23:00
Bogura | 401 | 06:00 | 385 | 00:00
Gopalganj | 399 | 15:00 | 381 | 22:00
Kaliakoir | 374 | 04:00 | 362 | 11:00
Madunaghat | 388 | 06:00 | 383 | 22:00
Meghnaghat | 383 | 06:00 | 373 | 22:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 221 | 12:00 | Kaliakoir | 233 | 04:00 | 224 | 11:00
AKSML | 230 | 06:00 | 224 | 00:00 | Keranigonj | 227 | 05:00 | 218 | 12:00
Aminbazar | 230 | 05:00 | 221 | 11:00 | Khulna(S) | 231 | 06:00 | 217 | 19:00
Ashuganj | 233 | 06:00 | 224 | 00:00 | Madunaghat | 230 | 05:00 | 226 | 10:00
Ashuganj-400 | 233 | 06:00 | 224 | 00:00 | Madunaghat-400 | 231 | 06:00 | 227 | 17:00
Baghabari | 234 | 06:00 | 225 | 18:00 | Maniknagar | 221 | 06:00 | 215 | 12:00
Barapukuria | 226 | 17:00 | 219 | 00:00 | Meghnaghat | 229 | 06:00 | 222 | 10:00
Barapukuria-230 | 226 | 17:00 | 219 | 00:00 | Meghnaghat-400 | 225 | 05:00 | 218 | 12:00
Barishal | 232 | 06:00 | 223 | 22:00 | Mirsorai | 233 | 18:30 | 225 | 02:00
Bheramara | 232 | 06:00 | 223 | 00:00 | Rajshahi | 231 | 06:00 | 220 | 00:00
Bhulta | 233 | 06:00 | 216 | 11:00 | Rampal | 230 | 06:00 | 218 | 18:30
Bibiana | 228 | 06:00 | 222 | 23:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 06:00 | 223 | 18:30 | Rampura | 232 | 06:00 | 216 | 11:00
Bogura | 238 | 06:00 | 229 | 00:00 | Shikalbaha | 229 | 18:30 | 224 | 01:00
Bogura-400 | 238 | 06:00 | 229 | 00:00 | Shyampur | 229 | 00:00 | 218 | 11:00
Borhanuddin | 237 | 04:00 | 229 | 22:00 | Siddhirganj | 222 | 04:00 | 216 | 23:00
BSRM | 233 | 18:30 | 224 | 00:00 | Sirajgonj | 240 | 06:00 | 234 | 00:00
Cumilla(N) | 227 | 10:00 | 216 | 00:00 | Sreepur | 229 | 06:00 | 220 | 12:00
Faridpur | 231 | 06:00 | 219 | 22:00 | Tongi | 230 | 04:00 | 218 | 11:00
Fenchuganj | 229 | 09:00 | 225 | 03:00
Ghorashal | 240 | 05:00 | 222 | 11:00
Ghorashal-230 | 231 | 06:00 | 218 | 11:00
Gopalganj | 232 | 8:00 | 221 | 12:00
GPH | 231 | 18:30 | 226 | 00:00
Haripur | 223 | 06:00 | 217 | 11:00
Hasnabad | 225 | 05:00 | 218 | 12:00
Hathazari | 231 | 05:00 | 222 | 23:00
Ishurdi | 235 | 06:00 | 226 | 18:30
Jhenaidah | 229 | 06:00 | 216 | 18:30
Kachua | 206 | 14:00 | 196 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 126 | 11:00 | Lalmonirhat | 130 | 09:00 | 123 | 13:00
Agargaon | 136 | 05:00 | 128 | 12:00 | Madanganj | 129 | 05:00 | 125 | 11:00
Agrabad | 131 | 06:00 | 127 | 17:00 | Madaripur | 134 | 07:00 | 128 | 23:00
AKS | 130 | 00:00 | 127 | 10:00 | Madartek | 135 | 06:00 | 124 | 12:00
Aminbazar | 135 | 05:00 | 130 | 10:00 | Madunaghat | 133 | 03:00 | 131 | 00:00
Amnura | 139 | 16:00 | 127 | 00:00 | Magura | 133 | 06:00 | 122 | 21:00
Ashuganj | 141 | 07:00 | 135 | 19:30 | Mahasthangarh | 132 | 06:00 | 126 | 00:00
Bagerhat | 131 | 08:00 | 118 | 00:00 | Maijdee | 123 | 13:00 | 112 | 00:00
Bajitpur | 132 | 05:00 | 124 | 23:00 | Manikganj | 132 | 06:00 | 121 | 15:00
Bakulia | 132 | 06:00 | 129 | 00:00 | Maniknagar | 135 | 03:00 | 129 | 12:00
Banani | 136 | 06:00 | 124 | 11:00 | Matarbari | 120 | 07:00 | 110 | 18:00
Bangabhaban | 134 | 03:00 | 129 | 12:00 | Matuail | 129.6 | 06:00 | 126 | 11:00
Barapukuria | 139 | 17:00 | 130 | 00:00 | Millgate | 135 | 04:00 | 126 | 11:00
Barguna | 136 | 08:00 | 129 | 22:00 | Mirpur | 135 | 06:00 | 128 | 10:00
Barishal | 134 | 07:00 | 125 | 21:00 | Mirzapur | 130 | 04:00 | 124 | 12:00
Barishal-230 | 133 | 06:00 | 126 | 22:00 | Mithapukur | 132 | 06:00 | 125 | 19:30
Baroaulia | 132 | 02:00 | 128 | 23:00 | MI_Cement | 130.6 | 05:00 | 125.5 | 12:00
Baroirhat | 131 | 07:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 04:00 | 125 | 11:00 | Mogbazar | 137 | 05:00 | 125 | 12:00
BashundharaCement | 129 | 05:00 | 125 | 11:00 | Mongla | 131 | 08:00 | 119 | 22:00
Beanibazar | 128 | 07:00 | 123 | 18:00 | Motijheel | 134 | 03:00 | 129 | 12:00
Benapole | 132 | 05:00 | 119 | 22:00 | Muktagacha | 133 | 18:30 | 126 | 00:00
Bhaluka | 130 | 08:00 | 122 | 12:00 | Munshiganj | 129 | 04:00 | 124 | 11:00
Bhandaria | 130 | 15:00 | 117 | 21:00 | Muradnagar | 126 | 06:00 | 120 | 00:00
Bhangura | 134 | 02:00 | 128 | 18:30 | Mymensingh | 135 | 18:30 | 114 | 23:00
Bheramara | 137 | 06:00 | 133 | 00:00 | Naogaon | 133 | 16:00 | 122 | 00:00
Bheramara(GK) | 137 | 07:00 | 132 | 18:30 | Narail | 132 | 09:00 | 120 | 22:00
Bhulta | 128 | 17:00 | 123 | 22:00 | Narinda | 135 | 03:00 | 129 | 12:00
Bog-Sherpur | 133 | 05:00 | 127 | 22:00 | Narshingdi | 134 | 07:00 | 119 | 21:00
Bogura | 134 | 06:00 | 128 | 00:00 | Natore | 133 | 06:00 | 127 | 00:00
Bogura-230 | 135 | 06:00 | 128 | 00:00 | Nawabganj | 135 | 05:00 | 128 | 12:00
Brahmanbaria | 135 | 08:00 | 128 | 00:00 | Netrakona | 124 | 05:00 | 112 | 23:00
Cantonment | 135 | 03:00 | 128 | 11:00 | New | 135 | 07:00 | 126 | 11:00
Chandina | 129 | 06:00 | 124 | 00:00 | Niamatpur | 139 | 06:00 | 133 | 00:00
Chandpur | 128 | 14:00 | 119 | 00:00 | Noapara | 134 | 06:00 | 123 | 22:00
Chandraghona | 134 | 06:00 | 131 | 00:00 | Pabna | 135 | 06:00 | 130 | 00:00
Chapai | 139 | 07:00 | 132 | 00:00 | Palashbari | 130 | 17:00 | 123 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 05:00 | 125 | 11:00 | Panchagarh | 133 | 17:00 | 126 | 12:00
Chauddagram | 126 | 06:00 | 121 | 00:00 | Patiya | 130 | 07:00 | 127 | 00:00
Chhatak | 128 | 06:00 | 120 | 23:00 | Patuakhali | 136 | 09:00 | 132 | 00:00
Chowmuhani | 124 | 17:00 | 113 | 00:00 | Payra | 139 | 05:00 | 133 | 00:00
Chuadanga | 131 | 06:00 | 120 | 00:00 | PHP | 130 | 06:00 | 126 | 00:00
Coxsbazar | 119 | 07:00 | 110 | 18:00 | Postogola | 133 | 05:00 | 128 | 12:00
Cumilla(N) | 129 | 06:00 | 124 | 00:00 | Purbachal | 136 | 05:00 | 125 | 11:00
Cumilla(S) | 132 | 04:00 | 123 | 00:00 | Purbasadipur | 132 | 17:00 | 125 | 00:00
Daganbhuiyan | 121 | 13:00 | 112 | 02:00 | Rahanpur | 140 | 07:00 | 135 | 00:00
Daudkandi | 124 | 06:00 | 118 | 00:00 | Rahanpur-400 | 140 | 05:00 | 135 | 00:00
DhakaUniversity | 136 | 06:00 | 126 | 11:00 | Rahim | 130 | 05:00 | 126 | 11:00
Dhamrai | 133 | 05:00 | 126 | 12:00 | Rajbari | 135 | 06:00 | 127 | 22:00
Dhanmondi | 137 | 03:00 | 126 | 11:00 | Rajendrapur | 133 | 17:00 | 122 | 12:00
Dohazari | 126 | 05:00 | 123 | 00:00 | Rajshahi | 133 | 06:00 | 126 | 00:00
Faridpur | 135 | 04:00 | 129 | 22:00 | Rajshahi-230 | 133 | 10:00 | 127 | 00:00
Fatullah | 137 | 05:00 | 131 | 11:00 | Ramganj | 124 | 14:00 | 113 | 00:00
Fenchuganj | 135 | 07:00 | 132 | 00:00 | Rampur | 130 | 04:00 | 126 | 16:00
Feni | 123 | 20:00 | 111 | 00:00 | Rampura | 136 | 05:00 | 126 | 11:00
Ghatail | 130 | 17:00 | 122 | 18:00 | Rangamati | 132 | 05:00 | 130 | 00:00
Ghorashal | 138 | 04:00 | 130 | 09:00 | Rangpur | 133 | 17:00 | 127 | 20:00
Goalpara | 136 | 09:00 | 125 | 22:00 | Ruppur | 137 | 05:00 | 132 | 00:00
Gollamari | 137 | 06:00 | 126 | 22:00 | Saidpur | 135 | 17:00 | 126 | 12:00
Gopalganj | 134 | 06:00 | 126 | 22:00 | Satkhira | 133 | 06:00 | 120 | 22:00
Gopalganj-400 | 136 | 06:00 | 125 | 22:00 | Satmasjid | 135 | 04:00 | 128 | 12:00
Gulshan | 136 | 06:00 | 125 | 12:00 | Savar | 134 | 02:00 | 128 | 10:00
Halishahar | 131 | 05:00 | 127 | 17:00 | SevenRings | 137 | 05:00 | 130 | 11:00
Haripur | 130 | 04:00 | 126 | 12:00 | ShahCement | 130 | 05:00 | 125 | 11:00
HaripurSBU | 130 | 04:00 | 126 | 12:00 | Shahjadpur | 137 | 02:00 | 133 | 00:00
Hasnabad | 133 | 03:00 | 128 | 11:00 | Shahjibazar | 135 | 07:00 | 128 | 00:00
Hathazari | 133 | 04:00 | 122 | 12:00 | Shahmirpur | 131 | 04:00 | 128 | 01:00
Ishurdi | 138 | 06:00 | 132 | 00:00 | Shariatpur | 133 | 05:00 | 124 | 23:00
Jaldhaka | 133 | 17:00 | 124 | 19:30 | Sherpur | 132 | 18:30 | 118 | 00:00
Jamalpur | 135 | 18:30 | 123 | 00:00 | Shikalbaha | 121 | 04:00 | 118 | 00:00
Jashore | 130 | 05:00 | 118 | 19:00 | Shikalbaha-230 | 133 | 18:00 | 130 | 00:00
Jhenaidah | 135 | 09:00 | 122 | 18:30 | Shitalakhya | 130.6 | 06:00 | 125.5 | 12:00
Jhenaidah-230 | 134 | 06:00 | 125 | 18:30 | Sholosohor | 133 | 06:00 | 130 | 00:00
Joydebpur | 132 | 19:00 | 123 | 11:00 | Shyampur | 137 | 05:00 | 133 | 00:00
Joypurhat | 134 | 16:00 | 121 | 00:00 | Shyampur-230 | 137 | 08:00 | 131 | 01:00
Juldah | 130 | 00:00 | 128 | 16:00 | Siddhirganj | 130 | 04:00 | 126 | 11:00
Kabirpur | 133 | 06:00 | 123 | 15:00 | Sirajganj | 132 | 06:00 | 126 | 23:00
Kachua | 129 | 14:00 | 122 | 00:00 | Sonargaon | 128 | 05:00 | 124 | 12:00
Kaliakoir | 135 | 04:00 | 127 | 11:00 | Sreemongol | 134 | 07:00 | 127 | 23:00
Kallyanpur | 134 | 04:00 | 129 | 10:00 | Sreepur | 133 | 06:00 | 126 | 12:00
Kalurghat | 134 | 18:30 | 130 | 00:00 | Srinagar | 135 | 05:00 | 128 | 12:00
Kamrangirchar | 136 | 07:00 | 128 | 10:00 | SSM | 134 | 12:00 | 132 | 00:00
Kaptai | 135 | 8:00 | 133 | 16:00 | Sunamganj | 126 | 10:00 | 119 | 18:00
Kasba | 125 | 06:00 | 119 | 00:00 | Sylhet | 129 | 07:00 | 125 | 00:00
Kazla | 135 | 07:00 | 129 | 12:00 | Sylhet-132 | 129 | 05:00 | 126 | 18:00
Keranigonj | 135 | 05:00 | 129 | 11:00 | Tangail | 127 | 19:00 | 121 | 12:00
Khagrachori | 132 | 06:00 | 129 | 00:00 | Taraganj | 133 | 17:00 | 126 | 00:00
Khulna | 136 | 08:00 | 124 | 22:00 | Thakurgaon | 131 | 17:00 | 124 | 12:00
Khulna(S) | 137 | 06:00 | 126 | 22:00 | TK | 133 | 02:00 | 131 | 10:00
Khulshi | 130 | 18:30 | 126 | 14:00 | Tongi | 135 | 04:00 | 128 | 11:00
Kishoreganj | 130 | 05:00 | 119 | 21:00 | Ullahpara | 134 | 05:00 | 128 | 18:30
Kodda | 130 | 05:00 | 122 | 08:00 | Ullon | 136 | 06:00 | 125 | 11:00
KSRM | 132 | 05:00 | 129 | 11:00 | Uttara | 135 | 05:00 | 128 | 10:00
Kulaura | 135 | 08:00 | 130 | 20:00 | UttaraNew | 135 | 05:00 | 128 | 11:00
Kurigram | 130 | 06:00 | 118 | 18:00 | Zigatola | 136 | 06:00 | 128 | 12:00
Kushtia | 136 | 14:00 | 128 | 18:30
Laksam | 129 | 14:00 | 121 | 00:00
Lakshmipur | 124 | 13:00 | 113 | 00:00
Lalbag | 136 | 07:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division