## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-10-2025 | [28 empty] | Date: | 05-10-2025 | [28 empty] | Date: | 05-10-2025 | [28 empty] | Date: | 05-10-2025 | [28 empty] | Date: | 05-10-2025 | [14 empty] | Date: | 05-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 233 | 48.5 | 17 | 70 | 15 | 0 | 0 | 0 | 154 | 0 | 320 | 145 | 65 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 106 | 0 | 12 | 66 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 2 | 280 | 0 | 0 | 18 | 8 | 15 | 203 | 0 | 0 | 0 | 1135 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 3 | 190 | 0 | 89 | 96 | 48 | 0 | 18 | 58 | 50 | 0 | 0 | 36 | 315 | 0 | 358 | 30 | 57 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 55 | 98 | 0 | 0 | 9 | 7060.5 | 833 | 335 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 978 | 0 | 1310.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 196 | 0 | 0 | 0 | 399 | 0 | 0 | 139 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 603 | 1150 | 0 | 6934.01 | 13994.51 | 108.02
01:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 234 | 35 | 0 | 68 | 15 | 0 | 0 | 0 | 150 | 0 | 300 | 147 | 115 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 98 | 0 | 8 | 66 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 10 | 280 | 0 | 0 | 39 | 0 | 16 | 188 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 0 | 201 | 0 | 87 | 97 | 48 | 0 | 18 | 65 | 48 | 0 | 0 | 36 | 310 | 0 | 386 | 30 | 57 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 78 | 55 | 101 | 0 | 0 | 6 | 7058 | 834 | 329 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 497 | 0 | 1302.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 142 | 48 | 35 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 601 | 1222 | 0 | 6509.28 | 13567.28 | 108.01
02:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 234 | 29.8 | 0 | 37 | 0 | 0 | 0 | 0 | 120 | 0 | 300 | 148 | 128 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 12 | 280 | 0 | 0 | 39 | 0 | 10 | 187 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 0 | 190 | 0 | 82 | 97 | 34 | 0 | 18 | 56 | 46 | 0 | 0 | 36 | 305 | 0 | 366 | 30 | 57 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 78 | 55 | 101 | 0 | 0 | 6 | 6728.8 | 834 | 322 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 1312.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 193 | 0 | 0 | 0 | 408 | 0 | 0 | 138 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 603 | 1222 | 0 | 6333.24 | 13062.04 | 108
03:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 194 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 160 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 13 | 280 | 0 | 0 | 39 | 0 | 0 | 187 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 0 | 195 | 0 | 68 | 97 | 34 | 0 | 18 | 47 | 44 | 0 | 0 | 36 | 310 | 0 | 382 | 30 | 57 | 155 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 55 | 101 | 0 | 0 | 6 | 6530 | 833 | 312 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 1316.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 0 | 138 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 495 | 1120 | 0 | 6125.77 | 12655.77 | 107.99
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 194 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 250 | 0 | 0 | 240 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 17 | 280 | 0 | 0 | 39 | 0 | 0 | 121 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 0 | 350 | 280 | 224 | 0 | 195 | 0 | 69 | 97 | 34 | 0 | 18 | 40 | 44 | 0 | 0 | 37 | 310 | 0 | 380 | 30 | 57 | 155 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 77 | 55 | 101 | 0 | 0 | 6 | 6461 | 834 | 312 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 1314.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 195 | 0 | 0 | 0 | 347 | 0 | 0 | 138 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 408 | 1096 | 0 | 5946.22 | 12407.22 | 107.98
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 194 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 245 | 0 | 0 | 240 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 17 | 280 | 0 | 0 | 24 | 0 | 0 | 121 | 0 | 0 | 0 | 1080 | 0 | 51 | 0 | 0 | 350 | 310 | 224 | 0 | 195 | 0 | 54 | 97 | 31 | 0 | 18 | 29 | 42 | 0 | 0 | 15 | 305 | 0 | 378 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 166 | 0 | 78 | 55 | 101 | 0 | 0 | 6 | 6290 | 833 | 309 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1320.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 191 | 0 | 0 | 0 | 345 | 0 | 0 | 138 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 115 | 220 | 0 | 408 | 1090 | 0 | 5837.65 | 12127.65 | 107.97
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 220 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 145 | 240 | 0 | 0 | 240 | 0 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.05 | 220 | 0 | 17 | 280 | 0 | 0 | 19 | 0 | 0 | 121 | 0 | 0 | 0 | 985 | 1 | 51 | 0 | 0 | 300 | 310 | 260 | 0 | 192 | 0 | 34 | 97 | 17 | 0 | 18 | 0 | 38 | 0 | 0 | 0 | 305 | 0 | 365 | 30 | 57 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 55 | 101 | 0 | 0.01 | 6 | 6077.06 | 833 | 309 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1118.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 192 | 0 | 0 | 0 | 342 | 0 | 0 | 138 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 115 | 220 | 0 | 360 | 1090 | 0 | 5535.36 | 11612.42 | 107.96
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 220 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 120 | 255 | 0 | 0 | 240 | 0 | 0 | 3 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.62 | 220 | 0 | 7 | 280 | 0 | 0 | 19 | 0 | 0 | 121 | 0 | 0 | 0 | 1000 | 7 | 51 | 0 | 0 | 230 | 354 | 280 | 0 | 199 | 0 | 16 | 97 | 0 | 0 | 18 | 0 | 38 | 0 | 1 | 0 | 310 | 0 | 389 | 30 | 57 | 156 | 0 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 78 | 62 | 101 | 0 | 5.64 | 6 | 6058.26 | 832 | 303 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.01 | 375 | 0 | 1023.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 14 | 0 | 0 | 3.52 | 194 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0.29 | 137 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.07 | 0 | 171 | 115 | 220 | 0 | 360 | 1050 | 0 | 5518.39 | 11576.65 | 107.95
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 100 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 120 | 250 | 0 | 0 | 240 | 0 | 0 | 3 | 90 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 220 | 0 | 2 | 280 | 0 | 0 | 19 | 0 | 0 | 121 | 0 | 0 | 0 | 1050 | 5 | 51 | 0 | 0 | 230 | 320 | 280 | 0 | 190 | 0 | 16 | 97 | 0 | 0 | 20 | 0 | 36 | 0 | 9 | 0 | 310 | 0 | 384 | 30 | 57 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 78 | 95 | 70 | 0 | 14.84 | 6 | 6005.51 | 832 | 303 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.16 | 376 | 0 | 1026.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 31 | 0 | 0 | 5.22 | 196 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 0.68 | 140 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0.19 | 0 | 247 | 115 | 220 | 0 | 348 | 1050 | 0 | 5615.51 | 11621.02 | 107.94
09:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 5 | 46 | 0 | 300 | 120 | 280 | 0 | 0 | 334 | 0 | 0 | 16 | 90 | 27.1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 220 | 0 | 2 | 280 | 0 | 0 | 32 | 0 | 0 | 121 | 0 | 0 | 0 | 1136 | 11 | 51 | 0 | 0 | 270 | 280 | 280 | 0 | 188 | 0 | 23 | 96 | 0 | 0 | 17 | 0 | 34 | 0 | 20 | 0 | 310 | 0 | 336 | 30 | 57 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 166 | 0 | 78 | 95 | 69 | 0 | 19.78 | 6 | 6195.2 | 833 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31.64 | 375 | 0 | 921.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.52 | 28 | 0 | 0 | 5.78 | 190 | 0 | 190 | 0 | 0 | 0 | 341 | 0 | 0.46 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 21 | 0.28 | 0 | 196 | 115 | 220 | 0 | 350 | 1115 | 0 | 5478.04 | 11673.24 | 107.93
10:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 50 | 0 | 300 | 120 | 305 | 0 | 0 | 331 | 0 | 0 | 10 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.05 | 220 | 0 | 2 | 282 | 0 | 0 | 47 | 0 | 0 | 136 | 0 | 0 | 0 | 1160 | 10 | 51 | 0 | 0 | 240 | 280 | 260 | 0 | 194 | 0 | 34 | 94 | 0 | 0 | 17 | 0 | 36 | 0 | 22 | 0 | 315 | 0 | 335 | 30 | 57 | 146 | 12 | 0 | 81 | 30 | 0 | 16 | 166 | 0 | 77 | 45 | 68 | 1 | 23.75 | 3 | 6223.8 | 833 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 379 | 0 | 819.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.48 | 20 | 0 | 0 | 7.6 | 176 | 0 | 160 | 0 | 0 | 0 | 365 | 0 | 1.05 | 141 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 1 | 0.7 | 0 | 170 | 115 | 220 | 0 | 348 | 1180 | 0 | 5437.94 | 11661.74 | 107.92
11:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 15.8 | 0 | 55 | 10 | 73 | 0 | 35 | 78 | 0 | 300 | 145 | 359 | 0 | 30 | 260 | 0 | 0 | 13 | 90 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3.82 | 220 | 0 | 2 | 280 | 10 | 0 | 46 | 0 | 11 | 82 | 0 | 0 | 0 | 1130 | 10 | 51 | 5 | 0 | 200 | 280 | 240 | 0 | 202 | 0 | 34 | 93 | 41 | 0 | 20 | 34 | 32 | 0 | 15 | 0 | 310 | 0 | 364 | 30 | 57 | 157 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 24 | 68 | 1 | 7.91 | 6 | 6422.53 | 833 | 281 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 93 | 381 | 0 | 819.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 87 | 0 | 0 | 40.41 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 3.54 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0.12 | 0 | 171 | 115 | 220 | 0 | 350 | 1178 | 0 | 5440.64 | 11863.17 | 107.91
12:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35.9 | 0 | 113 | 30 | 145 | 20 | 35 | 90 | 0 | 300 | 142 | 357 | 0 | 55 | 321 | 0 | 0 | 13 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 7 | 0 | 2 | 0 | 0 | 0 | 3.19 | 220 | 0 | 7 | 282 | 17 | 0 | 49 | 0 | 86 | 83 | 0 | 0 | 0 | 1192 | 13 | 51 | 66 | 0 | 195 | 280 | 230 | 0 | 200 | 0 | 34 | 93 | 133 | 0 | 20 | 62 | 32 | 0 | 9 | 0 | 305 | 0 | 386 | 30 | 57 | 148 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 8 | 62 | 1 | 15.53 | 6 | 7029.62 | 833 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 89 | 380 | 0 | 820.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.72 | 50 | 0 | 0 | 31.66 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 2.25 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0.48 | 0 | 170 | 115 | 220 | 0 | 352 | 1200 | 0 | 5437.98 | 12467.6 | 107.9
13:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35.6 | 10 | 113 | 47 | 125 | 45 | 35 | 90 | 0 | 300 | 149 | 330 | 0 | 55 | 328 | 0 | 0 | 16 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 1.3 | 219 | 18 | 16 | 281 | 107 | 0 | 50 | 7 | 105 | 85 | 0 | 0 | 0 | 1168 | 16 | 51 | 88 | 0 | 165 | 280 | 230 | 0 | 179 | 0 | 34 | 93 | 163 | 9 | 20 | 68 | 38 | 11 | 27 | 0 | 315 | 0 | 388 | 30 | 57 | 158 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 76 | 8 | 61 | 1 | 3.76 | 6 | 7343.66 | 833 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 378 | 0 | 825.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.13 | 37 | 0 | 0 | 13.05 | 160 | 0 | 203 | 0 | 0 | 0 | 414 | 0 | 1.02 | 147 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0.44 | 0 | 224 | 115 | 220 | 0 | 351 | 1220 | 0 | 5545.78 | 12889.44 | 107.89
14:00 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35.9 | 17 | 113 | 60 | 258 | 55 | 35 | 90 | 0 | 300 | 142 | 303 | 0 | 35 | 330 | 0 | 0 | 24 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 98 | 0 | 9 | 0 | 23 | 0 | 0 | 0 | 1.37 | 218 | 31 | 13 | 280 | 138 | 0 | 50 | 17 | 96 | 142 | 0 | 0 | 0 | 1145 | 15 | 51 | 105 | 0 | 165 | 155 | 230 | 0 | 190 | 0 | 34 | 94 | 180 | 9 | 17 | 59 | 38 | 34 | 54 | 24 | 305 | 0 | 362 | 30 | 57 | 155 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 77 | 8 | 60 | 1 | 9.62 | 3 | 7483.89 | 833 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 378 | 0 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.37 | 8 | 0 | 0 | 7.06 | 197 | 0 | 198 | 0 | 0 | 0 | 402 | 0 | 0.76 | 148 | 47 | 0 | 4 | 0 | 0 | 0 | 0 | 0.5 | 5 | 0.32 | 0 | 271 | 115 | 180 | 0 | 301 | 1220 | 0 | 5553.01 | 13036.9 | 107.88
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 36.2 | 17 | 113 | 45 | 245 | 55 | 35 | 90 | 0 | 300 | 140 | 300 | 0 | 35 | 330 | 0 | 0 | 9 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 98 | 0 | 9 | 0 | 23 | 0 | 0 | 0 | 1.94 | 220 | 29 | 6 | 280 | 132 | 0 | 50 | 17 | 95 | 211 | 0 | 0 | 0 | 1132 | 13 | 51 | 98 | 0 | 280 | 0 | 230 | 0 | 188 | 0 | 34 | 96 | 170 | 9 | 17 | 33 | 38 | 43 | 42 | 28 | 305 | 0 | 361 | 30 | 57 | 153 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 77 | 8 | 60 | 0 | 10.86 | 5 | 7359 | 833 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 370 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.39 | 0 | 0 | 0 | 13.82 | 180 | 0 | 180 | 0 | 0 | 0 | 332 | 0 | 1.34 | 145 | 47 | 0 | 8 | 0 | 0 | 0 | 0 | 1.1 | 37 | 0.45 | 0 | 265 | 100 | 180 | 0 | 302 | 1232 | 0 | 5408.1 | 12767.1 | 107.87
16:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35.8 | 17 | 100 | 30 | 195 | 30 | 39 | 90 | 0 | 300 | 143 | 298 | 0 | 35 | 333 | 0 | 0 | 7 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 92 | 0 | 18 | 16 | 23 | 0 | 0 | 0 | 1.16 | 221 | 15 | 10 | 278 | 60 | 0 | 50 | 17 | 66 | 211 | 0 | 0 | 0 | 1140 | 4 | 51 | 40 | 0 | 360 | 0 | 230 | 0 | 189 | 0 | 37 | 96 | 136 | 9 | 20 | 27 | 30 | 16 | 8 | 28 | 305 | 0 | 361 | 30 | 57 | 143 | 12 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 77 | 8 | 61 | 0 | 3.54 | 6 | 7024.5 | 833 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 370 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.21 | 180 | 0 | 150 | 0 | 0 | 0 | 341 | 0 | 0.12 | 147 | 47 | 0 | 4 | 0 | 0 | 0 | 0 | 1.1 | 10 | 0.08 | 16 | 272 | 100 | 180 | 0 | 301 | 1120 | 0 | 5255.71 | 12280.21 | 107.86
17:00 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35.8 | 21 | 87 | 30 | 195 | 30 | 55 | 90 | 0 | 300 | 143 | 301 | 0 | 35 | 300 | 0 | 0 | 1 | 52 | 27 | 22 | 0 | 0 | 6 | 15 | 92 | 0 | 15 | 16 | 23 | 0 | 0 | 0 | 0.09 | 222 | 14 | 13 | 278 | 60 | 0 | 50 | 17 | 65 | 211 | 0 | 0 | 0 | 1028 | 1 | 51 | 40 | 0 | 410 | 0 | 230 | 0 | 189 | 0 | 50 | 97 | 126 | 9 | 17 | 32 | 30 | 16 | 1 | 28 | 310 | 0 | 362 | 30 | 57 | 143 | 12 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 15 | 63 | 0 | 0 | 6 | 6973.89 | 832 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.98 | 370 | 0 | 1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 337 | 0 | 0 | 145 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 0.3 | 16 | 221 | 100 | 180 | 0 | 301 | 1055 | 0 | 5211.28 | 12185.17 | 107.86
18:00 | 0 | 76 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 35.6 | 35 | 88 | 30 | 225 | 30 | 36 | 90 | 0 | 300 | 148 | 297 | 0 | 55 | 300 | 0 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 13 | 20 | 96 | 0 | 18 | 41 | 44 | 0 | 0 | 0 | 0 | 222 | 31 | 13 | 280 | 140 | 0 | 50 | 17 | 66 | 211 | 0 | 0 | 0 | 1120 | 0 | 51 | 48 | 0 | 410 | 0 | 280 | 0 | 193 | 0 | 51 | 104 | 126 | 0 | 19 | 48 | 36 | 16 | 0 | 28 | 300 | 0 | 366 | 30 | 57 | 140 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 65 | 63 | 0 | 0 | 5 | 7451.6 | 833 | 202 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 344 | 0 | 0 | 148 | 47 | 35 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 274 | 115 | 220 | 0 | 300 | 1050 | 11 | 5705 | 13156.6 | 107.86
19:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35.8 | 35 | 98 | 0 | 175 | 30 | 35 | 90 | 0 | 300 | 148 | 330 | 0 | 35 | 300 | 0 | 0 | 0 | 70 | 0 | 22 | 0 | 0 | 25 | 30 | 105 | 0 | 6 | 66 | 50 | 0 | 0 | 0 | 0 | 222 | 63 | 19 | 280 | 60 | 0 | 50 | 17 | 68 | 211 | 0 | 0 | 0 | 1124 | 0 | 51 | 90 | 0 | 340 | 0 | 300 | 0 | 192 | 0 | 69 | 104 | 155 | 0 | 19 | 14 | 36 | 8 | 0 | 28 | 300 | 0 | 347 | 30 | 57 | 139 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 63 | 0 | 0 | 5 | 7212.8 | 833 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 340 | 0 | 0 | 144 | 48 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 243 | 100 | 180 | 0 | 300 | 1095 | 17 | 5617 | 12829.8 | 107.86
19:30 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 36 | 35 | 34 | 0 | 145 | 30 | 35 | 90 | 0 | 300 | 155 | 380 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 10 | 22 | 0 | 0 | 15 | 0 | 90 | 0 | 2 | 66 | 50 | 0 | 0 | 0 | 0 | 222 | 51 | 17 | 280 | 34 | 0 | 36 | 17 | 63 | 211 | 0 | 0 | 0 | 1165 | 0 | 51 | 50 | 0 | 350 | 0 | 300 | 0 | 202 | 0 | 69 | 105 | 97 | 0 | 19 | 16 | 36 | 8 | 0 | 29 | 310 | 0 | 383 | 30 | 57 | 147 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 65 | 0 | 0 | 6 | 7093 | 833 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 365 | 0 | 0 | 147 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 247 | 100 | 180 | 0 | 300 | 1105 | 17 | 5712 | 12805
20:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35.8 | 35 | 36 | 0 | 145 | 30 | 35 | 90 | 0 | 300 | 154 | 392 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 0 | 15 | 0 | 80 | 0 | 4 | 66 | 52 | 0 | 0 | 0 | 0 | 222 | 33 | 20 | 280 | 34 | 0 | 33 | 17 | 64 | 211 | 0 | 0 | 0 | 1162 | 0 | 51 | 50 | 13 | 355 | 0 | 310 | 0 | 200 | 0 | 69 | 105 | 100 | 0 | 19 | 15 | 38 | 8 | 0 | 29 | 305 | 0 | 388 | 30 | 57 | 156 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 66 | 0 | 0 | 6 | 7127.8 | 833 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 375 | 0 | 0 | 142 | 48 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 248 | 100 | 180 | 0 | 299 | 1110 | 17 | 5760 | 12887.8 | 107.86
21:00 | 0 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 36.3 | 35 | 34 | 0 | 145 | 30 | 35 | 72 | 0 | 300 | 148 | 385 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 0 | 15 | 0 | 71 | 0 | 0 | 66 | 52 | 0 | 0 | 0 | 0 | 222 | 32 | 21 | 280 | 32 | 0 | 33 | 17 | 64 | 207 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 38 | 340 | 0 | 330 | 0 | 200 | 0 | 64 | 105 | 96 | 0 | 20 | 15 | 36 | 8 | 0 | 29 | 305 | 0 | 387 | 30 | 57 | 157 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 66 | 0 | 0 | 6 | 7096.8 | 834 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1369.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 360 | 0 | 0 | 145 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 248 | 115 | 220 | 0 | 300 | 1110 | 17 | 5741.59 | 12838.39 | 107.86
22:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 36 | 19 | 34 | 0 | 145 | 30 | 35 | 72 | 0 | 300 | 150 | 390 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 0 | 15 | 0 | 72 | 0 | 0 | 66 | 52 | 0 | 0 | 0 | 0 | 222 | 33 | 26 | 280 | 33 | 0 | 33 | 17 | 67 | 207 | 0 | 0 | 0 | 1180 | 0 | 51 | 50 | 35 | 364 | 0 | 330 | 0 | 207 | 0 | 34 | 105 | 100 | 0 | 20 | 15 | 40 | 8 | 0 | 0 | 310 | 0 | 398 | 30 | 57 | 161 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 66 | 0 | 0 | 6 | 7137.5 | 833 | 173 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1327.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 185 | 0 | 0 | 0 | 360 | 0 | 0 | 145 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 115 | 220 | 0 | 300 | 1126 | 17 | 5798.54 | 12936.04 | 107.85
23:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 18 | 17 | 34 | 0 | 145 | 30 | 35 | 72 | 0 | 300 | 153 | 395 | 0 | 17 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 0 | 16 | 0 | 70 | 0 | 1 | 66 | 52 | 0 | 0 | 0 | 0 | 221 | 34 | 28 | 280 | 34 | 0 | 33 | 17 | 68 | 192 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 35 | 421 | 0 | 330 | 0 | 200 | 0 | 34 | 105 | 100 | 0 | 20 | 16 | 42 | 8 | 0 | 0 | 310 | 0 | 399 | 30 | 57 | 161 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 55 | 25 | 66 | 0 | 0 | 6 | 7147.5 | 833 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 1325.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 170 | 0 | 0 | 0 | 347 | 0 | 0 | 145 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 115 | 220 | 0 | 302 | 1224 | 17 | 5850.05 | 12997.55 | 107.85
Total KWH | 0 | 1393920 | 360000 | 0 | 0 | 0 | 0 | 0 | 8481600 | 0 | 1707180 | 521280 | 292680 | 1413936 | 295680 | 2465433 | 496294 | 531349 | 1591200 | 0 | 7450500 | 3420393 | 7058336 | 0 | 435154 | 7001830 | 0 | 0 | 123570 | 2167200 | 523200 | 524520 | 0 | 0 | 135491 | 70255 | 1162560 | 0 | 182400 | 673913 | 389712 | 0 | 0 | 0 | 20863 | 5279611 | 430700 | 304800 | 6778181.82 | 824655 | 0 | 481440 | 201238.2 | 1093964 | 3869119 | 0 | 0 | 0 | 27070906 | 116910 | 1241660 | 923345 | 133818 | 7523000 | 4299800 | 6313800 | 0 | 4772000 | 0 | 1121280 | 2361200 | 2004960 | 47040 | 416210 | 746700 | 908160 | 207437 | 222473 | 379760 | 7512500 | 0 | 9352000 | 716000 | 1342200 | 3682718 | 184056 | 0 | 1920960 | 713760 | 0 | 392000 | 3404930 | 28800 | 1747200 | 1015200 | 1741440 | 5350 | 128410 | 139680 | 164991821.02 | 20167272 | 6298560 | 0 | 3360 | 12928 | 912000 | 0 | 0 | 0 | 0 | 0 | 560160 | 9592725 | 0 | 26918182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197218 | 298990 | 0 | 0 | 152256 | 4536036 | 0 | 4411036 | 0 | 0 | 0 | 8945745 | 0 | 13200 | 3511000 | 1104000 | 298582 | 18579 | 293865 | 0 | 0 | 0 | 10883.4 | 89180 | 3571 | 159456 | 5869000 | 2667000 | 5343610 | 0 | 8661818.18 | 27902545.45 | 118800 | 139071558.03 | 304063379.05

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-10-2025 | during | 06-10-2025 | during | 06-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 355 | 338 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 148 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 20 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35.9 | 35.6 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 36 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 27 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 225 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 88 | 149 | 149 | 115 | 115 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 76 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 90 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 357 | 297 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2253.9 | 2256.6 | 5834.4 | 5804.4 | 3131.56 | 3159.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 49 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 222 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 83 | 211 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 86 | 66 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 44 | 56 | 70 | 56 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 41 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 13 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 96 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.19 | 0 | 3.77 | 0 | 3.77 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 20 | 300 | 300 | 16 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 31 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 13 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 140 | 159.86 | 159.86 | 159.86 | 159.86 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1192 | 1120 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 18 | 2 | 1 | 2 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 282 | 280 | 280 | 280 | 280 | 280 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1971.19 | 2382 | 3035.49 | 3054.72 | 2480.99 | 2584.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 230 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 195 | 410 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 47 | 47 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 5 | 5 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 66 | 48 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 104 | 163 | 163 | 97 | 97 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 133 | 126 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 36 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 62 | 48 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 51 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 9 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1405 | 1410 | 2668.86 | 2603.86 | 2337.16 | 2281.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-10-2025 | during | 06-10-2025 | during | 06-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 62 | 63 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 65 | 150 | 150 | 150 | 150 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.53 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 5 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 169.53 | 210 | 512.2 | 461 | 458.7 | 407.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 60 | 60 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 140 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 8 | 25 | 25 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 366 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1230 | 1193 | 1295 | 1295 | 1203 | 1203
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 833 | 833 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 60 | 60 | 60 | 60 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 272 | 202 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 380 | 374 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1612 | 1467 | 2748 | 2658 | 1987 | 1897
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 352 | 300 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1050 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 11 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 274 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2057.48 | 2018 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 33.72 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 160 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 150 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 344 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.25 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 820.47 | 1292 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 31.66 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 50 | 0 | 80 | 0 | 80 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1578.1 | 1946 | 3165.47 | 3020.87 | 3047.81 | 2903.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 47 | 48 | 48 | 48 | 48 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 140 | 148 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 44 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 0 | 0 | 134.35 | 0 | 134.35 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 190.4 | 274 | 611.35 | 446 | 611.35 | 446
System Total |  |  |  |  | 28823.2 | 28365.955 | 12467.6 | 13156.6 | 22017.77 | 21489.85 | 17221.57 | 16844.65
Forecast Scenario (06-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12900 |  | 0 |  | 12900
|  |  |  | 1:00 | 12540 |  | 0 |  | 12540
|  |  |  | 2:00 | 12270 |  | 0 |  | 12270
|  |  |  | 3:00 | 11950 |  | 0 |  | 11950
|  |  |  | 4:00 | 11750 |  | 0 |  | 11750
|  |  |  | 5:00 | 11530 |  | 0 |  | 11530
|  |  |  | 6:00 | 11280 |  | 0 |  | 11280
|  |  |  | 7:00 | 11350 |  | 0 |  | 11350
|  |  |  | 8:00 | 11270 |  | 0 |  | 11270
|  |  |  | 9:00 | 11620 |  | 0 |  | 11620
|  |  |  | 10:00 | 12110 |  | 0 |  | 12110
|  |  |  | 11:00 | 12500 |  | 0 |  | 12500
|  |  |  | 12:00 | 13000 |  | 0 |  | 13000
|  |  |  | 13:00 | 13410 |  | 0 |  | 13410
|  |  |  | 14:00 | 13480 |  | 0 |  | 13480
|  |  |  | 15:00 | 13510 |  | 0 |  | 13510
|  |  |  | 16:00 | 13390 |  | 0 |  | 13390
|  |  |  | 17:00 | 13110 |  | 0 |  | 13110
|  |  |  | 18:00 | 14010 |  | 0 |  | 14010
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 14600 |  | 0 |  | 14600
|  |  |  | 19:30 | 15040 |  | 0 |  | 15040
|  |  |  | 20:00 | 15230 |  | 0 |  | 15230
|  |  |  | 21:00 | 15270 |  | 0 |  | 15270
|  |  |  | 22:00 | 15400 |  | 0 |  | 15400
|  |  |  | 23:00 | 15300 |  | 0 |  | 15300
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 13000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15270.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15270.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.78 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 10:55 hrs on 06-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12467.6 | MW | 12:00 Hr. | Energy Generated |  |  | 304.0634 |  | MKWHr.
| Day Peak Demand |  |  | 12467.6 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13156.6 | MW | 18:00 Hr. | Energy Demand |  |  | 304.0634 |  | MKWHr.
| Evening Peak Demand |  |  | 13156.6 | MW | 18:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 11576.65 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 938.32 |  | MMCFD
| Maximum Generation of the Day |  |  | 13994.51 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.8834 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.1676 | 0 | 11.9641 | 0 | 0 | 0.12357 | 0 | 0 | 48.2553 | Gas | 130.5675 | Gas | 463456460.07
| Chattogram Zone |  |  | 4.1739 | 33.8491 | 5.4639 | 0 | 5.2796 | 0.13777 | 0 | 0.1824 | 49.0867 | Coal | 90.4902 | Coal | 516745452.2429
| Cumilla Zone |  |  | 27.0615 | 0 | 5.4305 | 0 | 0 | 0.22247 | 0.90816 | 0 | 33.6226 | HFO | 26.6764 | HFO | 491355331.766
| Mymensingh Zone |  |  | 1.7414 | 0 | 2.9309 | 0 | 0 | 0.13376 | 0 | 0 | 4.8061 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2211 | Hydro | 5.2796 | Hydro | 527961.1
| Khulna Zone |  |  | 6.2986 | 9.5927 | 0.016288 | 0 | 0 | 0.56016 | 21.0793 | 0 | 37.547 | Solar | 1.9616 | Solar | 27839033.644
| Barishal Zone |  |  | 8.0106 | 42.4334 | 0.27826 | 0 | 0 | 0.003571 | 0 | 0 | 50.7258 | Import | 48.9056 | Import | 286323297.98
| Rajshahi Zone |  |  | 17.8928 | 0 | 0 | 0 | 0 | 0.66166 | 26.9182 | 0 | 45.4727 | Wind | 0.1824 | Wind | 2688576
| Rangpur Zone |  |  | 0 | 4.615 | 0.59245 | 0 | 0 | 0.11864 | 0 | 0 | 5.3261
| Total |  |  | 130.5675 | 90.4902 | 26.6764 | 0 | 5.2796 | 1.9616 | 48.9056 | 0.1824 | 304.0634
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 463456460.07 |  | Hydro | 527961.1
|  |  |  | Coal | 516745452.2429 |  | Solar | 27839033.644
|  |  |  | HFO | 491355331.766 |  | Import | 286323297.98
|  |  |  | HSD | 0 |  | Wind | 2688576
[5 empty] | Total: | 178,89,36,112 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1673 | Peak Hr Flow | 833.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 19372581.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.9182 | Peak Hr Flow | 1292.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1954 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.90816 | Peak Hr Flow | 36.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2585 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.9936 | Peak Hr Flow | 2161.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5263
|  |  |  | Chattogram |  | 0 |  | 1409
|  |  |  | Cumilla |  | 0 |  | 1341
|  |  |  | Mymensingh |  | 0 |  | 735
|  |  |  | Sylhet |  | 0 |  | 593
|  |  |  | Khulna |  | 0 |  | 1404
|  |  |  | Barishal |  | 0 |  | 446
|  |  |  | Rajshahi |  | 0 |  | 1055
|  |  |  | Rangpur |  | 0 |  | 706
|  |  |  | Total |  | 0 |  | 12952
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 08:50 | Jaldhaka-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance Relay,
B-phase, Zone-2 relays Due to Distance Relay, B-phase, Zone-2
|  | 08:19 | Kalurghat 132/33kV S/S TRFO-01(506T) LT is restored.
| 08:24 | 17:16 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D
| 08:33 | 08:55 | Bagerhat-Mongla 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance R
Phase Zone 2/3 relays Due to Unknown
| 08:40 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT11 was shutdown
| 08:43 | 17:20 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Annual Maintenance(Schedule
Shutdown)
| 09:04 | 16:25 | Bogura-Sirajganj 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to annual shutdown
| 09:40 | 17:01 | Jaldhaka 132/33kV S/S 416T-2 HT Scheduled S/D Due to Annual maintenance
| 09:41 | 17:03 | Jaldhaka 132/33kV S/S 416T-2 LT Scheduled S/D Due to Annual maintenance
| 10:24 | 10:42 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Rangpur 132/33kV end showing QUADRAMHO | [7 empty] | 10.0MW load
|  |  | SHPM 101 relays Due to Due to heavy rain thundering and lightning. | [7 empty] | interrup. Rangpur
132/33kV end
| 11:24 | 17:44 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D Due to PRD Maintenance
| 11:24 | 17:44 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D Due to PRD maintenance
| 11:51 | 13:58 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Red hot 33KV bus, PBS side | [7 empty] | 10.0MW load
interrup.
| 11:51 | 13:59 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Red hot 33KV bus, PBS side | [7 empty] | 10.0MW load
interrup.
| 12:04 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Bhandaria
Line trip fault check.
|  | 12:17 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 13:30 |  | Shikalbaha 225 MW CCPP ST was sync.
| 14:29 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 15:04 | 16:57 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Red hot
| 15:04 | 16:57 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Red Hot | [7 empty] | 12.0MW load
interrup.
| 16:43 | 17:58 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to Red hot maintenance of PBS | [7 empty] | 10.0MW load
|  |  | Bamna | [7 empty] | interrup.
|  | 16:43 | Chandraghona-Madunaghat 132 kV Ckt-1 is restored.
| 16:44 | 17:57 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Red hot maintenance for PBS | [7 empty] | 10.0MW load
interrup.
|  | 17:33 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
|  | 17:37 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
| 17:38 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
|  | 17:44 | Rahanpur 400/132kV S/S AT-02 HT is restored.
|  | 17:44 | Rahanpur 400/132kV S/S AT-02 LT is restored.
| 18:00 |  | Evening peak Generation is 13156 MW
| 19:48 | 20:04 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing Zone-1 trip,R-
Phase, auto reclose blocking relays.
|  | 22:56 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
| 06:00 |  | Minimum Generation is 10959 MW.
| 06:46 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Scheduled S/D Due to Earthwire change &
OPGW installation work
| 07:47 |  | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
Annual maintenance and from Chandraghona 132/33kV end Due to Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 338 | 8481600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7450500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3420393 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 496294 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7001830 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.6 | 521280 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 295680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 36 | 531349 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 435154 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27 | 523200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 524520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 360000 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 225 | 2465433 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 1413936 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 76 | 1393920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1591200 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 123570 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 292680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 297 | 7058336 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 1707180 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 2167200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2256.6 | 48255255
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 201238.2 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 116910 | 33kV grid Low Voltage & Low Irradiation
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 481440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5279611 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 211 | 3869119 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 66 | 1093964 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 44 | 389712 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 41 | 673913 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 304800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 1162560 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20863 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 20 | 70255 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 31 | 430700 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 135491 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 140 | 824655 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1120 | 27070906 | Coal shortage due to non-payment from BPDB
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 18 | 182400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 280 | 6778181.82 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2382 | 49086719.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 4772000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 4299800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 6313800 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 410 | 7523000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 133818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1241660 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 48 | 923345 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 379760 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2361200 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 126 | 2004960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 36 | 908160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 207437 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 416210 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 48 | 746700 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 47040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 1121280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 222473 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1410 | 33622643
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 63 | 1741440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 1015200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1747200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 128410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 5 | 139680 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 28800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 210 | 4806080
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1342200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3682718 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713760 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1920960 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3404930 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 184056 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7512500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 9352000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1193 | 29221124
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 833 | 20167272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 3360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 12928 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 202 | 6298560 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 560160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 374 | 9592725 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1467 | 37547005
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 300 | 8661818.18 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 159456 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2667000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 27902545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5343610 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 11 | 118800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5869000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3571 | -
Barishal Area Total |  |  |  |  | 2858 | 2018 | 50725800.63
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 197218 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4536036 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 150 | 4411036 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 344 | 8945745 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13200 | Low irradiation
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1292 | 26918182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 152256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 298990 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1946 | 45472663
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1104000 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 148 | 3511000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 44 | 293865 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 10883.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 298582 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 18579 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 89180 | -
Rangpur Area Total |  |  |  |  | 950 | 274 | 5326089.4
Eastern Grid Total |  |  |  |  | 17385.715 | 7451.6 | 164991821.02
Western Grid Total |  |  |  |  | 10980.24 | 5705 | 139071558.03
National Grid Total |  |  |  |  | 28365.955 | 13156.6 | 304063379.05
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-10-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9341.01 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3611.5 | MW
i) Dhaka area |  |  | 5262.86 |  | MW | i) Khulna area |  |  |  | 1404 | MW
ii) Chattogram area |  |  | 1408.7 |  | MW | ii) Barishal area |  |  |  | 446.5 | MW
iii) Cumilla area |  |  | 1341.45 |  | MW | iii) Rajshahi area |  |  |  | 1055 | MW
iv) Mymensingh area |  |  | 735 |  | MW | iv) Rangpur area |  |  |  | 706 | MW
v) Sylhet area |  |  | 593 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12952.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 01:00 | 67 | Hathazari | 84 | 20:00 | 133 | PHP | 2 | 03:00
2 | AKSML | 128 | 07:00 | 68 | Ishurdi | 67 | 13:00 | 134 | Pabna | 86 | 18:30
3 | Aftabnagar | 38 | 12:00 | 69 | Jaldhaka | 53 | 18:00 | 135 | Palashbari | 100 | 00:00
4 | Agargaon | 133 | 14:00 | 70 | Jamalpur | 108 | 00:00 | 136 | Panchagarh | 39 | 18:30
5 | Agrabad | 90 | 18:00 | 71 | Jashore | 130 | 18:30 | 137 | Patiya | 11 | 19:00
6 | Amnura | 23 | 00:00 | 72 | Jhenaidah | 115 | 00:00 | 138 | Patuakhali | 66.5 | 21:00
7 | Ashuganj | 75 | 01:00 | 73 | Joydebpur | 151 | 18:00 | 139 | Payra | 32 | 00:00
8 | BSRM | 113 | 10:00 | 74 | Joypurhat | 50 | 21:00 | 140 | Postogola | 64 | 13:00
9 | Bagerhat | 80 | 18:00 | 75 | Juldah | 21.5 | 12:00 | 141 | Purbachal | 20 | 14:00
10 | Bajitpur | 96 | 18:30 | 76 | KSRM | 9 | 02:00 | 142 | Purbasadipur | 90 | 18:30
11 | Bakulia | 97 | 18:00 | 77 | Kabirpur | 270 | 09:00 | 143 | Rahanpur | 30 | 21:00
12 | Banani | 52.6 | 13:00 | 78 | Kachua | 88 | 21:00 | 144 | Rahim | 26 | 12:00
13 | Bangabhaban | 24 | 10:00 | 79 | Kallyanpur | 99 | 00:00 | 145 | Rajbari | 70 | 00:00
14 | Barapukuria | 53 | 18:30 | 80 | Kalurghat | 40 | 15:00 | 146 | Rajendrapur | 132 | 18:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi | 90 | 00:00
16 | Barishal | 115 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 85 | 13:00
17 | Barishal-230 | 100 | 22:00 | 83 | Kasba | 37 | 21:00 | 149 | Ramganj | 112 | 00:00
18 | Baroaulia | 60 | 18:00 | 84 | Kazla | 91 | 01:00 | 150 | Rampur | 42 | 18:00
19 | Baroirhat | 61 | 18:00 | 85 | Keranigonj | 96 | 18:00 | 151 | Rangamati | 18 | 18:30
20 | Bashundhara | 201 | 13:00 | 86 | Khagrachori | 28 | 19:00 | 152 | Rangpur | 114 | 00:00
21 | BashundharaCement | 9 | 20:00 | 87 | Khulna | 70 | 13:00 | 153 | Ruppur | 7.2 | 11:00
22 | Beanibazar | 74 | 19:30 | 88 | Khulshi | 200 | 16:00 | 154 | SSM | 0 | 00:00
23 | Benapole | 53 | 00:00 | 89 | Kishoreganj | 128 | 19:00 | 155 | Saidpur | 86 | 18:30
24 | Bhaluka | 134 | 00:00 | 90 | Kodda | 303 | 12:00 | 156 | Satkhira | 119 | 00:00
25 | Bhandaria | 54 | 00:00 | 91 | Kulaura | 51 | 18:00 | 157 | Satmasjid | 99 | 13:00
26 | Bhangura | 31 | 00:00 | 92 | Kurigram | 50 | 07:00 | 158 | Savar | 220 | 15:00
27 | Bheramara(GK) | 59 | 00:00 | 93 | Kushtia | 138 | 18:30 | 159 | SevenRings | 15.25 | 01:00
28 | Bhulta | 216 | 19:00 | 94 | Laksam | 32 | 00:00 | 160 | ShahCement | 26 | 01:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Lakshmipur | 32 | 00:00 | 161 | Shahjadpur | 70 | 00:00
30 | Bogura | 141 | 19:00 | 96 | Lalbag | 60 | 13:00 | 162 | Shahjibazar | 128 | 21:00
31 | Borhanuddin | 94 | 20:00 | 97 | Lalmonirhat | 42 | 00:00 | 163 | Shahmirpur | 59 | 00:00
32 | Brahmanbaria | 127 | 20:00 | 98 | MI_Cement | 18.5 | 02:00 | 164 | Shariatpur | 89 | 21:00
33 | Cantonment | 136 | 14:00 | 99 | Madanganj | 32 | 18:00 | 165 | Sherpur | 136 | 00:00
34 | Chandina | 13.34 | 01:00 | 100 | Madaripur | 109 | 22:00 | 166 | Shikalbaha | 24 | 18:00
35 | Chandpur | 90 | 01:00 | 101 | Madartek | 84.79 | 18:30 | 167 | Shitalakhya | 85.1 | 12:00
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 56 | 13:00 | 168 | Sholosohor | 50 | 18:00
37 | Chapai | 54 | 12:00 | 103 | Magura | 56 | 00:00 | 169 | Shyampur | 100 | 17:00
38 | Charsaidpur | 26 | 21:00 | 104 | Mahasthangarh | 68 | 00:00 | 170 | Siddhirganj | 123 | 15:00
39 | Chauddagram | 69 | 01:00 | 105 | Maijdee | 22 | 01:00 | 171 | Sirajganj | 89 | 00:00
40 | Chhatak | 38 | 00:00 | 106 | Manikganj | 114 | 00:00 | 172 | Sonargaon | 133 | 18:00
41 | Chowmuhani | 176 | 00:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sreemongol | 80 | 18:00
42 | Chuadanga | 103 | 00:00 | 108 | Matarbari | 52 | 18:30 | 174 | Sreepur | 121 | 18:00
43 | Coxsbazar | 139 | 18:30 | 109 | Matuail | 68 | 12:00 | 175 | Srinagar | 44.86 | 18:30
44 | Cumilla(N) | 136 | 00:00 | 110 | Millgate | 126 | 15:00 | 176 | Sunamganj | 58 | 00:00
45 | Cumilla(S) | 146 | 13:00 | 111 | Mirpur | 122 | 16:00 | 177 | Sylhet | 53 | 00:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Mirsorai | 12 | 15:00 | 178 | Sylhet-132 | 128 | 18:00
47 | Daudkandi | 145 | 18:30 | 113 | Mirzapur | 51 | 21:00 | 179 | TK | 25 | 18:00
48 | DhakaUniversity | 98 | 13:00 | 114 | Mithapukur | 54 | 00:00 | 180 | Tangail | 152 | 00:00
49 | Dhamrai | 126 | 16:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 16 | 18:00
50 | Dhanmondi | 136.5 | 13:00 | 116 | Mogbazar | 107.6 | 13:00 | 182 | Thakurgaon | 78 | 18:30
51 | Dohazari | 99 | 20:00 | 117 | Mongla | 37 | 18:00 | 183 | Tongi | 126 | 11:00
52 | Faridpur | 153 | 00:00 | 118 | Motijheel | 51 | 13:00 | 184 | Ullahpara | 30 | 00:00
53 | Fatullah | 111 | 16:00 | 119 | Muktagacha | 30 | 00:00 | 185 | Ullon | 50 | 18:00
54 | Fenchuganj | 43 | 18:00 | 120 | Munshiganj | 106 | 23:00 | 186 | Uttara | 84 | 13:00
55 | Feni | 120 | 18:00 | 121 | Muradnagar | 41 | 18:30 | 187 | UttaraNew | 58 | 15:00
56 | GPH | 75 | 02:00 | 122 | Mymensingh | 178 | 00:00 | 188 | Zigatola | 71 | 13:00
57 | Ghatail | 68 | 01:00 | 123 | Naogaon | 99 | 01:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 58 | 18:30
59 | Ghorashal-230 | 98 | 12:00 | 125 | Narinda | 66 | 13:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 180 | 19:00
61 | Gollamari | 88 | 18:00 | 127 | Natore | 127 | 00:00
62 | Gopalganj | 102 | 18:30 | 128 | Nawabganj | 42.4 | 00:00
63 | Gulshan | 126 | 13:00 | 129 | Netrakona | 124 | 00:00
64 | Halishahar | 85 | 13:00 | 130 | New | 57.2 | 12:00
65 | HaripurSBU | 137 | 13:00 | 131 | Niamatpur | 52 | 18:30
66 | Hasnabad | 81 | 18:00 | 132 | Noapara | 42 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13994.51 | 0 |  | 13994.51
1:00 | 13567.28 | 0 |  | 13567.28
2:00 | 13062.04 | 0 |  | 13062.04
3:00 | 12655.77 | 0 |  | 12655.77
4:00 | 12407.22 | 0 |  | 12407.22
5:00 | 12127.65 | 0 |  | 12127.65
6:00 | 11612.42 | 0 |  | 11612.42
7:00 | 11576.65 | 0 |  | 11576.65
8:00 | 11621.02 | 0 |  | 11621.02
9:00 | 11673.24 | 0 |  | 11673.24
10:00 | 11661.74 | 0 |  | 11661.74
11:00 | 11863.17 | 0 |  | 11863.17
12:00 | 12467.6 | 0 |  | 12467.6
13:00 | 12889.44 | 0 |  | 12889.44
14:00 | 13036.9 | 0 |  | 13036.9
15:00 | 12767.1 | 0 |  | 12767.1
16:00 | 12280.21 | 0 |  | 12280.21
17:00 | 12185.17 | 0 |  | 12185.17
18:00 | 13156.6 | 0 |  | 13156.6
19:00 | 12829.8 | 0 |  | 12829.8
19:30 | 12805 | 0 |  | 12805
20:00 | 12887.8 | 0 |  | 12887.8
21:00 | 12838.39 | 0 |  | 12838.39
22:00 | 12936.04 | 0 |  | 12936.04
23:00 | 12997.55 | 0 |  | 12997.55
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7060.5 | 6934.01 | 13994.51 | DAILY GENERATION CURVE
00:30 | 7059.25 | 6721.645 | 13780.895
01:00 | 7058 | 6509.28 | 13567.28 | 05-10-2025
01:30 | 6893.4 | 6421.26 | 13314.66
02:00 | 6728.8 | 6333.24 | 13062.04
02:30 | 6629.4 | 6229.505 | 12858.905
03:00 | 6530 | 6125.77 | 12655.77
03:30 | 6495.5 | 6035.995 | 12531.495
04:00 | 6461 | 5946.22 | 12407.22
04:30 | 6375.5 | 5891.935 | 12267.435
05:00 | 6290 | 5837.65 | 12127.65
05:30 | 6183.53 | 5686.505 | 11870.035
06:00 | 6077.06 | 5535.36 | 11612.42
06:30 | 6067.66 | 5526.875 | 11594.535
07:00 | 6058.26 | 5518.39 | 11576.65
07:30 | 6031.885 | 5566.95 | 11598.835
08:00 | 6005.51 | 5615.51 | 11621.02
08:30 | 6100.355 | 5546.775 | 11647.13
09:00 | 6195.2 | 5478.04 | 11673.24
09:30 | 6209.5 | 5457.99 | 11667.49
10:00 | 6223.8 | 5437.94 | 11661.74
10:30 | 6323.165 | 5439.29 | 11762.455
11:00 | 6422.53 | 5440.64 | 11863.17
11:30 | 6726.075 | 5439.31 | 12165.385
12:00 | 7029.62 | 5437.98 | 12467.6
12:30 | 7186.64 | 5491.88 | 12678.52
13:00 | 7343.66 | 5545.78 | 12889.44
13:30 | 7413.775 | 5549.395 | 12963.17
14:00 | 7483.89 | 5553.01 | 13036.9
14:30 | 7421.445 | 5480.555 | 12902
15:00 | 7359 | 5408.1 | 12767.1
15:30 | 7191.75 | 5331.905 | 12523.655
16:00 | 7024.5 | 5255.71 | 12280.21
16:30 | 6999.195 | 5233.495 | 12232.69
17:00 | 6973.89 | 5211.28 | 12185.17
17:30 | 7212.745 | 5458.14 | 12670.885
18:00 | 7451.6 | 5705 | 13156.6
18:30 | 7332.2 | 5661 | 12993.2
19:00 | 7212.8 | 5617 | 12829.8
19:30 | 7093 | 5712 | 12805
20:00 | 7127.8 | 5760 | 12887.8
20:30 | 7112.3 | 5750.795 | 12863.095 |  | Executive Engineer
21:00 | 7096.8 | 5741.59 | 12838.39 |  | Network Operation Division
21:30 | 7117.15 | 5770.065 | 12887.215
22:00 | 7137.5 | 5798.54 | 12936.04
22:30 | 7142.5 | 5824.295 | 12966.795
23:00 | 7147.5 | 5850.05 | 12997.55

## En-Curve
QF-LDC-12
Date | 05-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4021 | 1657 | 833 | 38 | 50 | 1310.01 | 219 | 4640 | 0 | 372 | 842.5 | 0 | 0 | 12 | 0 | DAILY ENERGY CURVE
00:30 | 4015 | 1676 | 833.5 | 38 | 49 | 1306.145 | 218.5 | 4446 | 0 | 363.5 | 825.25 | 0 | 0 | 10 | 0 | 05-10-2025
01:00 | 4009 | 1695 | 834 | 38 | 48 | 1302.28 | 218 | 4252 | 0 | 355 | 808 | 0 | 0 | 8 | 0
01:30 | 3981 | 1698.5 | 834 | 38 | 47 | 1307.26 | 218 | 4188.5 | 0 | 320 | 677.4 | 0 | 0 | 5 | 0 | Energy Generated | 304.0634 |  | MKWHr
02:00 | 3953 | 1702 | 834 | 38 | 46 | 1312.24 | 218 | 4125 | 0 | 285 | 546.8 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3962 | 1701 | 833.5 | 38 | 45 | 1314.505 | 218 | 4027 | 0 | 269.5 | 444.9 | 0 | 0 | 5.5 | 0 | Total Energy Requirement | 304.0634 |  | MKWHr
03:00 | 3971 | 1700 | 833 | 38 | 44 | 1316.77 | 218 | 3929 | 0 | 254 | 343 | 0 | 0 | 9 | 0
03:30 | 3883.5 | 1747 | 833.5 | 38 | 44 | 1315.495 | 218 | 3873.5 | 0 | 228.5 | 340 | 0 | 0 | 10 | 0
04:00 | 3796 | 1794 | 834 | 38 | 44 | 1314.22 | 218 | 3818 | 0 | 203 | 337 | 0 | 0 | 11 | 0
04:30 | 3801.5 | 1787.5 | 833.5 | 38 | 43 | 1317.435 | 218.5 | 3726 | 0 | 175.5 | 315.5 | 0 | 0 | 11 | 0
05:00 | 3807 | 1781 | 833 | 38 | 42 | 1320.65 | 219 | 3634 | 0 | 148 | 294 | 0 | 0 | 11 | 0
05:30 | 3791.5 | 1787 | 833 | 38 | 40 | 1219.505 | 219.5 | 3537 | 0.53 | 131.5 | 260 | 0 | 0 | 12.5 | 0
06:00 | 3776 | 1793 | 833 | 38 | 38 | 1118.36 | 220 | 3440 | 1.06 | 115 | 226 | 0 | 0 | 14 | 0
06:30 | 3805 | 1776.5 | 832.5 | 38 | 38 | 1070.96 | 220 | 3430.5 | 30.075 | 128 | 213 | 0 | 0 | 12 | 0
07:00 | 3834 | 1760 | 832 | 38 | 38 | 1023.56 | 220 | 3421 | 59.09 | 141 | 200 | 0 | 0 | 10 | 0
07:30 | 3806 | 1714 | 832 | 38 | 37 | 1024.845 | 220 | 3479.5 | 78.49 | 141 | 223 | 0 | 0 | 5 | 0
08:00 | 3778 | 1668 | 832 | 38 | 36 | 1026.13 | 220 | 3538 | 97.89 | 141 | 246 | 0 | 0 | 0 | 0
08:30 | 3765 | 1628.55 | 832.5 | 38 | 35 | 973.895 | 220 | 3589 | 138.685 | 141 | 285.5 | 0 | 0 | 0 | 0
09:00 | 3752 | 1589.1 | 833 | 38 | 34 | 921.66 | 220 | 3640 | 179.48 | 141 | 325 | 0 | 0 | 0 | 0
09:30 | 3725 | 1603.05 | 833 | 38 | 35 | 870.585 | 220 | 3674 | 199.855 | 141 | 326 | 0 | 0 | 2 | 0
10:00 | 3698 | 1617 | 833 | 38 | 36 | 819.51 | 220 | 3708 | 220.23 | 141 | 327 | 0 | 0 | 4 | 0
10:30 | 3589 | 1661.5 | 833 | 38 | 34 | 819.64 | 220 | 3693 | 253.415 | 163.5 | 450.9 | 0 | 0 | 6.5 | 0
11:00 | 3480 | 1706 | 833 | 38 | 32 | 819.77 | 220 | 3678 | 286.6 | 186 | 574.8 | 0 | 0 | 9 | 0
11:30 | 3505 | 1698.5 | 833 | 38 | 32 | 820.12 | 220 | 3721 | 275.415 | 206 | 808.35 | 0 | 0 | 8 | 0
12:00 | 3530 | 1691 | 833 | 38 | 32 | 820.47 | 220 | 3764 | 264.23 | 226 | 1041.9 | 0 | 0 | 7 | 0
12:30 | 3579 | 1695.5 | 833 | 38 | 35 | 823.155 | 219.5 | 3790 | 219.115 | 244.5 | 1194.25 | 0 | 0 | 7.5 | 0
13:00 | 3628 | 1700 | 833 | 38 | 38 | 825.84 | 219 | 3816 | 174 | 263 | 1346.6 | 0 | 0 | 8 | 0
13:30 | 3572.5 | 1652 | 833 | 38 | 38 | 852.42 | 218.5 | 3803 | 197 | 288 | 1462.25 | 0 | 0 | 8.5 | 0
14:00 | 3517 | 1604 | 833 | 38 | 38 | 879 | 218 | 3790 | 220 | 313 | 1577.9 | 0 | 0 | 9 | 0
14:30 | 3466.5 | 1597 | 833 | 38 | 38 | 872 | 219 | 3781.5 | 204.45 | 292.5 | 1551.05 | 0 | 0 | 9 | 0
15:00 | 3416 | 1590 | 833 | 38 | 38 | 865 | 220 | 3773 | 188.9 | 272 | 1524.2 | 0 | 0 | 9 | 0
15:30 | 3441.5 | 1586.5 | 833 | 38 | 34 | 886 | 220.5 | 3724 | 124.155 | 253.5 | 1369 | 0 | 0 | 13.5 | 0
16:00 | 3467 | 1583 | 833 | 38 | 30 | 907 | 221 | 3675 | 59.41 | 235 | 1213.8 | 0 | 0 | 18 | 0
16:30 | 3459 | 1591.5 | 832.5 | 38 | 30 | 974.5 | 221.5 | 3560 | 40.39 | 234.5 | 1234.3 | 0 | 0 | 16.5 | 0
17:00 | 3451 | 1600 | 832 | 38 | 30 | 1042 | 222 | 3445 | 21.37 | 234 | 1254.8 | 0 | 0 | 15 | 0
17:30 | 3492.5 | 1613 | 832.5 | 38 | 33 | 1167 | 222 | 3519 | 10.685 | 298.5 | 1428.2 | 0 | 0 | 16.5 | 0
18:00 | 3534 | 1626 | 833 | 38 | 36 | 1292 | 222 | 3593 | 0 | 363 | 1601.6 | 0 | 0 | 18 | 0
18:30 | 3478.5 | 1607.5 | 833 | 38 | 36 | 1307 | 222 | 3599.5 | 0 | 318.5 | 1541.2 | 0 | 0 | 12 | 0
19:00 | 3423 | 1589 | 833 | 38 | 36 | 1322 | 222 | 3606 | 0 | 274 | 1480.8 | 0 | 0 | 6 | 0
19:30 | 3522 | 1672 | 833 | 38 | 36 | 1384 | 222 | 3665 | 0 | 275 | 1156 | 0 | 0 | 2 | 0
20:00 | 3546 | 1714 | 833 | 38 | 38 | 1426 | 222 | 3661 | 0 | 275 | 1130.8 | 0 | 0 | 4 | 0
20:30 | 3544 | 1741.25 | 833.5 | 38 | 37 | 1397.795 | 222 | 3661 | 0 | 276.5 | 1110.05 | 0 | 0 | 2 | 0
21:00 | 3542 | 1768.5 | 834 | 38 | 36 | 1369.59 | 222 | 3661 | 0 | 278 | 1089.3 | 0 | 0 | 0 | 0
21:30 | 3597.5 | 1777.5 | 833.5 | 38 | 38 | 1348.565 | 222 | 3695 | 0 | 266 | 1071.15 | 0 | 0 | 0 | 0
22:00 | 3653 | 1786.5 | 833 | 38 | 40 | 1327.54 | 222 | 3729 | 0 | 254 | 1053 | 0 | 0 | 0 | 0
22:30 | 3642.5 | 1794.5 | 833 | 38 | 41 | 1326.295 | 221.5 | 3771 | 0 | 254 | 1044.5 | 0 | 0 | 0.5 | 0
23:00 | 3632 | 1802.5 | 833 | 38 | 42 | 1325.05 | 221 | 3813 | 0 | 254 | 1036 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 18:30 | 369 | 00:00 | Payra | 410 | 17:00 | 403 | 00:00
Ashuganj | 410 | 6:00 | 388 | 15:00 | Rahanpur | 412 | 12:00 | 397 | 00:00
Bhulta | 404 | 06:00 | 382 | 10:00 | Rampal | 398 | 17:00 | 385 | 01:00
Bibiana | 391 | 18:30 | 380 | 00:00
BIPTC | 403 | 07:00 | 397 | 00:00
Bogura | 403 | 11:00 | 385 | 20:00
Gopalganj | 394 | 18:30 | 381 | 1:00
Kaliakoir | 379 | 18:30 | 362 | 00:00
Madunaghat | 392 | 19:00 | 381 | 00:00
Meghnaghat | 388 | 18:30 | 373 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 18:30 | 221 | 10:00 | Kaliakoir | 236 | 18:30 | 224 | 10:00
AKSML | 233 | 17:00 | 225 | 01:00 | Keranigonj | 244 | 05:00 | 218 | 00:00
Aminbazar | 231 | 18:30 | 221 | 10:00 | Khulna(S) | 229 | 17:00 | 218 | 00:00
Ashuganj | 233 | 18:30 | 224 | 00:00 | Madunaghat | 234 | 18:00 | 226 | 01:00
Ashuganj-400 | 233 | 18:30 | 224 | 00:00 | Madunaghat-400 | 234 | 19:00 | 226 | 00:00
Baghabari | 234 | 06:00 | 226 | 00:00 | Maniknagar | 224 | 21:00 | 215 | 00:00
Barapukuria | 228 | 11:00 | 220 | 18:00 | Meghnaghat | 232 | 21:00 | 222 | 09:00
Barapukuria-230 | 228 | 11:00 | 220 | 18:00 | Meghnaghat-400 | 227 | 21:00 | 218 | 10:00
Barishal | 232 | 17:00 | 224 | 00:00 | Mirsorai | 240 | 15:00 | 226 | 00:00
Bheramara | 234 | 06:00 | 225 | 00:00 | Rajshahi | 233 | 10:00 | 222 | 00:00
Bhulta | 231 | 06:00 | 210 | 10:00 | Rampal | 227 | 07:00 | 217 | 01:00
Bibiana | 230 | 19:30 | 222 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 08:00 | 225 | 00:00 | Rampura | 230 | 06:00 | 214 | 10:00
Bogura | 240 | 10:00 | 230 | 00:00 | Shikalbaha | 232 | 17:00 | 223 | 10:00
Bogura-400 | 240 | 11:00 | 230 | 00:00 | Shyampur | 226 | 18:30 | 217 | 00:00
Borhanuddin | 235 | 07:00 | 230 | 00:00 | Siddhirganj | 225 | 21:00 | 216 | 10:00
BSRM | 237 | 14:00 | 224 | 10:00 | Sirajgonj | 240 | 06:00 | 234 | 00:00
Cumilla(N) | 227 | 18:30 | 215 | 10:00 | Sreepur | 230 | 20:00 | 222 | 00:00
Faridpur | 231 | 18:00 | 220 | 00:00 | Tongi | 233 | 21:00 | 219 | 09:00
Fenchuganj | 229 | 06:00 | 224 | 00:00
Ghorashal | 235 | 18:30 | 225 | 00:00
Ghorashal-230 | 230 | 18:30 | 218 | 10:00
Gopalganj | 232 | 17:00 | 221 | 00:00
GPH | 234 | 14:00 | 225 | 10:00
Haripur | 225 | 21:00 | 216 | 10:00
Hasnabad | 227 | 18:00 | 219 | 00:00
Hathazari | 233 | 18:00 | 222 | 00:00
Ishurdi | 237 | 11:00 | 227 | 00:00
Jhenaidah | 230 | 09:00 | 218 | 00:00
Kachua | 223 | 18:30 | 203 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 21:00 | 122 | 10:00 | Lalmonirhat | 135 | 11:00 | 125 | 18:00
Agargaon | 135 | 21:00 | 128 | 11:00 | Madanganj | 131 | 21:00 | 125 | 10:00
Agrabad | 131 | 13:00 | 126 | 10:00 | Madaripur | 134 | 17:00 | 128 | 00:00
AKS | 131 | 19:00 | 126 | 01:00 | Madartek | 138 | 01:00 | 124 | 10:00
Aminbazar | 137 | 18:30 | 130 | 08:00 | Madunaghat | 136 | 17:00 | 130 | 01:00
Amnura | 139 | 09:00 | 128 | 00:00 | Magura | 134 | 17:00 | 123 | 00:00
Ashuganj | 140 | 07:00 | 135 | 00:00 | Mahasthangarh | 136 | 11:00 | 127 | 00:00
Bagerhat | 132 | 09:00 | 119 | 00:00 | Maijdee | 135 | 15:00 | 118 | 00:00
Bajitpur | 132 | 20:00 | 124 | 00:00 | Manikganj | 130 | 18:30 | 122 | 00:00
Bakulia | 134 | 17:00 | 129 | 10:00 | Maniknagar | 136 | 21:00 | 129 | 11:00
Banani | 135 | 06:00 | 124 | 10:00 | Matarbari | 119 | 16:00 | 112 | 01:00
Bangabhaban | 135 | 21:00 | 129 | 10:00 | Matuail | 132 | 21:00 | 125 | 10:00
Barapukuria | 139 | 09:00 | 130 | 18:00 | Millgate | 135 | 19:00 | 125 | 10:00
Barguna | 135 | 17:00 | 130 | 01:00 | Mirpur | 135 | 18:30 | 129 | 08:00
Barishal | 134 | 17:00 | 127 | 00:00 | Mirzapur | 137 | 18:00 | 126 | 00:00
Barishal-230 | 133 | 17:00 | 126 | 00:00 | Mithapukur | 136 | 11:00 | 125 | 02:00
Baroaulia | 133 | 17:00 | 129 | 00:00 | MI_Cement | 132 | 21:00 | 126 | 00:00
Baroirhat | 132 | 13:00 | 127 | 01:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 21:00 | 124 | 10:00 | Mogbazar | 136 | 06:00 | 125 | 9:00
BashundharaCement | 131 | 21:00 | 125 | 10:00 | Mongla | 131 | 07:00 | 119 | 00:00
Beanibazar | 128 | 07:00 | 123 | 00:00 | Motijheel | 135 | 21:00 | 129 | 10:00
Benapole | 132 | 09:00 | 119 | 00:00 | Muktagacha | 137 | 18:00 | 128 | 00:00
Bhaluka | 133 | 19:30 | 123 | 00:00 | Munshiganj | 131 | 20:00 | 124 | 10:00
Bhandaria | 132 | 17:00 | 118 | 00:00 | Muradnagar | 129 | 18:30 | 120 | 00:00
Bhangura | 135 | 17:00 | 129 | 00:00 | Mymensingh | 139 | 18:00 | 115 | 00:00
Bheramara | 138 | 08:00 | 134 | 00:00 | Naogaon | 135 | 10:00 | 124 | 00:00
Bheramara(GK) | 139 | 16:00 | 133 | 00:00 | Narail | 133 | 15:00 | 122 | 00:00
Bhulta | 128 | 21:00 | 123 | 00:00 | Narinda | 136 | 21:00 | 129 | 11:00
Bog-Sherpur | 135 | 10:00 | 128 | 00:00 | Narshingdi | 132 | 07:00 | 120 | 00:00
Bogura | 137 | 11:00 | 129 | 00:00 | Natore | 135 | 10:00 | 128 | 00:00
Bogura-230 | 137 | 11:00 | 129 | 00:00 | Nawabganj | 135 | 19:00 | 128 | 00:00
Brahmanbaria | 133 | 06:00 | 127 | 00:00 | Netrakona | 126 | 20:00 | 113 | 00:00
Cantonment | 134 | 06:00 | 128 | 12:00 | New | 134 | 19:00 | 127 | 09:00
Chandina | 133 | 18:30 | 124 | 00:00 | Niamatpur | 140 | 10:00 | 133 | 00:00
Chandpur | 140 | 15:00 | 125 | 00:00 | Noapara | 134 | 09:00 | 123 | 00:00
Chandraghona | 135 | 17:00 | 132 | 00:00 | Pabna | 137 | 16:00 | 131 | 00:00
Chapai | 139 | 10:00 | 133 | 00:00 | Palashbari | 135 | 11:00 | 123 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 20:00 | 125 | 10:00 | Panchagarh | 134 | 06:00 | 124 | 13:00
Chauddagram | 133 | 18:30 | 120 | 09:00 | Patiya | 132 | 17:00 | 127 | 00:00
Chhatak | 130 | 18:30 | 120 | 00:00 | Patuakhali | 136 | 18:30 | 132 | 00:00
Chowmuhani | 132 | 15:00 | 119 | 00:00 | Payra | 136 | 08:00 | 133 | 00:00
Chuadanga | 134 | 16:00 | 121 | 00:00 | PHP | 131 | 07:00 | 126 | 00:00
Coxsbazar | 118 | 07:00 | 112 | 20:00 | Postogola | 134 | 19:00 | 129 | 00:00
Cumilla(N) | 132 | 18:30 | 123 | 10:00 | Purbachal | 135 | 05:00 | 123 | 10:00
Cumilla(S) | 133 | 06:00 | 123 | 00:00 | Purbasadipur | 131 | 09:00 | 124 | 13:00
Daganbhuiyan | 134 | 15:00 | 119 | 02:00 | Rahanpur | 141 | 11:00 | 135 | 00:00
Daudkandi | 127 | 21:00 | 119 | 00:00 | Rahanpur-400 | 141 | 09:00 | 136 | 00:00
DhakaUniversity | 136 | 21:00 | 125 | 10:00 | Rahim | 132 | 21:00 | 125 | 11:00
Dhamrai | 136 | 18:00 | 126 | 09:00 | Rajbari | 137 | 18:00 | 127 | 00:00
Dhanmondi | 136 | 21:00 | 124 | 10:00 | Rajendrapur | 140 | 18:30 | 123 | 00:00
Dohazari | 129 | 17:00 | 123 | 02:00 | Rajshahi | 134 | 09:00 | 127 | 00:00
Faridpur | 137 | 18:00 | 129 | 00:00 | Rajshahi-230 | 134 | 10:00 | 127 | 00:00
Fatullah | 137 | 19:00 | 131 | 10:00 | Ramganj | 136 | 16:00 | 120 | 00:00
Fenchuganj | 135 | 06:00 | 132 | 00:00 | Rampur | 132 | 18:00 | 127 | 10:00
Feni | 132 | 18:30 | 118 | 00:00 | Rampura | 135 | 06:00 | 124 | 10:00
Ghatail | 136 | 18:00 | 125 | 01:00 | Rangamati | 134 | 18:00 | 130 | 10:00
Ghorashal | 140 | 19:00 | 130 | 10:00 | Rangpur | 136 | 11:00 | 120 | 01:00
Goalpara | 136 | 17:00 | 126 | 00:00 | Ruppur | 138 | 08:00 | 133 | 00:00
Gollamari | 136 | 17:00 | 126 | 00:00 | Saidpur | 133 | 09:00 | 127 | 13:00
Gopalganj | 133 | 09:00 | 126 | 00:00 | Satkhira | 133 | 09:00 | 121 | 00:00
Gopalganj-400 | 135 | 17:00 | 129 | 00:00 | Satmasjid | 134 | 19:00 | 128 | 10:00
Gulshan | 135 | 06:00 | 124 | 10:00 | Savar | 136 | 18:30 | 130 | 08:00
Halishahar | 133 | 17:00 | 127 | 10:00 | SevenRings | 140 | 18:30 | 131 | 10:00
Haripur | 132 | 21:00 | 126 | 10:00 | ShahCement | 132 | 20:00 | 125 | 10:00
HaripurSBU | 132 | 21:00 | 126 | 00:00 | Shahjadpur | 138 | 11:00 | 133 | 00:00
Hasnabad | 134 | 21:00 | 129 | 00:00 | Shahjibazar | 134 | 06:00 | 127 | 00:00
Hathazari | 135 | 14:00 | 130 | 08:00 | Shahmirpur | 134 | 18:00 | 128 | 10:00
Ishurdi | 139 | 08:00 | 134 | 00:00 | Shariatpur | 132 | 08:00 | 124 | 00:00
Jaldhaka | 132 | 08:00 | 126 | 13:00 | Sherpur | 138 | 09:00 | 123 | 00:00
Jamalpur | 138 | 08:00 | 128 | 00:00 | Shikalbaha | 124 | 18:00 | 118 | 10:00
Jashore | 131 | 07:00 | 120 | 00:00 | Shikalbaha-230 | 136 | 17:00 | 129 | 09:00
Jhenaidah | 137 | 16:00 | 124 | 00:00 | Shitalakhya | 132 | 21:00 | 126 | 00:00
Jhenaidah-230 | 136 | 17:00 | 126 | 00:00 | Sholosohor | 134 | 17:00 | 130 | 10:00
Joydebpur | 145 | 18:30 | 124 | 10:00 | Shyampur | 135 | 21:00 | 132 | 11:00
Joypurhat | 135 | 10:00 | 123 | 00:00 | Shyampur-230 | 137 | 20:00 | 131 | 10:00
Juldah | 133 | 19:00 | 128 | 10:00 | Siddhirganj | 132 | 21:00 | 126 | 00:00
Kabirpur | 138 | 18:00 | 124 | 10:00 | Sirajganj | 134 | 11:00 | 127 | 00:00
Kachua | 140 | 18:30 | 127 | 00:00 | Sonargaon | 130 | 21:00 | 124 | 00:00
Kaliakoir | 139 | 18:30 | 129 | 00:00 | Sreemongol | 133 | 08:00 | 127 | 00:00
Kallyanpur | 136 | 19:30 | 130 | 10:00 | Sreepur | 135 | 20:00 | 124 | 13:00
Kalurghat | 134 | 13:00 | 131 | 01:00 | Srinagar | 134 | 19:00 | 128 | 00:00
Kamrangirchar | 134 | 21:00 | 127 | 11:00 | SSM | 138 | 17:00 | 132 | 00:00
Kaptai | 136 | 14:00 | 134 | 2:00 | Sunamganj | 128 | 19:00 | 120 | 00:00
Kasba | 129 | 18:30 | 120 | 00:00 | Sylhet | 129 | 07:00 | 125 | 00:00
Kazla | 134 | 22:00 | 129 | 11:00 | Sylhet-132 | 129 | 19:00 | 126 | 00:00
Keranigonj | 134 | 06:00 | 128 | 11:00 | Tangail | 137 | 18:30 | 124 | 00:00
Khagrachori | 133 | 17:00 | 130 | 01:00 | Taraganj | 134 | 09:00 | 128 | 00:00
Khulna | 135 | 17:00 | 125 | 00:00 | Thakurgaon | 133 | 06:00 | 123 | 13:00
Khulna(S) | 136 | 09:00 | 127 | 00:00 | TK | 134 | 13:00 | 130 | 10:00
Khulshi | 132 | 18:30 | 126 | 10:00 | Tongi | 136 | 18:30 | 129 | 09:00
Kishoreganj | 131 | 19:30 | 120 | 00:00 | Ullahpara | 135 | 11:00 | 129 | 00:00
Kodda | 141 | 18:30 | 123 | 09:00 | Ullon | 135 | 22:00 | 124 | 10:00
KSRM | 131 | 03:00 | 130 | 00:00 | Uttara | 135 | 21:00 | 128 | 10:00
Kulaura | 134 | 06:00 | 131 | 00:00 | UttaraNew | 135 | 19:00 | 128 | 08:00
Kurigram | 134 | 11:00 | 122 | 18:00 | Zigatola | 134 | 06:00 | 128 | 13:00
Kushtia | 138 | 16:00 | 129 | 00:00
Laksam | 139 | 16:00 | 125 | 00:00
Lakshmipur | 135 | 16:00 | 119 | 00:00
Lalbag | 134 | 19:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division