## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-10-2025 | during | 07-10-2025 | during | 07-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 358 | 343 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 140 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 42 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35.9 | 47.6 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 90 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25.5 | 26 | 33 | 33 | 33 | 33
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 63 | 115 | 149 | 149 | 115 | 115 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 104 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 500 | 410 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 234 | 234 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2155.4 | 2626.6 | 5372.4 | 5354.4 | 3366.31 | 3406.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 203 | 200 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 24 | 97 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 38 | 56 | 70 | 56 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 18 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 92 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.8 | 0 | 3.8 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 40 | 300 | 300 | 16 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 15 | 65 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 32 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 60 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1165 | 1145 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 1 | 5 | 6 | 5 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 280 | 285 | 285 | 285 | 280 | 280 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1952 | 2418 | 3039.52 | 3063.72 | 2480.02 | 2588.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 410 | 400 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 0 | 46.7 | 46.7 | 10 | 10 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 3 | 3 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 38 | 38 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 65 | 123 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 104 | 103 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 32 | 156 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 38 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 59 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 24 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1353 | 1570 | 2673.86 | 2603.86 | 2212.16 | 2151.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-10-2025 | during | 07-10-2025 | during | 07-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 59 | 40 | 157.5 | 157.5 | 101 | 101 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 16 | 153 | 9.5 | 9.5 | 150 | 150 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 77 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.24 | 0 | 36 | 0 | 36 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 180.24 | 276 | 357.7 | 320.5 | 425.7 | 388.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 60 | 60 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 164 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 6 | 25 | 25 | 12 | 12 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 334 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1251 | 1169 | 1293 | 1293 | 1202 | 1202
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 848 | 847 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 149 | 128 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 49 | 0 | 45 | 0 | 45 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 373 | 370 | 370 | 370 | 370 | 370
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1457 | 1383 | 2693 | 2648 | 2498 | 2453
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 511 | 611 | 0 | 0 | 300 | 300 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1105 | 1152 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 130 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 273 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.79 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2227.79 | 2517 | 2147 | 2146 | 2264 | 2263
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 58.26 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 10 | 0 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 340 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 94 | 94 | 94 | 94 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 87 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.67 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1058.37 | 1435.12 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.95 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1808.25 | 2053.12 | 3179.47 | 3024.87 | 3062.69 | 2908.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 47 | 48 | 48 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 141 | 145 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.4 | 0 | 2 | 0 | 2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 30 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 15 | 0 | 15 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 96 | 0 | 176.08 | 0 | 176.08 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 350.4 | 405 | 639.08 | 446 | 639.08 | 446
System Total |  |  |  |  | 28823.2 | 28365.955 | 12735.08 | 14417.72 | 21395.03 | 20900.35 | 18149.96 | 17806.28
Forecast Scenario (07-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14100 |  | 0 |  | 14100
|  |  |  | 1:00 | 13630 |  | 0 |  | 13630
|  |  |  | 2:00 | 13210 |  | 0 |  | 13210
|  |  |  | 3:00 | 12720 |  | 0 |  | 12720
|  |  |  | 4:00 | 12420 |  | 0 |  | 12420
|  |  |  | 5:00 | 12180 |  | 0 |  | 12180
|  |  |  | 6:00 | 11720 |  | 0 |  | 11720
|  |  |  | 7:00 | 11690 |  | 0 |  | 11690
|  |  |  | 8:00 | 11610 |  | 0 |  | 11610
|  |  |  | 9:00 | 11910 |  | 0 |  | 11910
|  |  |  | 10:00 | 12250 |  | 0 |  | 12250
|  |  |  | 11:00 | 12450 |  | 0 |  | 12450
|  |  |  | 12:00 | 13000 |  | 0 |  | 13000
|  |  |  | 13:00 | 13130 |  | 0 |  | 13130
|  |  |  | 14:00 | 13270 |  | 0 |  | 13270
|  |  |  | 15:00 | 13610 |  | 0 |  | 13610
|  |  |  | 16:00 | 13490 |  | 0 |  | 13490
|  |  |  | 17:00 | 13230 |  | 0 |  | 13230
|  |  |  | 18:00 | 13600 |  | 0 |  | 13600
|  |  |  | 18:30 | 12900 |  | 0 |  | 12900
|  |  |  | 19:00 | 14280 |  | 0 |  | 14280
|  |  |  | 19:30 | 14650 |  | 0 |  | 14650
|  |  |  | 20:00 | 14800 |  | 0 |  | 14800
|  |  |  | 21:00 | 14750 |  | 0 |  | 14750
|  |  |  | 22:00 | 14800 |  | 0 |  | 14800
|  |  |  | 23:00 | 14750 |  | 0 |  | 14750
Probable Maximum Temperature: |  |  | 31.20°C
Probable Maximum Demand at Day Peak: |  |  | 13000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 316.60 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:00 hrs on 07-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-10-2025 | [28 empty] | Date: | 06-10-2025 | [28 empty] | Date: | 06-10-2025 | [28 empty] | Date: | 06-10-2025 | [28 empty] | Date: | 06-10-2025 | [14 empty] | Date: | 06-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 18 | 17 | 37 | 0 | 145 | 30 | 0 | 72 | 0 | 300 | 148 | 400 | 0 | 35 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 0 | 21 | 0 | 71 | 0 | 1 | 66 | 52 | 0 | 0 | 0 | 0 | 219 | 43 | 29 | 280 | 33 | 0 | 33 | 17 | 79 | 194 | 0 | 0 | 0 | 1160 | 0 | 51 | 67 | 8 | 345 | 0 | 330 | 0 | 196 | 0 | 34 | 106 | 113 | 0 | 20 | 16 | 40 | 8 | 0 | 0 | 310 | 0 | 386 | 30 | 57 | 160 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 5 | 65 | 43 | 66 | 0 | 0 | 6 | 7112.5 | 833 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 1307.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 343 | 0 | 0 | 144 | 49 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 115 | 220 | 0 | 302 | 1232 | 17 | 5849.53 | 12962.03 | 107.85
01:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 18 | 0 | 68 | 0 | 95 | 0 | 0 | 72 | 0 | 300 | 148 | 373 | 0 | 35 | 300 | 0 | 0 | 0 | 70 | 20.5 | 22 | 0 | 0 | 27 | 0 | 56 | 0 | 26 | 66 | 52 | 0 | 0 | 0 | 0 | 218 | 68 | 28 | 280 | 0 | 0 | 33 | 0 | 95 | 194 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 0 | 345 | 0 | 330 | 0 | 190 | 0 | 58 | 105 | 121 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 300 | 0 | 366 | 30 | 57 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 65 | 43 | 67 | 0 | 0 | 6 | 6975.5 | 833 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1199.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 345 | 0 | 0 | 143 | 49 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 302 | 1120 | 17 | 5604.34 | 12579.84 | 107.84
02:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 18 | 0 | 68 | 0 | 0 | 0 | 0 | 72 | 0 | 300 | 146 | 374 | 0 | 35 | 300 | 0 | 0 | 0 | 35 | 20.5 | 22 | 0 | 0 | 27 | 0 | 0 | 0 | 13 | 50 | 0 | 0 | 0 | 0 | 0 | 218 | 63 | 29 | 280 | 0 | 0 | 33 | 0 | 93 | 194 | 0 | 0 | 0 | 1130 | 0 | 51 | 100 | 0 | 345 | 0 | 330 | 0 | 184 | 0 | 68 | 105 | 124 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 305 | 0 | 359 | 30 | 57 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 17 | 65 | 43 | 67 | 0 | 0 | 6 | 6668.5 | 838 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1213.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 148 | 50 | 35 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 302 | 1090 | 17 | 5521.07 | 12189.57 | 107.84
03:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 54 | 0 | 300 | 145 | 368 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 0 | 0 | 0 | 0 | 0 | 217 | 51 | 29 | 280 | 0 | 0 | 33 | 0 | 91 | 194 | 0 | 0 | 0 | 1130 | 0 | 51 | 30 | 0 | 345 | 0 | 330 | 0 | 186 | 0 | 69 | 106 | 100 | 0 | 20 | 0 | 36 | 0 | 0 | 0 | 300 | 0 | 358 | 30 | 57 | 141 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 17 | 65 | 24 | 74 | 0 | 0 | 6 | 6400.5 | 837 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1106.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 335 | 0 | 0 | 148 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 302 | 1080 | 0 | 5335.63 | 11736.13 | 107.84
04:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 54 | 0 | 300 | 145 | 370 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 29 | 280 | 0 | 0 | 33 | 0 | 34 | 194 | 0 | 0 | 0 | 1120 | 0 | 51 | 12 | 0 | 346 | 0 | 330 | 0 | 183 | 0 | 69 | 106 | 51 | 0 | 20 | 0 | 36 | 0 | 0 | 0 | 300 | 0 | 354 | 30 | 57 | 139 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 65 | 24 | 75 | 0 | 0 | 6 | 6148.5 | 836 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1113.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 332 | 0 | 0 | 147 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 302 | 1080 | 0 | 5341.08 | 11489.58 | 107.83
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 153 | 378 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 29 | 280 | 0 | 0 | 33 | 0 | 17 | 194 | 0 | 0 | 0 | 1060 | 0 | 51 | 10 | 0 | 347 | 0 | 330 | 0 | 197 | 0 | 17 | 106 | 17 | 0 | 20 | 0 | 34 | 0 | 0 | 0 | 305 | 0 | 383 | 30 | 57 | 144 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 65 | 16 | 75 | 0 | 0 | 6 | 5966.5 | 843 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1015.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 366 | 0 | 0 | 144 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 115 | 220 | 0 | 302 | 1090 | 0 | 5220.55 | 11187.05 | 107.83
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 148 | 383 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 20.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 29 | 280 | 0 | 0 | 0 | 0 | 16 | 194 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 0 | 347 | 0 | 330 | 0 | 191 | 0 | 16 | 106 | 0 | 0 | 20 | 0 | 32 | 0 | 1 | 0 | 315 | 0 | 375 | 30 | 57 | 147 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 65 | 16 | 75 | 0 | 0.03 | 6 | 5873.53 | 843 | 173 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 1011.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 345 | 0 | 0 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 176 | 115 | 220 | 0 | 302 | 1000 | 0 | 5086.95 | 10960.48 | 107.82
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 17 | 6 | 0 | 0 | 0 | 14 | 0 | 300 | 153 | 386 | 0 | 0 | 300 | 0 | 0 | 3 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 0 | 0.14 | 220 | 0 | 29 | 280 | 0 | 0 | 0 | 0 | 14 | 194 | 0 | 0 | 0 | 1050 | 2 | 51 | 0 | 0 | 345 | 0 | 330 | 0 | 201 | 0 | 15 | 106 | 0 | 0 | 20 | 0 | 30 | 0 | 7 | 0 | 310 | 0 | 391 | 30 | 57 | 148 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 19 | 75 | 0 | 6.36 | 6 | 5932.5 | 843 | 171 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 375 | 0 | 1029.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.21 | 10 | 0 | 0 | 2.07 | 160 | 0 | 140 | 0 | 0 | 0 | 381 | 0 | 0.11 | 138 | 49 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 5 | 0.04 | 0 | 173 | 115 | 220 | 0 | 411 | 1000 | 0 | 5268.93 | 11201.43 | 107.81
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 15 | 0 | 300 | 153 | 395 | 0 | 0 | 300 | 0 | 0 | 10 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 1.88 | 220 | 0 | 8 | 280 | 0 | 0 | 0 | 0 | 15 | 200 | 0 | 0 | 0 | 1075 | 5 | 51 | 0 | 0 | 345 | 0 | 330 | 0 | 204 | 0 | 17 | 106 | 0 | 0 | 20 | 0 | 30 | 0 | 11 | 0 | 310 | 0 | 396 | 30 | 57 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 32 | 70 | 0 | 5.01 | 6 | 6039.89 | 848 | 174 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 376 | 0 | 1022.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.35 | 53 | 0 | 0 | 2.15 | 160 | 0 | 140 | 0 | 0 | 0 | 378 | 0 | 0.22 | 140 | 48 | 0 | 4 | 0 | 0 | 0 | 0 | 0.04 | 17 | 0.14 | 0 | 173 | 115 | 220 | 0 | 401 | 1000 | 0 | 5330.17 | 11370.06 | 107.82
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 0 | 17 | 15 | 0 | 300 | 150 | 390 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 220 | 0 | 4 | 280 | 0 | 0 | 0 | 0 | 15 | 199 | 0 | 0 | 0 | 1161 | 12 | 51 | 0 | 0 | 345 | 0 | 330 | 0 | 196 | 0 | 16 | 104 | 0 | 0 | 20 | 0 | 30 | 0 | 8 | 0 | 310 | 0 | 384 | 30 | 57 | 156 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 16 | 63 | 1 | 12.78 | 6 | 6051.34 | 848 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 375 | 0 | 1021.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 86 | 0 | 0 | 15.99 | 160 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 1.4 | 142 | 48 | 0 | 18 | 0 | 0 | 0 | 0 | 0.4 | 73 | 0.23 | 0 | 172 | 115 | 220 | 0 | 426 | 1052 | 0 | 5502.77 | 11554.11 | 107.82
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 47 | 15 | 0 | 0 | 35 | 44 | 0 | 300 | 151 | 390 | 0 | 0 | 250 | 0 | 0 | 19 | 17 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 220 | 0 | 3 | 280 | 0 | 0 | 7 | 0 | 14 | 200 | 0 | 0 | 0 | 1166 | 3 | 51 | 0 | 0 | 345 | 0 | 330 | 0 | 200 | 10 | 15 | 104 | 0 | 0 | 20 | 0 | 28 | 0 | 34 | 0 | 315 | 0 | 387 | 30 | 57 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 16 | 63 | 1 | 7.51 | 2 | 6142.17 | 848 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 374 | 0 | 931.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.89 | 37 | 0 | 0 | 8.39 | 160 | 0 | 140 | 0 | 0 | 0 | 388 | 0 | 1.08 | 144 | 48 | 0 | 6 | 0 | 0 | 0 | 0 | 0.2 | 152 | 0.37 | 0 | 216 | 115 | 220 | 0 | 461 | 1100 | 0 | 5634.24 | 11776.41 | 107.82
11:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 25.5 | 8 | 51 | 15 | 30 | 0 | 35 | 90 | 0 | 300 | 152 | 475 | 0 | 35 | 250 | 0 | 0 | 24 | 17 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.67 | 220 | 8 | 4 | 280 | 0 | 0 | 32 | 0 | 15 | 203 | 0 | 0 | 0 | 1177 | 15 | 51 | 21 | 0 | 360 | 0 | 330 | 0 | 206 | 20 | 16 | 104 | 15 | 0 | 20 | 0 | 30 | 0 | 70 | 0 | 310 | 0 | 390 | 30 | 57 | 155 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 16 | 63 | 1 | 25.56 | 2 | 6578.73 | 848 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 373 | 0 | 927.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.64 | 17 | 0 | 0 | 8.64 | 110 | 0 | 140 | 0 | 0 | 0 | 378 | 0 | 0.5 | 141 | 49 | 0 | 27 | 0 | 0 | 0 | 0 | 0.6 | 79 | 0.31 | 0 | 230 | 115 | 220 | 0 | 460 | 1090 | 0 | 5494.59 | 12073.32 | 107.81
12:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35.9 | 17 | 63 | 15 | 95 | 0 | 35 | 90 | 0 | 300 | 150 | 500 | 0 | 35 | 280 | 0 | 0 | 31 | 52 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 15 | 4 | 280 | 0 | 0 | 33 | 0 | 24 | 203 | 0 | 0 | 0 | 1165 | 8 | 51 | 65 | 0 | 410 | 0 | 330 | 0 | 201 | 20 | 24 | 104 | 32 | 0 | 20 | 0 | 32 | 0 | 64 | 0 | 320 | 0 | 385 | 30 | 57 | 157 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 16 | 59 | 0 | 21.24 | 6 | 6891.64 | 848 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 373 | 0 | 1058.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.26 | 91 | 0 | 0 | 34.95 | 10 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 1.67 | 141 | 48 | 30 | 34 | 0 | 0 | 0 | 0 | 1.4 | 96 | 0.79 | 0 | 276 | 115 | 220 | 0 | 511 | 1105 | 0 | 5843.44 | 12735.08 | 107.81
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 35.9 | 17 | 100 | 15 | 145 | 0 | 35 | 90 | 0 | 300 | 143 | 500 | 0 | 35 | 280 | 0 | 0 | 34 | 52 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 218 | 14 | 13 | 280 | 0 | 0 | 33 | 0 | 47 | 204 | 0 | 0 | 0 | 1140 | 1 | 51 | 92 | 0 | 400 | 0 | 330 | 0 | 190 | 10 | 34 | 104 | 77 | 0 | 20 | 0 | 38 | 0 | 63 | 0 | 305 | 0 | 360 | 30 | 57 | 154 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 16 | 59 | 2 | 31.48 | 6 | 6985.69 | 848 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 374 | 0 | 1158.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.44 | 109 | 0 | 0 | 45.01 | 0 | 0 | 140 | 0 | 0 | 0 | 404 | 0 | 3.27 | 142 | 48 | 35 | 13 | 0 | 0 | 0 | 0 | 5.5 | 108 | 0.64 | 0 | 271 | 115 | 220 | 0 | 561 | 1100 | 0 | 5991.6 | 12977.29 | 107.81
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35.6 | 17 | 114 | 15 | 145 | 0 | 35 | 90 | 0 | 300 | 147 | 470 | 0 | 35 | 280 | 0 | 0 | 10 | 52 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55 | 217 | 15 | 10 | 283 | 0 | 0 | 33 | 0 | 17 | 204 | 0 | 0 | 0 | 1155 | 0 | 51 | 108 | 0 | 400 | 0 | 280 | 0 | 192 | 0 | 34 | 103 | 93 | 0 | 20 | 0 | 34 | 0 | 63 | 0 | 300 | 0 | 377 | 30 | 57 | 153 | 10 | 0 | 78 | 30 | 0 | 16 | 165 | 4 | 77 | 16 | 58 | 2 | 22.6 | 0 | 6895.75 | 848 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 375 | 0 | 1264.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.93 | 97 | 0 | 0 | 53.1 | 0 | 0 | 140 | 0 | 0 | 0 | 342 | 0 | 5.23 | 141 | 47 | 35 | 30 | 0 | 0 | 0 | 0 | 4 | 105 | 0.44 | 0 | 273 | 115 | 180 | 0 | 614 | 1095 | 0 | 6038.74 | 12934.49 | 107.81
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35.9 | 17 | 115 | 15 | 145 | 0 | 35 | 90 | 0 | 300 | 149 | 432 | 0 | 35 | 330 | 0 | 0 | 5 | 35 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.35 | 218 | 15 | 6 | 281 | 0 | 0 | 38 | 0 | 14 | 205 | 0 | 0 | 0 | 1164 | 1 | 51 | 117 | 0 | 415 | 0 | 280 | 0 | 198 | 0 | 34 | 102 | 93 | 0 | 20 | 0 | 36 | 0 | 37 | 0 | 305 | 0 | 383 | 30 | 57 | 146 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 77 | 40 | 32 | 1 | 14.37 | 0 | 6918.62 | 848 | 137 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 373 | 0 | 1260.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.33 | 71 | 0 | 0 | 41.66 | 0 | 0 | 140 | 0 | 0 | 0 | 369 | 0 | 3.78 | 143 | 47 | 0 | 23 | 0 | 0 | 0 | 0 | 2.9 | 111 | 0.37 | 0 | 275 | 115 | 220 | 0 | 614 | 1100 | 0 | 6009.13 | 12927.75 | 107.8
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35.9 | 17 | 90 | 15 | 110 | 0 | 35 | 54 | 0 | 300 | 152 | 429 | 0 | 35 | 331 | 0 | 0 | 2 | 35 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.48 | 219 | 15 | 6 | 282 | 0 | 0 | 50 | 0 | 14 | 205 | 0 | 0 | 0 | 1160 | 3 | 51 | 70 | 0 | 405 | 0 | 285 | 0 | 196 | 0 | 34 | 102 | 94 | 0 | 19 | 0 | 36 | 0 | 16 | 0 | 310 | 0 | 366 | 30 | 57 | 161 | 10 | 0 | 81 | 30 | 0 | 16 | 164 | 17 | 77 | 70 | 32 | 1 | 6.09 | 5 | 6808.47 | 848 | 137 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 372 | 0 | 1267.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.47 | 40 | 0 | 0 | 10.25 | 0 | 0 | 140 | 0 | 0 | 0 | 409 | 0 | 0.91 | 144 | 46 | 0 | 12 | 0 | 0 | 0 | 0 | 2.4 | 47 | 0.09 | 0 | 277 | 115 | 220 | 0 | 614 | 1108 | 0 | 5876.67 | 12685.14 | 107.8
17:00 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35.9 | 23 | 78 | 45 | 95 | 0 | 35 | 54 | 0 | 300 | 144 | 440 | 0 | 0 | 335 | 0 | 0 | 3 | 70 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.14 | 220 | 0 | 12 | 285 | 0 | 0 | 50 | 0 | 0 | 204 | 0 | 0 | 0 | 1123 | 1 | 51 | 70 | 0 | 395 | 0 | 280 | 0 | 185 | 0 | 34 | 103 | 100 | 0 | 19 | 0 | 34 | 0 | 4 | 0 | 310 | 0 | 357 | 30 | 57 | 163 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 77 | 77 | 35 | 0 | 1.63 | 6 | 6750.67 | 849 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 371 | 0 | 1365.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.82 | 11 | 0 | 0 | 6.73 | 0 | 0 | 140 | 0 | 0 | 0 | 393 | 0 | 0.91 | 145 | 46 | 19 | 3 | 7 | 0 | 0 | 0 | 0.8 | 25 | 0.03 | 0 | 268 | 115 | 220 | 0 | 614 | 1112 | 2 | 5897.4 | 12648.07 | 107.8
18:00 | 0 | 59 | 16 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 38 | 35 | 94 | 69 | 260 | 18 | 38 | 102 | 0 | 300 | 153 | 379 | 0 | 50 | 330 | 0 | 0 | 0 | 130 | 26 | 22 | 0 | 0 | 7 | 15 | 31 | 0 | 0 | 66 | 38 | 0 | 0 | 0 | 0 | 221 | 5 | 9 | 285 | 104 | 0 | 50 | 4 | 23 | 204 | 0 | 0 | 0 | 1194 | 0 | 51 | 97 | 0 | 395 | 0 | 280 | 0 | 208 | 0 | 53 | 103 | 100 | 2 | 19 | 35 | 40 | 7 | 0 | 20 | 305 | 0 | 383 | 30 | 57 | 147 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 95 | 35 | 0 | 0 | 6 | 7609 | 848 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1377.7 | 0 | 0 | 0 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 410 | 0 | 0 | 144 | 46 | 80 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 115 | 220 | 0 | 612 | 1113 | 78 | 6120.7 | 13729.7 | 107.8
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 47.6 | 35 | 115 | 90 | 278 | 42 | 55 | 104 | 0 | 300 | 140 | 410 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 32 | 40 | 92 | 0 | 1 | 66 | 38 | 0 | 0 | 0 | 0 | 221 | 65 | 18 | 285 | 60 | 0 | 50 | 8 | 97 | 200 | 0 | 0 | 0 | 1145 | 0 | 51 | 123 | 0 | 400 | 0 | 280 | 0 | 190 | 0 | 90 | 103 | 156 | 8 | 19 | 59 | 38 | 25 | 0 | 28 | 300 | 0 | 334 | 30 | 57 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 77 | 153 | 40 | 0 | 0 | 6 | 8059.6 | 847 | 128 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1435.12 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 145 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 273 | 115 | 220 | 0 | 611 | 1152 | 130 | 6358.12 | 14417.72 | 107.8
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 47.2 | 35 | 115 | 15 | 278 | 0 | 35 | 103 | 0 | 300 | 141 | 410 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 15 | 15 | 30 | 0 | 1 | 66 | 38 | 0 | 0 | 0 | 0 | 222 | 80 | 14 | 285 | 0 | 0 | 50 | 8 | 96 | 200 | 0 | 0 | 0 | 1160 | 0 | 51 | 126 | 0 | 390 | 0 | 280 | 0 | 195 | 0 | 90 | 104 | 171 | 8 | 19 | 0 | 38 | 8 | 0 | 28 | 315 | 0 | 338 | 30 | 57 | 141 | 6 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 77 | 153 | 41 | 0 | 0 | 6 | 7749.2 | 848 | 128 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1441.03 | 0 | 0 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 367 | 0 | 0 | 144 | 47 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 611 | 1170 | 140 | 6365.03 | 14114.23 | 107.8
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 46 | 35 | 116 | 15 | 278 | 0 | 35 | 98 | 0 | 300 | 145 | 419 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 15 | 15 | 24 | 0 | 0 | 66 | 38 | 0 | 0 | 0 | 0 | 222 | 79 | 15 | 285 | 0 | 0 | 50 | 8 | 95 | 200 | 0 | 0 | 0 | 1160 | 0 | 51 | 127 | 0 | 390 | 0 | 280 | 0 | 199 | 0 | 89 | 104 | 172 | 8 | 19 | 0 | 40 | 0 | 0 | 28 | 305 | 0 | 358 | 30 | 57 | 143 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 153 | 40 | 0 | 0 | 6 | 7753 | 848 | 128 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1441.72 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 363 | 0 | 0 | 144 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 611 | 1160 | 136 | 6349.72 | 14102.72 | 107.8
21:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 47.4 | 17 | 116 | 15 | 278 | 0 | 35 | 99 | 0 | 300 | 148 | 455 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 16 | 15 | 12 | 0 | 0 | 66 | 38 | 0 | 0 | 0 | 0 | 222 | 83 | 9 | 285 | 0 | 0 | 50 | 8 | 96 | 187 | 0 | 0 | 0 | 1160 | 0 | 51 | 127 | 0 | 390 | 0 | 280 | 0 | 194 | 0 | 91 | 105 | 179 | 9 | 19 | 0 | 40 | 0 | 0 | 22 | 310 | 0 | 343 | 30 | 57 | 146 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 153 | 47 | 0 | 0 | 6 | 7762.4 | 848 | 128 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1409.79 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 398 | 0 | 0 | 144 | 47 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 612 | 1165 | 140 | 6356.79 | 14119.19 | 107.8
22:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 18 | 17 | 115 | 0 | 284 | 0 | 35 | 96 | 0 | 300 | 147 | 444 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 26.5 | 22 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 66 | 38 | 0 | 0 | 0 | 0 | 222 | 80 | 15 | 285 | 0 | 0 | 50 | 0 | 91 | 187 | 0 | 0 | 0 | 1150 | 0 | 51 | 117 | 0 | 390 | 0 | 280 | 0 | 191 | 0 | 85 | 105 | 176 | 8 | 19 | 0 | 40 | 0 | 0 | 28 | 305 | 0 | 340 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 153 | 61 | 0 | 0 | 6 | 7614.5 | 848 | 128 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1422.8 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 402 | 0 | 0 | 143 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 612 | 1160 | 130 | 6360.8 | 13975.3 | 107.8
23:00 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 16 | 17 | 115 | 0 | 295 | 0 | 35 | 70 | 0 | 300 | 151 | 445 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 26.5 | 22 | 0 | 0 | 15 | 0 | 0 | 0 | 3 | 66 | 38 | 0 | 0 | 0 | 0 | 222 | 80 | 16 | 285 | 0 | 0 | 33 | 0 | 92 | 187 | 0 | 0 | 0 | 1155 | 0 | 51 | 113 | 0 | 387 | 0 | 280 | 0 | 196 | 0 | 38 | 105 | 168 | 0 | 19 | 0 | 42 | 0 | 0 | 22 | 305 | 0 | 351 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 96 | 59 | 0 | 0 | 6 | 7431.5 | 848 | 126 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1412.88 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 145 | 47 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 611 | 1158 | 136 | 6327.88 | 13759.38 | 107.8
Total KWH | 0 | 1008960 | 363840 | 0 | 0 | 0 | 0 | 0 | 8503200 | 0 | 0 | 525600 | 305640 | 1818000 | 378240 | 2698778 | 99821 | 529472 | 1584000 | 0 | 7585500 | 3578298 | 10087727 | 0 | 530613 | 7376940 | 0 | 0 | 125324 | 1395600 | 550200 | 524.16 | 0 | 0 | 205745 | 125455 | 238080 | 0 | 79200 | 824684 | 240000 | 0 | 0 | 0 | 9785 | 5272084 | 797890 | 383520 | 6792727.27 | 187345 | 0 | 800640 | 57929.4 | 1236981 | 4554749 | 0 | 0 | 0 | 27234543 | 57375 | 1242080 | 1699490 | 0 | 8990500 | 0 | 748800 | 0 | 4745000 | 71496 | 1119360 | 2518670 | 2101440 | 44520 | 453180 | 94620 | 855360 | 47981 | 393091 | 159680 | 7444000 | 0 | 9175000 | 716000 | 1343760 | 3635673 | 194976 | 0 | 1973760 | 717408 | 0 | 391000 | 4406530 | 168120 | 1768800 | 1447200 | 1316160 | 9150 | 167090 | 128160 | 158433064.83 | 20463272 | 3680928 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 341280 | 9010909 | 0 | 28958181 | 0 | 0 | 0 | 56448 | 323328 | 0 | 260016 | 0 | 0 | 350320 | 699490 | 0 | 0 | 238496 | 1894364 | 0 | 3691236 | 0 | 0 | 0 | 8915636 | 0 | 17760 | 3569000 | 1093963 | 970293 | 158347 | 700166 | 0 | 0 | 0 | 16918.92 | 941760 | 3430 | 35136 | 6065000 | 2749000 | 5454310 | 0 | 11687272.72 | 26900363.64 | 879600 | 141038224.28 | 299471289.11

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12735.08 | MW | 12:00 Hr. | Energy Generated |  |  | 299.4713 |  | MKWHr.
| Day Peak Demand |  |  | 12735.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14417.72 | MW | 19:00 Hr. | Energy Demand |  |  | 299.4713 |  | MKWHr.
| Evening Peak Demand |  |  | 14417.72 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 10960.48 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 920.03 |  | MMCFD
| Maximum Generation of the Day |  |  | 14417.72 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.0011 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.6824 | 0 | 11.2386 | 0 | 0 | 0.12532 | 0 | 0 | 49.0463 | Gas | 119.0901 | Gas | 425002121.53
| Chattogram Zone |  |  | 4.9383 | 34.0273 | 4.7147 | 0 | 5.2721 | 0.06716 | 0 | 0.0792 | 49.0987 | Coal | 92.3538 | Coal | 509997526.1452
| Cumilla Zone |  |  | 18.7697 | 0 | 5.2671 | 0 | 0 | 0.39309 | 0.85536 | 0 | 25.2853 | HFO | 27.9577 | HFO | 508675021.732
| Mymensingh Zone |  |  | 1.3162 | 0 | 3.5123 | 0 | 0 | 0.17624 | 0 | 0 | 5.0047 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.9981 | Hydro | 5.2721 | Hydro | 527208.4
| Khulna Zone |  |  | 3.6809 | 9.0109 | 0 | 0 | 0 | 0.34128 | 21.3753 | 0 | 34.4084 | Solar | 3.5296 | Solar | 51245349.3832
| Barishal Zone |  |  | 8.2033 | 44.6526 | 0.91474 | 0 | 0 | 0.00343 | 0 | 0 | 53.7741 | Import | 51.1888 | Import | 300550779.45
| Rajshahi Zone |  |  | 14.5012 | 0 | 0.63979 | 0 | 0 | 1.3061 | 28.9582 | 0 | 45.4053 | Wind | 0.0792 | Wind | 1167408
| Rangpur Zone |  |  | 0 | 4.663 | 1.6705 | 0 | 0 | 1.117 | 0 | 0 | 7.4504
| Total |  |  | 119.0901 | 92.3538 | 27.9577 | 0 | 5.2721 | 3.5296 | 51.1888 | 0.0792 | 299.4713
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 425002121.53 |  | Hydro | 527208.4
|  |  |  | Coal | 509997526.1452 |  | Solar | 51245349.3832
|  |  |  | HFO | 508675021.732 |  | Import | 300550779.45
|  |  |  | HSD | 0 |  | Wind | 1167408
[5 empty] | Total: | 179,71,65,414 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4633 | Peak Hr Flow | 847.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37415842.96 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.9582 | Peak Hr Flow | 1435.12 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1931 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.85536 | Peak Hr Flow | 38.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2606 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.2768 | Peak Hr Flow | 2320.12 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5213
|  |  |  | Chattogram |  | 0 |  | 1348
|  |  |  | Cumilla |  | 0 |  | 1373
|  |  |  | Mymensingh |  | 0 |  | 1141
|  |  |  | Sylhet |  | 0 |  | 542
|  |  |  | Khulna |  | 0 |  | 1586
|  |  |  | Barishal |  | 0 |  | 434
|  |  |  | Rajshahi |  | 0 |  | 1354
|  |  |  | Rangpur |  | 0 |  | 869
|  |  |  | Total |  | 0 |  | 13860
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 16:50 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Annual Maintenence Work.
| 08:08 | 16:49 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Annual Maintenence Work.
| 08:20 | 16:54 | Jaldhaka 132/33kV S/S 416T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:21 | 16:53 | Jaldhaka 132/33kV S/S 416T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:25 | 14:52 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Annual
maintenance work
| 08:31 | 17:04 | Meghnaghat 400/230kV S/S 400 kV Bus -01 Project Work S/D Due to Project work shutdown.
| 08:35 |  | Ghatail 132/33kV S/S T-1 LT Scheduled S/D Due to Neutral Bushing oil leakage
| 08:36 |  | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Neutral Bushing oil leakage
| 08:42 | 16:22 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D
| 08:42 | 16:24 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D
| 09:14 |  | Siddhirganj 132/33kV S/S T-1 LT Scheduled S/D Due to Schedule Shutdown by DPDC.
| 09:15 |  | Siddhirganj 132/33kV S/S T-1 HT Scheduled S/D Due to Schedule Shutdown by DPDC.
| 09:40 | 17:27 | Thakurgaon 132/33kV S/S T-1(422T) HT Scheduled S/D Due to For Annual maintenance
| 09:40 | 17:27 | Thakurgaon 132/33kV S/S T-1(422T) LT Scheduled S/D Due to For Annual maintenance
| 10:52 |  | Sirajganj 225 MW CCPP Unit-1 ST was shutdown due to gas shortage.
| 11:03 | 12:36 | Mithapukur 132/33kV S/S TR-2 (414T) HT Forced S/D Due to For 33kV incomer CT (B-phase) | [7 empty] | 12.0MW load
|  |  | red-hot maintenance work. | [7 empty] | interrup.
| 11:03 | 12:37 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to For 33kV incomer CT (B-phase) | [7 empty] | 12.0MW load
|  |  | red-hot maintenance work. | [7 empty] | interrup.
| 11:18 | 11:52 | Madunaghat-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to Forced
shutdown due to flushing at DS point.
| 11:24 | 11:59 | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing Main
protection-01, REL670 relays Due to Rangamati Ckt-02 tripped due to thundering.
| 11:33 | 11:43 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Rangpur 132/33kV end showing QUADRAMHO | [7 empty] | 30.0MW load
|  |  | SHPM 101 relays Due to Unknown | [7 empty] | interrup. Rangpur
132/33kV end
| 11:52 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 11:54 | 17:16 | Lakshmipur 132/33kV S/S Transformer-1 HT Project Work S/D Due to asd | [7 empty] | 10.0MW load
interrup.
| 11:54 | 17:16 | Lakshmipur 132/33kV S/S Transformer-1 LT Project Work S/D Due to RTCC PANEL PROBLEM | [7 empty] | 10.0MW load
interrup.
| 12:00 |  | Day Peak Generation is 12730 MW.
| 12:08 | 16:54 | BIPTC S/S Block-01, Trafo-02 HT Scheduled S/D Due to Oil leakage in 33/0.4 KV 2 MVA
Auxiliary Transformer.
| 12:09 |  | Sirajganj 225 MW CCPP Unit-1 GT was shutdown due to gas shortage.
| 12:09 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 12:39 |  | Madunaghat-Meghnaghat 400kV Ckt-1 Forced S/D from Meghnaghat 400/230kV end Due to Forced
shutdown due to flushing at DS point.
| 12:56 | 13:10 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Lockout & O/C,E/F Relay relays Due to
Shaistaganj Feeder fault
| 12:56 | 13:11 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing 132 & 33 KV Side Lockout Relay & OC/EF
relays Due to Shayestagonj feeder fault
| 12:56 | 13:18 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Locout Relay O/C,E/F Relay relays Due
to Shaistaganj Feeder Fault
| 12:56 | 13:15 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Lockout Relay, O/C,E/F Relay relays Due
to Shaistaganj Feeder
| 13:13 | 14:46 | Panchagarh 132/33kV S/S T-1(407T) HT Forced S/D Due to Red hot of 33kV bus section 01
Y-Phase
| 13:29 | 14:22 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing | [7 empty] | 21.0MW load
|  |  | Distance relays. | [7 empty] | interrup.
Brahmanbaria
132/33kV end
| 13:29 | 14:22 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing | [7 empty] | 20.0MW load
|  |  | Distance Relay relays. | [7 empty] | interrup.
Brahmanbaria
132/33kV end
| 15:26 |  | Meghnaghat 400/230kV S/S Meghnaghat-Reliance PP 400KV Ckt-2 Scheduled S/D Due to shutdown
due to maintenance work at Reliance ckt-2 DS point.
| 15:46 | 17:49 | Jashore 132/33kV S/S T-1 LT Forced S/D Due to 33kv busbur PBS riser maintanence. | [7 empty] | 10.0MW load
interrup.
| 15:46 | 17:49 | Jashore 132/33kV S/S T-1 HT Forced S/D Due to 33kv busbur PBS riser maintanence. | [7 empty] | 10.0MW load
interrup.
|  | 16:41 | Chandraghona-Madunaghat 132 kV Ckt-1 is restored.
| 17:08 | 18:27 | Lakshmipur 132/33kV S/S Transformer-2 LT Project Work S/D Due to RTCC Panel Announciator
Problem
| 17:15 | 17:21 | AKSML-Baroaulia 132kV Ckt-1 Tripped from Baroaulia 132/33kV end showing Null relays Due
to Unexpected
|  | 17:35 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
| 18:49 | 19:31 | Madaripur-Shariatpur 132kV Ckt-2 Tripped from Madaripur 132/33kV end showing Distance
Relay relays Due to lightning and from Shariatpur 132/33kV end showing Distance
Relay(Main protection) relays Due to Distance Trip(Main Protection
Operate) Zone-1 Trip
|  | 20:06 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 21:30 | 22:22 | Bhangura 132/33kV S/S 33KV Single Bus Forced S/D Due to Red hot remove | [7 empty] | 37.0MW load
interrup.
|  | 22:42 | Baroaulia-KSRM 132 kV Ckt-1 is restored.
|  | 22:47 | KSRM 132/33kV S/S Baraulia Main is restored.
|  | 22:50 | KSRM 132/33kV S/S Transformer-02 LT is restored.
|  | 22:52 | KSRM 132/33kV S/S Transformer-01 HT is restored.
|  | 22:59 | KSRM 132/33kV S/S Transformer-03 LT is restored.
| 06:00 |  | -
| 06:00 |  | Minimum Generation is 11377 MW.
| 07:08 |  | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Red hot maintenance (Atrai 33kV feeder)
| 07:09 |  | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Red hot maintenance (Atrai 33kV feeder)
| 07:31 |  | Meghnaghat 400/230kV S/S 400 kV Bus -02 Scheduled S/D Due to 400 kV Bus- 02 shutdown for
project work.
| 07:57 |  | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
for annual maintenance and deadline checking. and from Chandraghona 132/33kV end Due to
Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 343 | 8503200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7585500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3578298 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 42 | 99821 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7376940 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.6 | 525600 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 90 | 378240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 529472 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 530613 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 550200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 524.16 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 363840 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 2698778 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1818000 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1008960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 104 | 1584000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 125324 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 305640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 410 | 10087727 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1395600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2626.6 | 49046277.16
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 57929.4 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 57375 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 800640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5272084 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 200 | 4554749 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1236981 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 240000 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 824684 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 383520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 238080 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9785 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 40 | 125455 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 65 | 797890 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 32 | 205745 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 60 | 187345 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 27234543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 79200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6792727.27 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2418 | 49098732.67
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4745000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 748800 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 400 | 8990500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 71496 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1242080 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 1699490 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 159680 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2518670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 2101440 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 38 | 855360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 47981 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 453180 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 59 | 94620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 44520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1119360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 393091 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1570 | 25285268
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 40 | 1316160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 1447200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1768800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 167090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 128160 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 168120 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 276 | 5004680
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1343760 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3635673 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717408 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1973760 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 4406530 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 391000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 194976 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7444000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 334 | 9175000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1169 | 29998107
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 847 | 20463272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 128 | 3680928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 341280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 370 | 9010909 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1383 | 34408389
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 611 | 11687272.72 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 35136 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2749000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1152 | 26900363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5454310 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 130 | 879600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 6065000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3430 | -
Barishal Area Total |  |  |  |  | 2858 | 2517 | 53774112.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 350320 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 1894364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3691236 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 340 | 8915636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 260016 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 87 | 323328 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 56448 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1435.12 | 28958181 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 238496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 699490 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2053.12 | 45405275
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1093963 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 145 | 3569000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 700166 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 16918.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 970293 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158347 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 941760 | -
Rangpur Area Total |  |  |  |  | 950 | 405 | 7450447.92
Eastern Grid Total |  |  |  |  | 17385.715 | 8059.6 | 158433064.83
Western Grid Total |  |  |  |  | 10980.24 | 6358.12 | 141038224.28
National Grid Total |  |  |  |  | 28365.955 | 14417.72 | 299471289.11
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9616.77 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4241.8 | MW
i) Dhaka area |  |  | 5212.98 |  | MW | i) Khulna area |  |  |  | 1585.7 | MW
ii) Chattogram area |  |  | 1347.5 |  | MW | ii) Barishal area |  |  |  | 433.5 | MW
iii) Cumilla area |  |  | 1373.29 |  | MW | iii) Rajshahi area |  |  |  | 1353.6 | MW
iv) Mymensingh area |  |  | 1141 |  | MW | iv) Rangpur area |  |  |  | 869 | MW
v) Sylhet area |  |  | 542 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13858.57 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 00:00 | 133 | PHP | 6 | 18:30
2 | AKSML | 138 | 15:00 | 68 | Ishurdi | 77 | 18:30 | 134 | Pabna | 100 | 18:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 72 | 18:30 | 135 | Palashbari | 104 | 18:30
4 | Agargaon | 135 | 13:00 | 70 | Jamalpur | 120 | 20:00 | 136 | Panchagarh | 49 | 18:30
5 | Agrabad | 84 | 14:00 | 71 | Jashore | 130 | 23:00 | 137 | Patiya | 11 | 00:00
6 | Amnura | 24 | 20:00 | 72 | Jhenaidah | 125 | 18:30 | 138 | Patuakhali | 67 | 23:00
7 | Ashuganj | 87 | 17:00 | 73 | Joydebpur | 147 | 18:30 | 139 | Payra | 30 | 00:00
8 | BSRM | 110 | 19:00 | 74 | Joypurhat | 58 | 18:30 | 140 | Postogola | 63 | 15:00
9 | Bagerhat | 77 | 00:00 | 75 | Juldah | 18 | 00:00 | 141 | Purbachal | 19 | 13:00
10 | Bajitpur | 69 | 00:00 | 76 | KSRM | 0 | 00:00 | 142 | Purbasadipur | 110 | 18:30
11 | Bakulia | 94 | 18:00 | 77 | Kabirpur | 250 | 09:00 | 143 | Rahanpur | 34 | 21:00
12 | Banani | 50 | 12:00 | 78 | Kachua | 94 | 21:00 | 144 | Rahim | 25 | 12:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kallyanpur | 99 | 13:00 | 145 | Rajbari | 84 | 18:30
14 | Barapukuria | 59 | 18:30 | 80 | Kalurghat | 40 | 11:00 | 146 | Rajendrapur | 123 | 18:30
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 80 | 12:00 | 147 | Rajshahi | 94 | 22:00
16 | Barishal | 109 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 88 | 13:00
17 | Barishal-230 | 96 | 18:30 | 83 | Kasba | 34 | 21:00 | 149 | Ramganj | 120 | 18:00
18 | Baroaulia | 61 | 14:00 | 84 | Kazla | 97 | 13:00 | 150 | Rampur | 43 | 00:00
19 | Baroirhat | 61 | 19:00 | 85 | Keranigonj | 94 | 18:30 | 151 | Rangamati | 16 | 18:00
20 | Bashundhara | 191 | 14:00 | 86 | Khagrachori | 26 | 19:30 | 152 | Rangpur | 141 | 18:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 70 | 13:00 | 153 | Ruppur | 7.6 | 15:00
22 | Beanibazar | 70 | 00:00 | 88 | Khulshi | 180 | 00:00 | 154 | SSM | 14 | 01:00
23 | Benapole | 70 | 18:30 | 89 | Kishoreganj | 118 | 19:00 | 155 | Saidpur | 96 | 18:30
24 | Bhaluka | 156 | 18:00 | 90 | Kodda | 282 | 19:00 | 156 | Satkhira | 117 | 19:30
25 | Bhandaria | 51 | 23:00 | 91 | Kulaura | 47 | 00:00 | 157 | Satmasjid | 100 | 13:00
26 | Bhangura | 38 | 23:00 | 92 | Kurigram | 62 | 18:30 | 158 | Savar | 224 | 12:00
27 | Bheramara(GK) | 65 | 18:30 | 93 | Kushtia | 152 | 18:30 | 159 | SevenRings | 10.06 | 00:00
28 | Bhulta | 214 | 10:00 | 94 | Laksam | 38 | 21:00 | 160 | ShahCement | 29 | 07:00
29 | Bog-Sherpur | 72 | 18:30 | 95 | Lakshmipur | 31 | 00:00 | 161 | Shahjadpur | 88 | 21:00
30 | Bogura | 150 | 19:00 | 96 | Lalbag | 61 | 13:00 | 162 | Shahjibazar | 119 | 00:00
31 | Borhanuddin | 94 | 22:00 | 97 | Lalmonirhat | 58 | 18:30 | 163 | Shahmirpur | 60 | 18:30
32 | Brahmanbaria | 126 | 00:00 | 98 | MI_Cement | 17 | 11:00 | 164 | Shariatpur | 86 | 21:00
33 | Cantonment | 138 | 13:00 | 99 | Madanganj | 32 | 12:00 | 165 | Sherpur | 148 | 18:30
34 | Chandina | 14.59 | 18:30 | 100 | Madaripur | 110 | 21:00 | 166 | Shikalbaha | 21 | 00:00
35 | Chandpur | 82 | 21:00 | 101 | Madartek | 84 | 22:00 | 167 | Shitalakhya | 85.7 | 12:00
36 | Chandraghona | 33 | 00:00 | 102 | Madunaghat | 55 | 18:00 | 168 | Sholosohor | 48 | 18:00
37 | Chapai | 60 | 20:00 | 103 | Magura | 66 | 18:30 | 169 | Shyampur | 98 | 00:00
38 | Charsaidpur | 36 | 11:00 | 104 | Mahasthangarh | 70 | 18:30 | 170 | Siddhirganj | 121 | 14:00
39 | Chauddagram | 70 | 18:00 | 105 | Maijdee | 21 | 21:00 | 171 | Sirajganj | 106 | 20:00
40 | Chhatak | 34 | 00:00 | 106 | Manikganj | 126 | 21:00 | 172 | Sonargaon | 134 | 15:00
41 | Chowmuhani | 189 | 18:30 | 107 | Maniknagar | 66 | 13:00 | 173 | Sreemongol | 76 | 00:00
42 | Chuadanga | 111 | 18:30 | 108 | Matarbari | 50 | 02:00 | 174 | Sreepur | 110 | 18:30
43 | Coxsbazar | 134 | 00:00 | 109 | Matuail | 68 | 15:00 | 175 | Srinagar | 45.73 | 22:00
44 | Cumilla(N) | 137 | 19:00 | 110 | Millgate | 125 | 16:00 | 176 | Sunamganj | 56 | 21:00
45 | Cumilla(S) | 150 | 18:00 | 111 | Mirpur | 119 | 12:00 | 177 | Sylhet | 49 | 00:00
46 | Daganbhuiyan | N/A | N/A | 112 | Mirsorai | 11 | 14:00 | 178 | Sylhet-132 | 111 | 18:00
47 | Daudkandi | 150 | 21:00 | 113 | Mirzapur | 46 | 00:00 | 179 | TK | 24 | 00:00
48 | DhakaUniversity | 90 | 13:00 | 114 | Mithapukur | 62 | 19:30 | 180 | Tangail | 158 | 21:00
49 | Dhamrai | 126 | 15:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 22 | 18:30
50 | Dhanmondi | 130 | 13:00 | 116 | Mogbazar | 96.6 | 14:00 | 182 | Thakurgaon | 91 | 18:30
51 | Dohazari | 105 | 18:30 | 117 | Mongla | 29 | 00:00 | 183 | Tongi | 119 | 12:00
52 | Faridpur | 162 | 18:30 | 118 | Motijheel | 49 | 13:00 | 184 | Ullahpara | 37 | 18:30
53 | Fatullah | 111 | 12:00 | 119 | Muktagacha | 34 | 18:00 | 185 | Ullon | 50 | 18:00
54 | Fenchuganj | 40 | 01:00 | 120 | Munshiganj | 110 | 23:00 | 186 | Uttara | 83 | 13:00
55 | Feni | 115 | 18:30 | 121 | Muradnagar | 39 | 18:30 | 187 | UttaraNew | 56 | 13:00
56 | GPH | 3 | 00:00 | 122 | Mymensingh | 187 | 18:30 | 188 | Zigatola | 68 | 12:00
57 | Ghatail | 81 | 18:00 | 123 | Naogaon | 109 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 56.5 | 18:30
59 | Ghorashal-230 | 94 | 13:00 | 125 | Narinda | 62 | 18:00
60 | Goalpara | 36 | 00:00 | 126 | Narshingdi | 169 | 00:00
61 | Gollamari | 88 | 13:00 | 127 | Natore | 142 | 18:30
62 | Gopalganj | 92 | 00:00 | 128 | Nawabganj | 42.8 | 20:00
63 | Gulshan | 124 | 13:00 | 129 | Netrakona | 122 | 21:00
64 | Halishahar | 77 | 11:00 | 130 | New | 57 | 15:00
65 | HaripurSBU | 140 | 17:00 | 131 | Niamatpur | 64 | 19:30
66 | Hasnabad | 82 | 19:00 | 132 | Noapara | 53 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12962.03 | 0 |  | 12962.03
1:00 | 12579.84 | 0 |  | 12579.84
2:00 | 12189.57 | 0 |  | 12189.57
3:00 | 11736.13 | 0 |  | 11736.13
4:00 | 11489.58 | 0 |  | 11489.58
5:00 | 11187.05 | 0 |  | 11187.05
6:00 | 10960.48 | 0 |  | 10960.48
7:00 | 11201.43 | 0 |  | 11201.43
8:00 | 11370.06 | 0 |  | 11370.06
9:00 | 11554.11 | 0 |  | 11554.11
10:00 | 11776.41 | 0 |  | 11776.41
11:00 | 12073.32 | 0 |  | 12073.32
12:00 | 12735.08 | 0 |  | 12735.08
13:00 | 12977.29 | 0 |  | 12977.29
14:00 | 12934.49 | 0 |  | 12934.49
15:00 | 12927.75 | 0 |  | 12927.75
16:00 | 12685.14 | 0 |  | 12685.14
17:00 | 12648.07 | 0 |  | 12648.07
18:00 | 13729.7 | 0 |  | 13729.7
19:00 | 14417.72 | 0 |  | 14417.72
19:30 | 14114.23 | 0 |  | 14114.23
20:00 | 14102.72 | 0 |  | 14102.72
21:00 | 14119.19 | 0 |  | 14119.19
22:00 | 13975.3 | 0 |  | 13975.3
23:00 | 13759.38 | 0 |  | 13759.38
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7112.5 | 5849.53 | 12962.03 | DAILY GENERATION CURVE
00:30 | 7044 | 5726.935 | 12770.935
01:00 | 6975.5 | 5604.34 | 12579.84 | 06-10-2025
01:30 | 6822 | 5562.705 | 12384.705
02:00 | 6668.5 | 5521.07 | 12189.57
02:30 | 6534.5 | 5428.35 | 11962.85
03:00 | 6400.5 | 5335.63 | 11736.13
03:30 | 6274.5 | 5338.355 | 11612.855
04:00 | 6148.5 | 5341.08 | 11489.58
04:30 | 6057.5 | 5280.815 | 11338.315
05:00 | 5966.5 | 5220.55 | 11187.05
05:30 | 5920.015 | 5153.75 | 11073.765
06:00 | 5873.53 | 5086.95 | 10960.48
06:30 | 5903.015 | 5177.94 | 11080.955
07:00 | 5932.5 | 5268.93 | 11201.43
07:30 | 5986.195 | 5299.55 | 11285.745
08:00 | 6039.89 | 5330.17 | 11370.06
08:30 | 6045.615 | 5416.47 | 11462.085
09:00 | 6051.34 | 5502.77 | 11554.11
09:30 | 6096.755 | 5568.505 | 11665.26
10:00 | 6142.17 | 5634.24 | 11776.41
10:30 | 6360.45 | 5564.415 | 11924.865
11:00 | 6578.73 | 5494.59 | 12073.32
11:30 | 6735.185 | 5669.015 | 12404.2
12:00 | 6891.64 | 5843.44 | 12735.08
12:30 | 6938.665 | 5917.52 | 12856.185
13:00 | 6985.69 | 5991.6 | 12977.29
13:30 | 6940.72 | 6015.17 | 12955.89
14:00 | 6895.75 | 6038.74 | 12934.49
14:30 | 6907.185 | 6023.935 | 12931.12
15:00 | 6918.62 | 6009.13 | 12927.75
15:30 | 6863.545 | 5942.9 | 12806.445
16:00 | 6808.47 | 5876.67 | 12685.14
16:30 | 6779.57 | 5887.035 | 12666.605
17:00 | 6750.67 | 5897.4 | 12648.07
17:30 | 7179.835 | 6009.05 | 13188.885
18:00 | 7609 | 6120.7 | 13729.7
18:30 | 7834.3 | 6239.41 | 14073.71
19:00 | 8059.6 | 6358.12 | 14417.72
19:30 | 7749.2 | 6365.03 | 14114.23
20:00 | 7753 | 6349.72 | 14102.72
20:30 | 7757.7 | 6353.255 | 14110.955 |  | Executive Engineer
21:00 | 7762.4 | 6356.79 | 14119.19 |  | Network Operation Division
21:30 | 7688.45 | 6358.795 | 14047.245
22:00 | 7614.5 | 6360.8 | 13975.3
22:30 | 7523 | 6344.34 | 13867.34
23:00 | 7431.5 | 6327.88 | 13759.38

## En-Curve
QF-LDC-12
Date | 06-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3514 | 1775.5 | 833 | 38 | 40 | 1307.53 | 219 | 3820 | 0 | 254 | 1160 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 3482 | 1748 | 833 | 38 | 39 | 1253.435 | 218.5 | 3754.5 | 0 | 254.5 | 1136.5 | 0 | 0 | 13.5 | 0 | 06-10-2025
01:00 | 3450 | 1720.5 | 833 | 38 | 38 | 1199.34 | 218 | 3689 | 0 | 255 | 1113 | 0 | 0 | 26 | 0
01:30 | 3438 | 1723 | 835.5 | 38 | 38 | 1206.205 | 218 | 3666 | 0 | 195.5 | 1007 | 0 | 0 | 19.5 | 0 | Energy Generated | 299.4713 |  | MKWHr
02:00 | 3426 | 1725.5 | 838 | 38 | 38 | 1213.07 | 218 | 3643 | 0 | 136 | 901 | 0 | 0 | 13 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3427.5 | 1714.5 | 837.5 | 38 | 37 | 1159.85 | 217.5 | 3638 | 0 | 127.5 | 754.5 | 0 | 0 | 11 | 0 | Total Energy Requirement | 299.4713 |  | MKWHr
03:00 | 3429 | 1703.5 | 837 | 38 | 36 | 1106.63 | 217 | 3633 | 0 | 119 | 608 | 0 | 0 | 9 | 0
03:30 | 3427.5 | 1703.5 | 836.5 | 38 | 36 | 1109.855 | 217.5 | 3627.5 | 0 | 101.5 | 508.5 | 0 | 0 | 6.5 | 0
04:00 | 3426 | 1703.5 | 836 | 38 | 36 | 1113.08 | 218 | 3622 | 0 | 84 | 409 | 0 | 0 | 4 | 0
04:30 | 3471.5 | 1716.5 | 839.5 | 38 | 35 | 1064.315 | 218.5 | 3560 | 0 | 71 | 322 | 0 | 0 | 2 | 0
05:00 | 3517 | 1729.5 | 843 | 38 | 34 | 1015.55 | 219 | 3498 | 0 | 58 | 235 | 0 | 0 | 0 | 0
05:30 | 3505 | 1735 | 843 | 38 | 33 | 1013.525 | 219.5 | 3434.5 | 0.74 | 58 | 193.5 | 0 | 0 | 0 | 0
06:00 | 3493 | 1740.5 | 843 | 38 | 32 | 1011.5 | 220 | 3371 | 1.48 | 58 | 152 | 0 | 0 | 0 | 0
06:30 | 3524.5 | 1743.25 | 843 | 38 | 31 | 1020.5 | 220 | 3423.5 | 22.705 | 61 | 152.5 | 0 | 0 | 1 | 0
07:00 | 3556 | 1746 | 843 | 38 | 30 | 1029.5 | 220 | 3476 | 43.93 | 64 | 153 | 0 | 0 | 2 | 0
07:30 | 3567.5 | 1743 | 845.5 | 38 | 30 | 1025.885 | 220 | 3484.5 | 86.86 | 77 | 166.5 | 0 | 0 | 1 | 0
08:00 | 3579 | 1740 | 848 | 38 | 30 | 1022.27 | 220 | 3493 | 129.79 | 90 | 180 | 0 | 0 | 0 | 0
08:30 | 3550.5 | 1732.5 | 848 | 38 | 30 | 1022.01 | 220 | 3574.5 | 191.075 | 73.5 | 182 | 0 | 0 | 0 | 0
09:00 | 3522 | 1725 | 848 | 38 | 30 | 1021.75 | 220 | 3656 | 252.36 | 57 | 184 | 0 | 0 | 0 | 0
09:30 | 3514.5 | 1734.5 | 848 | 38 | 29 | 976.53 | 220 | 3722.5 | 304.23 | 57 | 221 | 0 | 0 | 0 | 0
10:00 | 3507 | 1744 | 848 | 38 | 28 | 931.31 | 220 | 3789 | 356.1 | 57 | 258 | 0 | 0 | 0 | 0
10:30 | 3488.5 | 1785.5 | 848 | 38 | 29 | 929.605 | 220 | 3794.5 | 356.01 | 61.5 | 367.75 | 0 | 0 | 6.5 | 0
11:00 | 3470 | 1827 | 848 | 38 | 30 | 927.9 | 220 | 3800 | 355.92 | 66 | 477.5 | 0 | 0 | 13 | 0
11:30 | 3473 | 1843.75 | 848 | 38 | 31 | 993.135 | 220 | 3849.5 | 423.615 | 92 | 585.7 | 0 | 0 | 6.5 | 0
12:00 | 3476 | 1860.5 | 848 | 38 | 32 | 1058.37 | 220 | 3899 | 491.31 | 118 | 693.9 | 0 | 0 | 0 | 0
12:30 | 3430 | 1853.25 | 848 | 38 | 35 | 1108.555 | 219 | 3907.5 | 507.98 | 117.5 | 791.4 | 0 | 0 | 0 | 0
13:00 | 3384 | 1846 | 848 | 38 | 38 | 1158.74 | 218 | 3916 | 524.65 | 117 | 888.9 | 0 | 0 | 0 | 0
13:30 | 3329 | 1807 | 848 | 38 | 36 | 1211.39 | 217.5 | 3949.5 | 506.25 | 117 | 896.25 | 0 | 0 | 0 | 0
14:00 | 3274 | 1768 | 848 | 38 | 34 | 1264.04 | 217 | 3983 | 487.85 | 117 | 903.6 | 0 | 0 | 0 | 0
14:30 | 3314 | 1768.5 | 848 | 38 | 35 | 1262.065 | 217.5 | 3990 | 438.305 | 108.5 | 910.75 | 0 | 0 | 0.5 | 0
15:00 | 3354 | 1769 | 848 | 38 | 36 | 1260.09 | 218 | 3997 | 388.76 | 100 | 917.9 | 0 | 0 | 1 | 0
15:30 | 3365.5 | 1778.5 | 848 | 38 | 36 | 1263.82 | 218.5 | 4000 | 279.225 | 108 | 870.4 | 0 | 0 | 0.5 | 0
16:00 | 3377 | 1788 | 848 | 38 | 36 | 1267.55 | 219 | 4003 | 169.69 | 116 | 822.9 | 0 | 0 | 0 | 0
16:30 | 3361 | 1793 | 848.5 | 38 | 35 | 1316.33 | 219.5 | 3983.5 | 118.875 | 151.5 | 801.4 | 0 | 0 | 0 | 0
17:00 | 3345 | 1798 | 849 | 38 | 34 | 1365.11 | 220 | 3964 | 68.06 | 187 | 779.9 | 0 | 0 | 0 | 0
17:30 | 3392 | 1759 | 848.5 | 38 | 37 | 1371.405 | 220.5 | 4005 | 34.03 | 292.5 | 1190.95 | 0 | 0 | 0 | 0
18:00 | 3439 | 1720 | 848 | 38 | 40 | 1377.7 | 221 | 4046 | 0 | 398 | 1602 | 0 | 0 | 0 | 0
18:30 | 3342 | 1732 | 847.5 | 38 | 39 | 1406.41 | 221 | 4037 | 0 | 450 | 1960.3 | 0 | 0 | 0.5 | 0
19:00 | 3245 | 1744 | 847 | 38 | 38 | 1435.12 | 221 | 4028 | 0 | 502 | 2318.6 | 0 | 0 | 1 | 0
19:30 | 3290 | 1746 | 848 | 38 | 38 | 1441.03 | 222 | 4062 | 0 | 432 | 1996.2 | 0 | 0 | 1 | 0
20:00 | 3303 | 1752 | 848 | 38 | 40 | 1441.72 | 222 | 4053 | 0 | 425 | 1980 | 0 | 0 | 0 | 0
20:30 | 3313 | 1772.5 | 848 | 38 | 40 | 1425.755 | 222 | 4055 | 0 | 422 | 1974.7 | 0 | 0 | 0 | 0
21:00 | 3323 | 1793 | 848 | 38 | 40 | 1409.79 | 222 | 4057 | 0 | 419 | 1969.4 | 0 | 0 | 0 | 0
21:30 | 3321 | 1790.75 | 848 | 38 | 40 | 1416.295 | 222 | 4048.5 | 0 | 405.5 | 1917.2 | 0 | 0 | 0 | 0
22:00 | 3319 | 1788.5 | 848 | 38 | 40 | 1422.8 | 222 | 4040 | 0 | 392 | 1865 | 0 | 0 | 0 | 0
22:30 | 3330.5 | 1791.5 | 848 | 38 | 41 | 1417.84 | 222 | 4044.5 | 0 | 389 | 1743.5 | 0 | 0 | 1.5 | 0
23:00 | 3342 | 1794.5 | 848 | 38 | 42 | 1412.88 | 222 | 4049 | 0 | 386 | 1622 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 03:00 | 369 | 11:00 | Payra | 411 | 06:00 | 407 | 13:00
Ashuganj | 402 | 2:00 | 380 | 11:00 | Rahanpur | 406 | 06:00 | 392 | 20:00
Bhulta | 400 | 02:00 | 377 | 11:00 | Rampal | 399 | 06:00 | 387 | 20:00
Bibiana | 388 | 02:00 | 381 | 11:00
BIPTC | 403 | 02:00 | 395 | 19:00
Bogura | 395 | 05:00 | 379 | 20:00
Gopalganj | 394 | 05:00 | 383 | 15:00
Kaliakoir | 374 | 06:00 | 360 | 11:00
Madunaghat | 394 | 19:00 | 385 | 11:00
Meghnaghat | 385 | 02:00 | 372 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 220 | 11:00 | Kaliakoir | 233 | 01:00 | 223 | 11:00
AKSML | 232 | 18:00 | 225 | 10:00 | Keranigonj | 227 | 06:00 | 217 | 11:00
Aminbazar | 231 | 06:00 | 221 | 11:00 | Khulna(S) | 229 | 06:00 | 215 | 22:00
Ashuganj | 235 | 06:00 | 222 | 11:00 | Madunaghat | 233 | 05:00 | 227 | 10:00
Ashuganj-400 | 334 | 2:00 | 218 | 11:00 | Madunaghat-400 | 235 | 19:00 | 227 | 11:00
Baghabari | 235 | 06:00 | 225 | 15:00 | Maniknagar | 222 | 04:00 | 212 | 11:00
Barapukuria | 225 | 01:00 | 219 | 15:00 | Meghnaghat | 230 | 04:00 | 220 | 11:00
Barapukuria-230 | 225 | 1:00 | 218 | 16:00 | Meghnaghat-400 | 225 | 01:00 | 218 | 11:00
Barishal | 232 | 06:00 | 226 | 18:00 | Mirsorai | 234 | 18:30 | 222 | 11:00
Bheramara | 234 | 06:00 | 223 | 18:00 | Rajshahi | 232 | 06:00 | 219 | 18:00
Bhulta | 231 | 02:00 | 214 | 11:00 | Rampal | 229 | 06:00 | 217 | 22:00
Bibiana | 228 | 06:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 236 | 06:00 | 222 | 18:00 | Rampura | 228 | 01:00 | 213 | 11:00
Bogura | 237 | 06:00 | 227 | 18:00 | Shikalbaha | 234 | 18:30 | 224 | 10:00
Bogura-400 | 236 | 05:00 | 227 | 20:00 | Shyampur | 233 | 00:00 | 216 | 11:00
Borhanuddin | 236 | 06:00 | 231 | 18:00 | Siddhirganj | 224 | 04:00 | 220 | 12:00
BSRM | 232 | 18:30 | 221 | 10:00 | Sirajgonj | 240 | 05:00 | 232 | 18:00
Cumilla(N) | 227 | 04:00 | 219 | 11:00 | Sreepur | 227 | 00:00 | 221 | 10:00
Faridpur | 229 | 06:00 | 221 | 22:00 | Tongi | 230 | 04:00 | 215 | 11:00
Fenchuganj | 230 | 05:00 | 226 | 11:00
Ghorashal | 235 | 02:00 | 230 | 00:00
Ghorashal-230 | 228 | 01:00 | 215 | 11:00
Gopalganj | 232 | 06:00 | 225 | 15:00
GPH | 233 | 18:30 | 225 | 10:00
Haripur | 223 | 04:00 | 215 | 11:00
Hasnabad | 226 | 04:00 | 217 | 11:00
Hathazari | 231 | 18:00 | 28 | 06:00
Ishurdi | 236 | 06:00 | 224 | 18:00
Jhenaidah | 229 | 06:00 | 216 | 21:00
Kachua | 220 | 19:00 | 213 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 22:00 | 124 | 12:00 | Lalmonirhat | 130 | 06:00 | 123 | 15:00
Agargaon | 136 | 05:00 | 127 | 12:00 | Madanganj | 129 | 18:00 | 124 | 10:00
Agrabad | 133 | 18:30 | 128 | 07:00 | Madaripur | 134 | 05:00 | 129 | 20:00
AKS | 132 | 18:30 | 128 | 08:00 | Madartek | 134 | 02:00 | 123 | 11:00
Aminbazar | 136 | 06:00 | 129 | 12:00 | Madunaghat | 134 | 00:00 | 131 | 10:00
Amnura | 137 | 03:00 | 126 | 18:00 | Magura | 132 | 06:00 | 122 | 22:00
Ashuganj | 140 | 03:00 | 136 | 11:00 | Mahasthangarh | 133 | 06:00 | 126 | 18:00
Bagerhat | 130 | 06:00 | 115 | 22:00 | Maijdee | 131 | 18:30 | 126 | 23:00
Bajitpur | 132 | 04:00 | 127 | 10:00 | Manikganj | 130 | 04:00 | 121 | 11:00
Bakulia | 134 | 03:00 | 129 | 10:00 | Maniknagar | 135 | 02:00 | 128 | 11:00
Banani | 134 | 01:00 | 124 | 11:00 | Matarbari | 118 | 11:00 | 113 | 00:00
Bangabhaban | 135 | 06:00 | 128 | 11:00 | Matuail | 130 | 02:00 | 125 | 10:00
Barapukuria | 138 | 01:00 | 128 | 15:00 | Millgate | 133 | 01:00 | 124 | 11:00
Barguna | 141 | 18:30 | 133 | 00:00 | Mirpur | 135 | 04:00 | 127 | 16:00
Barishal | 133 | 07:00 | 127 | 18:00 | Mirzapur | 130 | 02:00 | 124 | 14:00
Barishal-230 | 133 | 06:00 | 128 | 18:00 | Mithapukur | 132 | 06:00 | 125 | 14:00
Baroaulia | 135 | 18:30 | 130 | 08:00 | MI_Cement | 130 | 00:00 | 125 | 10:00
Baroirhat | 131 | 00:00 | 125 | 16:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 02:00 | 123 | 11:00 | Mogbazar | 136 | 23:00 | 124 | 12:00
BashundharaCement | 129 | 18:30 | 124 | 10:00 | Mongla | 131 | 06:00 | 117 | 22:00
Beanibazar | 129 | 08:00 | 125 | 00:00 | Motijheel | 134 | 00:00 | 125 | 06:00
Benapole | 131 | 06:00 | 118 | 22:00 | Muktagacha | 135 | 08:00 | 127 | 18:00
Bhaluka | 129 | 00:00 | 123 | 10:00 | Munshiganj | 129 | 03:00 | 123 | 11:00
Bhandaria | 130 | 06:00 | 110 | 21:00 | Muradnagar | 128 | 06:00 | 123 | 11:00
Bhangura | 134 | 05:00 | 127 | 23:00 | Mymensingh | 136 | 08:00 | 117 | 18:00
Bheramara | 138 | 06:00 | 131 | 21:00 | Naogaon | 130 | 05:00 | 122 | 23:00
Bheramara(GK) | 137 | 06:00 | 131 | 21:00 | Narail | 132 | 06:00 | 120 | 21:00
Bhulta | 127 | 07:00 | 122 | 11:00 | Narinda | 135 | 2:00 | 128 | 11:00
Bog-Sherpur | 134 | 06:00 | 127 | 18:00 | Narshingdi | 131 | 06:00 | 118 | 12:00
Bogura | 134 | 05:00 | 129 | 18:00 | Natore | 134 | 05:00 | 127 | 18:00
Bogura-230 | 134 | 05:00 | 129 | 16:00 | Nawabganj | 134 | 02:00 | 127 | 11:00
Brahmanbaria | 134 | 14:00 | 130 | 00:00 | Netrakona | 123 | 15:00 | 117 | 18:00
Cantonment | 135 | 02:00 | 127 | 11:00 | New | 134 | 03:00 | 126 | 11:00
Chandina | 131 | 02:00 | 127 | 11:00 | Niamatpur | 138 | 04:00 | 132 | 00:00
Chandpur | 139 | 18:30 | 133 | 10:00 | Noapara | 133 | 06:00 | 122 | 21:00
Chandraghona | 136 | 18:30 | 132 | 05:00 | Pabna | 136 | 06:00 | 128 | 18:00
Chapai | 137 | 03:00 | 132 | 15:00 | Palashbari | 130 | 03:00 | 123 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 02:00 | 124 | 11:00 | Panchagarh | 135 | 01:00 | 121 | 15:00
Chauddagram | 131 | 18:30 | 126 | 15:00 | Patiya | 133 | 18:30 | 127 | 10:00
Chhatak | 128 | 08:00 | 123 | 00:00 | Patuakhali | 140 | 18:30 | 134 | 00:00
Chowmuhani | 131 | 18:30 | 121 | 22:00 | Payra | 138 | 18:30 | 135 | 00:00
Chuadanga | 131 | 05:00 | 118 | 21:00 | PHP | 131 | 07:00 | 125 | 16:00
Coxsbazar | 121 | 08:00 | 113 | 00:00 | Postogola | 134 | 06:00 | 128 | 11:00
Cumilla(N) | 132 | 04:00 | 128 | 10:00 | Purbachal | 135 | 23:00 | 124 | 11:00
Cumilla(S) | 133 | 00:00 | 127 | 11:00 | Purbasadipur | 134 | 01:00 | 122 | 16:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Rahanpur | 139 | 05:00 | 134 | 19:30
Daudkandi | 125 | 00:00 | 119 | 11:00 | Rahanpur-400 | 140 | 06:00 | 134 | 19:30
DhakaUniversity | 135 | 02:00 | 124 | 11:00 | Rahim | 130 | 02:00 | 126 | 10:00
Dhamrai | 133 | 05:00 | 125 | 12:00 | Rajbari | 134 | 05:00 | 128 | 20:00
Dhanmondi | 135 | 04:00 | 125 | 11:00 | Rajendrapur | 136 | 20:00 | 122 | 11:00
Dohazari | 128 | 18:30 | 124 | 10:00 | Rajshahi | 134 | 06:00 | 126 | 18:00
Faridpur | 137 | 06:00 | 130 | 22:00 | Rajshahi-230 | 133 | 06:00 | 127 | 15:00
Fatullah | 137 | 06:00 | 130 | 12:00 | Ramganj | 133 | 18:30 | 128 | 22:00
Fenchuganj | 136 | 08:00 | 134 | 00:00 | Rampur | 133 | 18:30 | 127 | 10:00
Feni | 131 | 18:30 | 125 | 18:00 | Rampura | 134 | 02:00 | 124 | 10:00
Ghatail | 131 | 17:00 | 124 | 14:00 | Rangamati | 136 | 18:30 | 132 | 02:00
Ghorashal | 138 | 02:00 | 131 | 10:00 | Rangpur | 133 | 05:00 | 126 | 14:00
Goalpara | 136 | 06:00 | 124 | 22:00 | Ruppur | 137 | 04:00 | 131 | 18:00
Gollamari | 135 | 06:00 | 126 | 22:00 | Saidpur | 133 | 21:00 | 123 | 15:00
Gopalganj | 134 | 06:00 | 126 | 22:00 | Satkhira | 132 | 06:00 | 119 | 22:00
Gopalganj-400 | 135 | 05:00 | 131 | 15:00 | Satmasjid | 135 | 02:00 | 130 | 02:00
Gulshan | 135 | 23:00 | 124 | 11:00 | Savar | 134 | 01:00 | 128 | 16:00
Halishahar | 134 | 18:30 | 128 | 09:00 | SevenRings | 138 | 02:00 | 130 | 11:00
Haripur | 130 | 02:00 | 125 | 11:00 | ShahCement | 130 | 02:00 | 124 | 11:00
HaripurSBU | 130 | 02:00 | 125 | 11:00 | Shahjadpur | 138 | 05:00 | 131 | 19:30
Hasnabad | 133 | 07:00 | 126 | 12:00 | Shahjibazar | 134 | 06:00 | 130 | 00:00
Hathazari | 135 | 00:00 | 130 | 14:00 | Shahmirpur | 134 | 18:30 | 128 | 10:00
Ishurdi | 138 | 04:00 | 131 | 22:00 | Shariatpur | 133 | 07:00 | 126 | 21:00
Jaldhaka | 130 | 00:00 | 121 | 15:00 | Sherpur | 135 | 08:00 | 122 | 14:00
Jamalpur | 137 | 08:00 | 132 | 10:00 | Shikalbaha | 125 | 18:30 | 119 | 10:00
Jashore | 130 | 05:00 | 119 | 21:00 | Shikalbaha-230 | 136 | 18:30 | 130 | 14:00
Jhenaidah | 135 | 06:00 | 122 | 21:00 | Shitalakhya | 130 | 00:00 | 125 | 10:00
Jhenaidah-230 | 135 | 06:00 | 125 | 21:00 | Sholosohor | 135 | 19:00 | 131 | 10:00
Joydebpur | 138 | 01:00 | 128 | 08:00 | Shyampur | 136 | 18:30 | 132 | 10:00
Joypurhat | 130 | 06:00 | 120 | 22:00 | Shyampur-230 | 137 | 06:00 | 131 | 11:00
Juldah | 133 | 18:30 | 130 | 09:00 | Siddhirganj | 130 | 02:00 | 125 | 11:00
Kabirpur | 133 | 18:30 | 123 | 11:00 | Sirajganj | 132 | 03:00 | 124 | 20:00
Kachua | 138 | 18:00 | 134 | 10:00 | Sonargaon | 128 | 04:00 | 123 | 11:00
Kaliakoir | 135 | 02:00 | 128 | 11:00 | Sreemongol | 134 | 14:00 | 129 | 00:00
Kallyanpur | 135 | 00:00 | 129 | 16:00 | Sreepur | 132 | 00:00 | 127 | 10:00
Kalurghat | 136 | 18:30 | 131 | 08:00 | Srinagar | 134 | 04:00 | 127 | 12:00
Kamrangirchar | 135 | 06:00 | 127 | 11:00 | SSM | 138 | 01:00 | 132 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 05:00 | 120 | 21:00
Kasba | 127 | 07:00 | 123 | 11:00 | Sylhet | 130 | 08:00 | 127 | 00:00
Kazla | 134 | 03:00 | 127 | 12:00 | Sylhet-132 | 129 | 02:00 | 127 | 00:00
Keranigonj | 135 | 06:00 | 127 | 12:00 | Tangail | 128 | 05:00 | 120 | 14:00
Khagrachori | 135 | 18:30 | 131 | 09:00 | Taraganj | 131 | 00:00 | 124 | 16:00
Khulna | 134 | 06:00 | 123 | 22:00 | Thakurgaon | 135 | 01:00 | 118 | 15:00
Khulna(S) | 136 | 06:00 | 125 | 22:00 | TK | 135 | 18:00 | 131 | 10:00
Khulshi | 132 | 18:30 | 127 | 10:00 | Tongi | 135 | 04:00 | 128 | 12:00
Kishoreganj | 130 | 04:00 | 124 | 18:00 | Ullahpara | 134 | 04:00 | 127 | 19:00
Kodda | 135 | 21:00 | 121 | 11:00 | Ullon | 135 | 23:00 | 124 | 11:00
KSRM | 0 | 00:00 | N/A | N/A | Uttara | 136 | 03:00 | 128 | 11:00
Kulaura | 134 | 04:00 | 132 | 00:00 | UttaraNew | 135 | 03:00 | 128 | 11:00
Kurigram | 131 | 05:00 | 122 | 08:00 | Zigatola | 135 | 04:00 | 127 | 12:00
Kushtia | 134 | 01:00 | 126 | 18:00
Laksam | 137 | 02:00 | 133 | 10:00
Lakshmipur | 131 | 18:30 | 126 | 23:00
Lalbag | 134 | 02:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division