## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-10-2025 | during | 08-10-2025 | during | 08-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 320 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 147 | 138 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 45 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 30 | 48 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 129 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 20.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 245 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 87 | 115 | 149 | 149 | 115 | 115 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 100 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 79 | 108 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 435 | 545 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2145 | 2753.5 | 5834.4 | 5804.4 | 3928.56 | 3956.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 21 | 25.5 | 25.5 | 25.5 | 17 | 17 | Engine Problem
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 201 | 207 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 14 | 62 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 44 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 13 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 27 | 80 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.96 | 0 | 3.81 | 0 | 3.81 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 66 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 31 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 104 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1159 | 1133 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 10 | 8 | 3 | 8 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2048.96 | 2426.5 | 3051.53 | 3042.72 | 2765.17 | 2756.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 196 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 260 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 410 | 385 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 20 | 20 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 8 | 8 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 122 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 29 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 105 | 163 | 163 | 106 | 106 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 15 | 105 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 76 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 60 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 4 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 37 | 87 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1275 | 1503 | 2668.86 | 2603.86 | 2127.16 | 2071.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-10-2025 | during | 08-10-2025 | during | 08-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 32 | 157.5 | 157.5 | 75 | 75 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 46 | 45 | 45 | 9.5 | 9.5 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 68 | 77 | 77 | 77 | 77 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.62 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 139.62 | 146 | 399.9 | 356 | 228.4 | 184.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 68 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 360 | 301 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1194 | 1159 | 1273 | 1273 | 1208 | 1208
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 874 | 874 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 123 | 116 | 410 | 410 | 174 | 174 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 371 | 371 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1500 | 1399 | 2728 | 2648 | 2297 | 2217
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 616 | 616 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1095 | 1180 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 274 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2320.18 | 2455 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 49.87 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 9 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 348 | 331 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.64 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1116.13 | 1372.3 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.32 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 68 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1781.96 | 2183.3 | 3187.47 | 3020.87 | 3060.09 | 2893.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 138 | 143 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 2 | 0 | 2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 166 | 0 | 170.17 | 0 | 170.17 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 393 | 403 | 640.17 | 448 | 640.17 | 448
System Total |  |  |  |  | 28823.2 | 28365.955 | 12797.72 | 14428.3 | 21930.33 | 21342.85 | 18218.55 | 17698.07
Forecast Scenario (08-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13640 |  | 0 |  | 13640
|  |  |  | 1:00 | 13130 |  | 0 |  | 13130
|  |  |  | 2:00 | 12530 |  | 0 |  | 12530
|  |  |  | 3:00 | 12260 |  | 0 |  | 12260
|  |  |  | 4:00 | 11850 |  | 0 |  | 11850
|  |  |  | 5:00 | 11700 |  | 0 |  | 11700
|  |  |  | 6:00 | 11370 |  | 0 |  | 11370
|  |  |  | 7:00 | 11580 |  | 0 |  | 11580
|  |  |  | 8:00 | 11690 |  | 0 |  | 11690
|  |  |  | 9:00 | 11740 |  | 0 |  | 11740
|  |  |  | 10:00 | 12060 |  | 0 |  | 12060
|  |  |  | 11:00 | 12450 |  | 0 |  | 12450
|  |  |  | 12:00 | 12790 |  | 0 |  | 12790
|  |  |  | 13:00 | 12950 |  | 0 |  | 12950
|  |  |  | 14:00 | 12770 |  | 0 |  | 12770
|  |  |  | 15:00 | 12790 |  | 0 |  | 12790
|  |  |  | 16:00 | 12470 |  | 0 |  | 12470
|  |  |  | 17:00 | 12350 |  | 0 |  | 12350
|  |  |  | 18:00 | 13830 |  | 0 |  | 13830
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14470 |  | 0 |  | 14470
|  |  |  | 19:30 | 14420 |  | 0 |  | 14420
|  |  |  | 20:00 | 14210 |  | 0 |  | 14210
|  |  |  | 21:00 | 14030 |  | 0 |  | 14030
|  |  |  | 22:00 | 13900 |  | 0 |  | 13900
|  |  |  | 23:00 | 13800 |  | 0 |  | 13800
Probable Maximum Temperature: |  |  | 31.20°C
Probable Maximum Demand at Day Peak: |  |  | 12790.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14470.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14470.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 306.36 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:10 hrs on 08-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-10-2025 | [28 empty] | Date: | 07-10-2025 | [28 empty] | Date: | 07-10-2025 | [28 empty] | Date: | 07-10-2025 | [28 empty] | Date: | 07-10-2025 | [14 empty] | Date: | 07-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 16 | 17 | 115 | 15 | 295 | 0 | 0 | 68 | 0 | 300 | 147 | 448 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 28.2 | 22 | 0 | 0 | 16 | 0 | 0 | 0 | 2 | 66 | 38 | 0 | 0 | 0 | 0 | 220 | 81 | 18 | 285 | 0 | 0 | 33 | 0 | 94 | 187 | 0 | 0 | 0 | 1150 | 0 | 51 | 108 | 0 | 391 | 0 | 280 | 0 | 190 | 0 | 37 | 105 | 169 | 0 | 19 | 0 | 42 | 0 | 0 | 22 | 305 | 0 | 337 | 30 | 57 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 45 | 59 | 0 | 0 | 6 | 7326.2 | 848 | 122 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1414.14 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 405 | 0 | 0 | 144 | 47 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 612 | 1162 | 134 | 6314.14 | 13640.34 | 107.8
01:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 18 | 0 | 115 | 15 | 195 | 0 | 0 | 64 | 0 | 300 | 148 | 444 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 66 | 38 | 0 | 0 | 0 | 0 | 219 | 84 | 19 | 285 | 0 | 0 | 33 | 0 | 91 | 187 | 0 | 0 | 0 | 1125 | 0 | 51 | 105 | 0 | 390 | 0 | 280 | 0 | 192 | 0 | 48 | 106 | 138 | 0 | 19 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 333 | 30 | 57 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 60 | 0 | 0 | 6 | 7051.2 | 848 | 122 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1410.28 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 411 | 0 | 0 | 143 | 48 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 614 | 1155 | 17 | 6079.28 | 13130.48 | 107.79
02:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 18 | 0 | 115 | 15 | 0 | 0 | 0 | 67 | 0 | 300 | 147 | 446 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 51 | 19 | 285 | 0 | 0 | 18 | 0 | 93 | 187 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 0 | 400 | 0 | 280 | 0 | 194 | 0 | 50 | 105 | 56 | 0 | 19 | 0 | 38 | 0 | 0 | 0 | 305 | 0 | 333 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 60 | 0 | 0 | 6 | 6578.2 | 848 | 122 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1413.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 413 | 0 | 0 | 141 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 616 | 1160 | 0 | 5954.17 | 12532.37 | 107.79
03:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 147 | 449 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 24 | 285 | 0 | 0 | 0 | 0 | 94 | 187 | 0 | 0 | 0 | 1154 | 0 | 51 | 0 | 0 | 400 | 0 | 280 | 0 | 193 | 0 | 51 | 106 | 17 | 0 | 19 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 351 | 30 | 57 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 9 | 60 | 0 | 0 | 6 | 6373.2 | 848 | 122 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1408.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 642 | 1110 | 0 | 5890.75 | 12263.95 | 107.79
04:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 446 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 27 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1148 | 0 | 51 | 0 | 0 | 405 | 0 | 280 | 0 | 191 | 0 | 16 | 106 | 0 | 0 | 19 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 338 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 78 | 9 | 63 | 0 | 0 | 6 | 6096.2 | 848 | 122 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1318.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 412 | 0 | 0 | 142 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 611 | 1095 | 0 | 5756.22 | 11852.42 | 107.78
05:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 148 | 445 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 28.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 0 | 408 | 0 | 280 | 0 | 196 | 0 | 0 | 106 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 305 | 0 | 356 | 30 | 57 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 63 | 0 | 0 | 6 | 6078.2 | 849 | 127 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1218.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 142 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 115 | 220 | 0 | 611 | 1090 | 0 | 5623.76 | 11701.96 | 107.78
06:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 146 | 448 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.02 | 220 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1130 | 1 | 51 | 0 | 0 | 409 | 0 | 280 | 0 | 188 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 32 | 0 | 0 | 0 | 315 | 0 | 332 | 30 | 57 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 9 | 63 | 0 | 0 | 6 | 6031.02 | 848 | 131 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1111.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 0 | 0 | 0.07 | 0 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 0 | 142 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 115 | 220 | 0 | 612 | 1000 | 0 | 5347.14 | 11378.16 | 107.78
07:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 152 | 460 | 0 | 0 | 335 | 0 | 0 | 3 | 52 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.6 | 221 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1160 | 3 | 51 | 0 | 0 | 409 | 0 | 280 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 15 | 0 | 32 | 0 | 9 | 0 | 305 | 0 | 360 | 30 | 57 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 63 | 0 | 1.64 | 6 | 6195.24 | 848 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.46 | 375 | 0 | 1023.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.18 | 1 | 0 | 0 | 2.48 | 0 | 0 | 140 | 0 | 0 | 0 | 410 | 0 | 0.22 | 140 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 28 | 0.06 | 0 | 219 | 115 | 220 | 0 | 614 | 1026 | 0 | 5394.09 | 11589.33 | 107.78
08:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 40 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 440 | 0 | 0 | 335 | 0 | 0 | 10 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.69 | 221 | 0 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1140 | 11 | 51 | 0 | 0 | 410 | 0 | 280 | 0 | 192 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 30 | 0 | 32 | 0 | 305 | 0 | 338 | 30 | 57 | 149 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 63 | 0 | 3.64 | 6 | 6145.33 | 867 | 129 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16.73 | 375 | 0 | 1014.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.69 | 8 | 0 | 0 | 7.68 | 0 | 0 | 140 | 0 | 0 | 0 | 385 | 0 | 0.74 | 139 | 47 | 0 | 6 | 0 | 0 | 0 | 0 | 1.4 | 48 | 0.2 | 0 | 273 | 115 | 220 | 0 | 613 | 1090 | 0 | 5547.53 | 11692.86 | 107.77
09:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 7 | 0 | 52 | 15 | 0 | 0 | 17 | 0 | 0 | 300 | 148 | 440 | 0 | 0 | 333 | 0 | 0 | 10 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 221 | 0 | 2 | 285 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 1172 | 16 | 51 | 0 | 0 | 410 | 0 | 280 | 0 | 195 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 28 | 0 | 62 | 0 | 305 | 0 | 320 | 30 | 57 | 139 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 30 | 1 | 15.66 | 6 | 6191.37 | 867 | 126 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36.58 | 375 | 0 | 1018.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.95 | 67 | 0 | 0 | 22.53 | 0 | 0 | 140 | 0 | 0 | 0 | 345 | 0 | 3.49 | 138 | 48 | 0 | 5 | 0 | 0 | 0 | 0 | 1.7 | 99 | 0.14 | 0 | 233 | 115 | 220 | 0 | 546 | 1090 | 0 | 5551.51 | 11742.88 | 107.76
10:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 16 | 0 | 52 | 40 | 35 | 4 | 35 | 58 | 0 | 300 | 151 | 450 | 0 | 17 | 332 | 0 | 0 | 24 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33 | 221 | 1 | 2 | 285 | 0 | 0 | 20 | 0 | 3 | 200 | 0 | 0 | 0 | 1165 | 19 | 51 | 1 | 0 | 410 | 0 | 280 | 0 | 200 | 0 | 0 | 105 | 2 | 0 | 19 | 0 | 32 | 0 | 71 | 0 | 310 | 0 | 322 | 30 | 57 | 149 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 9 | 30 | 1 | 28.38 | 4 | 6475.71 | 868 | 125 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 374 | 0 | 1021.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.65 | 23 | 0 | 0 | 39.57 | 0 | 0 | 140 | 0 | 0 | 0 | 358 | 0 | 2.56 | 138 | 48 | 0 | 11 | 0 | 0 | 0 | 0 | 0.4 | 96 | 0.12 | 0 | 217 | 115 | 220 | 0 | 547 | 1100 | 0 | 5590.68 | 12066.39 | 107.76
11:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17.5 | 9 | 68 | 45 | 45 | 15 | 35 | 59 | 0 | 300 | 143 | 445 | 0 | 17 | 332 | 0 | 0 | 17 | 52 | 21 | 22 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 3.47 | 222 | 15 | 2 | 285 | 0 | 0 | 45 | 1 | 14 | 200 | 0 | 0 | 0 | 1100 | 19 | 51 | 10 | 0 | 405 | 0 | 280 | 0 | 185 | 0 | 22 | 105 | 16 | 0 | 19 | 0 | 32 | 0 | 80 | 0 | 310 | 0 | 285 | 30 | 57 | 143 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 30 | 1 | 50.28 | 2 | 6558.25 | 874 | 123 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 91 | 372 | 0 | 1112.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.04 | 79 | 0 | 0 | 61.72 | 0 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 5.5 | 138 | 48 | 0 | 35 | 0 | 0 | 0 | 0 | 3 | 164 | 0.11 | 0 | 260 | 115 | 180 | 0 | 612 | 1094 | 0 | 5891.53 | 12449.78 | 107.76
12:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 30 | 17 | 87 | 45 | 45 | 15 | 35 | 79 | 0 | 300 | 147 | 435 | 0 | 17 | 330 | 0 | 0 | 21 | 52 | 21 | 15 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 2.96 | 222 | 14 | 5 | 285 | 0 | 0 | 46 | 21 | 14 | 201 | 0 | 0 | 0 | 1159 | 19 | 51 | 20 | 0 | 410 | 0 | 280 | 0 | 196 | 0 | 37 | 105 | 15 | 4 | 20 | 0 | 66 | 0 | 71 | 0 | 305 | 0 | 360 | 30 | 57 | 144 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 30 | 2 | 15.62 | 6 | 6802.58 | 874 | 123 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 371 | 0 | 1116.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.87 | 68 | 0 | 0 | 64.32 | 0 | 0 | 130 | 0 | 0 | 0 | 348 | 0 | 5.64 | 138 | 47 | 0 | 36 | 0 | 0 | 0 | 0 | 6 | 166 | 0.18 | 0 | 274 | 115 | 220 | 0 | 616 | 1095 | 0 | 5995.14 | 12797.72 | 107.76
13:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35.6 | 17 | 87 | 15 | 95 | 15 | 35 | 108 | 0 | 300 | 140 | 530 | 0 | 35 | 331 | 0 | 0 | 7 | 35 | 0 | 15 | 0 | 0 | 0 | 0 | 60 | 0 | 8 | 33 | 0 | 0 | 0 | 0 | 3.18 | 220 | 14 | 10 | 285 | 0 | 0 | 46 | 25 | 14 | 207 | 0 | 0 | 0 | 1143 | 13 | 51 | 50 | 0 | 400 | 0 | 260 | 0 | 192 | 0 | 51 | 103 | 42 | 9 | 17 | 0 | 72 | 0 | 60 | 0 | 310 | 0 | 316 | 30 | 50 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 77 | 9 | 30 | 2 | 0.6 | 6 | 6958.38 | 873 | 121 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 96 | 372 | 0 | 1152.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.16 | 83 | 0 | 0 | 63.21 | 0 | 0 | 130 | 0 | 0 | 0 | 345 | 0 | 5.63 | 138 | 47 | 0 | 31 | 0 | 0 | 0 | 0 | 2.4 | 159 | 0.22 | 0 | 274 | 115 | 220 | 0 | 616 | 1100 | 0 | 5992.43 | 12950.81 | 107.76
14:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35.9 | 17 | 87 | 0 | 95 | 15 | 35 | 108 | 0 | 300 | 144 | 545 | 0 | 35 | 335 | 0 | 0 | 4 | 0 | 20.8 | 22 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 33 | 0 | 0 | 0 | 0 | 1.25 | 218 | 15 | 9 | 285 | 0 | 0 | 50 | 25.5 | 14 | 207 | 0 | 0 | 0 | 1166 | 15 | 51 | 20 | 0 | 385 | 0 | 260 | 0 | 198 | 0 | 59 | 104 | 81 | 9 | 19 | 0 | 80 | 0 | 52 | 0 | 305 | 0 | 332 | 30 | 50 | 162 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 28 | 2 | 0.45 | 6 | 7017.9 | 874 | 117 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 372 | 0 | 1162.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.83 | 55 | 0 | 0 | 31.67 | 0 | 0 | 130 | 0 | 0 | 0 | 349 | 0 | 2.3 | 139 | 47 | 0 | 19 | 0 | 0 | 0 | 0 | 5.6 | 160 | 0.13 | 0 | 256 | 115 | 220 | 0 | 551 | 1100 | 0 | 5756.38 | 12774.28 | 107.76
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35.9 | 17 | 89 | 0 | 45 | 0 | 35 | 108 | 0 | 300 | 143 | 545 | 0 | 35 | 335 | 0 | 0 | 8 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 33 | 0 | 0 | 0 | 0 | 1.91 | 218 | 16 | 4 | 285 | 0 | 0 | 50 | 25.5 | 15 | 207 | 0 | 0 | 0 | 1160 | 13 | 51 | 20 | 0 | 385 | 0 | 260 | 0 | 195 | 0 | 72 | 105 | 83 | 9 | 7 | 0 | 70 | 0 | 49 | 0 | 315 | 0 | 346 | 30 | 50 | 160 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 30 | 2 | 0.72 | 6 | 6944.03 | 875 | 114 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 373 | 0 | 1266.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.21 | 65 | 0 | 0 | 44.54 | 0 | 0 | 130 | 0 | 0 | 0 | 349 | 0 | 2.59 | 137 | 47 | 0 | 17 | 0 | 0 | 0 | 0 | 4 | 117 | 0.28 | 0 | 257 | 115 | 220 | 0 | 549 | 1110 | 0 | 5848.72 | 12792.75 | 107.75
16:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35.9 | 17 | 72 | 30 | 45 | 0 | 35 | 108 | 0 | 300 | 140 | 535 | 0 | 17 | 335 | 0 | 0 | 13 | 17 | 19.8 | 22 | 0 | 0 | 0 | 0 | 82 | 0 | 22 | 33 | 0 | 0 | 0 | 0 | 0.82 | 218 | 15 | 4 | 285 | 0 | 0 | 50 | 25.5 | 14 | 207 | 0 | 0 | 0 | 1139 | 5 | 51 | 20 | 0 | 385 | 0 | 260 | 0 | 191 | 0 | 34 | 105 | 34 | 9 | 11 | 0 | 66 | 0 | 19 | 0 | 310 | 0 | 330 | 30 | 68 | 160 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 30 | 1 | 2.86 | 6 | 6773.88 | 874 | 106 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 372 | 0 | 1263.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.22 | 33 | 0 | 0 | 16.09 | 0 | 0 | 130 | 0 | 0 | 0 | 343 | 0 | 1.12 | 143 | 46 | 0 | 10 | 0 | 0 | 0 | 0 | 2.3 | 64 | 0.3 | 0 | 254 | 115 | 220 | 0 | 550 | 1108 | 0 | 5704.5 | 12478.38 | 107.75
17:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35.9 | 24 | 71 | 30 | 45 | 0 | 35 | 108 | 0 | 300 | 139 | 545 | 0 | 17 | 335 | 0 | 0 | 2 | 17 | 19.3 | 22 | 0 | 0 | 0 | 0 | 84 | 0 | 13 | 33 | 1 | 0 | 0 | 0 | 0.07 | 218 | 15 | 11 | 285 | 0 | 0 | 50 | 25.5 | 14 | 207 | 0 | 0 | 0 | 1166 | 1 | 51 | 35 | 0 | 395 | 0 | 260 | 0 | 198 | 0 | 32 | 105 | 32 | 0 | 17 | 0 | 60 | 0 | 2 | 0 | 305 | 0 | 346 | 30 | 68 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 76 | 9 | 30 | 0 | 2.75 | 6 | 6825.52 | 875 | 106 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 374 | 0 | 1266.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.46 | 10 | 0 | 0 | 7.45 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0.62 | 144 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 4 | 0.11 | 0 | 256 | 115 | 220 | 0 | 503 | 1080 | 0 | 5532.95 | 12358.47 | 107.74
18:00 | 0 | 77 | 16 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 39.1 | 34 | 86 | 129 | 195 | 27 | 35 | 108 | 0 | 300 | 151 | 510 | 0 | 55 | 330 | 0 | 0 | 0 | 142 | 19.3 | 22 | 0 | 0 | 5 | 0 | 84 | 0 | 4 | 66 | 29 | 0 | 0 | 0 | 0 | 218 | 22 | 14 | 285 | 86 | 0 | 50 | 25.5 | 15 | 207 | 0 | 0 | 0 | 1195 | 0 | 51 | 78 | 0 | 385 | 0 | 260 | 0 | 211 | 0 | 46 | 105 | 49 | 0 | 19 | 34 | 66 | 1 | 0 | 27 | 305 | 0 | 362 | 30 | 68 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 46 | 30 | 0 | 0 | 0 | 7660.9 | 874 | 113 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1364.77 | 0 | 0 | 0 | 50 | 35 | 0 | 80 | 13 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 404 | 0 | 0 | 145 | 47 | 100 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 615 | 1070 | 0 | 6176.77 | 13837.67 | 107.74
19:00 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 48 | 35 | 115 | 129 | 245 | 45 | 35 | 108 | 0 | 300 | 138 | 545 | 0 | 55 | 335 | 0 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 31 | 30 | 80 | 0 | 10 | 66 | 44 | 0 | 0 | 0 | 0 | 220 | 66 | 13 | 285 | 104 | 0 | 50 | 25.5 | 62 | 207 | 0 | 0 | 0 | 1133 | 0 | 51 | 122 | 0 | 385 | 0 | 260 | 0 | 181 | 0 | 87 | 105 | 105 | 0 | 17 | 60 | 76 | 25 | 0 | 29 | 305 | 0 | 301 | 30 | 68 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 46 | 32 | 0 | 0 | 0 | 7988 | 874 | 116 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1372.3 | 0 | 9 | 0 | 100 | 106 | 0 | 80 | 37 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 331 | 0 | 0 | 143 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 616 | 1180 | 17 | 6440.3 | 14428.3 | 107.73
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 47.2 | 35 | 115 | 129 | 195 | 30 | 55 | 108 | 0 | 300 | 142 | 544 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 24.5 | 17 | 0 | 0 | 42 | 15 | 85 | 0 | 0 | 66 | 58 | 0 | 0 | 0 | 0 | 221 | 85 | 16 | 285 | 60 | 0 | 50 | 25.5 | 93 | 207 | 0 | 0 | 0 | 1158 | 0 | 51 | 127 | 0 | 395 | 0 | 260 | 0 | 193 | 0 | 90 | 105 | 75 | 0 | 16 | 33 | 70 | 25 | 0 | 29 | 305 | 0 | 316 | 30 | 68 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 46 | 33 | 0 | 0 | 0 | 7966.2 | 874 | 116 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1368.74 | 0 | 29 | 0 | 50 | 50 | 0 | 95 | 37 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 407 | 0 | 0 | 144 | 46 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 617 | 1190 | 17 | 6455.74 | 14421.94
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 45 | 0 | 115 | 129 | 145 | 30 | 55 | 108 | 0 | 300 | 142 | 535 | 0 | 55 | 335 | 0 | 0 | 0 | 125 | 23.5 | 0 | 0 | 0 | 41 | 15 | 82 | 0 | 6 | 66 | 50 | 0 | 0 | 0 | 0 | 221 | 94 | 19 | 285 | 31 | 0 | 50 | 25.5 | 94 | 207 | 0 | 0 | 0 | 1147 | 0 | 51 | 127 | 0 | 390 | 0 | 260 | 0 | 193 | 0 | 90 | 105 | 84 | 0 | 17 | 0 | 76 | 8 | 0 | 29 | 305 | 0 | 314 | 30 | 68 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 47 | 32 | 0 | 0 | 0 | 7777 | 873 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1360.6 | 0 | 40 | 0 | 35 | 35 | 0 | 95 | 39 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 410 | 0 | 0 | 145 | 47 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 616 | 1190 | 17 | 6440.6 | 14217.6 | 107.73
21:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 33.4 | 0 | 115 | 108 | 45 | 15 | 35 | 108 | 0 | 300 | 144 | 540 | 0 | 55 | 335 | 0 | 0 | 0 | 108 | 24.2 | 0 | 0 | 0 | 42 | 15 | 83 | 0 | 2 | 66 | 51 | 0 | 0 | 0 | 0 | 221 | 101 | 20 | 285 | 0 | 0 | 50 | 25.5 | 95 | 202 | 0 | 0 | 0 | 1160 | 0 | 51 | 123 | 0 | 375 | 0 | 260 | 0 | 197 | 0 | 90 | 105 | 79 | 0 | 19 | 0 | 78 | 0 | 0 | 29 | 310 | 0 | 326 | 30 | 68 | 153 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 32 | 0 | 0 | 0 | 7583.1 | 874 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1361 | 0 | 40 | 0 | 0 | 35 | 0 | 95 | 38 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 0 | 146 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 616 | 1230 | 17 | 6455 | 14038.1 | 107.72
22:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17.5 | 0 | 115 | 78 | 45 | 0 | 35 | 108 | 0 | 300 | 144 | 544 | 0 | 55 | 335 | 0 | 0 | 0 | 108 | 24.2 | 0 | 0 | 0 | 42 | 15 | 82 | 0 | 10 | 66 | 51 | 0 | 0 | 0 | 0 | 221 | 107 | 25 | 285 | 0 | 0 | 33 | 25.5 | 63 | 202 | 0 | 0 | 0 | 1164 | 0 | 51 | 118 | 0 | 380 | 0 | 260 | 0 | 196 | 0 | 89 | 105 | 79 | 0 | 19 | 0 | 78 | 0 | 0 | 29 | 310 | 0 | 333 | 30 | 68 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 7514.2 | 874 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1362 | 0 | 40 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 0 | 147 | 47 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 616 | 1230 | 17 | 6330 | 13844.2 | 107.71
23:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17.5 | 0 | 115 | 64 | 45 | 0 | 35 | 72 | 0 | 300 | 150 | 544 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 24.2 | 0 | 0 | 0 | 43 | 15 | 82 | 0 | 2 | 66 | 51 | 0 | 0 | 0 | 0 | 222 | 106 | 26 | 285 | 0 | 0 | 33 | 8 | 40 | 187 | 0 | 0 | 0 | 1168 | 0 | 51 | 122 | 0 | 380 | 0 | 260 | 0 | 205 | 0 | 89 | 106 | 78 | 0 | 19 | 0 | 74 | 0 | 0 | 29 | 305 | 0 | 346 | 30 | 68 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 7388.7 | 874 | 123 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1367 | 0 | 40 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 0 | 148 | 47 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 615 | 1232 | 17 | 6271 | 13659.7 | 107.7
Total KWH | 0 | 2069760 | 304800 | 0 | 0 | 0 | 0 | 0 | 8586000 | 0 | 0 | 518400 | 250200 | 1884816 | 956640 | 1722742 | 220386 | 529615 | 1584000 | 0 | 7583000 | 3521425 | 11880000 | 0 | 530467 | 8016758 | 0 | 0 | 105649 | 1568400 | 530400 | 428760 | 0 | 0 | 258436 | 125455 | 1014720 | 0 | 116640 | 853251 | 304560 | 0 | 0 | 0 | 21121 | 5277887 | 911640 | 369120 | 6829090.91 | 185673 | 0 | 739680 | 307038.6 | 849745 | 4738436 | 0 | 0 | 0 | 27736361 | 135000 | 1231244 | 1207709 | 0 | 9511000 | 0 | 6630000 | 0 | 4768000 | 0 | 1109760 | 2481610 | 1127040 | 47040 | 419190 | 90060 | 1294080 | 36245 | 488855 | 183360 | 7478500 | 0 | 8476000 | 717000 | 1410000 | 3684600 | 172968 | 0 | 1947840 | 723744 | 0 | 391000 | 3405720 | 4320 | 1752000 | 468000 | 930240 | 12450 | 126720 | 104880 | 165997247.51 | 20951272 | 3031200 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 363600 | 9040000 | 0 | 29825055 | 0 | 189963 | 0 | 193152 | 323040 | 0 | 636080 | 129254 | 0 | 187468 | 564800 | 84714 | 0 | 377248 | 0 | 0 | 3518518 | 0 | 0 | 0 | 9218400 | 0 | 33480 | 3483000 | 1093963 | 815303 | 179037 | 613776 | 0 | 0 | 0 | 23888.28 | 1134000 | 1378 | 0 | 6458000 | 2750000 | 5492810 | 0 | 14305454.54 | 27537454.55 | 182400 | 143649708.37 | 309646955.88

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12797.72 | MW | 12:00 Hr. | Energy Generated |  |  | 309.647 |  | MKWHr.
| Day Peak Demand |  |  | 12797.72 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.041 |  | MKWHr.
| Evening Peak Generation |  |  | 14428.3 | MW | 19:00 Hr. | Energy Demand |  |  | 309.688 |  | MKWHr.
| Evening Peak Demand |  |  | 14471.15 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 11378.16 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 910.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 14428.3 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.9012 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.5463 | 0 | 12.1402 | 0 | 0 | 0.10565 | 0 | 0 | 52.7922 | Gas | 124.0435 | Gas | 439909500.83
| Chattogram Zone |  |  | 5.1076 | 34.5655 | 5.5502 | 0 | 5.2779 | 0.15612 | 0 | 0.11664 | 50.7739 | Coal | 96.4833 | Coal | 519800653.7667
| Cumilla Zone |  |  | 25.041 | 0 | 3.8012 | 0 | 0 | 0.48885 | 1.2941 | 0 | 30.6252 | HFO | 26.9885 | HFO | 495666251.318
| Mymensingh Zone |  |  | 0.93024 | 0 | 2.3292 | 0 | 0 | 0.13917 | 0 | 0 | 3.3986 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4074 | Hydro | 5.2779 | Hydro | 527788.7
| Khulna Zone |  |  | 3.0312 | 9.04 | 0 | 0 | 0 | 0.3636 | 21.8633 | 0 | 34.2981 | Solar | 3.7547 | Solar | 57100368.1888
| Barishal Zone |  |  | 8.2428 | 48.3009 | 0.1824 | 0 | 0 | 0.001378 | 0 | 0 | 56.7275 | Import | 52.9824 | Import | 312563719.47
| Rajshahi Zone |  |  | 12.7369 | 0 | 1.5562 | 0 | 0 | 1.163 | 29.8251 | 0 | 45.2812 | Wind | 0.11664 | Wind | 1719273.6
| Rangpur Zone |  |  | 0 | 4.577 | 1.4291 | 0 | 0 | 1.3369 | 0 | 0 | 7.343
| Total |  |  | 124.0435 | 96.4833 | 26.9885 | 0 | 5.2779 | 3.7547 | 52.9824 | 0.11664 | 309.647
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 439909500.83 |  | Hydro | 527788.7
|  |  |  | Coal | 519800653.7667 |  | Solar | 57100368.1888
|  |  |  | HFO | 495666251.318 |  | Import | 312563719.47
|  |  |  | HSD | 0 |  | Wind | 1719273.6
[5 empty] | Total: | 182,72,87,555 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9513 | Peak Hr Flow | 874.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43715970.95 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.8251 | Peak Hr Flow | 1372.30 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1822 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2941 | Peak Hr Flow | 76.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2462 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.0704 | Peak Hr Flow | 2322.30 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5129
|  |  |  | Chattogram |  | 0 |  | 1429
|  |  |  | Cumilla |  | 0 |  | 1393
|  |  |  | Mymensingh |  | 41 |  | 1093
|  |  |  | Sylhet |  | 0 |  | 586
|  |  |  | Khulna |  | 0 |  | 1649
|  |  |  | Barishal |  | 0 |  | 372
|  |  |  | Rajshahi |  | 0 |  | 1421
|  |  |  | Rangpur |  | 0 |  | 971
|  |  |  | Total |  | 41 |  | 14043
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:12 | 17:04 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Annual Maintenance Work.
| 08:13 | 17:03 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Annual Maintenance Work.
| 08:15 | 17:27 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to Earthwire change
and OPGW Installation.
| 08:48 | 13:58 | Baroirhat-PHP 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to Annual
Maintenance Work
| 09:20 | 17:48 | Thakurgaon 132/33kV S/S T-2(412T) LT Scheduled S/D Due to Annual Maintenance
| 09:20 | 17:47 | Thakurgaon 132/33kV S/S T-2(412T) HT Scheduled S/D Due to Annual Maintenance
| 09:27 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Relay Change
Work
|  | 09:27 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 09:28 | Naogaon 132/33kV S/S T-3 LT is restored.
| 09:34 |  | Meghnaghat CCPP(Summit) GT-2 Ready with remarks:- GT-2 was shut down as per NLDC demand
at 07:24 hrs on 03.10.2025 and declared ready for operation at 07:30 hrs on 03.10.2025.
| 10:07 | 10:47 | Maijdee 132/33kV S/S Tr-02 LT Scheduled S/D Due to Transformer-2, OTI & WTI don't show
correct temperature in SAS.
| 10:08 | 10:42 | Maijdee 132/33kV S/S Tr-02 HT Scheduled S/D Due to Transformer-2, OTI & WTI don't show
the correct temperature in SAS.
| 10:13 |  | Jaldhaka 132kv Bus Couplep bay- S/D.
| 10:25 | 11:59 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to T- 1 Shutdown due to red-hot | [7 empty] | 25.6MW load
|  |  | maintenance work in Shodor doptor 33kv feeder by PBS-01. | [7 empty] | interrup.
| 10:25 | 11:58 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to T- 1 Shutdown due to red-hot | [7 empty] | 25.6MW load
|  |  | maintenance work in Shodor doptor 33kv feeder by PBS-01. | [7 empty] | interrup.
| 11:23 | 14:01 | Barishal-Bhola 230 kV Ckt-1 Forced S/D from Barishal 230/132kV end Due to Pole
discrimincy at Bhola end.
| 11:45 | 13:05 | Baghabari-Shahjadpur 132 kV Ckt-2 Forced S/D from Shahjadpur 132/33kV end Due to Red hot
maintenance work.
| 12:00 |  | Day Peak Generation: 12794 MW.
| 13:38 | 13:53 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing Distance Relay relays Due to
Trip by R-Y phase, Zone 01
| 13:38 | 13:53 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Tripped showing Distance Relay relays Due to
Trip by R-Y phase, Zone 01
| 13:40 |  | Jaldhaka 132kv Bus Couplep bay- Syn
| 15:30 |  | Bagerhat-Mongla 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance Relay
Trip A phase Zone-2 25.2km relays.
| 15:30 |  | Bagerhat–Mongla 132kV ckt-1 tripped due to a conductor tearing.
|  | 16:10 | Chandraghona-Madunaghat 132 kV Ckt-1 is restored.
|  | 17:13 | Meghnaghat 400/230kV S/S 400 kV Bus -02 is restored.
| 19:00 |  | Evening Peak Generation is 14427 MW.
| 02:09 |  | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing ABB relays. | [7 empty] | and 95.0MW load
|  |  | and from Mirpur 132/33kV end showing Main protection, DEF logic contoroller. relays Due | [7 empty] | interrup. Mirpur
|  |  | to Tripped due to fault. | [7 empty] | 132/33kV end
| 02:09 | 02:52 | Aminbazar-Mirpur 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing ABB relays.
| 06:12 |  | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Tr-1( A,B) 132KV & 33KV CT Ratio | [7 empty] | 5.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 06:12 |  | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Tr-1( A,B) 132KV & 33KV CT Ratio | [7 empty] | 5.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 07:05 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to Pbs taken shutdown due
to red hot.
| 07:05 | 07:21 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Pbs taken shutdown
due to red hot
| 07:06 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Pbs taken shutdown due
to red hot
| 07:36 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to Earthwire change &
OPGW installation work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 320 | 8586000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7583000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 138 | 3521425 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 45 | 220386 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 8016758 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48 | 518400 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 129 | 956640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 529615 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 530467 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 530400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 428760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 304800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 1722742 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1884816 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 100 | 2069760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1584000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 105649 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 250200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 545 | 11880000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1568400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2753.5 | 52792218
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 307038.6 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135000 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 739680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5277887 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 207 | 4738436 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 62 | 849745 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 44 | 304560 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 853251 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 369120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 1014720 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 125455 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 66 | 911640 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 31 | 258436 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 104 | 185673 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1133 | 27736361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 116640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6829090.91 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2426.5 | 50773854.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 181 | 4768000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 260 | 6630000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 385 | 9511000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1231244 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 1207709 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 183360 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2481610 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 105 | 1127040 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1294080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 36245 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 419190 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 60 | 90060 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 47040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 1109760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 488855 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1503 | 30625193
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 32 | 930240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 46 | 468000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1752000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 126720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 104880 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 4320 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 146 | 3398610
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1410000 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3684600 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 723744 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1947840 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3405720 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 391000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 172968 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7478500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 301 | 8476000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1159 | 28407372
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 874 | 20951272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 116 | 3031200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 363600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 371 | 9040000 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1399 | 34298072
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 616 | 14305454.54 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2750000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 27537454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5492810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 182400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6458000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1378 | -
Barishal Area Total |  |  |  |  | 2858 | 2455 | 56727497.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 187468 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 9 | 189963 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 129254 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3518518 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 331 | 9218400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 84714 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 636080 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 106 | 323040 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 100 | 193152 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1372.3 | 29825055 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 377248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 564800 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2183.3 | 45281172
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1093963 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 143 | 3483000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 613776 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23888.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 815303 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 179037 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1134000 | -
Rangpur Area Total |  |  |  |  | 950 | 403 | 7342967.28
Eastern Grid Total |  |  |  |  | 17385.715 | 7988 | 165997247.51
Western Grid Total |  |  |  |  | 10980.24 | 6440.3 | 143649708.37
National Grid Total |  |  |  |  | 28365.955 | 14428.3 | 309646955.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9589.41 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4413.3 | MW
i) Dhaka area |  |  | 5129.01 |  | MW | i) Khulna area |  |  |  | 1648.6 | MW
ii) Chattogram area |  |  | 1429.2 |  | MW | ii) Barishal area |  |  |  | 372.5 | MW
iii) Cumilla area |  |  | 1393.2 |  | MW | iii) Rajshahi area |  |  |  | 1421.2 | MW
iv) Mymensingh area |  |  | 1052 |  | MW | iv) Rangpur area |  |  |  | 971 | MW
v) Sylhet area |  |  | 586 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14002.71 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 19:00 | 133 | PHP | 6 | 01:00
2 | AKSML | 129.3 | 23:00 | 68 | Ishurdi | 78 | 18:30 | 134 | Pabna | 99 | 19:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 78 | 18:30 | 135 | Palashbari | 110 | 18:30
4 | Agargaon | 125 | 12:00 | 70 | Jamalpur | 120 | 21:00 | 136 | Panchagarh | 59 | 18:30
5 | Agrabad | 90 | 18:00 | 71 | Jashore | 134 | 18:30 | 137 | Patiya | 10.6 | 23:00
6 | Amnura | 26 | 21:00 | 72 | Jhenaidah | 126 | 18:30 | 138 | Patuakhali | 64 | 00:00
7 | Ashuganj | 83 | 00:00 | 73 | Joydebpur | 150 | 12:00 | 139 | Payra | 30 | 00:00
8 | BSRM | 116 | 19:30 | 74 | Joypurhat | 61 | 19:00 | 140 | Postogola | 66 | 13:00
9 | Bagerhat | 71 | 00:00 | 75 | Juldah | 17.5 | 00:00 | 141 | Purbachal | 19 | 13:00
10 | Bajitpur | 81 | 22:00 | 76 | KSRM | 27 | 12:00 | 142 | Purbasadipur | 116 | 18:30
11 | Bakulia | 98 | 18:30 | 77 | Kabirpur | 260 | 11:00 | 143 | Rahanpur | 35 | 21:00
12 | Banani | 47.4 | 13:00 | 78 | Kachua | 88 | 00:00 | 144 | Rahim | 24 | 00:00
13 | Bangabhaban | 22 | 10:00 | 79 | Kallyanpur | 99 | 13:00 | 145 | Rajbari | 80 | 18:30
14 | Barapukuria | 64 | 18:30 | 80 | Kalurghat | 42 | 11:00 | 146 | Rajendrapur | 122 | 12:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 77 | 13:00 | 147 | Rajshahi | 100 | 18:30
16 | Barishal | 108 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajshahi-230 | 102 | 19:00
17 | Barishal-230 | 88 | 00:00 | 83 | Kasba | 34 | 22:00 | 149 | Ramganj | 112 | 00:00
18 | Baroaulia | 64 | 13:00 | 84 | Kazla | 99 | 19:00 | 150 | Rampur | 41 | 19:00
19 | Baroirhat | 61 | 18:00 | 85 | Keranigonj | 91 | 19:30 | 151 | Rangamati | 17 | 18:30
20 | Bashundhara | 195 | 13:00 | 86 | Khagrachori | 28 | 18:00 | 152 | Rangpur | 146 | 18:30
21 | BashundharaCement | 12 | 09:00 | 87 | Khulna | 67 | 13:00 | 153 | Ruppur | 8.6 | 16:00
22 | Beanibazar | 70 | 18:00 | 88 | Khulshi | 202 | 18:30 | 154 | SSM | 12 | 03:00
23 | Benapole | 56 | 00:00 | 89 | Kishoreganj | 117 | 19:30 | 155 | Saidpur | 103 | 19:00
24 | Bhaluka | 142 | 19:00 | 90 | Kodda | 298 | 15:00 | 156 | Satkhira | 113 | 00:00
25 | Bhandaria | 51 | 20:00 | 91 | Kulaura | 49 | 18:30 | 157 | Satmasjid | 97 | 13:00
26 | Bhangura | 36 | 18:00 | 92 | Kurigram | 66 | 18:00 | 158 | Savar | 214 | 11:00
27 | Bheramara(GK) | 65 | 18:00 | 93 | Kushtia | 151 | 18:30 | 159 | SevenRings | 5.25 | 17:00
28 | Bhulta | 216 | 15:00 | 94 | Laksam | 33 | 00:00 | 160 | ShahCement | 25 | 00:00
29 | Bog-Sherpur | 72 | 18:30 | 95 | Lakshmipur | 29 | 21:00 | 161 | Shahjadpur | 86 | 19:30
30 | Bogura | 160 | 20:00 | 96 | Lalbag | 60 | 11:00 | 162 | Shahjibazar | 121 | 21:00
31 | Borhanuddin | 92 | 00:00 | 97 | Lalmonirhat | 62 | 18:30 | 163 | Shahmirpur | 56 | 21:00
32 | Brahmanbaria | 125 | 22:00 | 98 | MI_Cement | 16.4 | 23:00 | 164 | Shariatpur | 80 | 00:00
33 | Cantonment | 136 | 13:00 | 99 | Madanganj | 30 | 19:00 | 165 | Sherpur | 132 | 18:00
34 | Chandina | 14.42 | 21:00 | 100 | Madaripur | 100 | 00:00 | 166 | Shikalbaha | 28 | 12:00
35 | Chandpur | 76 | 00:00 | 101 | Madartek | 86 | 00:00 | 167 | Shitalakhya | 87.9 | 12:00
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 56 | 18:30 | 168 | Sholosohor | 48 | 15:00
37 | Chapai | 62 | 22:00 | 103 | Magura | 62 | 18:30 | 169 | Shyampur | 96 | 12:00
38 | Charsaidpur | 37 | 00:00 | 104 | Mahasthangarh | 74 | 18:30 | 170 | Siddhirganj | 119 | 10:00
39 | Chauddagram | 66 | 23:00 | 105 | Maijdee | 21 | 00:00 | 171 | Sirajganj | 110 | 19:30
40 | Chhatak | 34 | 00:00 | 106 | Manikganj | 123 | 19:30 | 172 | Sonargaon | 130 | 15:00
41 | Chowmuhani | 187 | 18:30 | 107 | Maniknagar | 64 | 13:00 | 173 | Sreemongol | 81 | 18:00
42 | Chuadanga | 115 | 18:30 | 108 | Matarbari | 52 | 22:00 | 174 | Sreepur | 105 | 12:00
43 | Coxsbazar | 140 | 18:00 | 109 | Matuail | 70 | 11:00 | 175 | Srinagar | 42.67 | 00:00
44 | Cumilla(N) | 140 | 19:00 | 110 | Millgate | 124 | 12:00 | 176 | Sunamganj | 57 | 23:00
45 | Cumilla(S) | 151 | 14:00 | 111 | Mirpur | 119 | 12:00 | 177 | Sylhet | 49 | 18:30
46 | Daganbhuiyan | 0 | 06:00 | 112 | Mirsorai | 12 | 15:00 | 178 | Sylhet-132 | 114 | 18:00
47 | Daudkandi | 149 | 20:00 | 113 | Mirzapur | 42 | 19:30 | 179 | TK | 22 | 18:00
48 | DhakaUniversity | 86 | 13:00 | 114 | Mithapukur | 68 | 18:30 | 180 | Tangail | 150 | 18:30
49 | Dhamrai | 136 | 18:00 | 115 | Modern | N/A | N/A | 181 | Taraganj | 20 | 18:00
50 | Dhanmondi | 110 | 13:00 | 116 | Mogbazar | 99.2 | 12:00 | 182 | Thakurgaon | 99 | 18:30
51 | Dohazari | 98 | 19:30 | 117 | Mongla | 49 | 12:00 | 183 | Tongi | 123 | 13:00
52 | Faridpur | 156 | 00:00 | 118 | Motijheel | 51 | 18:00 | 184 | Ullahpara | 39 | 18:30
53 | Fatullah | 110 | 11:00 | 119 | Muktagacha | 33 | 18:00 | 185 | Ullon | 48 | 13:00
54 | Fenchuganj | 40 | 18:00 | 120 | Munshiganj | 109 | 20:00 | 186 | Uttara | 80 | 12:00
55 | Feni | 113 | 18:00 | 121 | Muradnagar | 41 | 18:30 | 187 | UttaraNew | 58 | 12:00
56 | GPH | 3 | 00:00 | 122 | Mymensingh | 180 | 16:00 | 188 | Zigatola | 68 | 19:00
57 | Ghatail | 72 | 00:00 | 123 | Naogaon | 117 | 21:00
58 | Ghorashal | 0 | 00:00 | 124 | Narail | 53 | 18:30
59 | Ghorashal-230 | 102 | 19:00 | 125 | Narinda | 66 | 13:00
60 | Goalpara | 36 | 12:00 | 126 | Narshingdi | 176 | 22:00
61 | Gollamari | 94 | 20:00 | 127 | Natore | 145 | 18:30
62 | Gopalganj | 93.8 | 18:30 | 128 | Nawabganj | 41.2 | 21:00
63 | Gulshan | 120 | 12:00 | 129 | Netrakona | 129 | 18:00
64 | Halishahar | 78 | 16:00 | 130 | New | 58 | 12:00
65 | HaripurSBU | 134 | 22:00 | 131 | Niamatpur | 68 | 21:00
66 | Hasnabad | 78 | 17:00 | 132 | Noapara | 41 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13640.34 | 0 |  | 13640.34
1:00 | 13130.48 | 0 |  | 13130.48
2:00 | 12532.37 | 0 |  | 12532.37
3:00 | 12263.95 | 0 |  | 12263.95
4:00 | 11852.42 | 0 |  | 11852.42
5:00 | 11701.96 | 0 |  | 11701.96
6:00 | 11378.16 | 0 |  | 11378.16
7:00 | 11589.33 | 0 |  | 11589.33
8:00 | 11692.86 | 0 |  | 11692.86
9:00 | 11742.88 | 0 |  | 11742.88
10:00 | 12066.39 | 0 |  | 12066.39
11:00 | 12449.78 | 0 |  | 12449.78
12:00 | 12797.72 | 0 |  | 12797.72
13:00 | 12950.81 | 0 |  | 12950.81
14:00 | 12774.28 | 0 |  | 12774.28
15:00 | 12792.75 | 0 |  | 12792.75
16:00 | 12478.38 | 0 |  | 12478.38
17:00 | 12358.47 | 0 |  | 12358.47
18:00 | 13837.67 | 0 |  | 13837.67
19:00 | 14428.3 | 41 |  | 14471.15
19:30 | 14421.94 | 0 |  | 14421.94
20:00 | 14217.6 | 0 |  | 14217.6
21:00 | 14038.1 | 0 |  | 14038.1
22:00 | 13844.2 | 0 |  | 13844.2
23:00 | 13659.7 | 0 |  | 13659.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7326.2 | 6314.14 | 13640.34 | DAILY GENERATION CURVE
00:30 | 7188.7 | 6196.71 | 13385.41
01:00 | 7051.2 | 6079.28 | 13130.48 | 07-10-2025
01:30 | 6814.7 | 6016.725 | 12831.425
02:00 | 6578.2 | 5954.17 | 12532.37
02:30 | 6475.7 | 5922.46 | 12398.16
03:00 | 6373.2 | 5890.75 | 12263.95
03:30 | 6234.7 | 5823.485 | 12058.185
04:00 | 6096.2 | 5756.22 | 11852.42
04:30 | 6087.2 | 5689.99 | 11777.19
05:00 | 6078.2 | 5623.76 | 11701.96
05:30 | 6054.61 | 5485.45 | 11540.06
06:00 | 6031.02 | 5347.14 | 11378.16
06:30 | 6113.13 | 5370.615 | 11483.745
07:00 | 6195.24 | 5394.09 | 11589.33
07:30 | 6170.285 | 5470.81 | 11641.095
08:00 | 6145.33 | 5547.53 | 11692.86
08:30 | 6168.35 | 5549.52 | 11717.87
09:00 | 6191.37 | 5551.51 | 11742.88
09:30 | 6333.54 | 5571.095 | 11904.635
10:00 | 6475.71 | 5590.68 | 12066.39
10:30 | 6516.98 | 5741.105 | 12258.085
11:00 | 6558.25 | 5891.53 | 12449.78
11:30 | 6680.415 | 5943.335 | 12623.75
12:00 | 6802.58 | 5995.14 | 12797.72
12:30 | 6880.48 | 5993.785 | 12874.265
13:00 | 6958.38 | 5992.43 | 12950.81
13:30 | 6988.14 | 5874.405 | 12862.545
14:00 | 7017.9 | 5756.38 | 12774.28
14:30 | 6980.965 | 5802.55 | 12783.515
15:00 | 6944.03 | 5848.72 | 12792.75
15:30 | 6858.955 | 5776.61 | 12635.565
16:00 | 6773.88 | 5704.5 | 12478.38
16:30 | 6799.7 | 5618.725 | 12418.425
17:00 | 6825.52 | 5532.95 | 12358.47
17:30 | 7243.21 | 5854.86 | 13098.07
18:00 | 7660.9 | 6176.77 | 13837.67
18:30 | 7824.45 | 6308.535 | 14132.985
19:00 | 7988 | 6440.3 | 14428.3
19:30 | 7966.2 | 6455.74 | 14421.94
20:00 | 7777 | 6440.6 | 14217.6
20:30 | 7680.05 | 6447.8 | 14127.85 |  | Executive Engineer
21:00 | 7583.1 | 6455 | 14038.1 |  | Network Operation Division
21:30 | 7548.65 | 6392.5 | 13941.15
22:00 | 7514.2 | 6330 | 13844.2
22:30 | 7451.45 | 6300.5 | 13751.95
23:00 | 7388.7 | 6271 | 13659.7

## En-Curve
QF-LDC-12
Date | 07-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3318 | 1798.2 | 848 | 38 | 42 | 1414.14 | 220 | 4044 | 0 | 384 | 1532 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3317 | 1798.7 | 848 | 38 | 40 | 1412.21 | 219.5 | 4029.5 | 0 | 363 | 1318 | 0 | 0 | 1.5 | 0 | 07-10-2025
01:00 | 3316 | 1799.2 | 848 | 38 | 38 | 1410.28 | 219 | 4015 | 0 | 342 | 1104 | 0 | 0 | 1 | 0
01:30 | 3325.5 | 1797.7 | 848 | 38 | 38 | 1411.725 | 218.5 | 4030 | 0 | 273 | 849.5 | 0 | 0 | 1.5 | 0 | Energy Generated | 309.647 |  | MKWHr
02:00 | 3335 | 1796.2 | 848 | 38 | 38 | 1413.17 | 218 | 4045 | 0 | 204 | 595 | 0 | 0 | 2 | 0 | Energy not Served | 0.041 |  | MKWHr
02:30 | 3346.5 | 1803.7 | 848 | 38 | 37 | 1410.96 | 217.5 | 4034.5 | 0 | 192.5 | 467 | 0 | 0 | 2.5 | 0 | Total Energy Requirement | 309.688 |  | MKWHr
03:00 | 3358 | 1811.2 | 848 | 38 | 36 | 1408.75 | 217 | 4024 | 0 | 181 | 339 | 0 | 0 | 3 | 0
03:30 | 3350.5 | 1810.2 | 848 | 38 | 36 | 1363.485 | 217.5 | 4000 | 0 | 159 | 232.5 | 0 | 0 | 3 | 0
04:00 | 3343 | 1809.2 | 848 | 38 | 36 | 1318.22 | 218 | 3976 | 0 | 137 | 126 | 0 | 0 | 3 | 0
04:30 | 3357.5 | 1807.7 | 848.5 | 38 | 35 | 1268.49 | 218.5 | 3961.5 | 0 | 120.5 | 117.5 | 0 | 0 | 4 | 0
05:00 | 3372 | 1806.2 | 849 | 38 | 34 | 1218.76 | 219 | 3947 | 0 | 104 | 109 | 0 | 0 | 5 | 0
05:30 | 3355 | 1812.6 | 848.5 | 38 | 33 | 1165.245 | 219.5 | 3852.5 | 0.715 | 104 | 104.5 | 0 | 0 | 6.5 | 0
06:00 | 3338 | 1819 | 848 | 38 | 32 | 1111.73 | 220 | 3758 | 1.43 | 104 | 100 | 0 | 0 | 8 | 0
06:30 | 3372 | 1823 | 848 | 38 | 32 | 1067.71 | 220.5 | 3812 | 31.035 | 129.5 | 104.5 | 0 | 0 | 5.5 | 0
07:00 | 3406 | 1827 | 848 | 38 | 32 | 1023.69 | 221 | 3866 | 60.64 | 155 | 109 | 0 | 0 | 3 | 0
07:30 | 3366.5 | 1798.5 | 857.5 | 38 | 31 | 1018.89 | 221 | 3914 | 110.705 | 163 | 120.5 | 0 | 0 | 1.5 | 0
08:00 | 3327 | 1770 | 867 | 38 | 30 | 1014.09 | 221 | 3962 | 160.77 | 171 | 132 | 0 | 0 | 0 | 0
08:30 | 3279 | 1762 | 867 | 38 | 29 | 1016.105 | 221 | 3924.5 | 260.265 | 171 | 150 | 0 | 0 | 0 | 0
09:00 | 3231 | 1754 | 867 | 38 | 28 | 1018.12 | 221 | 3887 | 359.76 | 171 | 168 | 0 | 0 | 0 | 0
09:30 | 3256.5 | 1768 | 867.5 | 38 | 30 | 1019.75 | 221 | 3880.5 | 393.885 | 183.5 | 246 | 0 | 0 | 0 | 0
10:00 | 3282 | 1782 | 868 | 38 | 32 | 1021.38 | 221 | 3874 | 428.01 | 196 | 324 | 0 | 0 | 0 | 0
10:30 | 3228.5 | 1752.5 | 871 | 38 | 32 | 1066.77 | 221.5 | 3891.5 | 532.065 | 215 | 409.25 | 0 | 0 | 0 | 0
11:00 | 3175 | 1723 | 874 | 38 | 32 | 1112.16 | 222 | 3909 | 636.12 | 234 | 494.5 | 0 | 0 | 0 | 0
11:30 | 3225.5 | 1736.5 | 874 | 38 | 49 | 1114.145 | 222 | 3947 | 628.855 | 234 | 554.75 | 0 | 0 | 0 | 0
12:00 | 3276 | 1750 | 874 | 38 | 66 | 1116.13 | 222 | 3985 | 621.59 | 234 | 615 | 0 | 0 | 0 | 0
12:30 | 3239 | 1794.5 | 873.5 | 38 | 69 | 1134.47 | 221 | 3980 | 578.995 | 219 | 722.8 | 0 | 0 | 4 | 0
13:00 | 3202 | 1839 | 873 | 38 | 72 | 1152.81 | 220 | 3975 | 536.4 | 204 | 830.6 | 0 | 0 | 8 | 0
13:30 | 3200 | 1861.9 | 873.5 | 38 | 76 | 1157.83 | 219 | 3945.5 | 448.315 | 179 | 851.5 | 0 | 0 | 12 | 0
14:00 | 3198 | 1884.8 | 874 | 38 | 80 | 1162.85 | 218 | 3916 | 360.23 | 154 | 872.4 | 0 | 0 | 16 | 0
14:30 | 3211.5 | 1879.4 | 874.5 | 38 | 75 | 1214.475 | 218 | 3917 | 351.74 | 136.5 | 849.4 | 0 | 0 | 18 | 0
15:00 | 3225 | 1874 | 875 | 38 | 70 | 1266.1 | 218 | 3918 | 343.25 | 119 | 826.4 | 0 | 0 | 20 | 0
15:30 | 3205.5 | 1866.9 | 874.5 | 38 | 68 | 1264.785 | 218 | 3907.5 | 263.48 | 142.5 | 765.4 | 0 | 0 | 21 | 0
16:00 | 3186 | 1859.8 | 874 | 38 | 66 | 1263.47 | 218 | 3897 | 183.71 | 166 | 704.4 | 0 | 0 | 22 | 0
16:30 | 3213 | 1867.55 | 874.5 | 38 | 63 | 1265.09 | 218 | 3876 | 109.885 | 166.5 | 709.4 | 0 | 0 | 17.5 | 0
17:00 | 3240 | 1875.3 | 875 | 38 | 60 | 1266.71 | 218 | 3855 | 36.06 | 167 | 714.4 | 0 | 0 | 13 | 0
17:30 | 3295.5 | 1862.3 | 874.5 | 38 | 63 | 1315.74 | 218 | 3946 | 18.03 | 379.5 | 1079 | 0 | 0 | 8.5 | 0
18:00 | 3351 | 1849.3 | 874 | 38 | 66 | 1364.77 | 218 | 4037 | 0 | 592 | 1443.6 | 0 | 0 | 4 | 0
18:30 | 3239 | 1862.4 | 874 | 38 | 71 | 1368.535 | 219 | 4059.5 | 0 | 631 | 1763.55 | 0 | 0 | 7 | 20.5
19:00 | 3127 | 1875.5 | 874 | 38 | 76 | 1372.3 | 220 | 4082 | 0 | 670 | 2083.5 | 0 | 0 | 10 | 41
19:30 | 3258 | 1874.5 | 874 | 38 | 70 | 1368.74 | 221 | 4117 | 0 | 709 | 1891.7 | 0 | 0 | 0 | 0
20:00 | 3256 | 1852.5 | 873 | 38 | 76 | 1360.6 | 221 | 4108 | 0 | 707 | 1719.5 | 0 | 0 | 6 | 0
20:30 | 3260.5 | 1861.35 | 873.5 | 38 | 77 | 1360.8 | 221 | 4135 | 0 | 684 | 1612.7 | 0 | 0 | 4 | 0
21:00 | 3265 | 1870.2 | 874 | 38 | 78 | 1361 | 221 | 4162 | 0 | 661 | 1505.9 | 0 | 0 | 2 | 0
21:30 | 3274.5 | 1875.7 | 874 | 38 | 78 | 1361.5 | 221 | 4164.5 | 0 | 626.5 | 1421.45 | 0 | 0 | 6 | 0
22:00 | 3284 | 1881.2 | 874 | 38 | 78 | 1362 | 221 | 4167 | 0 | 592 | 1337 | 0 | 0 | 10 | 0
22:30 | 3271 | 1882.2 | 874 | 38 | 76 | 1364.5 | 221.5 | 4170 | 0 | 576 | 1272.75 | 0 | 0 | 6 | 0
23:00 | 3258 | 1883.2 | 874 | 38 | 74 | 1367 | 222 | 4173 | 0 | 560 | 1208.5 | 0 | 0 | 2 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 06:00 | 123 | 22:00 | Payra | 408 | 00:00 | 404 | 22:00
Ashuganj | 400 | 0:00 | 382 | 12:00 | Rahanpur | 404 | 09:00 | 392 | 02:00
Bhulta | 397 | 23:00 | 379 | 12:00 | Rampal | 398 | 01:00 | 389 | 00:00
Bibiana | 388 | 19:00 | 381 | 12:00
BIPTC | 402 | 03:00 | 392 | 18:30
Bogura | 393 | 09:00 | 380 | 22:00
Gopalganj | 392 | 07:00 | 381 | 06:00
Kaliakoir | 374 | 19:00 | 363 | 12:00
Madunaghat | 393 | 20:00 | 387 | 04:00
Meghnaghat | 386 | 19:00 | 378 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 06:00 | 222 | 12:00 | Kaliakoir | 233 | 19:00 | 225 | 12:00
AKSML | 235 | 19:00 | 226 | 04:00 | Keranigonj | 226 | 19:00 | 219 | 12:00
Aminbazar | 230 | 05:00 | 223 | 23:00 | Khulna(S) | 229 | 09:00 | 219 | 00:00
Ashuganj | 230 | 00:00 | 224 | 12:00 | Madunaghat | 234 | 19:00 | 228 | 07:00
Ashuganj-400 | 230 | 0:00 | 220 | 12:00 | Madunaghat-400 | 234 | 19:00 | 228 | 05:00
Baghabari | 233 | 07:00 | 225 | 00:00 | Maniknagar | 221 | 05:00 | 217 | 09:00
Barapukuria | 223 | 09:00 | 217 | 18:30 | Meghnaghat | 229 | 05:00 | 224 | 12:00
Barapukuria-230 | 223 | 9:00 | 216 | 18:00 | Meghnaghat-400 | 225 | 06:00 | 220 | 12:00
Barishal | 232 | 07:00 | 228 | 00:00 | Mirsorai | 232 | 19:00 | 223 | 03:00
Bheramara | 235 | 08:00 | 226 | 00:00 | Rajshahi | 233 | 09:00 | 223 | 00:00
Bhulta | 230 | 23:00 | 217 | 12:00 | Rampal | 228 | 08:00 | 220 | 00:00
Bibiana | 229 | 06:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 09:00 | 225 | 00:00 | Rampura | 227 | 06:00 | 214 | 12:00
Bogura | 235 | 09:00 | 226 | 23:00 | Shikalbaha | 233 | 19:00 | 226 | 10:00
Bogura-400 | 235 | 09:00 | 227 | 23:00 | Shyampur | 224 | 06:00 | 218 | 12:00
Borhanuddin | 237 | 08:00 | 232 | 00:00 | Siddhirganj | 223 | 18:00 | 218 | 12:00
BSRM | 231 | 19:00 | 223 | 03:00 | Sirajgonj | 238 | 06:00 | 234 | 00:00
Cumilla(N) | 225 | 18:30 | 220 | 09:00 | Sreepur | 227 | 06:00 | 220 | 12:00
Faridpur | 229 | 06:00 | 223 | 00:00 | Tongi | 228 | 19:30 | 220 | 09:00
Fenchuganj | 230 | 06:00 | 227 | 02:00
Ghorashal | 230 | 00:00 | 225 | 14:00
Ghorashal-230 | 227 | 00:00 | 215 | 12:00
Gopalganj | 231 | 06:00 | 226 | 00:00
GPH | 233 | 19:00 | 226 | 03:00
Haripur | 222 | 06:00 | 218 | 12:00
Hasnabad | 226 | 19:00 | 219 | 12:00
Hathazari | 233 | 18:30 | 223 | 11:00
Ishurdi | 236 | 08:00 | 227 | 00:00
Jhenaidah | 232 | 08:00 | 220 | 00:00
Kachua | 219 | 18:30 | 211 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 01:00 | 130 | 21:00 | Lalmonirhat | 128 | 02:00 | 119 | 18:00
Agargaon | 134 | 05:00 | 129 | 12:00 | Madanganj | 129 | 19:30 | 125 | 10:00
Agrabad | 133 | 18:30 | 127 | 09:00 | Madaripur | 135 | 09:00 | 130 | 00:00
AKS | 131 | 18:30 | 128 | 05:00 | Madartek | 134 | 01:00 | 125 | 12:00
Aminbazar | 135 | 19:00 | 130 | 23:00 | Madunaghat | 136 | 19:00 | 132 | 04:00
Amnura | 137 | 07:00 | 129 | 13:00 | Magura | 137 | 06:00 | 128 | 00:00
Ashuganj | 140 | 08:00 | 135 | 12:00 | Mahasthangarh | 131 | 09:00 | 125 | 22:00
Bagerhat | 131 | 15:00 | 118 | 00:00 | Maijdee | 130 | 18:30 | 125 | 02:00
Bajitpur | 130 | 04:00 | 127 | 00:00 | Manikganj | 128 | 05:00 | 120 | 11:00
Bakulia | 135 | 18:30 | 128 | 09:00 | Maniknagar | 134 | 06:00 | 129 | 12:00
Banani | 133 | 05:00 | 124 | 12:00 | Matarbari | 120 | 16:00 | 112 | 18:00
Bangabhaban | 134 | 06:00 | 129 | 12:00 | Matuail | 130 | 20:00 | 126 | 12:00
Barapukuria | 135 | 00:00 | 127 | 18:30 | Millgate | 132 | 00:00 | 124 | 12:00
Barguna | 139 | 00:00 | 133 | 06:00 | Mirpur | 134 | 19:00 | 129 | 12:00
Barishal | 133 | 06:00 | 131 | 00:00 | Mirzapur | 130 | 06:00 | 124 | 15:00
Barishal-230 | 134 | 17:00 | 129 | 00:00 | Mithapukur | 130 | 09:00 | 123 | 18:30
Baroaulia | 133 | 21:00 | 130 | 10:00 | MI_Cement | 131 | 20:00 | 127 | 12:00
Baroirhat | 129 | 18:30 | 124 | 03:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 134 | 06:00 | 121 | 17:00 | Mogbazar | 135 | 23:00 | 125 | 12:00
BashundharaCement | 129 | 19:30 | 125 | 10:00 | Mongla | 132 | 15:00 | 120 | 00:00
Beanibazar | 128 | 07:00 | 125 | 00:00 | Motijheel | 134 | 06:00 | 129 | 12:00
Benapole | 132 | 16:00 | 121 | 00:00 | Muktagacha | 130 | 08:00 | 124 | 12:00
Bhaluka | 128 | 08:00 | 125 | 12:00 | Munshiganj | 130 | 18:00 | 126 | 00:00
Bhandaria | 129 | 14:00 | 112 | 00:00 | Muradnagar | 128 | 19:00 | 124 | 01:00
Bhangura | 133 | 06:00 | 127 | 00:00 | Mymensingh | 132 | 08:00 | 117 | 16:00
Bheramara | 137 | 09:00 | 132 | 00:00 | Naogaon | 130 | 08:00 | 122 | 01:00
Bheramara(GK) | 136 | 07:00 | 132 | 00:00 | Narail | 138 | 09:00 | 128 | 18:30
Bhulta | 127 | 18:00 | 120 | 02:00 | Narinda | 134 | 6:00 | 129 | 12:00
Bog-Sherpur | 132 | 09:00 | 127 | 22:00 | Narshingdi | 130 | 08:00 | 121 | 12:00
Bogura | 134 | 10:00 | 128 | 02:00 | Natore | 134 | 09:00 | 127 | 00:00
Bogura-230 | 133 | 09:00 | 128 | 01:00 | Nawabganj | 134 | 05:00 | 128 | 12:00
Brahmanbaria | 132 | 05:00 | 128 | 12:00 | Netrakona | 125 | 10:00 | 120 | 05:00
Cantonment | 134 | 05:00 | 128 | 12:00 | New | 133 | 00:00 | 126 | 12:00
Chandina | 131 | 18:30 | 128 | 01:00 | Niamatpur | 138 | 07:00 | 132 | 00:00
Chandpur | 137 | 18:30 | 130 | 04:00 | Noapara | 134 | 10:00 | 125 | 00:00
Chandraghona | 136 | 19:00 | 133 | 02:00 | Pabna | 135 | 08:00 | 130 | 00:00
Chapai | 137 | 09:00 | 133 | 00:00 | Palashbari | 128 | 09:00 | 122 | 03:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 19:00 | 127 | 00:00 | Panchagarh | 134 | 20:00 | 120 | 08:00
Chauddagram | 131 | 19:00 | 127 | 00:00 | Patiya | 133 | 19:00 | 128 | 04:00
Chhatak | 128 | 05:00 | 122 | 23:00 | Patuakhali | 140 | 00:00 | 133 | 23:00
Chowmuhani | 130 | 18:30 | 121 | 00:00 | Payra | 137 | 00:00 | 135 | 03:00
Chuadanga | 136 | 01:00 | 126 | 00:00 | PHP | 130 | 19:00 | 125 | 00:00
Coxsbazar | 119 | 16:00 | 111 | 18:00 | Postogola | 133 | 05:00 | 129 | 12:00
Cumilla(N) | 132 | 18:30 | 128 | 02:00 | Purbachal | 134 | 23:00 | 124 | 12:00
Cumilla(S) | 133 | 03:00 | 127 | 13:00 | Purbasadipur | 131 | 00:00 | 121 | 13:00
Daganbhuiyan | 129 | 11:00 | 127 | 12:00 | Rahanpur | 139 | 09:00 | 134 | 00:00
Daudkandi | 125 | 00:00 | 121 | 01:00 | Rahanpur-400 | 139 | 09:00 | 135 | 00:00
DhakaUniversity | 135 | 00:00 | 125 | 12:00 | Rahim | 130 | 18:30 | 126 | 12:00
Dhamrai | 132 | 04:00 | 126 | 09:00 | Rajbari | 134 | 07:00 | 129 | 00:00
Dhanmondi | 134 | 22:00 | 128 | 09:00 | Rajendrapur | 136 | 00:00 | 123 | 12:00
Dohazari | 130 | 22:00 | 125 | 00:00 | Rajshahi | 134 | 09:00 | 127 | 00:00
Faridpur | 136 | 07:00 | 131 | 00:00 | Rajshahi-230 | 134 | 08:00 | 128 | 00:00
Fatullah | 136 | 06:00 | 132 | 12:00 | Ramganj | 132 | 18:30 | 126 | 06:00
Fenchuganj | 135 | 04:00 | 133 | 22:00 | Rampur | 133 | 18:30 | 127 | 09:00
Feni | 130 | 18:30 | 126 | 12:00 | Rampura | 134 | 23:00 | 124 | 12:00
Ghatail | 128 | 06:00 | 119 | 18:00 | Rangamati | 135 | 19:00 | 132 | 08:00
Ghorashal | 137 | 00:00 | 132 | 14:00 | Rangpur | 131 | 01:00 | 124 | 18:30
Goalpara | 137 | 17:00 | 127 | 00:00 | Ruppur | 137 | 08:00 | 132 | 00:00
Gollamari | 137 | 16:00 | 129 | 00:00 | Saidpur | 131 | 05:00 | 123 | 18:30
Gopalganj | 135 | 11:00 | 128 | 00:00 | Satkhira | 135 | 15:00 | 123 | 00:00
Gopalganj-400 | 135 | 06:00 | 132 | 00:00 | Satmasjid | 134 | 08:00 | 129 | 12:00
Gulshan | 134 | 23:00 | 125 | 12:00 | Savar | 135 | 19:00 | 128 | 09:00
Halishahar | 133 | 18:30 | 129 | 07:00 | SevenRings | 138 | 20:00 | 131 | 12:00
Haripur | 130 | 06:00 | 127 | 12:00 | ShahCement | 131 | 19:00 | 127 | 00:00
HaripurSBU | 130 | 18:00 | 127 | 12:00 | Shahjadpur | 135 | 05:00 | 131 | 00:00
Hasnabad | 132 | 04:00 | 130 | 09:00 | Shahjibazar | 133 | 06:00 | 129 | 21:00
Hathazari | 136 | 18:30 | 132 | 01:00 | Shahmirpur | 133 | 18:30 | 129 | 09:00
Ishurdi | 138 | 09:00 | 132 | 00:00 | Shariatpur | 134 | 07:00 | 128 | 00:00
Jaldhaka | 128 | 00:00 | 119 | 18:30 | Sherpur | 129 | 09:00 | 115 | 18:00
Jamalpur | 131 | 08:00 | 121 | 01:00 | Shikalbaha | 124 | 19:00 | 119 | 09:00
Jashore | 137 | 08:00 | 127 | 00:00 | Shikalbaha-230 | 135 | 19:00 | 131 | 05:00
Jhenaidah | 138 | 05:00 | 123 | 00:00 | Shitalakhya | 131 | 20:00 | 127 | 12:00
Jhenaidah-230 | 138 | 08:00 | 130 | 00:00 | Sholosohor | 135 | 18:30 | 131 | 09:00
Joydebpur | 136 | 19:30 | 126 | 10:00 | Shyampur | 137 | 06:00 | 133 | 11:00
Joypurhat | 129 | 09:00 | 119 | 22:00 | Shyampur-230 | 136 | 06:00 | 132 | 12:00
Juldah | 133 | 19:00 | 129 | 01:00 | Siddhirganj | 130 | 06:00 | 127 | 10:00
Kabirpur | 134 | 19:00 | 122 | 12:00 | Sirajganj | 131 | 09:00 | 125 | 20:00
Kachua | 138 | 18:30 | 131 | 05:00 | Sonargaon | 128 | 05:00 | 126 | 00:00
Kaliakoir | 135 | 19:00 | 129 | 12:00 | Sreemongol | 133 | 08:00 | 129 | 12:00
Kallyanpur | 135 | 19:00 | 131 | 09:00 | Sreepur | 132 | 06:00 | 127 | 12:00
Kalurghat | 135 | 18:30 | 132 | 04:00 | Srinagar | 134 | 05:00 | 129 | 11:00
Kamrangirchar | 134 | 06:00 | 128 | 12:00 | SSM | 136 | 00:00 | 132 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 06:00 | 120 | 00:00
Kasba | 127 | 18:00 | 122 | 12:00 | Sylhet | 130 | 08:00 | 127 | 00:00
Kazla | 133 | 03:00 | 130 | 11:00 | Sylhet-132 | 129 | 04:00 | 127 | 00:00
Keranigonj | 134 | 06:00 | 129 | 12:00 | Tangail | 128 | 13:00 | 121 | 18:00
Khagrachori | 134 | 19:00 | 130 | 12:00 | Taraganj | 129 | 09:00 | 123 | 07:00
Khulna | 135 | 08:00 | 126 | 00:00 | Thakurgaon | 134 | 00:00 | 118 | 08:00
Khulna(S) | 137 | 16:00 | 128 | 00:00 | TK | 136 | 18:30 | 132 | 06:00
Khulshi | 132 | 19:30 | 127 | 09:00 | Tongi | 135 | 04:00 | 129 | 11:00
Kishoreganj | 129 | 06:00 | 125 | 18:00 | Ullahpara | 133 | 06:00 | 128 | 00:00
Kodda | 136 | 01:00 | 124 | 15:00 | Ullon | 134 | 00:00 | 124 | 12:00
KSRM | 135 | 22:00 | 130 | 04:00 | Uttara | 134 | 19:30 | 126 | 12:00
Kulaura | 135 | 07:00 | 132 | 00:00 | UttaraNew | 134 | 19:00 | 128 | 09:00
Kurigram | 128 | 11:00 | 119 | 18:30 | Zigatola | 134 | 07:00 | 129 | 10:00
Kushtia | 133 | 09:00 | 127 | 00:00
Laksam | 137 | 19:00 | 131 | 22:00
Lakshmipur | 130 | 19:00 | 125 | 03:00
Lalbag | 133 | 05:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division