## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-10-2025 | [28 empty] | Date: | 08-10-2025 | [28 empty] | Date: | 08-10-2025 | [28 empty] | Date: | 08-10-2025 | [28 empty] | Date: | 08-10-2025 | [14 empty] | Date: | 08-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 18 | 10 | 115 | 64 | 45 | 0 | 0 | 72 | 0 | 300 | 145 | 550 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 25.2 | 22 | 0 | 0 | 47 | 15 | 83 | 0 | 2 | 66 | 51 | 0 | 0 | 0 | 0 | 222 | 109 | 27 | 285 | 0 | 0 | 33 | 8 | 21 | 187 | 0 | 0 | 0 | 1145 | 0 | 51 | 127 | 0 | 380 | 0 | 260 | 0 | 194 | 0 | 71 | 106 | 83 | 0 | 17 | 0 | 78 | 0 | 0 | 29 | 315 | 0 | 350 | 30 | 68 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 7365.2 | 874 | 126 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1363 | 0 | 40 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 348 | 0 | 0 | 148 | 47 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 616 | 1232 | 17 | 6207 | 13572.2 | 107.69
01:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 18 | 0 | 105 | 30 | 45 | 0 | 0 | 72 | 0 | 300 | 149 | 540 | 0 | 35 | 335 | 0 | 0 | 0 | 70 | 25.4 | 22 | 0 | 0 | 16 | 0 | 51 | 0 | 3 | 66 | 15 | 0 | 0 | 0 | 0 | 220 | 106 | 29 | 285 | 0 | 0 | 33 | 8 | 17 | 187 | 0 | 0 | 0 | 1127 | 0 | 51 | 80 | 0 | 380 | 0 | 260 | 0 | 191 | 0 | 69 | 106 | 78 | 0 | 17 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 336 | 30 | 68 | 153 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 7000.4 | 874 | 129 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1361 | 0 | 40 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 339 | 0 | 0 | 146 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 616 | 1120 | 17 | 6013 | 13013.4 | 107.68
02:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 18 | 0 | 75 | 15 | 0 | 0 | 0 | 72 | 0 | 300 | 143 | 539 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 0 | 0 | 0 | 0 | 218 | 85 | 29 | 285 | 0 | 0 | 33 | 0 | 17 | 187 | 0 | 0 | 0 | 1132 | 0 | 51 | 40 | 0 | 390 | 0 | 260 | 0 | 193 | 0 | 69 | 106 | 51 | 0 | 17 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 341 | 30 | 68 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6705.4 | 874 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 348 | 0 | 0 | 148 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 616 | 1092 | 17 | 5868 | 12573.4 | 107.67
03:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 18 | 0 | 42 | 15 | 0 | 0 | 0 | 54 | 0 | 300 | 143 | 505 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 25.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 29 | 285 | 0 | 0 | 33 | 0 | 17 | 187 | 0 | 0 | 0 | 1137 | 0 | 51 | 0 | 0 | 395 | 0 | 260 | 0 | 192 | 0 | 52 | 106 | 17 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 295 | 0 | 302 | 30 | 68 | 143 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6363.4 | 874 | 141 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 343 | 0 | 0 | 140 | 47 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 115 | 180 | 0 | 616 | 1082 | 17 | 5717 | 12080.4 | 107.66
04:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 15 | 0 | 300 | 143 | 530 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 29 | 285 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 0 | 395 | 0 | 260 | 0 | 193 | 0 | 52 | 106 | 0 | 0 | 18 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 309 | 30 | 68 | 148 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6108.4 | 873 | 148 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 399 | 0 | 0 | 142 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 616 | 1094 | 0 | 5640 | 11748.4 | 107.65
05:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 555 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 29 | 285 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 0 | 395 | 0 | 260 | 0 | 203 | 0 | 0 | 106 | 0 | 0 | 18 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 321 | 30 | 68 | 156 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6046.4 | 874 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 405 | 0 | 0 | 146 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 115 | 220 | 0 | 616 | 1050 | 0 | 5498 | 11544.4 | 107.64
06:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 146 | 555 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0.03 | 222 | 0 | 8 | 285 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1005 | 1 | 51 | 0 | 0 | 412 | 0 | 260 | 0 | 198 | 0 | 0 | 107 | 0 | 0 | 18 | 0 | 60 | 0 | 1 | 0 | 315 | 0 | 320 | 30 | 68 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6022.43 | 874 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 388 | 0 | 0 | 141 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 115 | 220 | 0 | 616 | 1000 | 0 | 5329 | 11351.43 | 107.63
07:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 146 | 555 | 0 | 0 | 335 | 0 | 0 | 4 | 35 | 23.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 0 | 0 | 0.64 | 222 | 0 | 25 | 285 | 0 | 0 | 14 | 0 | 0 | 187 | 0 | 0 | 0 | 1050 | 6 | 51 | 0 | 0 | 412 | 0 | 260 | 0 | 198 | 0 | 0 | 106 | 0 | 5 | 19 | 0 | 58 | 0 | 15 | 0 | 315 | 0 | 319 | 30 | 68 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 32 | 0 | 4.79 | 0 | 6172.83 | 874 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11.08 | 364 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 8 | 0 | 0 | 7.46 | 0 | 0 | 130 | 0 | 0 | 0 | 389 | 0 | 0.68 | 140 | 49 | 0 | 4 | 0 | 0 | 0 | 0 | 0.7 | 8 | 0.08 | 0 | 203 | 115 | 220 | 0 | 492 | 1010 | 0 | 5345.13 | 11517.96 | 107.62
08:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 144 | 548 | 0 | 0 | 335 | 0 | 0 | 11 | 35 | 23.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 16 | 0 | 0 | 0 | 0 | 1.51 | 222 | 0 | 11 | 285 | 0 | 0 | 19 | 0 | 0 | 198 | 0 | 0 | 0 | 1040 | 13 | 51 | 0 | 0 | 385 | 0 | 260 | 0 | 194 | 0 | 0 | 106 | 0 | 9 | 19 | 0 | 60 | 0 | 43 | 0 | 310 | 0 | 304 | 30 | 68 | 154 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 33 | 0 | 15.62 | 0 | 6134.53 | 890 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 358 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.24 | 29 | 0 | 0 | 15.53 | 0 | 0 | 130 | 0 | 0 | 0 | 345 | 0 | 1.79 | 138 | 49 | 0 | 5 | 0 | 0 | 0 | 0 | 2.4 | 74 | 0.26 | 0 | 199 | 115 | 220 | 0 | 462 | 1052 | 0 | 5452.22 | 11586.75 | 107.61
09:00 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 24 | 30 | 0 | 0 | 17 | 0 | 0 | 300 | 144 | 550 | 0 | 0 | 334 | 0 | 0 | 16 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 2.56 | 222 | 0 | 3 | 285 | 0 | 0 | 22 | 0 | 0 | 201 | 0 | 0 | 0 | 1051 | 11 | 51 | 0 | 0 | 385 | 0 | 260 | 0 | 195 | 0 | 0 | 104 | 0 | 0 | 19 | 0 | 62 | 0 | 21 | 0 | 310 | 0 | 317 | 30 | 68 | 157 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 27 | 1 | 20.37 | 0 | 6119.93 | 890 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 356 | 0 | 1120.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.44 | 62 | 0 | 0 | 39.92 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 3.33 | 140 | 49 | 0 | 19 | 0 | 0 | 0 | 0 | 3.6 | 79 | 0.2 | 0 | 200 | 115 | 220 | 0 | 461 | 1051 | 0 | 5570.58 | 11690.51 | 107.6
10:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 35 | 0 | 0 | 300 | 149 | 550 | 0 | 0 | 331 | 0 | 0 | 21 | 35 | 22 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 1.55 | 222 | 0 | 6 | 285 | 0 | 0 | 40 | 2 | 0 | 202 | 0 | 0 | 0 | 1118 | 20 | 51 | 0 | 0 | 390 | 0 | 240 | 0 | 201 | 0 | 1 | 103 | 0 | 0 | 6 | 0 | 58 | 0 | 69 | 0 | 315 | 0 | 373 | 30 | 68 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 28 | 1 | 39.6 | 0 | 6401.15 | 897 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 358 | 0 | 1117.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.24 | 80 | 0 | 0 | 48.07 | 0 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 4.34 | 136 | 49 | 0 | 24 | 0 | 0 | 0 | 0 | 4.8 | 46 | 0.75 | 0 | 241 | 115 | 220 | 0 | 461 | 1050 | 0 | 5646.55 | 12047.7 | 107.59
11:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17.5 | 11 | 50 | 15 | 7 | 0 | 35 | 75 | 0 | 300 | 145 | 520 | 0 | 17 | 332 | 0 | 0 | 0 | 52 | 21.5 | 9 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 16 | 0 | 0 | 0 | 0 | 2.22 | 222 | 13 | 2 | 285 | 0 | 0 | 50 | 22 | 10 | 204 | 0 | 0 | 0 | 1163 | 9 | 51 | 6 | 0 | 390 | 0 | 240 | 0 | 200 | 0 | 38 | 103 | 24 | 0 | 6 | 0 | 60 | 0 | 77 | 0 | 320 | 0 | 354 | 30 | 68 | 158 | 9 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 26 | 1 | 48.18 | 0 | 6671.4 | 899 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 356 | 0 | 1114.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.93 | 77 | 0 | 0 | 52.95 | 0 | 0 | 130 | 0 | 0 | 0 | 410 | 0 | 5.05 | 148 | 49 | 0 | 24 | 0 | 0 | 0 | 0 | 6.9 | 88 | 0.65 | 0 | 277 | 115 | 220 | 0 | 394 | 1116 | 2 | 5785.65 | 12457.05 | 107.58
12:00 | 0 | 71 | 16 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17.5 | 17 | 68 | 15 | 65 | 0 | 35 | 90 | 0 | 300 | 141 | 520 | 0 | 35 | 300 | 0 | 0 | 32 | 70 | 0 | 22 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 1.16 | 222 | 48 | 2 | 285 | 25 | 0 | 50 | 25 | 17 | 203 | 0 | 0 | 0 | 1164 | 10 | 51 | 40 | 0 | 385 | 0 | 240 | 0 | 193 | 0 | 51 | 102 | 61 | 0 | 8 | 0 | 66 | 0 | 25 | 0 | 315 | 0 | 321 | 30 | 68 | 156 | 9 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 26 | 2 | 22.49 | 2 | 6889.15 | 899 | 148 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 350 | 0 | 1251.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.45 | 107 | 0 | 0 | 55.5 | 0 | 0 | 130 | 0 | 0 | 0 | 363 | 0 | 5.11 | 137 | 48 | 0 | 23 | 0 | 0 | 0 | 0 | 5.9 | 92 | 0.5 | 0 | 307 | 115 | 220 | 0 | 365 | 1165 | 17 | 5996.43 | 12885.58 | 107.57
13:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 33 | 17 | 132 | 30 | 110 | 7 | 35 | 90 | 0 | 300 | 146 | 525 | 0 | 35 | 300 | 0 | 0 | 31 | 70 | 21.2 | 22 | 0 | 0 | 12 | 0 | 51 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0.76 | 222 | 71 | 3 | 285 | 45 | 0 | 50 | 25.5 | 17 | 203 | 0 | 0 | 0 | 1144 | 13 | 51 | 85 | 0 | 385 | 0 | 270 | 0 | 193 | 0 | 51 | 100 | 100 | 0 | 17 | 0 | 78 | 0 | 8 | 0 | 310 | 0 | 348 | 30 | 68 | 151 | 9 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 68 | 48 | 12 | 1 | 30.9 | 6 | 7320.36 | 900 | 140 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 346 | 0 | 1316.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.96 | 100 | 0 | 0 | 57.36 | 0 | 0 | 130 | 0 | 0 | 0 | 356 | 0 | 5.08 | 141 | 48 | 0 | 28 | 0 | 0 | 0 | 0 | 6.7 | 38 | 0.28 | 0 | 307 | 115 | 220 | 0 | 301 | 1216 | 17 | 5909.42 | 13229.78 | 107.56
14:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35.9 | 15 | 133 | 30 | 110 | 15 | 35 | 90 | 0 | 300 | 143 | 510 | 0 | 55 | 335 | 0 | 0 | 26 | 70 | 21.2 | 22 | 0 | 0 | 15 | 0 | 50 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0.78 | 219 | 80 | 2 | 285 | 15 | 0 | 50 | 25.5 | 17 | 201 | 0 | 0 | 0 | 1115 | 7 | 51 | 97 | 0 | 353 | 0 | 270 | 0 | 186 | 0 | 51 | 100 | 96 | 0 | 16 | 0 | 76 | 0 | 25 | 10 | 305 | 0 | 325 | 30 | 68 | 151 | 10 | 0 | 81 | 20 | 0 | 16 | 165 | 9 | 66 | 48 | 11 | 1 | 39 | 0 | 7238.38 | 899 | 136 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.51 | 347 | 0 | 1314.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.99 | 82 | 0 | 0 | 49.32 | 0 | 0 | 130 | 0 | 0 | 0 | 339 | 0 | 4.38 | 141 | 48 | 0 | 12 | 0 | 0 | 0 | 0 | 5.2 | 66 | 0.25 | 0 | 256 | 115 | 180 | 0 | 301 | 1180 | 17 | 5729.15 | 12967.53 | 107.55
15:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35.6 | 17 | 133 | 36 | 110 | 15 | 35 | 90 | 0 | 300 | 150 | 530 | 0 | 35 | 328 | 0 | 0 | 19 | 70 | 22.5 | 22 | 0 | 0 | 15 | 0 | 50 | 0 | 4 | 48 | 0 | 0 | 0 | 0 | 0.79 | 218 | 97 | 7 | 285 | 17 | 0 | 50 | 25.5 | 17 | 203 | 0 | 0 | 0 | 1159 | 5 | 51 | 100 | 0 | 350 | 0 | 280 | 0 | 200 | 0 | 55 | 100 | 100 | 0 | 17 | 0 | 74 | 0 | 15 | 10 | 310 | 0 | 364 | 30 | 68 | 157 | 10 | 0 | 81 | 20 | 0 | 16 | 165 | 17 | 66 | 48 | 12 | 1 | 26.12 | 0 | 7368.51 | 899 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.87 | 346 | 0 | 1319.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.42 | 5 | 0 | 0 | 33.91 | 0 | 0 | 130 | 0 | 0 | 0 | 410 | 0 | 3.21 | 145 | 48 | 0 | 7 | 0 | 0 | 0 | 0 | 1.9 | 20 | 0.05 | 0 | 277 | 115 | 220 | 0 | 301 | 1110 | 17 | 5640.64 | 13009.15 | 107.54
16:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 35.9 | 17 | 133 | 45 | 110 | 15 | 36 | 90 | 0 | 300 | 144 | 520 | 0 | 35 | 330 | 0 | 0 | 11 | 70 | 20.5 | 22 | 0 | 0 | 21 | 15 | 50 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 0.51 | 218 | 104 | 9 | 285 | 15 | 0 | 50 | 25.5 | 17 | 203 | 0 | 0 | 0 | 1143 | 2 | 51 | 100 | 0 | 355 | 0 | 290 | 0 | 188 | 0 | 69 | 102 | 100 | 0 | 18 | 0 | 68 | 0 | 11 | 14 | 315 | 0 | 324 | 30 | 68 | 157 | 10 | 0 | 79 | 0 | 0 | 16 | 165 | 17 | 66 | 47 | 12 | 0 | 14.73 | 0 | 7306.14 | 899 | 130 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 345 | 0 | 1315.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.56 | 19 | 0 | 0 | 3.49 | 0 | 0 | 130 | 0 | 0 | 0 | 401 | 0 | 0.4 | 146 | 48 | 0 | 7 | 0 | 0 | 0 | 0 | 1 | 24 | 0.13 | 0 | 275 | 115 | 220 | 0 | 310 | 1100 | 17 | 5582.81 | 12888.95 | 107.54
17:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35.9 | 21 | 128 | 50 | 110 | 15 | 55 | 90 | 0 | 300 | 142 | 510 | 0 | 35 | 331 | 0 | 0 | 3 | 70 | 20.5 | 22 | 0 | 0 | 28 | 20 | 51 | 0 | 2 | 48 | 0 | 17 | 0 | 0 | 0 | 219 | 94 | 12 | 285 | 45 | 0 | 50 | 25.5 | 17 | 203 | 0 | 0 | 0 | 1088 | 1 | 51 | 103 | 0 | 330 | 0 | 290 | 0 | 179 | 0 | 69 | 103 | 98 | 0 | 17 | 5 | 66 | 0 | 4 | 14 | 310 | 0 | 313 | 30 | 68 | 154 | 10 | 0 | 81 | 0 | 0 | 16 | 165 | 17 | 66 | 47 | 12 | 0 | 2.2 | 4 | 7246.1 | 899 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.35 | 346 | 0 | 1315.43 | 0 | 27 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 5.86 | 6 | 0 | 0 | 1.08 | 0 | 0 | 130 | 0 | 0 | 0 | 337 | 0 | 0.11 | 145 | 48 | 0 | 3 | 6 | 0 | 0 | 0 | 0.6 | 4 | 0.05 | 0 | 268 | 115 | 220 | 0 | 305 | 1095 | 17 | 5501.48 | 12747.58 | 107.53
18:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 40.5 | 35 | 125 | 105 | 195 | 45 | 35 | 126 | 0 | 350 | 143 | 450 | 0 | 55 | 325 | 0 | 0 | 0 | 125 | 20.5 | 0 | 0 | 0 | 30 | 30 | 89 | 0 | 3 | 48 | 29 | 17 | 0 | 0 | 0 | 220 | 92 | 19 | 285 | 80 | 0 | 50 | 25.5 | 105 | 203 | 0 | 0 | 0 | 1156 | 0 | 51 | 113 | 0 | 320 | 0 | 300 | 0 | 207 | 0 | 70 | 104 | 93 | 0 | 17 | 18 | 72 | 2 | 0 | 30 | 305 | 0 | 369 | 30 | 68 | 146 | 7 | 0 | 81 | 0 | 0 | 16 | 165 | 17 | 66 | 47 | 12 | 0 | 0 | 0 | 7907.5 | 899 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 1350.29 | 0 | 47 | 0 | 35 | 1 | 0 | 96 | 13 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 0 | 142 | 49 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 307 | 1082 | 17 | 5885.29 | 13792.79 | 107.52
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 50.3 | 35 | 132 | 127 | 295 | 55 | 35 | 126 | 0 | 400 | 133 | 550 | 0 | 55 | 335 | 0 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 75 | 80 | 100 | 0 | 0 | 65 | 56 | 34 | 0 | 0 | 0 | 221 | 97 | 6 | 285 | 134 | 0 | 50 | 25.5 | 105 | 203 | 0 | 0 | 0 | 1211 | 0 | 51 | 122 | 0 | 320 | 0 | 300 | 0 | 181 | 0 | 90 | 104 | 131 | 6 | 19 | 62 | 66 | 16 | 0 | 27 | 305 | 0 | 298 | 30 | 68 | 158 | 8 | 0 | 81 | 0 | 0 | 16 | 165 | 17 | 66 | 47 | 12 | 0 | 0 | 1 | 8478.3 | 899 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 1354.21 | 0 | 47 | 0 | 100 | 92 | 0 | 96 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 388 | 0 | 0 | 145 | 49 | 110 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 307 | 1200 | 17 | 6256.21 | 14734.51 | 107.52
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 43.3 | 35 | 133 | 127 | 295 | 55 | 35 | 126 | 0 | 400 | 144 | 535 | 0 | 55 | 335 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 0 | 85 | 80 | 100 | 0 | 0 | 65 | 58 | 37 | 0 | 0 | 0 | 221 | 103 | 14 | 285 | 140 | 0 | 50 | 25.5 | 105 | 201 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 0 | 320 | 0 | 300 | 0 | 192 | 0 | 90 | 104 | 142 | 9 | 19 | 68 | 68 | 16 | 0 | 33 | 300 | 0 | 315 | 30 | 68 | 153 | 8 | 0 | 81 | 20 | 0 | 16 | 166 | 17 | 66 | 47 | 12 | 0 | 0 | 0 | 8588.8 | 661 | 102 | 0 | 0 | 6 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 1413 | 0 | 47 | 0 | 113 | 108 | 0 | 96 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 405 | 0 | 0 | 145 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 307 | 115 | 220 | 0 | 307 | 1200 | 17 | 6131 | 14719.8
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 44.2 | 35 | 133 | 75 | 295 | 55 | 35 | 126 | 0 | 400 | 146 | 530 | 0 | 55 | 335 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 0 | 81 | 80 | 99 | 0 | 2 | 65 | 58 | 54.36 | 0 | 0 | 0 | 222 | 103 | 15 | 285 | 135 | 0 | 50 | 8 | 105 | 198 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 0 | 320 | 0 | 300 | 0 | 188 | 0 | 90 | 104 | 139 | 9 | 19 | 50 | 70 | 0 | 0 | 36 | 300 | 0 | 311 | 30 | 68 | 150 | 8 | 0 | 81 | 20 | 0 | 16 | 166 | 17 | 67 | 47 | 12 | 0 | 0 | 0 | 8474.56 | 601 | 103 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 1435.59 | 0 | 47 | 0 | 113 | 100 | 0 | 96 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 399 | 0 | 0 | 144 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 307 | 115 | 220 | 0 | 306 | 1200 | 17 | 6112.59 | 14587.15 | 107.52
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 45.3 | 17 | 133 | 75 | 295 | 55 | 35 | 126 | 0 | 400 | 147 | 540 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 85 | 80 | 101 | 0 | 0 | 65 | 58 | 54.36 | 0 | 0 | 0 | 222 | 105 | 20 | 285 | 137 | 0 | 50 | 8 | 51 | 196 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 0 | 320 | 0 | 300 | 0 | 188 | 0 | 62 | 104 | 143 | 9 | 17 | 29 | 70 | 0 | 0 | 36 | 310 | 0 | 312 | 30 | 68 | 152 | 8 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 47 | 18 | 0 | 0 | 0 | 8391.16 | 601 | 103 | 0 | 2 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 1443 | 0 | 47 | 0 | 113 | 113 | 0 | 96 | 38 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 401 | 0 | 0 | 147 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 306 | 1210 | 17 | 6195 | 14586.16 | 107.52
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 33 | 17 | 133 | 75 | 295 | 55 | 35 | 108 | 0 | 400 | 147 | 520 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20.5 | 21 | 0 | 0 | 85 | 80 | 106 | 0 | 0 | 65 | 59 | 54.36 | 0 | 0 | 0 | 222 | 106 | 12 | 285 | 150 | 0 | 50 | 8 | 34 | 192 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 320 | 0 | 300 | 0 | 193 | 0 | 56 | 105 | 144 | 0 | 17 | 29 | 70 | 0 | 0 | 36 | 300 | 0 | 334 | 30 | 68 | 154 | 8 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 47 | 16 | 0 | 0 | 0 | 8341.86 | 601 | 99 | 0 | 11 | 45 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 1433 | 0 | 47 | 0 | 113 | 113 | 0 | 96 | 38 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 147 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 307 | 115 | 220 | 0 | 306 | 1222 | 17 | 6138 | 14479.86 | 107.51
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 18 | 17 | 133 | 75 | 277 | 55 | 35 | 72 | 0 | 400 | 148 | 500 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 90 | 52 | 106 | 0 | 0 | 65 | 59 | 54.36 | 0 | 0 | 0 | 222 | 106 | 13 | 285 | 140 | 0 | 50 | 8 | 23 | 192 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 0 | 320 | 0 | 300 | 0 | 195 | 0 | 47 | 105 | 145 | 0 | 17 | 29 | 76 | 0 | 0 | 35 | 300 | 0 | 323 | 30 | 68 | 155 | 8 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 68 | 47 | 17 | 0 | 0 | 0 | 8187.36 | 601 | 99 | 0 | 19 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 1440 | 0 | 47 | 0 | 113 | 113 | 0 | 96 | 38 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 146 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 307 | 115 | 220 | 0 | 306 | 1222 | 17 | 6147 | 14334.36 | 107.51
Total KWH | 0 | 1944960 | 341280 | 0 | 0 | 0 | 0 | 0 | 8733600 | 0 | 0 | 519120 | 305280 | 2150352 | 1023840 | 2571818 | 443450 | 530064 | 1585440 | 0 | 8075000 | 3491316 | 12710000 | 0 | 531065 | 7952567 | 0 | 0 | 204820 | 1905600 | 426600 | 424080 | 0 | 0 | 648600 | 471709 | 1065600 | 0 | 69120 | 1090197 | 379776 | 345447 | 0 | 0 | 19199 | 5299422 | 1482036 | 381120 | 6821818.18 | 995273 | 0 | 937440 | 294516 | 648181 | 4638352 | 0 | 0 | 0 | 27234543 | 90855 | 1240492 | 1624218 | 0 | 8769500 | 0 | 6674000 | 0 | 4762000 | 0 | 1114560 | 2472290 | 1711200 | 47880 | 371249 | 240540 | 1608960 | 34565 | 340609 | 235400 | 7503000 | 0 | 8323000 | 716000 | 1593840 | 3703418 | 201096 | 0 | 1927680 | 524352 | 0 | 392000 | 4405440 | 118800 | 1612800 | 1149600 | 500160 | 9650 | 258380 | 26400 | 172996535.18 | 20152000 | 3328992 | 0 | 26880 | 162560 | 912000 | 0 | 0 | 0 | 0 | 0 | 370800 | 8596364 | 0 | 30884396 | 0 | 372243 | 0 | 639840 | 652800 | 0 | 774096 | 190433 | 66038 | 348756 | 536970 | 166401 | 0 | 372000 | 0 | 0 | 3401273 | 0 | 0 | 0 | 9054472 | 0 | 33540 | 3526000 | 1124073 | 834155 | 164504 | 826166 | 0 | 0 | 0 | 35926.44 | 560160 | 3265 | 130752 | 6240000 | 2744000 | 5453810 | 0 | 10144440 | 27905454.55 | 298800 | 141034359.99 | 314030895.17

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-10-2025 | during | 09-10-2025 | during | 09-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 395 | 330 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 141 | 133 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 50.3 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 20.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 65 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 132 | 149 | 149 | 115 | 115 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 71 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 126 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 520 | 550 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2209.5 | 2963.8 | 5834.4 | 5804.4 | 3982.11 | 4046.11
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25 | 25.5 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 203 | 203 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 60 | 60 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 26 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 6 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 20 | 100 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.16 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 80 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 34 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 48 | 97 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 75 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 25 | 134 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1164 | 1211 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 3 | 1 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2098.16 | 2747.5 | 3259.47 | 3261.72 | 3011.11 | 3013.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 193 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 300 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 385 | 320 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 122 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 27 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 104 | 163 | 163 | 106 | 106 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 61 | 131 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 66 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 62 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 6 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 25 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1222 | 1495 | 2663.86 | 2603.86 | 2335.86 | 2284.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-10-2025 | during | 09-10-2025 | during | 09-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 26 | 12 | 157.5 | 157.5 | 63 | 63 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 45 | 45 | 45 | 45 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 66 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22.49 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 2 | 1 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 168.49 | 143 | 385.9 | 346 | 220.9 | 181
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 68 | 0 | 0 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 158 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 9 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 321 | 298 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1191 | 1129 | 1215 | 1215 | 1226 | 1226
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 899 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 148 | 120 | 410 | 410 | 174 | 174 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 350 | 353 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1533 | 1410 | 2390 | 2312 | 1729 | 1651
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 365 | 307 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1165 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2189.5 | 2166 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.45 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 363 | 388 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 92 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.11 | 0 | 5.4 | 0 | 5.4 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1251.97 | 1354.21 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.5 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1968.03 | 2267.21 | 3184.27 | 3017.87 | 3110.89 | 2944.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 49 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 137 | 145 | 145 | 145 | 145 | 145 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 109 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 92 | 0 | 164.79 | 0 | 164.79 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 305.9 | 413 | 641.79 | 443 | 641.79 | 443
System Total |  |  |  |  | 28823.2 | 28365.955 | 12885.58 | 14734.51 | 21721.69 | 21149.85 | 18271.66 | 17802.82
Forecast Scenario (09-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13900 |  | 0 |  | 13900
|  |  |  | 1:00 | 12700 |  | 0 |  | 12700
|  |  |  | 2:00 | 12280 |  | 0 |  | 12280
|  |  |  | 3:00 | 11800 |  | 0 |  | 11800
|  |  |  | 4:00 | 11480 |  | 0 |  | 11480
|  |  |  | 5:00 | 11280 |  | 0 |  | 11280
|  |  |  | 6:00 | 11100 |  | 0 |  | 11100
|  |  |  | 7:00 | 11280 |  | 0 |  | 11280
|  |  |  | 8:00 | 11360 |  | 0 |  | 11360
|  |  |  | 9:00 | 11480 |  | 0 |  | 11480
|  |  |  | 10:00 | 11850 |  | 0 |  | 11850
|  |  |  | 11:00 | 12270 |  | 0 |  | 12270
|  |  |  | 12:00 | 12710 |  | 0 |  | 12710
|  |  |  | 13:00 | 13400 |  | 0 |  | 13400
|  |  |  | 14:00 | 12790 |  | 0 |  | 12790
|  |  |  | 15:00 | 12830 |  | 0 |  | 12830
|  |  |  | 16:00 | 12710 |  | 0 |  | 12710
|  |  |  | 17:00 | 12570 |  | 0 |  | 12570
|  |  |  | 18:00 | 13620 |  | 0 |  | 13620
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14630 |  | 0 |  | 14630
|  |  |  | 19:30 | 14600 |  | 0 |  | 14600
|  |  |  | 20:00 | 14460 |  | 0 |  | 14460
|  |  |  | 21:00 | 14800 |  | 0 |  | 14800
|  |  |  | 22:00 | 14220 |  | 0 |  | 14220
|  |  |  | 23:00 | 13920 |  | 0 |  | 13920
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12710.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 305.44 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:30 hrs on 09-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12885.58 | MW | 12:00 Hr. | Energy Generated |  |  | 314.0309 |  | MKWHr.
| Day Peak Demand |  |  | 12885.58 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.227 |  | MKWHr.
| Evening Peak Generation |  |  | 14734.51 | MW | 19:00 Hr. | Energy Demand |  |  | 314.2579 |  | MKWHr.
| Evening Peak Demand |  |  | 14801.51 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 11351.43 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 913.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 14734.51 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.2995 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.8132 | 0 | 13.8523 | 0 | 0 | 0.20482 | 0 | 0 | 55.8703 | Gas | 124.8947 | Gas | 442722248.01
| Chattogram Zone |  |  | 5.0195 | 34.0564 | 8.3588 | 0 | 5.2994 | 0.11005 | 0 | 0.06912 | 52.9132 | Coal | 91.5927 | Coal | 514147158.7371
| Cumilla Zone |  |  | 24.2895 | 0 | 5.0084 | 0 | 0 | 0.34061 | 1.609 | 0 | 31.2475 | HFO | 35.2682 | HFO | 653055539.68
| Mymensingh Zone |  |  | 0.50016 | 0 | 2.9076 | 0 | 0 | 0.26803 | 0 | 0 | 3.6758 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2898 | Hydro | 5.2994 | Hydro | 529942.2
| Khulna Zone |  |  | 3.329 | 8.5964 | 0.18944 | 0 | 0 | 0.3708 | 21.064 | 0 | 33.5496 | Solar | 3.3494 | Solar | 48127707.6424
| Barishal Zone |  |  | 8.1978 | 44.2899 | 0.42955 | 0 | 0 | 0.003265 | 0 | 0 | 52.9205 | Import | 53.5574 | Import | 318626136.28
| Rajshahi Zone |  |  | 12.4557 | 0 | 2.8619 | 0 | 0 | 1.2913 | 30.8844 | 0 | 47.4933 | Wind | 0.06912 | Wind | 1018828.8
| Rangpur Zone |  |  | 0 | 4.6501 | 1.6603 | 0 | 0 | 0.76059 | 0 | 0 | 7.071
| Total |  |  | 124.8947 | 91.5927 | 35.2682 | 0 | 5.2994 | 3.3494 | 53.5574 | 0.06912 | 314.0309
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 442722248.01 |  | Hydro | 529942.2
|  |  |  | Coal | 514147158.7371 |  | Solar | 48127707.6424
|  |  |  | HFO | 653055539.68 |  | Import | 318626136.28
|  |  |  | HSD | 0 |  | Wind | 1018828.8
[5 empty] | Total: | 197,82,27,561 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.152 | Peak Hr Flow | 899.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39943837.87 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.8844 | Peak Hr Flow | 1354.21 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1595 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.609 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2376 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.6454 | Peak Hr Flow | 2319.21 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5310
|  |  |  | Chattogram |  | 0 |  | 1411
|  |  |  | Cumilla |  | 0 |  | 1371
|  |  |  | Mymensingh |  | 64 |  | 1118
|  |  |  | Sylhet |  | 0 |  | 608
|  |  |  | Khulna |  | 0 |  | 1712
|  |  |  | Barishal |  | 0 |  | 408
|  |  |  | Rajshahi |  | 0 |  | 1388
|  |  |  | Rangpur |  | 0 |  | 927
|  |  |  | Total |  | 64 |  | 14253
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:22 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT is restored.
|  | 08:23 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT is restored.
| 08:30 | 16:43 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Annual Maintenance Work.
| 08:30 | 17:02 | Thakurgaon 132/33kV S/S T-2(412T) LT Scheduled S/D Due to Annual maintenance.
| 08:30 | 17:02 | Thakurgaon 132/33kV S/S T-2(412T) HT Scheduled S/D Due to Annual maintenance.
| 08:31 | 16:42 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Annual Maintenance Work.
| 08:33 | 16:45 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end. and from
Chandraghona 132/33kV end Due to Annual Maintenance
| 08:40 | 13:56 | Bagerhat-Mongla 132 kV Ckt-1 Forced S/D from Mongla 132/33kV end Due to Maintenance work
of Bagerhat -Mongla line-1 due to its R-Phase conductor rupture.
|  | 08:53 | Kulaura 132/33kV S/S TR-1 AB HT is restored.
|  | 08:54 | Kulaura 132/33kV S/S TR-1 AB LT is restored.
| 09:15 | 16:30 | Jaldhaka 132/33kV S/S Bus A Scheduled S/D Due to Annual Maintenance
| 09:17 | 15:36 | Bogura 230/132kV S/S 230KV Main 1 Scheduled S/D Due to Annual Maintenance
| 10:05 | 17:39 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end. and from
Kachua 230/132/33kV end Due to Shutdown was taken by Cumilla south.
| 10:38 | 15:02 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shutdown
by ALDC
| 11:00 | 12:43 | Saidpur 132/33kV S/S RPC Bank-01 Scheduled S/D Due to Annual maintenances
|  | 11:22 | Ghatail 132/33kV S/S T-1 HT is restored.
|  | 11:24 | Ghatail 132/33kV S/S T-1 LT is restored.
| 11:55 |  | Rangpur 132/33kV T-1 and T-2 transformers 33kV sides tripped showing O/C and E/F relay
due to 33kV Kawnia(PBS) feeder fault. Then, 132/33kV T-1 transformer was switched on at
12:05 hrs. Restoration of 132/33kV T-2 transformer is delayed due to 33kV bus coupler PT
problem. Now, about 55MW interruption is occurring due to this.
| 12:46 | 13:12 | Amnura 132/33kV S/S T-2 (416T) LT Tripped showing O/C & E/F relays Due to Fault in | [7 empty] | 6.0MW load
|  |  | Gobratala 33 kV feeder | [7 empty] | interrup.
| 12:46 | 13:12 | Amnura 132/33kV S/S T-1 (406T) LT Tripped showing O/C & E/F relays Due to Fault in | [7 empty] | 6.0MW load
|  |  | Gobratola 33kV feeder. | [7 empty] | interrup.
| 13:07 | 13:13 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to NESCO Auxiliary Transformer DS maintenance
| 13:12 | 17:14 | Rangpur 132/33kV S/S T-2 (404T) LT Forced S/D Due to Kaunia feeder fault & 33 Bus l A | [7 empty] | 50.0MW load
|  |  | fault & PT problem one phase | [7 empty] | interrup.
| 13:12 | 17:14 | Rangpur 132/33kV S/S T-2 (404T) HT Forced S/D Due to Kaunia feeder fault & 33 Bus l A | [7 empty] | 50.0MW load
|  |  | fault & PT problem one phase | [7 empty] | interrup.
|  | 13:56 | Bagerhat-Mongla 132 kV Ckt-1 is restored.
| 14:23 | 16:28 | Barishal-Barishal(N) 132 kV Ckt-2 Tripped from Barishal 132/33kV end showing Distance R
phase.Zone -1 & AR block. relays Due to Due to bad weather. and from Barishal 230/132kV
end showing ABB REL650 Dist zone 1 Loop L1N relays Due to None
| 15:15 | 17:41 | Shahjibazar 132/33kV S/S BPDB 60 MW Scheduled S/D Due to Bushing Hotspot Maintenance
|  | 18:12 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
| 19:00 |  | Evening Peak Generation is 14733 MW
| 23:36 | 00:02 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Tripped showing Siprotec siemens | [7 empty] | 35.0MW load
|  |  | relays Due to Feeder fault | [7 empty] | interrup.
| 23:47 | 01:36 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Baludanga 33kv feeder's 33kv Bus DS Red hot
manitenance.
| 23:48 | 01:35 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Baludanga 33kv feeder's 33kv Bus DS Red hot
manitenance.
|  | 05:06 | Sylhet 132/33kV S/S T4 LT is restored.
| 05:17 | 05:56 | Sylhet 132/33kV S/S T4 LT Tripped showing O/C relays Due to 33 KV Amborkhana-1 Feeder | [7 empty] | 19.0MW load
|  |  | Fault | [7 empty] | interrup.
| 05:17 |  | Sylhet 132/33kV S/S T2 LT Tripped showing E/F (Inst) relays Due to 33 KV Amborkhana-1 | [7 empty] | 28.0MW load
|  |  | Feeder Fault | [7 empty] | interrup.
| 05:17 |  | Sylhet 132/33kV S/S T2 HT Tripped showing O/C, Phase-A relays Due to 33 KV Amborkhana-1 | [7 empty] | 28.0MW load
|  |  | feeder Fault | [7 empty] | interrup.
| 05:22 | 05:56 | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to 33 KV Amborkhana-1 Feeder Fault | [7 empty] | 19.0MW load
interrup.
| 05:23 |  | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to 33 KV Amborkhana-1 Feeder Fault | [7 empty] | 28.0MW load
interrup.
| 05:23 |  | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to 33 KV Amborkhana-1 Feeder Fault | [7 empty] | 28.0MW load
interrup.
| 06:00 |  | Minimum Generation is 11387 MW.
| 06:52 | 07:33 | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 330 | 8733600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8075000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 133 | 3491316 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 443450 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7952567 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50.3 | 519120 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 1023840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 530064 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 531065 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 426600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 424080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 341280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 2571818 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2150352 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1944960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1585440 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204820 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 305280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 12710000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1905600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6657.724 | 2963.8 | 55870252
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 294516 | Engine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 90855 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 937440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5299422 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 203 | 4638352 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 648181 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 379776 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 1090197 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 381120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 100 | 1065600 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 471709 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 34 | 345447 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 97 | 1482036 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 75 | 648600 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 134 | 995273 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1211 | 27234543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 69120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6821818.18 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2747.5 | 52913204.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 181 | 4762000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 300 | 6674000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 8769500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1240492 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 1624218 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 235400 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2472290 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 131 | 1711200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1608960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 34565 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 371249 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 240540 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 6 | 47880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1114560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 340609 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1495 | 31247463
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 500160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1149600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 66 | 1612800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 258380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 1 | 26400 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 118800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 143 | 3675790
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1593840 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 158 | 3703418 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 524352 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1927680 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4405440 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 201096 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7503000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 298 | 8323000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1129 | 29289826
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 20152000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 26880 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 162560 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 120 | 3328992 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 370800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 353 | 8596364 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1410 | 33549596
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 10144440 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 130752 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2744000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 27905454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5453810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 298800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6240000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3265 | -
Barishal Area Total |  |  |  |  | 2858 | 2166 | 52920521.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 348756 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 372243 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 190433 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3401273 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 388 | 9054472 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 166401 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 66038 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 774096 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 92 | 652800 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 100 | 639840 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1354.21 | 30884396 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 372000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 536970 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2267.21 | 47493258
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1124073 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 145 | 3526000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 109 | 826166 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35926.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 834155 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 164504 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 560160 | -
Rangpur Area Total |  |  |  |  | 950 | 413 | 7070984.44
Eastern Grid Total |  |  |  |  | 17385.715 | 8478.3 | 172996535.18
Western Grid Total |  |  |  |  | 10980.24 | 6256.21 | 141034359.99
National Grid Total |  |  |  |  | 28365.955 | 14734.51 | 314030895.17
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9753.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4434.1 | MW
i) Dhaka area |  |  | 5309.52 |  | MW | i) Khulna area |  |  |  | 1712 | MW
ii) Chattogram area |  |  | 1410.6 |  | MW | ii) Barishal area |  |  |  | 407.5 | MW
iii) Cumilla area |  |  | 1371.1 |  | MW | iii) Rajshahi area |  |  |  | 1387.6 | MW
iv) Mymensingh area |  |  | 1054 |  | MW | iv) Rangpur area |  |  |  | 927 | MW
v) Sylhet area |  |  | 608 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14187.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 18:00 | 133 | Niamatpur | 64 | 21:00
2 | AKSML | 137.1 | 23:00 | 68 | Ishurdi | 76 | 18:30 | 134 | Noapara | 38 | 00:00
3 | Aftabnagar | 38 | 19:30 | 69 | Jaldhaka | 78 | 18:30 | 135 | PHP | 6 | 00:00
4 | Agargaon | 124 | 12:00 | 70 | Jamalpur | 105 | 00:00 | 136 | Pabna | 99 | 19:30
5 | Agrabad | 88 | 15:00 | 71 | Jashore | 145 | 18:30 | 137 | Palashbari | 108 | 18:30
6 | Amnura | 24 | 00:00 | 72 | Jhenaidah | 125 | 18:00 | 138 | Panchagarh | 61 | 18:30
7 | Ashuganj | 89 | 20:00 | 73 | Joydebpur | 161 | 13:00 | 139 | Patiya | 11 | 00:00
8 | BSRM | 119 | 03:00 | 74 | Joypurhat | 52 | 22:00 | 140 | Patuakhali | 72 | 22:00
9 | Bagerhat | 80 | 21:00 | 75 | Juldah | 16 | 00:00 | 141 | Payra | 28 | 20:00
10 | Bajitpur | 80 | 18:30 | 76 | KSRM | 39 | 18:00 | 142 | Postogola | 67 | 13:00
11 | Bakulia | 97 | 15:00 | 77 | Kabirpur | 252 | 11:00 | 143 | Purbachal | 21 | 19:30
12 | Banani | 45.6 | 10:00 | 78 | Kachua | 92 | 18:00 | 144 | Purbasadipur | 112 | 18:30
13 | Bangabhaban | 21 | 10:00 | 79 | Kallyanpur | 102 | 18:00 | 145 | Rahanpur | 35 | 21:00
14 | Barapukuria | 53 | 18:30 | 80 | Kalurghat | 43 | 12:00 | 146 | Rahim | 24 | 18:00
15 | Barguna | 14 | 18:00 | 81 | Kamrangirchar | 77 | 12:00 | 147 | Rajbari | 82 | 22:00
16 | Barishal | 112 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 131 | 18:30
17 | Barishal-230 | 90 | 21:00 | 83 | Kasba | 34 | 19:00 | 149 | Rajshahi | 98 | 21:00
18 | Baroaulia | 59 | 09:00 | 84 | Kazla | 102 | 19:00 | 150 | Rajshahi-230 | 94 | 13:00
19 | Baroirhat | 63 | 18:00 | 85 | Keranigonj | 97 | 18:30 | 151 | Ramganj | 112 | 19:30
20 | Bashundhara | 186 | 12:00 | 86 | Khagrachori | 30 | 18:30 | 152 | Rampur | 43 | 00:00
21 | BashundharaCement | 12 | 00:00 | 87 | Khulna | 63 | 18:30 | 153 | Rangamati | 16 | 19:00
22 | Beanibazar | 76 | 19:30 | 88 | Khulshi | 182 | 19:00 | 154 | Rangpur | 149 | 18:30
23 | Benapole | 58 | 18:30 | 89 | Kishoreganj | 130 | 20:00 | 155 | Ruppur | 8 | 10:00
24 | Bhaluka | 160 | 18:30 | 90 | Kodda | 305 | 16:00 | 156 | SSM | 16 | 01:00
25 | Bhandaria | 50 | 21:00 | 91 | Kulaura | 50 | 21:00 | 157 | Saidpur | 108 | 18:30
26 | Bhangura | 37 | 21:00 | 92 | Kurigram | 64 | 18:30 | 158 | Satkhira | 119 | 21:00
27 | Bheramara(GK) | 63 | 18:30 | 93 | Kushtia | 150 | 18:30 | 159 | Satmasjid | 96 | 18:00
28 | Bhulta | 218 | 00:00 | 94 | Laksam | 37 | 19:30 | 160 | Savar | 186 | 22:00
29 | Bog-Sherpur | 72 | 21:00 | 95 | Lakshmipur | 32 | 20:00 | 161 | SevenRings | 5.61 | 11:00
30 | Bogura | 149 | 00:00 | 96 | Lalbag | 61 | 12:00 | 162 | ShahCement | 25 | 21:00
31 | Borhanuddin | 93 | 21:00 | 97 | Lalmonirhat | 60 | 19:00 | 163 | Shahjadpur | 90 | 19:00
32 | Brahmanbaria | 130 | 20:00 | 98 | MI_Cement | 16 | 00:00 | 164 | Shahjibazar | 125 | 22:00
33 | Cantonment | 134 | 13:00 | 99 | Madanganj | 32 | 11:00 | 165 | Shahmirpur | 54 | 18:00
34 | Chandina | 17.19 | 12:00 | 100 | Madaripur | 105 | 21:00 | 166 | Shariatpur | 85 | 21:00
35 | Chandpur | 82 | 20:00 | 101 | Madartek | 84 | 23:00 | 167 | Sherpur | 130 | 00:00
36 | Chandraghona | 37 | 18:30 | 102 | Madunaghat | 59 | 23:00 | 168 | Shikalbaha | 30 | 11:00
37 | Chapai | 63 | 21:00 | 103 | Magura | 65 | 19:00 | 169 | Shitalakhya | 85 | 16:00
38 | Charsaidpur | 39 | 00:00 | 104 | Mahasthangarh | 72 | 00:00 | 170 | Sholosohor | 47 | 18:00
39 | Chauddagram | 69 | 19:30 | 105 | Maijdee | 21 | 21:00 | 171 | Shyampur | 96 | 11:00
40 | Chhatak | 38 | 20:00 | 106 | Manikganj | 128 | 19:30 | 172 | Siddhirganj | 126 | 12:00
41 | Chowmuhani | 177 | 20:00 | 107 | Maniknagar | 64 | 13:00 | 173 | Sirajganj | 118 | 19:00
42 | Chuadanga | 111 | 21:00 | 108 | Matarbari | 49 | 00:00 | 174 | Sonargaon | 135 | 23:00
43 | Coxsbazar | 133 | 18:00 | 109 | Matuail | 67 | 12:00 | 175 | Sreemongol | 75 | 00:00
44 | Cumilla(N) | 132 | 14:00 | 110 | Metrorail_Motijheel | 28 | 18:00 | 176 | Sreepur | 103 | 19:00
45 | Cumilla(S) | 147 | 14:00 | 111 | Metrorail_Uttara | 7 | 13:00 | 177 | Srinagar | 46.96 | 23:00
46 | Daganbhuiyan | 0 | 05:00 | 112 | Millgate | 133 | 12:00 | 178 | Sunamganj | 62 | 21:00
47 | Daudkandi | 153 | 19:30 | 113 | Mirpur | 121 | 18:00 | 179 | Sylhet | 52 | 18:30
48 | DhakaUniversity | 93 | 13:00 | 114 | Mirsorai | 11 | 11:00 | 180 | Sylhet-132 | 118 | 18:30
49 | Dhamrai | 134 | 18:30 | 115 | Mirzapur | 40 | 18:00 | 181 | TK | 22 | 00:00
50 | Dhanmondi | 128.7 | 13:00 | 116 | Mithapukur | 64 | 18:00 | 182 | Tangail | 164 | 20:00
51 | Dohazari | 101 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 21 | 19:30
52 | Faridpur | 170 | 22:00 | 118 | Mogbazar | 95.8 | 12:00 | 184 | Thakurgaon | 96 | 18:30
53 | Fatullah | 114 | 12:00 | 119 | Mongla | 46 | 12:00 | 185 | Tongi | 147 | 11:00
54 | Fenchuganj | 40 | 19:00 | 120 | Motijheel | 54 | 12:00 | 186 | Ullahpara | 38 | 18:30
55 | Feni | 120 | 18:30 | 121 | Muktagacha | 36 | 18:00 | 187 | Ullon | 56 | 20:00
56 | GPH | 9 | 22:00 | 122 | Munshiganj | 113 | 21:00 | 188 | Uttara | 74 | 13:00
57 | Ghatail | 76 | 18:00 | 123 | Muradnagar | 39 | 22:00 | 189 | UttaraNew | 58 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 191 | 18:30 | 190 | Zigatola | 70 | 18:00
59 | Ghorashal-230 | 100 | 00:00 | 125 | Naogaon | 115 | 22:00
60 | Goalpara | 33 | 00:00 | 126 | Narail | 58 | 19:30
61 | Gollamari | 104 | 20:00 | 127 | Narinda | 66 | 13:00
62 | Gopalganj | 109 | 19:00 | 128 | Narshingdi | 176 | 22:00
63 | Gulshan | 116 | 11:00 | 129 | Natore | 146 | 18:30
64 | Halishahar | 83 | 15:00 | 130 | Nawabganj | 47.2 | 22:00
65 | HaripurSBU | 142 | 16:00 | 131 | Netrakona | 135 | 21:00
66 | Hasnabad | 80 | 19:00 | 132 | New | 55 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13572.2 | 0 |  | 13572.2
1:00 | 13013.4 | 0 |  | 13013.4
2:00 | 12573.4 | 0 |  | 12573.4
3:00 | 12080.4 | 0 |  | 12080.4
4:00 | 11748.4 | 0 |  | 11748.4
5:00 | 11544.4 | 0 |  | 11544.4
6:00 | 11351.43 | 0 |  | 11351.43
7:00 | 11517.96 | 0 |  | 11517.96
8:00 | 11586.75 | 0 |  | 11586.75
9:00 | 11690.51 | 0 |  | 11690.51
10:00 | 12047.7 | 0 |  | 12047.7
11:00 | 12457.05 | 0 |  | 12457.05
12:00 | 12885.58 | 0 |  | 12885.58
13:00 | 13229.78 | 0 |  | 13229.78
14:00 | 12967.53 | 0 |  | 12967.53
15:00 | 13009.15 | 0 |  | 13009.15
16:00 | 12888.95 | 0 |  | 12888.95
17:00 | 12747.58 | 0 |  | 12747.58
18:00 | 13792.79 | 0 |  | 13792.79
19:00 | 14734.51 | 64 |  | 14801.51
19:30 | 14719.8 | 49 |  | 14770.8
20:00 | 14587.15 | 47 |  | 14636.15
21:00 | 14586.16 | 33 |  | 14620.16
22:00 | 14479.86 | 39 |  | 14520.62
23:00 | 14334.36 | 44 |  | 14380.34
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7365.2 | 6207 | 13572.2 | DAILY GENERATION CURVE
00:30 | 7182.8 | 6110 | 13292.8
01:00 | 7000.4 | 6013 | 13013.4 | 08-10-2025
01:30 | 6852.9 | 5940.5 | 12793.4
02:00 | 6705.4 | 5868 | 12573.4
02:30 | 6534.4 | 5792.5 | 12326.9
03:00 | 6363.4 | 5717 | 12080.4
03:30 | 6235.9 | 5678.5 | 11914.4
04:00 | 6108.4 | 5640 | 11748.4
04:30 | 6077.4 | 5569 | 11646.4
05:00 | 6046.4 | 5498 | 11544.4
05:30 | 6034.415 | 5413.5 | 11447.915
06:00 | 6022.43 | 5329 | 11351.43
06:30 | 6097.63 | 5337.065 | 11434.695
07:00 | 6172.83 | 5345.13 | 11517.96
07:30 | 6153.68 | 5398.675 | 11552.355
08:00 | 6134.53 | 5452.22 | 11586.75
08:30 | 6127.23 | 5511.4 | 11638.63
09:00 | 6119.93 | 5570.58 | 11690.51
09:30 | 6260.54 | 5608.565 | 11869.105
10:00 | 6401.15 | 5646.55 | 12047.7
10:30 | 6536.275 | 5716.1 | 12252.375
11:00 | 6671.4 | 5785.65 | 12457.05
11:30 | 6780.275 | 5891.04 | 12671.315
12:00 | 6889.15 | 5996.43 | 12885.58
12:30 | 7104.755 | 5952.925 | 13057.68
13:00 | 7320.36 | 5909.42 | 13229.78
13:30 | 7279.37 | 5819.285 | 13098.655
14:00 | 7238.38 | 5729.15 | 12967.53
14:30 | 7303.445 | 5684.895 | 12988.34
15:00 | 7368.51 | 5640.64 | 13009.15
15:30 | 7337.325 | 5611.725 | 12949.05
16:00 | 7306.14 | 5582.81 | 12888.95
16:30 | 7276.12 | 5542.145 | 12818.265
17:00 | 7246.1 | 5501.48 | 12747.58
17:30 | 7576.8 | 5693.385 | 13270.185
18:00 | 7907.5 | 5885.29 | 13792.79
18:30 | 8192.9 | 6070.75 | 14263.65
19:00 | 8478.3 | 6256.21 | 14734.51
19:30 | 8588.8 | 6131 | 14719.8
20:00 | 8474.56 | 6112.59 | 14587.15
20:30 | 8432.86 | 6153.795 | 14586.655 |  | Executive Engineer
21:00 | 8391.16 | 6195 | 14586.16 |  | Network Operation Division
21:30 | 8366.51 | 6166.5 | 14533.01
22:00 | 8341.86 | 6138 | 14479.86
22:30 | 8264.61 | 6142.5 | 14407.11
23:00 | 8187.36 | 6147 | 14334.36

## En-Curve
QF-LDC-12
Date | 08-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3231 | 1920.2 | 874 | 38 | 78 | 1363 | 222 | 4118 | 0 | 561 | 1165 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3212.5 | 1910.3 | 874 | 38 | 78 | 1362 | 221 | 4051 | 0 | 493.5 | 1050 | 0 | 0 | 2.5 | 0 | 08-10-2025
01:00 | 3194 | 1900.4 | 874 | 38 | 78 | 1361 | 220 | 3984 | 0 | 426 | 935 | 0 | 0 | 3 | 0
01:30 | 3208.5 | 1897.9 | 874 | 38 | 75 | 1366 | 219 | 3976 | 0 | 336.5 | 798.5 | 0 | 0 | 4 | 0 | Energy Generated | 314.0309 |  | MKWHr
02:00 | 3223 | 1895.4 | 874 | 38 | 72 | 1371 | 218 | 3968 | 0 | 247 | 662 | 0 | 0 | 5 | 0 | Energy not Served | 0.227 |  | MKWHr
02:30 | 3200.5 | 1846.4 | 874 | 38 | 71 | 1372.5 | 218.5 | 3913 | 0 | 238 | 548.5 | 0 | 0 | 6.5 | 0 | Total Energy Requirement | 314.2579 |  | MKWHr
03:00 | 3178 | 1797.4 | 874 | 38 | 70 | 1374 | 219 | 3858 | 0 | 229 | 435 | 0 | 0 | 8 | 0
03:30 | 3219.5 | 1836.9 | 873.5 | 38 | 68 | 1324.5 | 219.5 | 3817.5 | 0 | 177.5 | 331.5 | 0 | 0 | 8 | 0
04:00 | 3261 | 1876.4 | 873 | 38 | 66 | 1275 | 220 | 3777 | 0 | 126 | 228 | 0 | 0 | 8 | 0
04:30 | 3280.5 | 1897.4 | 873.5 | 38 | 67 | 1218.5 | 220.5 | 3734.5 | 0 | 118.5 | 194 | 0 | 0 | 4 | 0
05:00 | 3300 | 1918.4 | 874 | 38 | 68 | 1162 | 221 | 3692 | 0 | 111 | 160 | 0 | 0 | 0 | 0
05:30 | 3302.5 | 1910.9 | 874 | 38 | 64 | 1111 | 221.5 | 3665 | 1.015 | 111 | 149 | 0 | 0 | 0 | 0
06:00 | 3305 | 1903.4 | 874 | 38 | 60 | 1060 | 222 | 3638 | 2.03 | 111 | 138 | 0 | 0 | 0 | 0
06:30 | 3305 | 1909.4 | 874 | 38 | 59 | 1088.5 | 222 | 3615.5 | 39.795 | 133.5 | 149.5 | 0 | 0 | 0.5 | 0
07:00 | 3305 | 1915.4 | 874 | 38 | 58 | 1117 | 222 | 3593 | 77.56 | 156 | 161 | 0 | 0 | 1 | 0
07:30 | 3261.5 | 1902.4 | 882 | 38 | 59 | 1118 | 222 | 3588 | 169.955 | 147.5 | 160.5 | 0 | 0 | 3.5 | 0
08:00 | 3218 | 1889.4 | 890 | 38 | 60 | 1119 | 222 | 3583 | 262.35 | 139 | 160 | 0 | 0 | 6 | 0
08:30 | 3228 | 1865.2 | 890 | 38 | 61 | 1119.545 | 222 | 3588 | 312.885 | 140 | 169.5 | 0 | 0 | 4.5 | 0
09:00 | 3238 | 1841 | 890 | 38 | 62 | 1120.09 | 222 | 3593 | 363.42 | 141 | 179 | 0 | 0 | 3 | 0
09:30 | 3277 | 1853 | 893.5 | 38 | 60 | 1118.72 | 222 | 3645.5 | 406.885 | 136.5 | 214 | 0 | 0 | 4 | 0
10:00 | 3316 | 1865 | 897 | 38 | 58 | 1117.35 | 222 | 3698 | 450.35 | 132 | 249 | 0 | 0 | 5 | 0
10:30 | 3318 | 1853.75 | 898 | 38 | 59 | 1115.76 | 222 | 3743 | 476.615 | 145.5 | 377.25 | 0 | 0 | 5.5 | 0
11:00 | 3320 | 1842.5 | 899 | 38 | 60 | 1114.17 | 222 | 3788 | 502.88 | 159 | 505.5 | 0 | 0 | 6 | 0
11:30 | 3275 | 1833.75 | 899 | 38 | 63 | 1183.07 | 222 | 3804.5 | 518.995 | 178.5 | 652.5 | 0 | 0 | 3 | 0
12:00 | 3230 | 1825 | 899 | 38 | 66 | 1251.97 | 222 | 3821 | 535.11 | 198 | 799.5 | 0 | 0 | 0 | 0
12:30 | 3250 | 1840.6 | 899.5 | 38 | 72 | 1284.005 | 222 | 3804.5 | 469.075 | 225.5 | 952.5 | 0 | 0 | 0 | 0
13:00 | 3270 | 1856.2 | 900 | 38 | 78 | 1316.04 | 222 | 3788 | 403.04 | 253 | 1105.5 | 0 | 0 | 0 | 0
13:30 | 3222 | 1824.2 | 899.5 | 38 | 77 | 1315.27 | 220.5 | 3730.5 | 394.735 | 257.5 | 1115.45 | 0 | 0 | 4 | 0
14:00 | 3174 | 1792.2 | 899 | 38 | 76 | 1314.5 | 219 | 3673 | 386.43 | 262 | 1125.4 | 0 | 0 | 8 | 0
14:30 | 3236 | 1834.85 | 899 | 38 | 75 | 1316.89 | 218.5 | 3672 | 291.85 | 265 | 1135.25 | 0 | 0 | 6 | 0
15:00 | 3298 | 1877.5 | 899 | 38 | 74 | 1319.28 | 218 | 3671 | 197.27 | 268 | 1145.1 | 0 | 0 | 4 | 0
15:30 | 3264 | 1871.5 | 899 | 38 | 71 | 1317.255 | 218 | 3661.5 | 165.045 | 268 | 1173.75 | 0 | 0 | 2 | 0
16:00 | 3230 | 1865.5 | 899 | 38 | 68 | 1315.23 | 218 | 3652 | 132.82 | 268 | 1202.4 | 0 | 0 | 0 | 0
16:30 | 3164.5 | 1857.5 | 899 | 38 | 67 | 1315.33 | 218.5 | 3616 | 85.035 | 320.5 | 1235.9 | 0 | 0 | 1 | 0
17:00 | 3099 | 1849.5 | 899 | 38 | 66 | 1315.43 | 219 | 3580 | 37.25 | 373 | 1269.4 | 0 | 0 | 2 | 0
17:30 | 3200.5 | 1829.5 | 899 | 38 | 69 | 1332.86 | 219.5 | 3627.5 | 18.625 | 501.5 | 1531.7 | 0 | 0 | 2.5 | 0
18:00 | 3302 | 1809.5 | 899 | 38 | 72 | 1350.29 | 220 | 3675 | 0 | 630 | 1794 | 0 | 0 | 3 | 0
18:30 | 3208.5 | 1891.5 | 899 | 38 | 69 | 1352.25 | 220.5 | 3766 | 0 | 685.5 | 2131.9 | 0 | 0 | 1.5 | 32
19:00 | 3115 | 1973.5 | 899 | 38 | 66 | 1354.21 | 221 | 3857 | 0 | 741 | 2469.8 | 0 | 0 | 0 | 64
19:30 | 3179 | 1947 | 661 | 38 | 68 | 1413 | 221 | 3866 | 0 | 758 | 2568.8 | 0 | 0 | 0 | 49
20:00 | 3155 | 1942 | 601 | 38 | 70 | 1435.59 | 222 | 3863 | 0 | 733 | 2525.56 | 0 | 0 | 2 | 47
20:30 | 3162.5 | 1965.75 | 601 | 38 | 70 | 1439.295 | 222 | 3867 | 0 | 746.5 | 2473.61 | 0 | 0 | 1 | 40
21:00 | 3170 | 1989.5 | 601 | 38 | 70 | 1443 | 222 | 3871 | 0 | 760 | 2421.66 | 0 | 0 | 0 | 33
21:30 | 3156.5 | 1970.5 | 601 | 38 | 70 | 1438 | 222 | 3877 | 0 | 760 | 2400.01 | 0 | 0 | 0 | 36
22:00 | 3143 | 1951.5 | 601 | 38 | 70 | 1433 | 222 | 3883 | 0 | 760 | 2378.36 | 0 | 0 | 0 | 39
22:30 | 3141 | 1943.75 | 601 | 38 | 73 | 1436.5 | 222 | 3883 | 0 | 760.5 | 2308.36 | 0 | 0 | 0 | 41.5
23:00 | 3139 | 1936 | 601 | 38 | 76 | 1440 | 222 | 3883 | 0 | 761 | 2238.36 | 0 | 0 | 0 | 44
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 372 | 12:00 | Payra | 409 | 07:00 | 404 | 01:00
Ashuganj | 403 | 22:00 | 381 | 11:00 | Rahanpur | 403 | 06:00 | 393 | 01:00
Bhulta | 401 | 22:00 | 376 | 11:00 | Rampal | 401 | 06:00 | 388 | 18:30
Bibiana | 389 | 19:00 | 382 | 11:00
BIPTC | 408 | 19:30 | 395 | 01:00
Bogura | 392 | 06:00 | 381 | 00:00
Gopalganj | 395 | 08:00 | 386 | 00:00
Kaliakoir | 375 | 19:30 | 363 | 10:00
Madunaghat | 395 | 23:00 | 387 | 11:00
Meghnaghat | 388 | 06:00 | 378 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 221 | 12:00 | Kaliakoir | 235 | 22:00 | 225 | 10:00
AKSML | 236 | 19:00 | 227 | 04:00 | Keranigonj | 227 | 06:00 | 218 | 12:00
Aminbazar | 230 | 02:00 | 222 | 12:00 | Khulna(S) | 231 | 06:00 | 217 | 18:30
Ashuganj | 231 | 17:00 | 220 | 11:00 | Madunaghat | 236 | 19:00 | 229 | 04:00
Ashuganj-400 | 231 | 17:00 | 220 | 11:00 | Madunaghat-400 | 236 | 20:00 | 229 | 11:00
Baghabari | 233 | 06:00 | 226 | 18:00 | Maniknagar | 222 | 05:00 | 214 | 12:00
Barapukuria | 224 | 22:00 | 217 | 01:00 | Meghnaghat | 230 | 06:00 | 222 | 13:00
Barapukuria-230 | 224 | 22:00 | 217 | 01:00 | Meghnaghat-400 | 226 | 06:00 | 219 | 12:00
Barishal | 233 | 04:00 | 228 | 00:00 | Mirsorai | 235 | 19:30 | 222 | 12:00
Bheramara | 236 | 22:00 | 224 | 18:30 | Rajshahi | 233 | 23:00 | 224 | 19:00
Bhulta | 231 | 22:00 | 215 | 11:00 | Rampal | 230 | 06:00 | 218 | 18:30
Bibiana | 228 | 07:00 | 225 | 02:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 223 | 18:30 | Rampura | 230 | 22:00 | 213 | 11:00
Bogura | 234 | 06:00 | 228 | 00:00 | Shikalbaha | 236 | 19:30 | 227 | 06:00
Bogura-400 | 234 | 06:00 | 227 | 01:00 | Shyampur | 225 | 06:00 | 218 | 12:00
Borhanuddin | 238 | 10:00 | 233 | 00:00 | Siddhirganj | 224 | 06:00 | 217 | 11:00
BSRM | 233 | 19:30 | 223 | 02:00 | Sirajgonj | 238 | 06:00 | 232 | 18:30
Cumilla(N) | 226 | 19:00 | 219 | 09:00 | Sreepur | 227 | 06:00 | 219 | 12:00
Faridpur | 231 | 06:00 | 224 | 00:00 | Tongi | 232 | 23:00 | 218 | 09:00
Fenchuganj | 231 | 07:00 | 227 | 00:00
Ghorashal | 230 | 01:00 | 220 | 11:00
Ghorashal-230 | 230 | 23:00 | 215 | 11:00
Gopalganj | 232 | 06:00 | 223 | 07:00
GPH | 234 | 19:00 | 227 | 02:00
Haripur | 223 | 05:00 | 216 | 12:00
Hasnabad | 225 | 19:00 | 219 | 12:00
Hathazari | 234 | 19:30 | 226 | 11:00
Ishurdi | 236 | 08:00 | 225 | 18:30
Jhenaidah | 233 | 06:00 | 217 | 18:30
Kachua | 220 | 15:00 | 210 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 00:00 | 124 | 11:00 | Lalmonirhat | 128 | 04:00 | 122 | 10:00
Agargaon | 136 | 06:00 | 129 | 11:00 | Madanganj | 129 | 04:00 | 125 | 10:00
Agrabad | 135 | 18:30 | 130 | 05:00 | Madaripur | 135 | 05:00 | 131 | 18:30
AKS | 132 | 19:30 | 129 | 02:00 | Madartek | 134 | 00:00 | 124 | 11:00
Aminbazar | 135 | 07:00 | 131 | 10:00 | Madunaghat | 137 | 19:00 | 132 | 10:00
Amnura | 137 | 19:30 | 129 | 12:00 | Magura | 135 | 05:00 | 124 | 18:30
Ashuganj | 140 | 06:00 | 135 | 11:00 | Mahasthangarh | 132 | 23:00 | 125 | 01:00
Bagerhat | 133 | 07:00 | 117 | 18:30 | Maijdee | 131 | 17:00 | 127 | 00:00
Bajitpur | 130 | 02:00 | 125 | 18:00 | Manikganj | 128 | 04:00 | 121 | 10:00
Bakulia | 136 | 18:30 | 130 | 10:00 | Maniknagar | 135 | 04:00 | 128 | 12:00
Banani | 137 | 00:00 | 123 | 11:00 | Matarbari | 122 | 14:00 | 113 | 18:00
Bangabhaban | 135 | 05:00 | 128 | 12:00 | Matuail | 130 | 05:00 | 125.3 | 12:00
Barapukuria | 137 | 22:00 | 128 | 01:00 | Metrorail_Motijheel | 133 | 21:00 | 128 | 12:00
Barguna | 136 | 14:00 | 134 | 00:00 | Metrorail_Uttara | 135 | 11:00 | 131 | 12:00
Barishal | 135 | 05:00 | 130 | 00:00 | Millgate | 133 | 05:00 | 123 | 11:00
Barishal-230 | 135 | 07:00 | 130 | 18:30 | Mirpur | 136 | 03:00 | 130 | 10:00
Baroaulia | 135 | 19:00 | 131 | 03:00 | Mirzapur | 130 | 19:00 | 124 | 18:00
Baroirhat | 130 | 19:00 | 125 | 12:00 | Mithapukur | 132 | 22:00 | 124 | 00:00
Bashundhara | 135 | 00:00 | 122 | 11:00 | MI_Cement | 130 | 06:00 | 125 | 12:00
BashundharaCement | 129 | 04:00 | 125 | 11:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 06:00 | 125 | 00:00 | Mogbazar | 137 | 23:00 | 124 | 11:00
Benapole | 132 | 07:00 | 120 | 18:30 | Mongla | 131 | 08:00 | 117 | 18:30
Bhaluka | 129 | 03:00 | 120 | 18:30 | Motijheel | 135 | 05:00 | 128 | 12:00
Bhandaria | 127 | 09:00 | 112 | 18:30 | Muktagacha | 130 | 09:00 | 115 | 18:00
Bhangura | 133 | 06:00 | 129 | 00:00 | Munshiganj | 130 | 17:00 | 125 | 11:00
Bheramara | 136 | 06:00 | 131 | 18:30 | Muradnagar | 128 | 06:00 | 123 | 12:00
Bheramara(GK) | 137 | 06:00 | 131 | 18:30 | Mymensingh | 130 | 06:00 | 112 | 18:00
Bhulta | 128 | 17:00 | 124 | 00:00 | Naogaon | 129 | 20:00 | 123 | 00:00
Bog-Sherpur | 133 | 23:00 | 127 | 00:00 | Narail | 139 | 06:00 | 122 | 18:30
Bogura | 135 | 23:00 | 128 | 00:00 | Narinda | 135 | 04:00 | 128 | 12:00
Bogura-230 | 134 | 20:00 | 128 | 00:00 | Narshingdi | 131 | 07:00 | 120 | 12:00
Brahmanbaria | 133 | 07:00 | 128 | 12:00 | Natore | 133 | 05:00 | 128 | 00:00
Cantonment | 135 | 02:00 | 128 | 12:00 | Nawabganj | 135 | 03:00 | 128 | 12:00
Chandina | 132 | 07:00 | 126 | 02:00 | Netrakona | 123 | 04:00 | 109 | 18:00
Chandpur | 140 | 17:00 | 132 | 05:00 | New | 134 | 22:00 | 125 | 11:00
Chandraghona | 139 | 19:00 | 133 | 04:00 | Niamatpur | 138 | 07:00 | 132 | 00:00
Chapai | 136 | 06:00 | 132 | 00:00 | Noapara | 135 | 07:00 | 124 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 06:00 | 125 | 12:00 | Pabna | 135 | 06:00 | 128 | 18:30
Chauddagram | 132 | 19:00 | 126 | 11:00 | Palashbari | 131 | 23:00 | 122 | 00:00
Chhatak | 128 | 03:00 | 121 | 21:00 | Panchagarh | 137 | 23:00 | 123 | 10:00
Chowmuhani | 131 | 17:00 | 127 | 00:00 | Patiya | 134 | 19:00 | 129 | 04:00
Chuadanga | 136 | 06:00 | 124 | 19:00 | Patuakhali | 136 | 11:00 | 132 | 01:00
Coxsbazar | 121 | 14:00 | 114 | 18:00 | Payra | 136 | 07:00 | 135 | 00:00
Cumilla(N) | 132 | 19:00 | 127 | 02:00 | PHP | 131 | 19:30 | 125 | 00:00
Cumilla(S) | 132 | 19:00 | 127 | 10:00 | Postogola | 134 | 06:00 | 129 | 10:00
Daganbhuiyan | 130 | 07:00 | 127 | 05:00 | Purbachal | 135 | 00:00 | 123 | 12:00
Daudkandi | 126 | 17:00 | 120 | 12:00 | Purbasadipur | 132 | 22:00 | 122 | 10:00
DhakaUniversity | 136 | 23:00 | 124 | 12:00 | Rahanpur | 138 | 05:00 | 134 | 00:00
Dhamrai | 132 | 07:00 | 126 | 12:00 | Rahanpur-400 | 138 | 06:00 | 135 | 00:00
Dhanmondi | 136 | 23:00 | 123 | 12:00 | Rahim | 130 | 04:00 | 126 | 11:00
Dohazari | 130 | 14:00 | 126 | 01:00 | Rajbari | 135 | 06:00 | 130 | 00:00
Faridpur | 136 | 09:00 | 132 | 00:00 | Rajendrapur | 137 | 21:00 | 121 | 18:30
Fatullah | 137 | 05:00 | 131 | 12:00 | Rajshahi | 133 | 07:00 | 128 | 18:30
Fenchuganj | 136 | 07:00 | 133 | 00:00 | Rajshahi-230 | 133 | 06:00 | 127 | 18:30
Feni | 130 | 05:00 | 127 | 00:00 | Ramganj | 134 | 17:00 | 128 | 00:00
Ghatail | 127 | 06:00 | 115 | 18:00 | Rampur | 135 | 21:00 | 130 | 10:00
Ghorashal | 138 | 00:00 | 129 | 11:00 | Rampura | 135 | 00:00 | 124 | 11:00
Goalpara | 137 | 08:00 | 126 | 18:30 | Rangamati | 135 | 17:00 | 132 | 10:00
Gollamari | 137 | 06:00 | 127 | 18:30 | Rangpur | 133 | 23:00 | 125 | 18:30
Gopalganj | 135 | 06:00 | 127 | 18:30 | Ruppur | 137 | 05:00 | 131 | 18:30
Gopalganj-400 | 136 | 06:00 | 132 | 00:00 | Saidpur | 132 | 21:00 | 124 | 13:00
Gulshan | 135 | 00:00 | 124 | 12:00 | Satkhira | 134 | 08:00 | 121 | 18:30
Halishahar | 135 | 19:00 | 130 | 11:00 | Satmasjid | 135 | 03:00 | 129 | 11:00
Haripur | 130 | 03:00 | 126 | 12:00 | Savar | 135 | 02:00 | 131 | 08:00
HaripurSBU | 130 | 03:00 | 127 | 10:00 | SevenRings | 139 | 22:00 | 130 | 10:00
Hasnabad | 134 | 05:00 | 129 | 10:00 | ShahCement | 130 | 06:00 | 126 | 10:00
Hathazari | 137 | 19:30 | 133 | 11:00 | Shahjadpur | 137 | 04:00 | 131 | 18:30
Ishurdi | 138 | 06:00 | 132 | 18:30 | Shahjibazar | 134 | 14:00 | 129 | 18:30
Jaldhaka | 130 | 23:00 | 120 | 00:00 | Shahmirpur | 135 | 19:00 | 131 | 03:00
Jamalpur | 130 | 06:00 | 114 | 18:00 | Shariatpur | 135 | 06:00 | 129 | 18:30
Jashore | 137 | 05:00 | 122 | 18:30 | Sherpur | 128 | 10:00 | 110 | 18:00
Jhenaidah | 138 | 05:00 | 123 | 19:00 | Shikalbaha | 125 | 17:00 | 120 | 03:00
Jhenaidah-230 | 139 | 06:00 | 126 | 18:30 | Shikalbaha-230 | 137 | 21:00 | 132 | 02:00
Joydebpur | 140 | 22:00 | 128 | 04:00 | Shitalakhya | 130.1 | 07:00 | 125 | 12:00
Joypurhat | 128 | 23:00 | 122 | 00:00 | Sholosohor | 136 | 19:00 | 132 | 01:00
Juldah | 135 | 19:00 | 130 | 10:00 | Shyampur | 137 | 22:00 | 132 | 11:00
Kabirpur | 135 | 19:00 | 122 | 11:00 | Shyampur-230 | 137 | 06:00 | 131 | 12:00
Kachua | 141 | 17:00 | 134 | 03:00 | Siddhirganj | 130 | 06:00 | 126 | 12:00
Kaliakoir | 136 | 19:00 | 129 | 10:00 | Sirajganj | 131 | 06:00 | 125 | 18:30
Kallyanpur | 136 | 14:00 | 125 | 04:00 | Sonargaon | 128 | 17:00 | 124 | 04:00
Kalurghat | 137 | 19:00 | 132 | 10:00 | Sreemongol | 133 | 07:00 | 129 | 00:00
Kamrangirchar | 134 | 04:00 | 128 | 10:00 | Sreepur | 132 | 06:00 | 125 | 18:30
Kaptai | 138 | 20:00 | 135 | 4:00 | Srinagar | 135 | 06:00 | 128 | 12:00
Kasba | 127 | 07:00 | 122 | 11:00 | SSM | 140 | 21:00 | 132 | 00:00
Kazla | 135 | 07:00 | 128 | 12:00 | Sunamganj | 125 | 07:00 | 121 | 00:00
Keranigonj | 135 | 06:00 | 128 | 12:00 | Sylhet | 130 | 07:00 | 126 | 18:00
Khagrachori | 134 | 19:00 | 130 | 11:00 | Sylhet-132 | 129 | 07:00 | 127 | 00:00
Khulna | 136 | 07:00 | 124 | 18:30 | Tangail | 127 | 19:00 | 118 | 18:00
Khulna(S) | 137 | 06:00 | 127 | 18:30 | Taraganj | 131 | 22:00 | 124 | 11:00
Khulshi | 133 | 19:00 | 129 | 10:00 | Thakurgaon | 136 | 23:00 | 120 | 14:00
Kishoreganj | 128 | 04:00 | 120 | 18:30 | TK | 135 | 17:00 | 132 | 10:00
Kodda | 136 | 00:00 | 122 | 11:00 | Tongi | 136 | 04:00 | 127 | 09:00
KSRM | 136 | 19:00 | 130 | 02:00 | Ullahpara | 133 | 06:00 | 128 | 18:30
Kulaura | 134 | 04:00 | 132 | 22:00 | Ullon | 134 | 00:00 | 123 | 12:00
Kurigram | 130 | 22:00 | 119 | 18:30 | Uttara | 134 | 02:00 | 123 | 10:00
Kushtia | 133 | 05:00 | 126 | 18:30 | UttaraNew | 135 | 04:00 | 130 | 03:00
Laksam | 139 | 17:00 | 133 | 00:00 | Zigatola | 135 | 06:00 | 128 | 12:00
Lakshmipur | 131 | 17:00 | 126 | 00:00
Lalbag | 134 | 05:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division