## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-10-2025 | during | 10-10-2025 | during | 10-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174 | 174 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 374 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 146 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 334 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 46 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 5 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 19.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 220 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 71 | 149 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 108 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 510 | 520 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2507.5 | 2883.5 | 5806.4 | 5788.4 | 3896.31 | 3972.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 210 | 200 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 95 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 62 | 68 | 68 | 68 | 68 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 48 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 17 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 105 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.9 | 0 | 3.77 | 0 | 3.77 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 105 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 103 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 85 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 82 | 128 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1181 | 960 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2176.9 | 2532.86 | 3265.49 | 3261.72 | 3017.63 | 3013.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 0 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 300 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 335 | 410 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 28 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 35 | 55 | 55 | 40 | 40 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 132 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 101 | 104 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 4 | 161 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 74 | 160 | 160 | 78 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1309 | 1598 | 2823.86 | 2763.86 | 2464.16 | 2413.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-10-2025 | during | 10-10-2025 | during | 10-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 7 | 0 | 157.5 | 157.5 | 34 | 34 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 48 | 45 | 45 | 45 | 45 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.37 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 168.37 | 132 | 385.9 | 346 | 208.9 | 169
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 67 | 70 | 70 | 60 | 60 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 163 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 6 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 356 | 357 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1236 | 1225 | 1223 | 1223 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 53 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 101 | 73 | 410 | 410 | 159 | 159 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 45 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 364 | 364 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1448 | 1463 | 2728 | 2688 | 2280 | 2240
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 308 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 282 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.33 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2034.33 | 2226 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 41.47 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 320 | 270 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.13 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1274 | 1396.12 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 26.89 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 19 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1814.49 | 2268.32 | 3191.46 | 3024.87 | 3118.08 | 2951.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 0 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 140 | 145 | 150 | 150 | 145 | 145 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 130 | 0 | 172.87 | 0 | 172.87 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 350.2 | 368 | 656.87 | 448 | 651.87 | 443
System Total |  |  |  |  | 28823.2 | 28365.955 | 13044.79 | 14696.68 | 22227.98 | 21689.85 | 18816.95 | 18381.82
Forecast Scenario (10-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14100 |  | 0 |  | 14100
|  |  |  | 1:00 | 13850 |  | 0 |  | 13850
|  |  |  | 2:00 | 13400 |  | 0 |  | 13400
|  |  |  | 3:00 | 13170 |  | 0 |  | 13170
|  |  |  | 4:00 | 12850 |  | 0 |  | 12850
|  |  |  | 5:00 | 12230 |  | 0 |  | 12230
|  |  |  | 6:00 | 12120 |  | 0 |  | 12120
|  |  |  | 7:00 | 11600 |  | 0 |  | 11600
|  |  |  | 8:00 | 11350 |  | 0 |  | 11350
|  |  |  | 9:00 | 11020 |  | 0 |  | 11020
|  |  |  | 10:00 | 11240 |  | 0 |  | 11240
|  |  |  | 11:00 | 11450 |  | 0 |  | 11450
|  |  |  | 12:00 | 12130 |  | 0 |  | 12130
|  |  |  | 13:00 | 12800 |  | 0 |  | 12800
|  |  |  | 14:00 | 12140 |  | 0 |  | 12140
|  |  |  | 15:00 | 11910 |  | 0 |  | 11910
|  |  |  | 16:00 | 11410 |  | 0 |  | 11410
|  |  |  | 17:00 | 10950 |  | 0 |  | 10950
|  |  |  | 18:00 | 11400 |  | 0 |  | 11400
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13400 |  | 0 |  | 13400
|  |  |  | 19:30 | 13450 |  | 0 |  | 13450
|  |  |  | 20:00 | 13300 |  | 0 |  | 13300
|  |  |  | 21:00 | 13100 |  | 0 |  | 13100
|  |  |  | 22:00 | 12900 |  | 0 |  | 12900
|  |  |  | 23:00 | 12800 |  | 0 |  | 12800
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13450.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13450.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 296.62 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:24 hrs on 10-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-10-2025 | [28 empty] | Date: | 09-10-2025 | [28 empty] | Date: | 09-10-2025 | [28 empty] | Date: | 09-10-2025 | [28 empty] | Date: | 09-10-2025 | [14 empty] | Date: | 09-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 18 | 17 | 133 | 75 | 277 | 30 | 0 | 35 | 0 | 400 | 147 | 495 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 3 | 22 | 0 | 0 | 85 | 16 | 101 | 0 | 0 | 65 | 59 | 54.36 | 0 | 0 | 0 | 222 | 105 | 21 | 285 | 32 | 0 | 50 | 4 | 92 | 192 | 0 | 0 | 0 | 1210 | 0 | 51 | 135 | 0 | 320 | 0 | 300 | 0 | 197 | 0 | 38 | 105 | 143 | 0 | 17 | 0 | 76 | 0 | 0 | 35 | 305 | 0 | 332 | 30 | 68 | 153 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 21 | 0 | 0 | 0 | 7907.36 | 601 | 98 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1434 | 0 | 47 | 0 | 50 | 50 | 0 | 96 | 36 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 146 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 306 | 1222 | 17 | 5912 | 13819.36 | 107.51
01:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 18 | 0 | 133 | 64 | 95 | 15 | 0 | 35 | 0 | 400 | 142 | 500 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 21 | 22 | 0 | 0 | 92 | 16 | 62 | 0 | 3 | 61 | 59 | 54.36 | 0 | 0 | 0 | 221 | 106 | 22 | 285 | 15 | 0 | 40 | 8 | 105 | 181 | 0 | 0 | 0 | 1123 | 0 | 51 | 128 | 0 | 393 | 0 | 300 | 0 | 182 | 0 | 48 | 105 | 150 | 0 | 18 | 0 | 68 | 0 | 0 | 35 | 310 | 0 | 300 | 30 | 68 | 157 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 29 | 0 | 0 | 0 | 7617.36 | 765 | 101 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1446 | 0 | 47 | 0 | 50 | 50 | 0 | 96 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 154 | 48 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 306 | 1112 | 17 | 5943 | 13560.36 | 107.5
02:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 18 | 0 | 105 | 64 | 30 | 0 | 0 | 35 | 0 | 400 | 152 | 490 | 0 | 35 | 335 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 15 | 16 | 0 | 0 | 3 | 66 | 32 | 0 | 0 | 0 | 0 | 219 | 103 | 23 | 285 | 0 | 0 | 19 | 0 | 105 | 181 | 0 | 0 | 0 | 1163 | 0 | 51 | 80 | 0 | 365 | 0 | 300 | 0 | 203 | 0 | 73 | 105 | 120 | 0 | 18 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 333 | 30 | 68 | 151 | 6 | 0 | 81 | 20 | 0 | 16 | 164 | 0 | 67 | 48 | 31 | 0 | 0 | 0 | 7145 | 901 | 102 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 143 | 48 | 70 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 306 | 1092 | 17 | 5667 | 12812 | 107.5
03:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 18 | 0 | 73 | 64 | 0 | 0 | 0 | 35 | 0 | 400 | 149 | 505 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 218 | 108 | 23 | 285 | 0 | 0 | 19 | 0 | 105 | 181 | 0 | 0 | 0 | 1163 | 0 | 51 | 30 | 0 | 350 | 0 | 300 | 0 | 199 | 0 | 72 | 105 | 85 | 0 | 18 | 0 | 64 | 0 | 0 | 0 | 315 | 0 | 333 | 30 | 68 | 159 | 6 | 0 | 81 | 20 | 0 | 16 | 164 | 0 | 67 | 48 | 31 | 0 | 0 | 0 | 6927 | 900 | 105 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 144 | 48 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 306 | 1098 | 17 | 5645 | 12572 | 107.49
04:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 56 | 47 | 0 | 0 | 0 | 35 | 0 | 400 | 144 | 495 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 217 | 68 | 27 | 285 | 0 | 0 | 0 | 0 | 68 | 181 | 0 | 0 | 0 | 1167 | 0 | 51 | 0 | 0 | 360 | 0 | 300 | 0 | 198 | 0 | 34 | 108 | 34 | 0 | 18 | 0 | 62 | 0 | 0 | 0 | 310 | 0 | 314 | 30 | 68 | 153 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 31 | 0 | 0 | 0 | 6552 | 901 | 106 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 144 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 308 | 1095 | 17 | 5603 | 12155 | 107.49
05:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 33 | 47 | 0 | 0 | 0 | 35 | 0 | 400 | 147 | 485 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 217 | 34 | 27 | 285 | 0 | 0 | 0 | 0 | 60 | 181 | 0 | 0 | 0 | 1138 | 0 | 51 | 0 | 0 | 365 | 0 | 300 | 0 | 191 | 0 | 34 | 108 | 0 | 0 | 18 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 312 | 30 | 68 | 150 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 31 | 0 | 0 | 5 | 6384 | 901 | 110 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 145 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 308 | 1090 | 0 | 5551 | 11935 | 107.48
06:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 33 | 30 | 0 | 0 | 0 | 0 | 0 | 370 | 146 | 470 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.04 | 219 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1110 | 1 | 51 | 0 | 0 | 380 | 0 | 300 | 0 | 189 | 0 | 0 | 106 | 0 | 0 | 17 | 0 | 56 | 0 | 2 | 0 | 300 | 0 | 314 | 30 | 68 | 149 | 0 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 31 | 0 | 0 | 6 | 6102.04 | 902 | 110 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 0 | 143 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 115 | 180 | 0 | 308 | 1085 | 0 | 5285 | 11387.04 | 107.48
07:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 33 | 63 | 0 | 0 | 0 | 0 | 0 | 370 | 149 | 505 | 0 | 0 | 335 | 0 | 0 | 1 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0.61 | 220 | 0 | 26 | 285 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1092 | 8 | 51 | 0 | 0 | 336 | 0 | 300 | 0 | 208 | 0 | 0 | 106 | 0 | 0 | 19 | 0 | 60 | 0 | 12 | 0 | 325 | 0 | 360 | 30 | 68 | 160 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 31 | 0 | 5.9 | 6 | 6302.51 | 901 | 113 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 347 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 13 | 0 | 0 | 5.55 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0.61 | 143 | 49 | 0 | 4 | 0 | 0 | 0 | 0 | 0.8 | 17 | 0.09 | 0 | 204 | 115 | 220 | 0 | 308 | 1105 | 0 | 5408.33 | 11710.84 | 107.47
08:00 | 0 | 88 | 12 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 33 | 63 | 0 | 0 | 0 | 0 | 0 | 370 | 145 | 505 | 0 | 0 | 335 | 0 | 0 | 4 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 1.64 | 220 | 0 | 10 | 285 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1150 | 12 | 51 | 0 | 0 | 345 | 0 | 300 | 0 | 188 | 0 | 0 | 107 | 0 | 0 | 19 | 0 | 60 | 0 | 6 | 0 | 320 | 0 | 332 | 30 | 68 | 162 | 6 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 27 | 1 | 17.99 | 0 | 6310.63 | 900 | 118 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 365 | 0 | 1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.87 | 39 | 0 | 0 | 10.79 | 0 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 1.51 | 141 | 47 | 0 | 11 | 0 | 0 | 0 | 0 | 2.4 | 72 | 0.25 | 0 | 198 | 115 | 220 | 0 | 308 | 1106 | 0 | 5510.82 | 11821.45 | 107.46
09:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 50 | 63 | 0 | 0 | 17 | 0 | 0 | 370 | 148 | 500 | 0 | 0 | 335 | 0 | 0 | 7 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2.15 | 221 | 0 | 4 | 285 | 0 | 0 | 1 | 0 | 0 | 202 | 0 | 0 | 0 | 1156 | 7 | 51 | 0 | 0 | 350 | 0 | 300 | 0 | 191 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 50 | 0 | 13 | 0 | 310 | 0 | 332 | 30 | 68 | 162 | 8 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 11 | 1 | 27.01 | 0 | 6343.16 | 900 | 108 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 365 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.26 | 59 | 0 | 0 | 25.6 | 0 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 1.89 | 142 | 49 | 0 | 21 | 0 | 0 | 0 | 0 | 4 | 106 | 0.17 | 0 | 200 | 115 | 220 | 0 | 308 | 1101 | 0 | 5556.92 | 11900.08 | 107.45
10:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 2 | 52 | 63 | 0 | 0 | 35 | 0 | 0 | 370 | 152 | 500 | 0 | 0 | 335 | 0 | 0 | 9 | 52 | 19.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.46 | 221 | 0 | 4 | 285 | 0 | 0 | 44 | 0 | 0 | 203 | 0 | 0 | 0 | 1156 | 20 | 43 | 0 | 0 | 375 | 0 | 255 | 0 | 190 | 0 | 1 | 104 | 0 | 0 | 19 | 0 | 54 | 0 | 76 | 0 | 315 | 0 | 333 | 30 | 68 | 162 | 10 | 0 | 81 | 20 | 0 | 16 | 165 | 0 | 67 | 48 | 10 | 2 | 36.56 | 0 | 6507.32 | 901 | 108 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 365 | 0 | 1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 65 | 0 | 0 | 24.4 | 0 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 3.13 | 117 | 47 | 0 | 28 | 0 | 0 | 0 | 0 | 5.4 | 137 | 0.53 | 0 | 275 | 115 | 220 | 0 | 308 | 1100 | 0 | 5699.56 | 12206.88 | 107.44
11:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17.5 | 17 | 65 | 63 | 105 | 6 | 35 | 49 | 0 | 370 | 151 | 500 | 0 | 0 | 335 | 0 | 0 | 18 | 52 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2.43 | 221 | 0 | 4 | 285 | 0 | 0 | 50 | 0 | 34 | 210 | 0 | 0 | 0 | 1124 | 20 | 43 | 26 | 0 | 335 | 0 | 300 | 0 | 180 | 0 | 42 | 103 | 0 | 0 | 17 | 0 | 54 | 0 | 72 | 0 | 315 | 0 | 303 | 30 | 68 | 161 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 10 | 2 | 40.39 | 0 | 6775.32 | 901 | 105 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 364 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.1 | 44 | 0 | 0 | 52 | 0 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 4.69 | 132 | 47 | 0 | 32 | 0 | 0 | 0 | 0 | 5.5 | 131 | 0.83 | 0 | 270 | 115 | 220 | 0 | 307 | 1101 | 0 | 5750.12 | 12525.44 | 107.43
12:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17.5 | 17 | 71 | 63 | 220 | 15 | 35 | 90 | 0 | 370 | 151 | 510 | 0 | 5 | 334 | 0 | 0 | 0 | 90 | 19 | 22 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 2.9 | 221 | 0 | 10 | 285 | 82 | 0 | 50 | 0 | 90 | 210 | 0 | 0 | 0 | 1181 | 4 | 51 | 108 | 0 | 335 | 0 | 300 | 0 | 203 | 0 | 51 | 101 | 4 | 0 | 19 | 0 | 66 | 0 | 71 | 0 | 320 | 0 | 356 | 30 | 68 | 160 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 66 | 49 | 7 | 2 | 44.37 | 0 | 7397.77 | 900 | 101 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 364 | 0 | 1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.47 | 19 | 0 | 0 | 26.89 | 0 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 3.13 | 140 | 49 | 0 | 27 | 0 | 0 | 0 | 0 | 4.2 | 130 | 0.33 | 0 | 282 | 115 | 220 | 0 | 307 | 1110 | 0 | 5647.02 | 13044.79 | 107.42
13:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 32 | 17 | 121 | 108 | 277 | 45 | 35 | 108 | 0 | 320 | 141 | 495 | 0 | 35 | 280 | 0 | 0 | 16 | 90 | 18.5 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 3.39 | 222 | 0 | 15 | 285 | 134 | 0 | 45 | 0 | 89 | 207 | 0 | 0 | 0 | 1110 | 13 | 51 | 118 | 0 | 335 | 0 | 300 | 0 | 184 | 0 | 51 | 101 | 98 | 0 | 6 | 0 | 72 | 0 | 70 | 0 | 310 | 0 | 315 | 30 | 68 | 160 | 10 | 0 | 81 | 30 | 0 | 16 | 166 | 0 | 67 | 49 | 0 | 0 | 42.26 | 0 | 7598.15 | 900 | 94 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 365 | 0 | 1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.38 | 79 | 0 | 0 | 37.2 | 0 | 0 | 130 | 0 | 0 | 0 | 320 | 0 | 3.05 | 143 | 48 | 0 | 32 | 0 | 0 | 0 | 0 | 1.9 | 168 | 0.23 | 0 | 270 | 115 | 180 | 0 | 306 | 1100 | 0 | 5750.76 | 13348.91 | 107.41
14:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 17 | 147 | 95 | 277 | 55 | 35 | 108 | 0 | 320 | 151 | 475 | 0 | 35 | 280 | 0 | 0 | 23 | 90 | 18.5 | 22 | 0 | 0 | 0 | 0 | 100 | 0 | 15 | 47 | 0 | 0 | 0 | 0 | 2.93 | 221 | 0 | 9 | 285 | 154 | 0 | 45 | 0 | 94 | 207 | 0 | 0 | 0 | 1181 | 17 | 51 | 112 | 0 | 325 | 0 | 300 | 0 | 205 | 0 | 51 | 102 | 115 | 0 | 17 | 0 | 64 | 0 | 49 | 13 | 315 | 0 | 373 | 30 | 68 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 49 | 0 | 2 | 46.64 | 0 | 7848.07 | 901 | 88 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 365 | 0 | 1318.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.73 | 57 | 0 | 0 | 19.67 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 2.12 | 142 | 48 | 0 | 26 | 0 | 0 | 0 | 0 | 3.9 | 137 | 0.72 | 0 | 204 | 115 | 180 | 0 | 306 | 1050 | 0 | 5519.64 | 13367.71 | 107.4
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35.9 | 17 | 149 | 100 | 277 | 55 | 35 | 108 | 0 | 370 | 142 | 460 | 0 | 35 | 330 | 0 | 0 | 11 | 90 | 18.5 | 22 | 0 | 0 | 1 | 5 | 101 | 0 | 10 | 46 | 0 | 0 | 0 | 0 | 2.16 | 221 | 0 | 6 | 285 | 144 | 0 | 40 | 0 | 95 | 204 | 0 | 0 | 0 | 1149 | 13 | 51 | 107 | 0 | 310 | 0 | 300 | 0 | 188 | 0 | 51 | 105 | 120 | 0 | 6 | 0 | 66 | 0 | 17 | 34 | 320 | 0 | 328 | 30 | 68 | 163 | 6 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 66 | 49 | 0 | 0 | 27.74 | 0 | 7746.3 | 900 | 82 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 365 | 0 | 1317.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.78 | 30 | 0 | 0 | 15.77 | 0 | 0 | 130 | 0 | 0 | 0 | 330 | 0 | 0.95 | 143 | 48 | 21 | 18 | 0 | 0 | 0 | 0 | 1.6 | 108 | 0.64 | 0 | 276 | 115 | 220 | 0 | 307 | 1108 | 2 | 5629.65 | 13375.95 | 107.39
16:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35.9 | 17 | 135 | 95 | 195 | 30 | 35 | 108 | 0 | 320 | 147 | 410 | 0 | 35 | 331 | 0 | 0 | 2 | 90 | 18.5 | 22 | 0 | 0 | 27 | 15 | 96 | 0 | 5 | 47 | 0 | 0 | 0 | 0 | 0.94 | 219 | 58 | 6 | 285 | 107 | 0 | 40 | 6 | 94 | 202 | 0 | 0 | 0 | 1102 | 3 | 51 | 107 | 0 | 310 | 0 | 300 | 0 | 0 | 0 | 51 | 104 | 108 | 1 | 17 | 0 | 60 | 0 | 13 | 36 | 305 | 0 | 346 | 30 | 68 | 163 | 6 | 0 | 78 | 30 | 0 | 16 | 165 | 0 | 66 | 49 | 0 | 0 | 2.12 | 0 | 7256.46 | 899 | 76 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.54 | 364 | 0 | 1282.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 31 | 0 | 0 | 4.08 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 0.35 | 142 | 48 | 35 | 10 | 0 | 0 | 0 | 0 | 2.2 | 54 | 0.03 | 0 | 277 | 115 | 220 | 0 | 307 | 1215 | 17 | 5598.48 | 12854.94 | 107.38
17:00 | 0 | 73 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35.9 | 20 | 132 | 95 | 195 | 30 | 35 | 108 | 0 | 320 | 147 | 420 | 0 | 35 | 331 | 0 | 0 | 1 | 142 | 18 | 22 | 0 | 0 | 30 | 15 | 95 | 0 | 3 | 48 | 0 | 0 | 0 | 0 | 0.14 | 218 | 66 | 13 | 285 | 97 | 0 | 40 | 8 | 95 | 201 | 0 | 0 | 0 | 1110 | 0 | 51 | 117 | 0 | 350 | 0 | 300 | 12 | 0 | 12 | 62 | 104 | 119 | 9 | 7 | 0 | 62 | 0 | 2 | 36 | 310 | 0 | 340 | 30 | 68 | 157 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 2 | 66 | 49 | 0 | 0 | 1.03 | 0 | 7430.07 | 900 | 70 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 0 | 0 | 3.5 | 363 | 0 | 1273.35 | 0 | 0 | 0 | 10 | 0 | 0 | 25 | 0 | 0 | 1.83 | 5 | 0 | 0 | 2 | 0 | 0 | 130 | 0 | 0 | 0 | 220 | 0 | 0.2 | 145 | 46 | 35 | 2 | 15 | 0 | 0 | 0 | 0.4 | 11 | 0.02 | 0 | 277 | 115 | 220 | 0 | 307 | 1120 | 17 | 5353.3 | 12783.37 | 107.37
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 38.8 | 35 | 149 | 126 | 277 | 38 | 55 | 108 | 0 | 400 | 149 | 520 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 18 | 22 | 0 | 0 | 40 | 45 | 100 | 0 | 1 | 48 | 24 | 17 | 0 | 0 | 0 | 219 | 73 | 18 | 285 | 145 | 0 | 40 | 10 | 101 | 201 | 0 | 0 | 0 | 1175 | 0 | 51 | 128 | 0 | 405 | 0 | 330 | 33 | 0 | 26 | 69 | 104 | 118 | 9 | 17 | 52 | 72 | 2 | 0 | 36 | 320 | 0 | 380 | 30 | 68 | 153 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 14 | 66 | 49 | 0 | 0 | 0 | 0 | 8312.8 | 900 | 70 | 0 | 14 | 45 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1358.58 | 0 | 0 | 0 | 70 | 56 | 0 | 94 | 16 | 16 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 220 | 0 | 0 | 144 | 48 | 90 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 290 | 115 | 220 | 0 | 307 | 1125 | 17 | 5871.58 | 14184.38 | 107.35
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 149 | 127 | 277 | 55 | 35 | 108 | 0 | 400 | 142 | 520 | 0 | 35 | 331 | 0 | 0 | 0 | 142 | 18 | 22 | 0 | 0 | 69 | 75 | 104 | 0 | 0 | 48 | 62 | 34 | 0 | 0 | 0 | 219 | 107 | 13 | 285 | 145 | 0 | 40 | 25.5 | 101 | 201 | 0 | 0 | 0 | 961 | 0 | 51 | 132 | 8 | 410 | 0 | 330 | 35 | 0 | 31 | 88 | 104 | 156 | 9 | 17 | 97 | 72 | 24 | 0 | 36 | 310 | 0 | 342 | 30 | 68 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 65 | 49 | 0 | 0 | 0 | 0 | 8357.5 | 899 | 73 | 0 | 26 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1401.18 | 0 | 33 | 0 | 113 | 109 | 0 | 94 | 29 | 43 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 0 | 145 | 46 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 307 | 115 | 220 | 0 | 308 | 1180 | 17 | 6314.18 | 14671.68 | 107.34
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 46 | 35 | 149 | 127 | 277 | 55 | 35 | 108 | 0 | 350 | 146 | 520 | 0 | 35 | 333 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 0 | 85 | 105 | 105 | 0 | 0 | 48 | 62 | 54.36 | 0 | 0 | 0 | 220 | 103 | 17 | 285 | 128 | 0 | 40 | 25.5 | 95 | 200 | 0 | 0 | 0 | 960 | 0 | 51 | 132 | 8 | 410 | 0 | 330 | 35 | 0 | 28 | 90 | 104 | 161 | 9 | 17 | 70 | 74 | 43 | 0 | 36 | 310 | 0 | 357 | 30 | 67 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 67 | 48 | 0 | 0 | 0 | 0 | 8371.36 | 900 | 73 | 0 | 35 | 53 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1396.12 | 0 | 47 | 0 | 113 | 113 | 0 | 94 | 38 | 52.2 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 0 | 145 | 0 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 308 | 1180 | 17 | 6325.32 | 14696.68 | 107.34
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 49.2 | 17 | 149 | 127 | 277 | 55 | 35 | 108 | 0 | 350 | 144 | 500 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 82 | 120 | 105 | 0 | 0 | 48 | 62 | 54.36 | 0 | 0 | 0 | 220 | 104 | 20 | 285 | 124 | 0 | 40 | 25.5 | 93 | 199 | 0 | 0 | 0 | 963 | 0 | 51 | 133 | 8 | 415 | 0 | 330 | 35 | 0 | 31 | 91 | 105 | 158 | 8 | 16 | 60 | 70 | 43 | 0 | 36 | 305 | 0 | 323 | 30 | 67 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 67 | 49 | 0 | 0 | 0 | 0 | 8290.06 | 900 | 80 | 0 | 30 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1404.76 | 0 | 47 | 0 | 113 | 113 | 0 | 94 | 38 | 52.2 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 0 | 145 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 271 | 115 | 220 | 0 | 307 | 1180 | 17 | 6327.96 | 14618.02 | 107.34
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 45.6 | 17 | 149 | 110 | 277 | 55 | 35 | 108 | 0 | 350 | 148 | 505 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 84 | 120 | 89 | 0 | 0 | 48 | 54 | 54.36 | 0 | 0 | 0 | 220 | 105 | 21 | 285 | 63 | 0 | 40 | 25.5 | 94 | 193 | 0 | 0 | 0 | 1002 | 0 | 51 | 138 | 8 | 350 | 0 | 330 | 37 | 30 | 33 | 61 | 105 | 160 | 9 | 16 | 17 | 72 | 25 | 0 | 36 | 300 | 0 | 346 | 30 | 67 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 17 | 67 | 48 | 0 | 0 | 0 | 0 | 8131.46 | 901 | 80 | 0 | 30 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1409.69 | 0 | 47 | 0 | 113 | 113 | 0 | 94 | 38 | 25 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 0 | 144 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 276 | 115 | 220 | 0 | 308 | 1180 | 17 | 6286.69 | 14418.15 | 107.33
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 45.4 | 17 | 149 | 110 | 277 | 55 | 35 | 108 | 0 | 350 | 143 | 505 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 84 | 120 | 80 | 0 | 0 | 48 | 54 | 54.36 | 0 | 0 | 0 | 220 | 104 | 25 | 285 | 63 | 0 | 40 | 8 | 93 | 191 | 0 | 0 | 0 | 1085 | 0 | 51 | 140 | 0 | 285 | 0 | 330 | 43 | 30 | 33 | 56 | 105 | 158 | 0 | 16 | 14 | 68 | 8 | 0 | 28 | 305 | 0 | 364 | 30 | 67 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 8080.76 | 899 | 40 | 0 | 30 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1402.04 | 0 | 47 | 0 | 113 | 113 | 0 | 95 | 38 | 8 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 290 | 0 | 0 | 145 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 275 | 115 | 220 | 0 | 307 | 1210 | 17 | 6237.04 | 14317.8 | 107.32
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 20.3 | 17 | 149 | 110 | 277 | 55 | 35 | 108 | 0 | 350 | 147 | 500 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20.3 | 21 | 0 | 0 | 86 | 120 | 62 | 0 | 0 | 48 | 54 | 54.36 | 0 | 0 | 0 | 222 | 105 | 25 | 285 | 65 | 0 | 30 | 8 | 91 | 173 | 0 | 0 | 0 | 1162 | 0 | 51 | 140 | 0 | 290 | 0 | 330 | 44 | 30 | 37 | 44 | 105 | 157 | 0 | 16 | 15 | 76 | 8 | 0 | 31 | 305 | 0 | 352 | 30 | 67 | 156 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 8078.96 | 900 | 0 | 0 | 30 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1387.67 | 0 | 47 | 0 | 50 | 113 | 0 | 95 | 37 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 290 | 0 | 0 | 145 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 278 | 115 | 220 | 0 | 307 | 1120 | 17 | 6024.67 | 14103.63 | 107.32
Total KWH | 0 | 2027520 | 303360 | 0 | 0 | 0 | 0 | 0 | 8769600 | 0 | 0 | 520200 | 302040 | 2490192 | 1970880 | 3561655 | 669325 | 529202 | 1578240 | 0 | 8887500 | 3529455 | 11822541 | 0 | 539251 | 7992085 | 0 | 0 | 92782 | 2396400 | 409800 | 502200 | 0 | 0 | 743945 | 787855 | 1177920 | 0 | 67200 | 896953 | 460800 | 403001 | 0 | 0 | 22441 | 5276098 | 1309745 | 412800 | 6829090.91 | 1333164 | 0 | 713280 | 154056.6 | 1813236 | 4584626 | 0 | 0 | 0 | 26978179 | 119070 | 1226508 | 1968800 | 33455 | 8425000 | 0 | 7474000 | 274560 | 3296000 | 221328 | 1113600 | 2509220 | 2130240 | 45360 | 345310 | 259920 | 1599360 | 140002 | 368000 | 385488 | 7576000 | 0 | 8443000 | 716000 | 1600800 | 3797509 | 179760 | 0 | 1926720 | 612000 | 0 | 391000 | 3405910 | 72360 | 1602000 | 1156800 | 265920 | 9600 | 259310 | 20880 | 176829408.51 | 21553455 | 2232288 | 0 | 162720 | 315904 | 912000 | 0 | 0 | 0 | 0 | 0 | 456480 | 8683636 | 0 | 32758350 | 0 | 292604 | 0 | 719040 | 834624 | 0 | 768528 | 238060 | 131174 | 197436 | 483554 | 133276 | 0 | 222000 | 0 | 0 | 3418409 | 0 | 0 | 0 | 7756436 | 0 | 20400 | 3517000 | 822981 | 1176992 | 213297 | 933532 | 0 | 0 | 0 | 33267.12 | 1068480 | 2589 | 461664 | 6568000 | 2762000 | 5440990 | 0 | 7381080 | 27437090.91 | 259200 | 140368537.03 | 317197945.54

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13044.79 | MW | 12:00 Hr. | Energy Generated |  |  | 317.1979 |  | MKWHr.
| Day Peak Demand |  |  | 13044.79 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.55 |  | MKWHr.
| Evening Peak Generation |  |  | 14696.68 | MW | 19:30 Hr. | Energy Demand |  |  | 317.7479 |  | MKWHr.
| Evening Peak Demand |  |  | 14770.96 | MW | 19:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 11387.04 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 888.7 |  | MMCFD
| Maximum Generation of the Day |  |  | 14696.68 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.675 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.9132 | 0 | 16.8883 | 0 | 0 | 0.092782 | 0 | 0 | 58.8942 | Gas | 121.2407 | Gas | 431566450.95
| Chattogram Zone |  |  | 4.9974 | 33.8073 | 9.794 | 0 | 5.2761 | 0.14151 | 0 | 0.0672 | 54.0835 | Coal | 88.2171 | Coal | 510510141.6119
| Cumilla Zone |  |  | 23.8054 | 0 | 6.0434 | 0 | 0 | 0.368 | 1.5994 | 0 | 31.8162 | HFO | 42.005 | HFO | 780417480.928
| Mymensingh Zone |  |  | 0.26592 | 0 | 2.852 | 0 | 0 | 0.26891 | 0 | 0 | 3.3869 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6487 | Hydro | 5.2761 | Hydro | 527609.8
| Khulna Zone |  |  | 2.2323 | 8.6836 | 0.47862 | 0 | 0 | 0.45648 | 22.4655 | 0 | 34.3165 | Solar | 3.5687 | Solar | 55904188.5052
| Barishal Zone |  |  | 8.203 | 41.3862 | 0.72086 | 0 | 0 | 0.002589 | 0 | 0 | 50.3126 | Import | 56.8232 | Import | 337375204.95
| Rajshahi Zone |  |  | 11.1748 | 0 | 3.1173 | 0 | 0 | 0.92339 | 32.7584 | 0 | 47.9739 | Wind | 0.0672 | Wind | 990528
| Rangpur Zone |  |  | 0 | 4.34 | 2.1105 | 0 | 0 | 1.315 | 0 | 0 | 7.7655
| Total |  |  | 121.2407 | 88.2171 | 42.005 | 0 | 5.2761 | 3.5687 | 56.8232 | 0.0672 | 317.1979
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431566450.95 |  | Hydro | 527609.8
|  |  |  | Coal | 510510141.6119 |  | Solar | 55904188.5052
|  |  |  | HFO | 780417480.928 |  | Import | 337375204.95
|  |  |  | HSD | 0 |  | Wind | 990528
[5 empty] | Total: | 211,72,91,604 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5535 | Peak Hr Flow | 900.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47902820.41 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.7584 | Peak Hr Flow | 1396.12 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1700 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5994 | Peak Hr Flow | 74.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2379 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.9112 | Peak Hr Flow | 2370.12 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5267
|  |  |  | Chattogram |  | 0 |  | 1425
|  |  |  | Cumilla |  | 0 |  | 1387
|  |  |  | Mymensingh |  | 62 |  | 1148
|  |  |  | Sylhet |  | 0 |  | 625
|  |  |  | Khulna |  | 0 |  | 1645
|  |  |  | Barishal |  | 0 |  | 423
|  |  |  | Rajshahi |  | 0 |  | 1406
|  |  |  | Rangpur |  | 0 |  | 911
|  |  |  | Total |  | 62 |  | 14237
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 12:34 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Oil filling and 132kV side (b
phase) CT top side maintenance due to temperature rise.
| 08:03 | 12:34 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Oil filling at 230/132 KV auto
Tr-1(Y-B ) Phase main tank conservatory,132KV side B Phase CT top side connector, 132 KV
CB Y Phase over temperature.
| 08:07 | 09:43 | Chandpur 132/33kV S/S 33 kV T-5 section Forced S/D Due to Auxiliary transformer fuse | [7 empty] | 25.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 08:12 | 09:33 | Chhatak 132/33kV S/S T-3 HT Forced S/D Due to Shutdown for T-3 GCB hydraulic oil leakage
problem.
| 08:19 | 09:58 | Bajitpur 132/33kV S/S Tr-1(404T) LT Forced S/D Due to 33 KV Bus section-1 shutdown for
feeder maintenance
| 08:20 | 09:54 | Bajitpur 132/33kV S/S Tr-1(404T) HT Forced S/D Due to 33 KV Bus section-1 shutdown for
feeder maintenance
| 08:26 | 18:38 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to OPGW CHANGE WORK
| 08:36 | 16:13 | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual Maintenance and from Rangamati 132/33kV end Due to Rangamati Chandraghona Ckt-01
taken shutdown due to annual maintenance.
| 08:38 | 17:09 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to Annual maintenance.
| 08:38 | 17:09 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to Annual maintenance.
| 09:05 | 14:30 | Jaldhaka 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance work.
| 09:13 | 15:22 | Bogura 230/132kV S/S 230KV Main 2 Scheduled S/D Due to Annual Maintenance
| 09:15 | 16:23 | Rahanpur 400/132kV S/S AT-01 LT Scheduled S/D Due to General checking & inspection
| 09:15 | 16:23 | Rahanpur 400/132kV S/S AT-01 HT Scheduled S/D Due to General checking & inspection
| 09:35 | 11:33 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Red hot | [7 empty] | 18.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 09:37 | 11:31 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Red hot | [7 empty] | 18.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
|  | 09:40 | Sylhet 132/33kV S/S T2 HT is restored.
|  | 09:42 | Sylhet 132/33kV S/S T2 LT is restored.
|  | 09:42 | Sylhet 132/33kV S/S T2 LT is restored.
|  | 09:42 | Sylhet 132/33kV S/S T2 LT is restored.
| 09:57 | 17:45 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to CNTIC work
| 10:04 | 17:29 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to CNTIC
and from Chowmuhani 132/33kV end Due to Order by NLDC
| 10:18 | 17:27 | Daganbhuiyan 132/33kV S/S Main Bus 1&2 Project Work S/D Due to CNTIC project work
| 10:52 |  | Gopalganj 400/132kV S/S 400kV Rooppur Tripped showing Deferential Relay relays Due to
Line Deferential fault.
| 11:40 | 21:57 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Tripped showing REF/SEF TRP relays. | [7 empty] | 33.0MW load
interrup.
| 11:40 | 21:57 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Tripped showing GENERAL TRIP, DIFF TRIP, REF/SEF | [7 empty] | 33.0MW load
|  |  | TRIP relays. | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 13041 MW
| 12:51 |  | Ishurdi-Ghorashal Ckt-2's new GIS bay is charged on the Ghorashal end.
| 12:54 | 13:41 | Chandina 132/33kV S/S TR-3 LT Scheduled S/D Due to Project work | [7 empty] | 7.0MW load
interrup.
| 12:56 | 13:49 | Barapukuria-Bogura 230 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing REL
521,REL 511 relays Due to Thundering
| 12:57 | 13:39 | Chandina 132/33kV S/S TR-3 HT Scheduled S/D Due to Project work | [7 empty] | 7.0MW load
interrup.
| 14:35 | 17:35 | Bakulia 132/33kV S/S T-4 (432T) HT Project Work S/D
| 15:54 |  | Ashuganj CCPP 225 MW Tripped with remarks:- GT
| 15:54 |  | Ashuganj 225 MW tripped due to the activation of generator protection.
| 17:19 |  | Barapukuria PS Unit-1 tripped.
|  | 17:28 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation is 14695 MW
| 20:01 |  | Ashuganj 225 MW GT was sync.
| 20:01 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
|  | 20:25 | Ghorasal-Tongi 230kV Ckt-2 is restored.
| 20:38 | 21:54 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Forced S/D Due to 33/11 kV T-4(PDB) DS red hot | [7 empty] | 15.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 20:39 | 21:54 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D Due to 33 kv 33/11 kv Tr-4 (PDB) DS | [7 empty] | 15.0MW load
|  |  | red hot maintenance. | [7 empty] | interrup.
| 22:25 |  | Bheramara 410 MW CCPP Shutdown with remarks:- STG
| 22:29 |  | Bheramara 410 MW CCPP was shutdown due to low gas pressure.
| 22:29 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GTG
| 00:57 | 02:18 | Bakulia 132/33kV S/S T-3 (422T) HT Forced S/D | [7 empty] | 20.0MW load
interrup.
| 01:05 |  | Barapukuria PS Unit-1 was sync.
| 06:13 |  | Hathazari-Madunaghat 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to Bus
Shutdown at Hathazari Grid
| 06:13 |  | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Bus
Shutdown at Hathazari grid
| 06:27 |  | Hathazari 230/132/33kV S/S MT-04 HT Project Work S/D Due to Project Work shutdown
| 06:30 |  | Hathazari 230/132/33kV S/S MT-04 LT Project Work S/D Due to Project Work shutdown
| 06:50 |  | Sylhet 225 MW CCPP was shutdown at 06:50 hrs. to change air-filter.
| 06:51 |  | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D Due to For maintenace work
| 07:00 |  | Minimum Generation: 11115 MW.
| 07:12 |  | Hathazari 230/132/33kV S/S 132KV MAIN BUS-01 Project Work S/D Due to Project Work
shutdown
| 07:15 |  | Jashore 132/33kV S/S T-3 HT Forced S/D | [7 empty] | 15.0MW load
interrup.
| 07:15 |  | Jashore 132/33kV S/S T-3 LT Forced S/D | [7 empty] | 15.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8769600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8887500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 146 | 3529455 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 669325 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7992085 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46 | 520200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 1970880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 529202 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 539251 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19.5 | 409800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 502200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 303360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 3561655 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2490192 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2027520 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1578240 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 92782 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 302040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 520 | 11822541 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2396400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2883.5 | 58894228
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 154056.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119070 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 713280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5276098 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 200 | 4584626 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 95 | 1813236 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 460800 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 48 | 896953 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 412800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 105 | 1177920 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 105 | 787855 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 403001 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 103 | 1309745 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 85 | 743945 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 128 | 1333164 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 960 | 26978179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 67200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6829090.91 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2532.86 | 54083460.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 3296000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7474000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 410 | 8425000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 28 | 221328 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 35 | 274560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 33455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1226508 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 1968800 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 385488 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2509220 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 161 | 2130240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 74 | 1599360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 140002 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 345310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 259920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 45360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1113600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 368000 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1598 | 31816151
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 265920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1156800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1602000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 259310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 20880 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 72360 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 132 | 3386870
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1600800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3797509 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 612000 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1926720 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3405910 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 391000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 179760 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7576000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 357 | 8443000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1225 | 28648699
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21553455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 162720 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 53 | 315904 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 73 | 2232288 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 456480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 364 | 8683636 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1463 | 34316483
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 308 | 7381080 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 461664 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2762000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 27437090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5440990 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 259200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6568000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2589 | -
Barishal Area Total |  |  |  |  | 2858 | 2226 | 50312613.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 197436 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 292604 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 238060 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3418409 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 270 | 7756436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 133276 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 131174 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 768528 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 834624 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 719040 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1396.12 | 32758350 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 222000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 483554 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2268.32 | 47973891
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 822981 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 145 | 3517000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 933532 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33267.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1176992 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 213297 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1068480 | -
Rangpur Area Total |  |  |  |  | 950 | 368 | 7765549.12
Eastern Grid Total |  |  |  |  | 17385.715 | 8371.36 | 176829408.51
Western Grid Total |  |  |  |  | 10980.24 | 6325.32 | 140368537.03
National Grid Total |  |  |  |  | 28365.955 | 14696.68 | 317197945.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-10-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9790.4 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4385.4 | MW
i) Dhaka area |  |  | 5266.87 |  | MW | i) Khulna area |  |  |  | 1645 | MW
ii) Chattogram area |  |  | 1425.4 |  | MW | ii) Barishal area |  |  |  | 423 | MW
iii) Cumilla area |  |  | 1387.13 |  | MW | iii) Rajshahi area |  |  |  | 1406.4 | MW
iv) Mymensingh area |  |  | 1086 |  | MW | iv) Rangpur area |  |  |  | 911 | MW
v) Sylhet area |  |  | 625 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14175.8 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 20:00 | 133 | Niamatpur | 70 | 21:00
2 | AKSML | 121.3 | 00:00 | 68 | Ishurdi | 68 | 00:00 | 134 | Noapara | 38 | 18:30
3 | Aftabnagar | 36 | 13:00 | 69 | Jaldhaka | 84 | 18:30 | 135 | PHP | 6 | 11:00
4 | Agargaon | 125 | 13:00 | 70 | Jamalpur | 107 | 22:00 | 136 | Pabna | 111 | 18:30
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 137 | 13:00 | 137 | Palashbari | 110 | 19:00
6 | Amnura | 27 | 21:00 | 72 | Jhenaidah | 124 | 18:00 | 138 | Panchagarh | 56 | 18:00
7 | Ashuganj | 80 | 00:00 | 73 | Joydebpur | 161 | 18:00 | 139 | Patiya | 11 | 00:00
8 | BSRM | 115 | 03:00 | 74 | Joypurhat | 58 | 19:30 | 140 | Patuakhali | 67.7 | 00:00
9 | Bagerhat | 77 | 19:30 | 75 | Juldah | 17 | 13:00 | 141 | Payra | 28 | 00:00
10 | Bajitpur | 89 | 21:00 | 76 | KSRM | 26 | 00:00 | 142 | Postogola | 69 | 13:00
11 | Bakulia | 99 | 19:30 | 77 | Kabirpur | 256 | 09:00 | 143 | Purbachal | 21 | 19:30
12 | Banani | 44 | 14:00 | 78 | Kachua | 88 | 00:00 | 144 | Purbasadipur | 122 | 18:30
13 | Bangabhaban | 21 | 10:00 | 79 | Kallyanpur | 99 | 18:00 | 145 | Rahanpur | 38 | 22:00
14 | Barapukuria | 63 | 18:30 | 80 | Kalurghat | 42 | 12:00 | 146 | Rahim | 25 | 23:00
15 | Barguna | 20 | 22:00 | 81 | Kamrangirchar | 78 | 18:00 | 147 | Rajbari | 78 | 18:30
16 | Barishal | 114 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 138 | 18:00
17 | Barishal-230 | 90 | 21:00 | 83 | Kasba | 34 | 20:00 | 149 | Rajshahi | 98 | 21:00
18 | Baroaulia | 60 | 11:00 | 84 | Kazla | 102 | 20:00 | 150 | Rajshahi-230 | 102 | 13:00
19 | Baroirhat | 64 | 19:00 | 85 | Keranigonj | 94 | 18:00 | 151 | Ramganj | 108 | 00:00
20 | Bashundhara | 189 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Rampur | 42 | 00:00
21 | BashundharaCement | 6 | 14:00 | 87 | Khulna | 72 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 80 | 18:00 | 88 | Khulshi | 203 | 18:00 | 154 | Rangpur | 148 | 18:30
23 | Benapole | 56 | 20:00 | 89 | Kishoreganj | 120 | 00:00 | 155 | Ruppur | 7.6 | 09:00
24 | Bhaluka | 157 | 19:00 | 90 | Kodda | 294 | 08:00 | 156 | SSM | 16 | 01:00
25 | Bhandaria | 48 | 00:00 | 91 | Kulaura | 49 | 18:00 | 157 | Saidpur | 101 | 18:30
26 | Bhangura | 36 | 18:30 | 92 | Kurigram | 66 | 19:30 | 158 | Satkhira | 112 | 00:00
27 | Bheramara(GK) | 63 | 18:00 | 93 | Kushtia | 158 | 18:30 | 159 | Satmasjid | 94 | 13:00
28 | Bhulta | 211 | 11:00 | 94 | Laksam | 37 | 01:00 | 160 | Savar | 236 | 15:00
29 | Bog-Sherpur | 76 | 18:30 | 95 | Lakshmipur | 32 | 19:30 | 161 | SevenRings | 15.05 | 16:00
30 | Bogura | 166 | 19:00 | 96 | Lalbag | 62 | 13:00 | 162 | ShahCement | 29 | 00:00
31 | Borhanuddin | 92 | 21:00 | 97 | Lalmonirhat | 58 | 21:00 | 163 | Shahjadpur | 90 | 19:00
32 | Brahmanbaria | 129 | 20:00 | 98 | MI_Cement | 16.3 | 12:00 | 164 | Shahjibazar | 120 | 00:00
33 | Cantonment | 134 | 13:00 | 99 | Madanganj | 32 | 00:00 | 165 | Shahmirpur | 51 | 18:00
34 | Chandina | 22.57 | 18:30 | 100 | Madaripur | 99 | 22:00 | 166 | Shariatpur | 84 | 21:00
35 | Chandpur | 86 | 19:00 | 101 | Madartek | 84 | 23:00 | 167 | Sherpur | 126 | 19:30
36 | Chandraghona | 37 | 18:30 | 102 | Madunaghat | 56 | 19:00 | 168 | Shikalbaha | 28 | 15:00
37 | Chapai | 63 | 20:00 | 103 | Magura | 59 | 18:00 | 169 | Shitalakhya | 88.6 | 12:00
38 | Charsaidpur | 42 | 16:00 | 104 | Mahasthangarh | 72 | 19:00 | 170 | Sholosohor | 46 | 14:00
39 | Chauddagram | 68 | 19:30 | 105 | Maijdee | 21 | 21:00 | 171 | Shyampur | 94 | 00:00
40 | Chhatak | 38 | 18:30 | 106 | Manikganj | 129 | 20:00 | 172 | Siddhirganj | 128 | 15:00
41 | Chowmuhani | 177 | 21:00 | 107 | Maniknagar | 62 | 14:00 | 173 | Sirajganj | 105 | 18:30
42 | Chuadanga | 107 | 00:00 | 108 | Matarbari | 50 | 18:00 | 174 | Sonargaon | 132 | 00:00
43 | Coxsbazar | 133 | 18:30 | 109 | Matuail | 66 | 15:00 | 175 | Sreemongol | 81 | 18:30
44 | Cumilla(N) | 142 | 19:00 | 110 | Metrorail_Motijheel | 30 | 16:00 | 176 | Sreepur | 101 | 18:00
45 | Cumilla(S) | 146 | 18:00 | 111 | Metrorail_Uttara | 10 | 16:00 | 177 | Srinagar | 44.86 | 00:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 132 | 15:00 | 178 | Sunamganj | 61 | 22:00
47 | Daudkandi | 151 | 20:00 | 113 | Mirpur | 118 | 18:00 | 179 | Sylhet | 53 | 18:00
48 | DhakaUniversity | 86 | 13:00 | 114 | Mirsorai | 11 | 15:00 | 180 | Sylhet-132 | 121 | 13:00
49 | Dhamrai | 140 | 18:00 | 115 | Mirzapur | 38 | 12:00 | 181 | TK | 24.5 | 23:00
50 | Dhanmondi | 124.7 | 13:00 | 116 | Mithapukur | 68 | 18:30 | 182 | Tangail | 162 | 22:00
51 | Dohazari | 99 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 23 | 18:00
52 | Faridpur | 166 | 19:00 | 118 | Mogbazar | 92.9 | 14:00 | 184 | Thakurgaon | 101 | 19:00
53 | Fatullah | 109 | 09:00 | 119 | Mongla | 39 | 00:00 | 185 | Tongi | 129 | 11:00
54 | Fenchuganj | 41 | 18:00 | 120 | Motijheel | 52 | 13:00 | 186 | Ullahpara | 35 | 18:30
55 | Feni | 119 | 18:00 | 121 | Muktagacha | 32 | 01:00 | 187 | Ullon | 60 | 19:30
56 | GPH | 5 | 18:30 | 122 | Munshiganj | 110 | 19:30 | 188 | Uttara | 77 | 13:00
57 | Ghatail | 74 | 07:00 | 123 | Muradnagar | 40 | 20:00 | 189 | UttaraNew | 72 | 22:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 190 | 19:30 | 190 | Zigatola | 69 | 19:00
59 | Ghorashal-230 | 98 | 19:00 | 125 | Naogaon | 121 | 20:00
60 | Goalpara | 24 | 00:00 | 126 | Narail | 55 | 18:00
61 | Gollamari | 100 | 20:00 | 127 | Narinda | 65 | 13:00
62 | Gopalganj | 105 | 18:30 | 128 | Narshingdi | 180 | 18:30
63 | Gulshan | 116 | 14:00 | 129 | Natore | 146 | 21:00
64 | Halishahar | 79 | 09:00 | 130 | Nawabganj | 45.4 | 22:00
65 | HaripurSBU | 141 | 16:00 | 131 | Netrakona | 137 | 20:00
66 | Hasnabad | 78 | 19:30 | 132 | New | 55 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13819.36 | 39 |  | 13860.12
1:00 | 13560.36 | 0 |  | 13560.36
2:00 | 12812 | 0 |  | 12812
3:00 | 12572 | 0 |  | 12572
4:00 | 12155 | 0 |  | 12155
5:00 | 11935 | 0 |  | 11935
6:00 | 11387.04 | 0 |  | 11387.04
7:00 | 11710.84 | 0 |  | 11710.84
8:00 | 11821.45 | 0 |  | 11821.45
9:00 | 11900.08 | 0 |  | 11900.08
10:00 | 12206.88 | 0 |  | 12206.88
11:00 | 12525.44 | 0 |  | 12525.44
12:00 | 13044.79 | 0 |  | 13044.79
13:00 | 13348.91 | 0 |  | 13348.91
14:00 | 13367.71 | 0 |  | 13367.71
15:00 | 13375.95 | 0 |  | 13375.95
16:00 | 12854.94 | 143 |  | 13004.38
17:00 | 12783.37 | 0 |  | 12783.37
18:00 | 14184.38 | 136 |  | 14326.5
19:00 | 14671.68 | 95 |  | 14770.96
19:30 | 14696.68 | 62 |  | 14761.47
20:00 | 14618.02 | 32 |  | 14651.46
21:00 | 14418.15 | 32 |  | 14451.59
22:00 | 14317.8 | 41 |  | 14360.65
23:00 | 14103.63 | 32 |  | 14137.07
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7907.36 | 5912 | 13819.36 | DAILY GENERATION CURVE
00:30 | 7762.36 | 5927.5 | 13689.86
01:00 | 7617.36 | 5943 | 13560.36 | 09-10-2025
01:30 | 7381.18 | 5805 | 13186.18
02:00 | 7145 | 5667 | 12812
02:30 | 7036 | 5656 | 12692
03:00 | 6927 | 5645 | 12572
03:30 | 6739.5 | 5624 | 12363.5
04:00 | 6552 | 5603 | 12155
04:30 | 6468 | 5577 | 12045
05:00 | 6384 | 5551 | 11935
05:30 | 6243.02 | 5418 | 11661.02
06:00 | 6102.04 | 5285 | 11387.04
06:30 | 6202.275 | 5346.665 | 11548.94
07:00 | 6302.51 | 5408.33 | 11710.84
07:30 | 6306.57 | 5459.575 | 11766.145
08:00 | 6310.63 | 5510.82 | 11821.45
08:30 | 6326.895 | 5533.87 | 11860.765
09:00 | 6343.16 | 5556.92 | 11900.08
09:30 | 6425.24 | 5628.24 | 12053.48
10:00 | 6507.32 | 5699.56 | 12206.88
10:30 | 6641.32 | 5724.84 | 12366.16
11:00 | 6775.32 | 5750.12 | 12525.44
11:30 | 7086.545 | 5698.57 | 12785.115
12:00 | 7397.77 | 5647.02 | 13044.79
12:30 | 7497.96 | 5698.89 | 13196.85
13:00 | 7598.15 | 5750.76 | 13348.91
13:30 | 7723.11 | 5635.2 | 13358.31
14:00 | 7848.07 | 5519.64 | 13367.71
14:30 | 7797.185 | 5574.645 | 13371.83
15:00 | 7746.3 | 5629.65 | 13375.95
15:30 | 7501.38 | 5614.065 | 13115.445
16:00 | 7256.46 | 5598.48 | 12854.94
16:30 | 7343.265 | 5475.89 | 12819.155
17:00 | 7430.07 | 5353.3 | 12783.37
17:30 | 7871.435 | 5612.44 | 13483.875
18:00 | 8312.8 | 5871.58 | 14184.38
18:30 | 8335.15 | 6092.88 | 14428.03
19:00 | 8357.5 | 6314.18 | 14671.68
19:30 | 8371.36 | 6325.32 | 14696.68
20:00 | 8290.06 | 6327.96 | 14618.02
20:30 | 8210.76 | 6307.325 | 14518.085 |  | Executive Engineer
21:00 | 8131.46 | 6286.69 | 14418.15 |  | Network Operation Division
21:30 | 8106.11 | 6261.865 | 14367.975
22:00 | 8080.76 | 6237.04 | 14317.8
22:30 | 8079.86 | 6130.855 | 14210.715
23:00 | 8078.96 | 6024.67 | 14103.63

## En-Curve
QF-LDC-12
Date | 09-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3146 | 1921 | 601 | 38 | 76 | 1434 | 222 | 3870 | 0 | 686 | 1825.36 | 0 | 0 | 0 | 39 | DAILY ENERGY CURVE
00:30 | 3164 | 1935.5 | 683 | 38 | 72 | 1440 | 221.5 | 3775.5 | 0 | 660 | 1698.86 | 0 | 0 | 1.5 | 19.5 | 09-10-2025
01:00 | 3182 | 1950 | 765 | 38 | 68 | 1446 | 221 | 3681 | 0 | 634 | 1572.36 | 0 | 0 | 3 | 0
01:30 | 3188 | 1945.5 | 833 | 38 | 67 | 1442 | 220 | 3685.5 | 0 | 478 | 1286.18 | 0 | 0 | 3 | 0 | Energy Generated | 317.1979 |  | MKWHr
02:00 | 3194 | 1941 | 901 | 38 | 66 | 1438 | 219 | 3690 | 0 | 322 | 1000 | 0 | 0 | 3 | 0 | Energy not Served | 0.55 |  | MKWHr
02:30 | 3195 | 1956 | 900.5 | 38 | 65 | 1438.5 | 218.5 | 3692.5 | 0 | 297.5 | 889 | 0 | 0 | 1.5 | 0 | Total Energy Requirement | 317.7479 |  | MKWHr
03:00 | 3196 | 1971 | 900 | 38 | 64 | 1439 | 218 | 3695 | 0 | 273 | 778 | 0 | 0 | 0 | 0
03:30 | 3187 | 1960 | 900.5 | 38 | 63 | 1435 | 217.5 | 3696 | 0 | 239 | 627.5 | 0 | 0 | 0 | 0
04:00 | 3178 | 1949 | 901 | 38 | 62 | 1431 | 217 | 3697 | 0 | 205 | 477 | 0 | 0 | 0 | 0
04:30 | 3174 | 1941.5 | 901 | 38 | 63 | 1438 | 217 | 3681 | 0 | 195 | 396.5 | 0 | 0 | 0 | 0
05:00 | 3170 | 1934 | 901 | 38 | 64 | 1445 | 217 | 3665 | 0 | 185 | 316 | 0 | 0 | 0 | 0
05:30 | 3146.5 | 1885.5 | 901.5 | 38 | 60 | 1387.5 | 218 | 3620 | 1.52 | 167.5 | 235 | 0 | 0 | 0 | 0
06:00 | 3123 | 1837 | 902 | 38 | 56 | 1330 | 219 | 3575 | 3.04 | 150 | 154 | 0 | 0 | 0 | 0
06:30 | 3180.5 | 1885.5 | 901.5 | 38 | 58 | 1324 | 219.5 | 3554 | 48.94 | 185 | 154 | 0 | 0 | 0 | 0
07:00 | 3238 | 1934 | 901 | 38 | 60 | 1318 | 220 | 3533 | 94.84 | 220 | 154 | 0 | 0 | 0 | 0
07:30 | 3217 | 1922.5 | 900.5 | 38 | 60 | 1316 | 220 | 3566.5 | 149.145 | 225.5 | 151 | 0 | 0 | 0 | 0
08:00 | 3196 | 1911 | 900 | 38 | 60 | 1314 | 220 | 3600 | 203.45 | 231 | 148 | 0 | 0 | 0 | 0
08:30 | 3175 | 1903 | 900 | 38 | 55 | 1316 | 220.5 | 3603 | 251.765 | 233 | 165.5 | 0 | 0 | 0 | 0
09:00 | 3154 | 1895 | 900 | 38 | 50 | 1318 | 221 | 3606 | 300.08 | 235 | 183 | 0 | 0 | 0 | 0
09:30 | 3145 | 1906.15 | 900.5 | 38 | 52 | 1313 | 221 | 3629.5 | 397.33 | 235 | 216 | 0 | 0 | 0 | 0
10:00 | 3136 | 1917.3 | 901 | 38 | 54 | 1308 | 221 | 3653 | 494.58 | 235 | 249 | 0 | 0 | 0 | 0
10:30 | 3126.5 | 1915.15 | 901 | 38 | 54 | 1313.5 | 221 | 3641.5 | 515.26 | 235 | 405.25 | 0 | 0 | 0 | 0
11:00 | 3117 | 1913 | 901 | 38 | 54 | 1319 | 221 | 3630 | 535.94 | 235 | 561.5 | 0 | 0 | 0 | 0
11:30 | 3156 | 1928 | 900.5 | 38 | 60 | 1296.5 | 221 | 3674 | 478.615 | 254 | 778 | 0 | 0 | 0.5 | 0
12:00 | 3195 | 1943 | 900 | 38 | 66 | 1274 | 221 | 3718 | 421.29 | 273 | 994.5 | 0 | 0 | 1 | 0
12:30 | 3120 | 1865.25 | 900 | 38 | 69 | 1303.5 | 221.5 | 3672.5 | 487.35 | 311.5 | 1199.75 | 0 | 0 | 8.5 | 0
13:00 | 3045 | 1787.5 | 900 | 38 | 72 | 1333 | 222 | 3627 | 553.41 | 350 | 1405 | 0 | 0 | 16 | 0
13:30 | 3073.5 | 1797.5 | 900.5 | 38 | 68 | 1325.75 | 221.5 | 3604 | 514.06 | 349.5 | 1450.5 | 0 | 0 | 15.5 | 0
14:00 | 3102 | 1807.5 | 901 | 38 | 64 | 1318.5 | 221 | 3581 | 474.71 | 349 | 1496 | 0 | 0 | 15 | 0
14:30 | 3107 | 1835 | 900.5 | 38 | 65 | 1318.205 | 221 | 3631 | 386.175 | 352.5 | 1504.95 | 0 | 0 | 12.5 | 0
15:00 | 3112 | 1862.5 | 900 | 38 | 66 | 1317.91 | 221 | 3681 | 297.64 | 356 | 1513.9 | 0 | 0 | 10 | 0
15:30 | 2992 | 1813 | 899.5 | 38 | 63 | 1300.335 | 220 | 3710.5 | 225.71 | 355 | 1490.9 | 0 | 0 | 7.5 | 71.5
16:00 | 2872 | 1763.5 | 899 | 38 | 60 | 1282.76 | 219 | 3740 | 153.78 | 354 | 1467.9 | 0 | 0 | 5 | 143
16:30 | 2860 | 1773.75 | 899.5 | 38 | 61 | 1278.055 | 218.5 | 3696.5 | 91.95 | 395 | 1502.9 | 0 | 0 | 4 | 71.5
17:00 | 2848 | 1784 | 900 | 38 | 62 | 1273.35 | 218 | 3653 | 30.12 | 436 | 1537.9 | 0 | 0 | 3 | 0
17:30 | 2931 | 1896 | 900 | 38 | 67 | 1315.965 | 218.5 | 3696 | 15.06 | 551.5 | 1852.85 | 0 | 0 | 2 | 68
18:00 | 3014 | 2008 | 900 | 38 | 72 | 1358.58 | 219 | 3739 | 0 | 667 | 2167.8 | 0 | 0 | 1 | 136
18:30 | 3007.5 | 2007 | 899.5 | 38 | 72 | 1379.88 | 219 | 3667.5 | 0 | 730 | 2407.15 | 0 | 0 | 0.5 | 115.5
19:00 | 3001 | 2006 | 899 | 38 | 72 | 1401.18 | 219 | 3596 | 0 | 793 | 2646.5 | 0 | 0 | 0 | 95
19:30 | 3021 | 1965.5 | 900 | 38 | 74 | 1396.12 | 220 | 3518 | 0 | 818 | 2746.06 | 0 | 0 | 0 | 62
20:00 | 2991 | 1941 | 900 | 38 | 70 | 1404.76 | 220 | 3515 | 0 | 810 | 2728.26 | 0 | 0 | 0 | 32
20:30 | 2980.5 | 1944.5 | 900.5 | 38 | 71 | 1407.225 | 220 | 3537.5 | 0 | 797.5 | 2621.36 | 0 | 0 | 0 | 32
21:00 | 2970 | 1948 | 901 | 38 | 72 | 1409.69 | 220 | 3560 | 0 | 785 | 2514.46 | 0 | 0 | 0 | 32
21:30 | 2938 | 1949 | 900 | 38 | 70 | 1405.865 | 220 | 3615.5 | 0 | 781.5 | 2450.11 | 0 | 0 | 0 | 36.5
22:00 | 2906 | 1950 | 899 | 38 | 68 | 1402.04 | 220 | 3671 | 0 | 778 | 2385.76 | 0 | 0 | 0 | 41
22:30 | 2875 | 1946.15 | 899.5 | 38 | 72 | 1394.855 | 221 | 3666 | 0 | 779 | 2319.21 | 0 | 0 | 0 | 36.5
23:00 | 2844 | 1942.3 | 900 | 38 | 76 | 1387.67 | 222 | 3661 | 0 | 780 | 2252.66 | 0 | 0 | 0 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 06:00 | 375 | 10:00 | Payra | 411 | 13:00 | 408 | 00:00
Ashuganj | 401 | 1:00 | 378 | 10:00 | Rahanpur | 400 | 18:00 | 391 | 15:00
Bhulta | 397 | 06:00 | 373 | 10:00 | Rampal | 400 | 06:00 | 386 | 19:30
Bibiana | 388 | 06:00 | 383 | 10:00
BIPTC | 406 | 00:00 | 394 | 15:00
Bogura | 390 | 18:00 | 378 | 15:00
Gopalganj | 394 | 06:00 | 388 | 15:00
Kaliakoir | 376 | 13:00 | 365 | 10:00
Madunaghat | 397 | 20:00 | 389 | 06:00
Meghnaghat | 389 | 20:00 | 379 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 222 | 10:00 | Kaliakoir | 235 | 22:00 | 224 | 10:00
AKSML | 238 | 19:00 | 226 | 10:00 | Keranigonj | 226 | 06:00 | 219 | 10:00
Aminbazar | 230 | 19:30 | 222 | 10:00 | Khulna(S) | 230 | 08:00 | 221 | 23:00
Ashuganj | 231 | 00:00 | 220 | 10:00 | Madunaghat | 236 | 19:00 | 228 | 10:00
Ashuganj-400 | 231 | 00:00 | 220 | 10:00 | Madunaghat-400 | 238 | 20:00 | 230 | 06:00
Baghabari | 233 | 00:00 | 225 | 22:00 | Maniknagar | 222 | 20:00 | 216 | 10:00
Barapukuria | 225 | 00:00 | 215 | 13:00 | Meghnaghat | 230 | 04:00 | 224 | 11:00
Barapukuria-230 | 225 | 00:00 | 215 | 13:00 | Meghnaghat-400 | 226 | 19:30 | 221 | 10:00
Barishal | 234 | 19:00 | 228 | 00:00 | Mirsorai | 235 | 18:30 | 223 | 10:00
Bheramara | 235 | 00:00 | 222 | 23:00 | Rajshahi | 233 | 02:00 | 220 | 23:00
Bhulta | 229 | 06:00 | 211 | 10:00 | Rampal | 229 | 06:00 | 221 | 23:00
Bibiana | 231 | 07:00 | 225 | 10:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 00:00 | 221 | 23:00 | Rampura | 228 | 01:00 | 210 | 10:00
Bogura | 233 | 00:00 | 226 | 15:00 | Shikalbaha | 236 | 19:30 | 227 | 09:00
Bogura-400 | 234 | 18:00 | 226 | 15:00 | Shyampur | 226 | 20:00 | 219 | 10:00
Borhanuddin | 236 | 06:00 | 233 | 00:00 | Siddhirganj | 224 | 19:00 | 219 | 10:00
BSRM | 235 | 19:00 | 224 | 03:00 | Sirajgonj | 238 | 03:00 | 233 | 11:00
Cumilla(N) | 227 | 18:30 | 220 | 10:00 | Sreepur | 226 | 06:00 | 219 | 11:00
Faridpur | 230 | 06:00 | 224 | 00:00 | Tongi | 232 | 00:00 | 218 | 09:00
Fenchuganj | 230 | 06:00 | 228 | 01:00
Ghorashal | 230 | 17:00 | 225 | 00:00
Ghorashal-230 | 228 | 00:00 | 213 | 10:00
Gopalganj | 232 | 06:00 | 227 | 00:00
GPH | 236 | 19:00 | 226 | 10:00
Haripur | 223 | 06:00 | 218 | 10:00
Hasnabad | 228 | 19:30 | 220 | 12:00
Hathazari | 235 | 19:00 | 223 | 10:00
Ishurdi | 234 | 00:00 | 223 | 23:00
Jhenaidah | 230 | 06:00 | 219 | 23:00
Kachua | 218 | 19:00 | 211 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 19:30 | 124 | 09:00 | Lalmonirhat | 127 | 00:00 | 124 | 09:00
Agargaon | 135 | 05:00 | 130 | 10:00 | Madanganj | 130 | 20:00 | 125 | 10:00
Agrabad | 134 | 19:00 | 128 | 10:00 | Madaripur | 136 | 13:00 | 132 | 00:00
AKS | 132 | 04:00 | 128 | 10:00 | Madartek | 134 | 00:00 | 121 | 10:00
Aminbazar | 137 | 19:30 | 131 | 09:00 | Madunaghat | 137 | 20:00 | 132 | 10:00
Amnura | 137 | 01:00 | 128 | 12:00 | Magura | 136 | 09:00 | 127 | 23:00
Ashuganj | 142 | 06:00 | 136 | 11:00 | Mahasthangarh | 132 | 00:00 | 126 | 13:00
Bagerhat | 132 | 08:00 | 120 | 00:00 | Maijdee | 133 | 19:00 | 127 | 00:00
Bajitpur | 130 | 06:00 | 125 | 12:00 | Manikganj | 129 | 06:00 | 119 | 10:00
Bakulia | 139 | 19:00 | 130 | 10:00 | Maniknagar | 134 | 05:00 | 129 | 12:00
Banani | 135 | 19:30 | 120 | 10:00 | Matarbari | 121 | 17:00 | 115 | 02:00
Bangabhaban | 134 | 05:00 | 129 | 10:00 | Matuail | 130 | 06:00 | 126 | 10:00
Barapukuria | 138 | 00:00 | 126 | 13:00 | Metrorail_Motijheel | 134 | 05:00 | 129 | 12:00
Barguna | 136 | 16:00 | 134 | 00:00 | Metrorail_Uttara | 136 | 19:30 | 130 | 10:00
Barishal | 137 | 19:00 | 130 | 00:00 | Millgate | 133 | 00:00 | 123 | 10:00
Barishal-230 | 136 | 19:00 | 130 | 00:00 | Mirpur | 135 | 18:30 | 130 | 10:00
Baroaulia | 135 | 19:30 | 130 | 09:00 | Mirzapur | 130 | 05:00 | 125 | 21:00
Baroirhat | 132 | 19:00 | 127 | 02:00 | Mithapukur | 132 | 00:00 | 122 | 13:00
Bashundhara | 135 | 18:30 | 121 | 10:00 | MI_Cement | 131 | 19:00 | 126 | 10:00
BashundharaCement | 130 | 19:30 | 125 | 10:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 05:00 | 124 | 18:00 | Mogbazar | 137 | 19:30 | 122 | 10:00
Benapole | 134 | 17:00 | 124 | 00:00 | Mongla | 132 | 07:00 | 121 | 00:00
Bhaluka | 129 | 16:00 | 123 | 11:00 | Motijheel | 134 | 05:00 | 129 | 10:00
Bhandaria | 130 | 09:00 | 115 | 00:00 | Muktagacha | 130 | 08:00 | 114 | 21:00
Bhangura | 133 | 01:00 | 127 | 23:00 | Munshiganj | 130 | 18:00 | 125 | 10:00
Bheramara | 135 | 00:00 | 128 | 23:00 | Muradnagar | 128 | 06:00 | 125 | 02:00
Bheramara(GK) | 135 | 00:00 | 127 | 23:00 | Mymensingh | 130 | 08:00 | 110 | 21:00
Bhulta | 127 | 18:00 | 124 | 09:00 | Naogaon | 129 | 00:00 | 123 | 13:00
Bog-Sherpur | 132 | 00:00 | 127 | 12:00 | Narail | 136 | 06:00 | 127 | 23:00
Bogura | 135 | 00:00 | 132 | 21:00 | Narinda | 134 | 05:00 | 129 | 12:00
Bogura-230 | 133 | 00:00 | 128 | 14:00 | Narshingdi | 132 | 05:00 | 121 | 10:00
Brahmanbaria | 135 | 06:00 | 129 | 10:00 | Natore | 132 | 00:00 | 126 | 23:00
Cantonment | 135 | 06:00 | 130 | 10:00 | Nawabganj | 134 | 06:00 | 129 | 10:00
Chandina | 133 | 19:00 | 129 | 10:00 | Netrakona | 125 | 16:00 | 114 | 20:00
Chandpur | 140 | 18:30 | 135 | 6:00 | New | 134 | 00:00 | 123 | 10:00
Chandraghona | 137 | 19:00 | 132 | 10:00 | Niamatpur | 136 | 17:00 | 132 | 13:00
Chapai | 135 | 08:00 | 132 | 13:00 | Noapara | 135 | 08:00 | 127 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 20:00 | 125 | 10:00 | Pabna | 134 | 06:00 | 127 | 23:00
Chauddagram | 132 | 18:30 | 128 | 00:00 | Palashbari | 130 | 00:00 | 122 | 13:00
Chhatak | 127 | 07:00 | 121 | 21:00 | Panchagarh | 137 | 00:00 | 119 | 13:00
Chowmuhani | 133 | 19:00 | 126 | 11:00 | Patiya | 134 | 19:30 | 129 | 10:00
Chuadanga | 133 | 07:00 | 125 | 23:00 | Patuakhali | 136 | 17:00 | 133 | 00:00
Coxsbazar | 120 | 16:00 | 115 | 11:00 | Payra | 136 | 00:00 | 135 | 12:00
Cumilla(N) | 132 | 04:00 | 129 | 10:00 | PHP | 132 | 19:00 | 126 | 04:00
Cumilla(S) | 133 | 18:30 | 127 | 18:00 | Postogola | 134 | 08:00 | 128 | 10:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 20:00 | 121 | 10:00
Daudkandi | 126 | 07:00 | 120 | 12:00 | Purbasadipur | 134 | 00:00 | 118 | 13:00
DhakaUniversity | 137 | 20:00 | 122 | 10:00 | Rahanpur | 137 | 05:00 | 134 | 11:00
Dhamrai | 133 | 14:00 | 126 | 10:00 | Rahanpur-400 | 137 | 06:00 | 134 | 14:00
Dhanmondi | 136 | 19:30 | 122 | 10:00 | Rahim | 130 | 06:00 | 126 | 12:00
Dohazari | 130 | 16:00 | 126 | 05:00 | Rajbari | 135 | 06:00 | 130 | 00:00
Faridpur | 137 | 06:00 | 132 | 00:00 | Rajendrapur | 137 | 00:00 | 123 | 10:00
Fatullah | 137 | 06:00 | 126 | 13:00 | Rajshahi | 132 | 00:00 | 126 | 23:00
Fenchuganj | 136 | 06:00 | 130 | 12:00 | Rajshahi-230 | 132 | 00:00 | 126 | 23:00
Feni | 132 | 19:00 | 126 | 10:00 | Ramganj | 134 | 19:00 | 125 | 12:00
Ghatail | 127 | 05:00 | 116 | 21:00 | Rampur | 134 | 01:00 | 128 | 10:00
Ghorashal | 138 | 00:00 | 130 | 12:00 | Rampura | 136 | 19:30 | 122 | 10:00
Goalpara | 137 | 08:00 | 128 | 21:00 | Rangamati | 135 | 19:00 | 131 | 09:00
Gollamari | 137 | 08:00 | 130 | 00:00 | Rangpur | 133 | 00:00 | 122 | 13:00
Gopalganj | 135 | 08:00 | 129 | 00:00 | Ruppur | 137 | 05:00 | 130 | 23:00
Gopalganj-400 | 136 | 06:00 | 133 | 00:00 | Saidpur | 134 | 00:00 | 120 | 13:00
Gulshan | 136 | 19:30 | 122 | 10:00 | Satkhira | 134 | 08:00 | 125 | 00:00
Halishahar | 135 | 19:00 | 129 | 10:00 | Satmasjid | 134 | 05:00 | 129 | 10:00
Haripur | 131 | 06:00 | 127 | 10:00 | Savar | 136 | 20:00 | 128 | 10:00
HaripurSBU | 131 | 06:00 | 117 | 12:00 | SevenRings | 138 | 00:00 | 128 | 10:00
Hasnabad | 133 | 18:30 | 128 | 10:00 | ShahCement | 131 | 20:00 | 125 | 10:00
Hathazari | 137 | 19:30 | 132 | 07:00 | Shahjadpur | 136 | 03:00 | 132 | 15:00
Ishurdi | 136 | 00:00 | 129 | 23:00 | Shahjibazar | 136 | 06:00 | 129 | 23:00
Jaldhaka | 131 | 00:00 | 118 | 13:00 | Shahmirpur | 135 | 19:00 | 130 | 09:00
Jamalpur | 130 | 07:00 | 114 | 21:00 | Shariatpur | 135 | 08:00 | 130 | 00:00
Jashore | 135 | 04:00 | 127 | 23:00 | Sherpur | 127 | 07:00 | 108 | 21:00
Jhenaidah | 137 | 05:00 | 119 | 23:00 | Shikalbaha | 125 | 18:30 | 119 | 10:00
Jhenaidah-230 | 137 | 06:00 | 130 | 23:00 | Shikalbaha-230 | 137 | 19:30 | 131 | 10:00
Joydebpur | 140 | 1:00 | 127 | 10:00 | Shitalakhya | 131 | 19:00 | 126 | 10:00
Joypurhat | 128 | 00:00 | 122 | 14:00 | Sholosohor | 136 | 19:00 | 132 | 09:00
Juldah | 135 | 18:30 | 130 | 09:00 | Shyampur | 136 | 08:00 | 134 | 12:00
Kabirpur | 135 | 13:00 | 122 | 10:00 | Shyampur-230 | 137 | 20:00 | 132 | 10:00
Kachua | 140 | 19:00 | 135 | 06:00 | Siddhirganj | 131 | 20:00 | 127 | 10:00
Kaliakoir | 135 | 11:00 | 131 | 10:00 | Sirajganj | 131 | 06:00 | 126 | 23:00
Kallyanpur | 136 | 04:00 | 130 | 10:00 | Sonargaon | 128 | 04:00 | 125 | 09:00
Kalurghat | 137 | 19:00 | 132 | 09:00 | Sreemongol | 134 | 08:00 | 129 | 18:00
Kamrangirchar | 134 | 04:00 | 128 | 10:00 | Sreepur | 131 | 06:00 | 126 | 11:00
Kaptai | 138 | 19:00 | 135 | 9:00 | Srinagar | 134 | 06:00 | 129 | 12:00
Kasba | 128 | 07:00 | 125 | 00:00 | SSM | 140 | 21:00 | 133 | 17:00
Kazla | 134 | 05:00 | 129 | 12:00 | Sunamganj | 125 | 04:00 | 119 | 22:00
Keranigonj | 134 | 06:00 | 129 | 10:00 | Sylhet | 130 | 06:00 | 126 | 18:00
Khagrachori | 135 | 19:30 | 130 | 10:00 | Sylhet-132 | 129 | 09:00 | 127 | 00:00
Khulna | 136 | 08:00 | 128 | 00:00 | Tangail | 128 | 05:00 | 118 | 21:00
Khulna(S) | 138 | 08:00 | 130 | 00:00 | Taraganj | 132 | 00:00 | 120 | 13:00
Khulshi | 133 | 19:00 | 128 | 09:00 | Thakurgaon | 137 | 00:00 | 117 | 13:00
Kishoreganj | 129 | 16:00 | 123 | 22:00 | TK | 136 | 19:00 | 133 | 04:00
Kodda | 136 | 00:00 | 123 | 10:00 | Tongi | 136 | 00:00 | 128 | 09:00
KSRM | 136 | 21:00 | 130 | 08:00 | Ullahpara | 132 | 00:00 | 128 | 12:00
Kulaura | 135 | 06:00 | 132 | 00:00 | Ullon | 136 | 19:30 | 124 | 09:00
Kurigram | 130 | 00:00 | 120 | 13:00 | Uttara | 134 | 06:00 | 122 | 10:00
Kushtia | 132 | 06:00 | 123 | 23:00 | UttaraNew | 136 | 19:30 | 131 | 00:00
Laksam | 138 | 17:00 | 133 | 10:00 | Zigatola | 134 | 05:00 | 130 | 10:00
Lakshmipur | 132 | 19:30 | 127 | 00:00
Lalbag | 134 | 06:00 | 129 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division