## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-10-2025 | [28 empty] | Date: | 10-10-2025 | [28 empty] | Date: | 10-10-2025 | [28 empty] | Date: | 10-10-2025 | [28 empty] | Date: | 10-10-2025 | [14 empty] | Date: | 10-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17.5 | 17 | 149 | 110 | 277 | 55 | 0 | 108 | 0 | 350 | 142 | 520 | 0 | 35 | 335 | 0 | 0 | 0 | 142 | 20.5 | 21 | 0 | 0 | 91 | 120 | 63 | 0 | 0 | 48 | 54 | 54.36 | 0 | 0 | 0 | 222 | 107 | 27 | 285 | 62 | 0 | 26 | 8 | 99 | 174 | 0 | 0 | 0 | 1160 | 0 | 51 | 142 | 0 | 260 | 0 | 330 | 36 | 123 | 5 | 17 | 105 | 165 | 0 | 16 | 15 | 78 | 8 | 0 | 35 | 315 | 0 | 336 | 30 | 67 | 158 | 0 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 8085.36 | 900 | 0 | 0 | 30 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1364.33 | 0 | 39 | 0 | 50 | 113 | 0 | 95 | 37 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 0 | 145 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 115 | 220 | 0 | 308 | 1102 | 17 | 6015.33 | 14100.69 | 107.32
01:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 149 | 93 | 195 | 55 | 0 | 54 | 0 | 350 | 142 | 500 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 20.8 | 21 | 0 | 0 | 86 | 120 | 52 | 0 | 1 | 48 | 54 | 54.36 | 0 | 0 | 0 | 222 | 104 | 27 | 285 | 62 | 0 | 26 | 0 | 95 | 174 | 0 | 0 | 0 | 1140 | 0 | 51 | 137 | 0 | 275 | 0 | 330 | 2 | 125 | 5 | 18 | 105 | 160 | 0 | 11 | 0 | 72 | 0 | 0 | 35 | 305 | 0 | 332 | 30 | 68 | 142 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 57 | 48 | 0 | 0 | 0 | 0 | 7694.16 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1364.23 | 0 | 39 | 0 | 50 | 113 | 0 | 95 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 350 | 0 | 0 | 147 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 307 | 1110 | 17 | 5922.23 | 13616.39 | 107.32
02:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 149 | 78 | 195 | 15 | 0 | 54 | 0 | 350 | 140 | 490 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 21.2 | 21 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 48 | 54 | 54.36 | 0 | 0 | 0 | 220 | 99 | 27 | 285 | 30 | 0 | 26 | 0 | 92 | 174 | 0 | 0 | 0 | 1140 | 0 | 51 | 135 | 0 | 290 | 0 | 330 | 2 | 125 | 5 | 17 | 105 | 156 | 0 | 11 | 0 | 74 | 0 | 0 | 35 | 305 | 0 | 317 | 30 | 68 | 141 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 66 | 48 | 0 | 0 | 0 | 0 | 7423.56 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1361.8 | 0 | 39 | 0 | 0 | 50 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 350 | 0 | 0 | 144 | 37 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 115 | 220 | 0 | 307 | 1100 | 17 | 5737.8 | 13161.36 | 107.32
03:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 149 | 47 | 95 | 15 | 0 | 54 | 0 | 350 | 147 | 510 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 21.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 0 | 0 | 0 | 0 | 219 | 106 | 27 | 285 | 0 | 0 | 26 | 0 | 94 | 174 | 0 | 0 | 0 | 1156 | 0 | 51 | 133 | 0 | 300 | 0 | 330 | 2 | 127 | 5 | 17 | 105 | 158 | 0 | 11 | 0 | 62 | 0 | 0 | 36 | 300 | 0 | 328 | 30 | 68 | 146 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 7062.2 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 1365.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 350 | 0 | 0 | 142 | 49 | 115 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 307 | 1105 | 17 | 5566.9 | 12629.1 | 107.32
04:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 149 | 16 | 0 | 0 | 0 | 54 | 0 | 350 | 141 | 510 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 21.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 218 | 106 | 27 | 285 | 0 | 0 | 0 | 0 | 96 | 174 | 0 | 0 | 0 | 1159 | 0 | 51 | 133 | 0 | 300 | 0 | 330 | 2 | 127 | 5 | 17 | 105 | 162 | 0 | 11 | 0 | 66 | 0 | 0 | 36 | 315 | 0 | 328 | 30 | 68 | 146 | 8 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 6870.2 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1365.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 350 | 0 | 0 | 143 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 308 | 1110 | 17 | 5460.17 | 12330.37 | 107.32
05:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 105 | 16 | 0 | 0 | 0 | 36 | 0 | 350 | 140 | 505 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 21.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 218 | 68 | 27 | 285 | 0 | 0 | 0 | 0 | 94 | 174 | 0 | 0 | 0 | 1155 | 0 | 51 | 20 | 0 | 312 | 0 | 330 | 2 | 122 | 5 | 17 | 106 | 100 | 0 | 11 | 0 | 62 | 0 | 0 | 36 | 305 | 0 | 325 | 30 | 68 | 142 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 5 | 6564.2 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1361.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 350 | 0 | 0 | 144 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 115 | 220 | 0 | 307 | 1098 | 0 | 5401.36 | 11965.56 | 107.32
06:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 138 | 500 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 178 | 34 | 27 | 285 | 0 | 0 | 0 | 0 | 51 | 180 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 0 | 315 | 0 | 330 | 2 | 123 | 5 | 15 | 106 | 0 | 0 | 10 | 0 | 62 | 0 | 1 | 0 | 305 | 0 | 310 | 30 | 68 | 148 | 6 | 0 | 81 | 30 | 0 | 16 | 165 | 0 | 67 | 48 | 0 | 0 | 0 | 0 | 6082.02 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1313.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 330 | 0 | 0 | 145 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 115 | 220 | 0 | 306 | 1100 | 0 | 5309.31 | 11391.33 | 107.32
07:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 146 | 515 | 0 | 0 | 334 | 0 | 0 | 3 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.22 | 179 | 0 | 23 | 285 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 1053 | 3 | 51 | 0 | 0 | 295 | 0 | 330 | 2 | 131 | 5 | 0 | 105 | 0 | 0 | 10 | 0 | 62 | 0 | 13 | 0 | 310 | 0 | 333 | 30 | 68 | 163 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 0 | 0 | 1.53 | 0 | 5846.75 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.04 | 367 | 0 | 1217.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.31 | 11 | 0 | 0 | 4.25 | 0 | 0 | 188 | 0 | 0 | 0 | 371 | 0 | 0.36 | 144 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 1.2 | 23 | 0.09 | 0 | 200 | 115 | 220 | 0 | 307 | 1098 | 0 | 5270.67 | 11117.42 | 107.32
08:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 139 | 515 | 0 | 0 | 334 | 0 | 0 | 15 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 180 | 0 | 23 | 285 | 0 | 0 | 21 | 0 | 0 | 180 | 0 | 0 | 0 | 1010 | 7 | 51 | 0 | 0 | 290 | 0 | 330 | 2 | 121 | 5 | 0 | 105 | 0 | 0 | 10 | 0 | 58 | 0 | 31 | 0 | 310 | 0 | 310 | 30 | 68 | 163 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 0 | 0 | 7.68 | 0 | 5803.38 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29.46 | 367 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.45 | 29 | 0 | 0 | 10.4 | 0 | 0 | 191 | 0 | 0 | 0 | 335 | 0 | 1.1 | 140 | 49 | 0 | 3 | 0 | 0 | 0 | 0 | 1.8 | 70 | 0.33 | 0 | 194 | 115 | 220 | 0 | 307 | 1108 | 0 | 5336.54 | 11139.92 | 107.32
09:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 138 | 495 | 0 | 0 | 334 | 0 | 0 | 24 | 35 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.67 | 180 | 0 | 24 | 285 | 0 | 0 | 26 | 0 | 0 | 200 | 0 | 0 | 0 | 962 | 13 | 51 | 0 | 0 | 295 | 0 | 330 | 2 | 118 | 5 | 0 | 104 | 0 | 0 | 10 | 0 | 54 | 0 | 49 | 0 | 300 | 0 | 303 | 29 | 68 | 163 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 0 | 2 | 13.27 | 0 | 5693.94 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80.84 | 367 | 0 | 1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.02 | 38 | 0 | 0 | 42.35 | 0 | 0 | 191 | 0 | 0 | 0 | 328 | 0 | 2.47 | 140 | 49 | 0 | 14 | 0 | 0 | 0 | 0 | 4.5 | 113 | 0.52 | 0 | 164 | 115 | 180 | 0 | 305 | 960 | 0 | 5189.7 | 10883.64 | 107.32
10:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 146 | 510 | 0 | 0 | 290 | 0 | 0 | 21 | 17 | 20 | 12 | 0 | 0 | 0 | 0 | 13 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.04 | 181 | 0 | 17 | 285 | 0 | 0 | 26 | 0 | 0 | 201 | 0 | 0 | 0 | 900 | 18 | 51 | 0 | 0 | 305 | 0 | 330 | 2 | 130 | 5 | 0 | 103 | 0 | 0 | 5 | 0 | 56 | 0 | 65 | 0 | 300 | 0 | 336 | 30 | 68 | 163 | 10 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 0 | 2 | 15.19 | 1 | 5659.23 | 927 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81.41 | 364 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.06 | 90 | 0 | 0 | 32.95 | 0 | 0 | 194 | 0 | 0 | 0 | 363 | 0 | 2.11 | 142 | 50 | 0 | 28 | 0 | 0 | 0 | 0 | 5.3 | 157 | 0.36 | 0 | 183 | 115 | 180 | 0 | 305 | 950 | 0 | 5277.19 | 10936.42 | 107.32
11:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 12 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 141 | 530 | 0 | 0 | 330 | 0 | 0 | 32 | 17 | 20 | 12 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 1.88 | 80 | 0 | 18 | 285 | 0 | 0 | 26 | 0 | 0 | 202 | 0 | 0 | 0 | 975 | 10 | 43 | 0 | 0 | 295 | 0 | 330 | 2 | 122 | 5 | 0 | 101 | 0 | 0 | 5 | 0 | 64 | 0 | 67 | 0 | 310 | 0 | 340 | 30 | 68 | 163 | 10 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 66 | 48 | 0 | 1 | 21.39 | 6 | 5760.27 | 926 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90.73 | 364 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.63 | 93 | 0 | 0 | 60.7 | 0 | 0 | 199 | 0 | 0 | 0 | 404 | 0 | 5.49 | 143 | 50 | 0 | 10 | 0 | 0 | 0 | 0 | 6.2 | 184 | 0.68 | 0 | 214 | 115 | 180 | 0 | 305 | 965 | 0 | 5408.43 | 11168.7 | 107.31
12:00 | 0 | 55 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 17 | 26 | 45 | 0 | 0 | 0 | 17 | 0 | 350 | 145 | 545 | 0 | 0 | 330 | 0 | 0 | 5 | 52 | 19 | 12 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 1.02 | 98 | 0 | 17 | 285 | 0 | 0 | 26 | 0 | 2 | 202 | 0 | 0 | 0 | 1152 | 13 | 51 | 0 | 0 | 295 | 0 | 330 | 2 | 127 | 5 | 1 | 101 | 0 | 0 | 10 | 0 | 70 | 0 | 52 | 0 | 305 | 0 | 340 | 30 | 68 | 163 | 10 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 66 | 48 | 0 | 2 | 46.43 | 6 | 6088.45 | 937 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94.38 | 364 | 0 | 1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.98 | 77 | 0 | 0 | 57.62 | 0 | 0 | 202 | 0 | 0 | 0 | 414 | 0 | 5.59 | 141 | 49 | 0 | 15 | 0 | 0 | 0 | 0 | 5.4 | 189 | 0.8 | 0 | 269 | 115 | 180 | 0 | 307 | 1054 | 0 | 5743.77 | 11832.22 | 107.32
13:00 | 0 | 72 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 53 | 60 | 40 | 0 | 17 | 51 | 0 | 420 | 131 | 540 | 0 | 0 | 332 | 0 | 0 | 10 | 80 | 19 | 12 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0.95 | 156 | 0 | 22 | 285 | 0 | 0 | 26 | 0 | 29 | 202 | 0 | 0 | 0 | 1123 | 18 | 51 | 0 | 0 | 290 | 0 | 325 | 2 | 123 | 5 | 16 | 101 | 1 | 0 | 8 | 0 | 74 | 0 | 74 | 0 | 310 | 0 | 340 | 30 | 68 | 163 | 10 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 66 | 48 | 0 | 2 | 49.22 | 0 | 6467.17 | 926 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 89.55 | 364 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.97 | 103 | 0 | 0 | 58.04 | 0 | 0 | 204 | 0 | 0 | 0 | 349 | 0 | 3.5 | 143 | 50 | 50 | 33 | 0 | 0 | 0 | 0 | 5.4 | 175 | 0.18 | 0 | 272 | 115 | 220 | 0 | 307 | 1080 | 0 | 5929.64 | 12396.81 | 107.32
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 17 | 72 | 30 | 60 | 0 | 35 | 52 | 0 | 320 | 145 | 455 | 0 | 0 | 335 | 0 | 0 | 6 | 52 | 0 | 10 | 0 | 0 | 0 | 0 | 29 | 0 | 1 | 0 | 46 | 0 | 0 | 0 | 1.25 | 172 | 0 | 22 | 285 | 0 | 0 | 26 | 7 | 51 | 202 | 0 | 0 | 0 | 990 | 15 | 51 | 0 | 0 | 325 | 0 | 300 | 2 | 60 | 5 | 29 | 100 | 17 | 0 | 8 | 0 | 62 | 0 | 18 | 0 | 300 | 0 | 332 | 30 | 67 | 163 | 10 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 66 | 48 | 0 | 2 | 45.37 | 0 | 6039.62 | 927 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32.35 | 364 | 0 | 1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.52 | 93 | 0 | 0 | 28.28 | 0 | 0 | 160 | 0 | 0 | 0 | 352 | 0 | 4.76 | 141 | 0 | 35 | 27 | 0 | 0 | 0 | 0 | 5.9 | 128 | 0.51 | 0 | 167 | 100 | 180 | 0 | 307 | 1087 | 0 | 5399.32 | 11438.94 | 107.32
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 17 | 45 | 15 | 60 | 0 | 35 | 47 | 0 | 320 | 147 | 440 | 0 | 0 | 280 | 0 | 0 | 1 | 52 | 17 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 1.18 | 172 | 0 | 22 | 285 | 0 | 0 | 26 | 8 | 17 | 198 | 0 | 0 | 0 | 990 | 3 | 51 | 0 | 0 | 393 | 0 | 260 | 2 | 29 | 22 | 30 | 105 | 17 | 0 | 8 | 0 | 62 | 0 | 46 | 0 | 310 | 0 | 321 | 30 | 67 | 163 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 66 | 48 | 0 | 1 | 24.24 | 0 | 5875.42 | 926 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 367 | 0 | 1220.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.02 | 9 | 0 | 0 | 27.71 | 0 | 0 | 160 | 0 | 0 | 0 | 363 | 0 | 1.98 | 142 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 3.8 | 97 | 0.11 | 0 | 171 | 100 | 180 | 0 | 306 | 1082 | 0 | 5246.36 | 11121.78 | 107.32
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 34 | 15 | 15 | 0 | 17 | 17 | 0 | 320 | 143 | 440 | 0 | 0 | 280 | 0 | 0 | 1 | 52 | 17 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 5 | 0 | 46 | 0 | 0 | 0 | 1.21 | 218 | 0 | 15 | 285 | 0 | 0 | 26 | 8 | 17 | 199 | 0 | 0 | 0 | 907 | 6 | 51 | 0 | 0 | 410 | 0 | 300 | 2 | 45 | 36 | 16 | 103 | 15 | 0 | 8 | 0 | 60 | 0 | 22 | 0 | 300 | 0 | 310 | 30 | 67 | 153 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 66 | 47 | 30 | 1 | 9.63 | 4 | 5767.84 | 926 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.63 | 368 | 0 | 1020.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 0 | 0 | 0 | 4 | 0 | 0 | 160 | 0 | 0 | 0 | 343 | 0 | 0.5 | 142 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 2.4 | 49 | 0.06 | 0 | 169 | 115 | 220 | 0 | 306 | 900 | 0 | 4777.24 | 10545.08 | 107.32
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 23 | 34 | 15 | 15 | 0 | 17 | 15 | 0 | 320 | 139 | 390 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 17 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | 46 | 0 | 0 | 0 | 0.11 | 218 | 0 | 15 | 280 | 0 | 0 | 26 | 8 | 14 | 200 | 0 | 0 | 0 | 980 | 2 | 51 | 0 | 0 | 415 | 0 | 300 | 2 | 52 | 34 | 16 | 104 | 15 | 4 | 8 | 0 | 56 | 0 | 1 | 0 | 300 | 0 | 291 | 30 | 67 | 151 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 1 | 66 | 47 | 30 | 0 | 1.98 | 0 | 5699.09 | 927 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 367 | 0 | 1086.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 325 | 0 | 0 | 142 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.6 | 19 | 0 | 0 | 162 | 115 | 220 | 0 | 307 | 900 | 0 | 4773.42 | 10472.51 | 107.31
18:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 35 | 50 | 90 | 145 | 6 | 27 | 52 | 0 | 350 | 149 | 325 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 1 | 50 | 46 | 0 | 0 | 0 | 0 | 219 | 28 | 25 | 285 | 35 | 0 | 26 | 8 | 48 | 201 | 0 | 0 | 0 | 1090 | 0 | 51 | 30 | 0 | 360 | 0 | 325 | 2 | 51 | 34 | 32 | 104 | 22 | 8 | 17 | 0 | 66 | 0 | 0 | 23 | 300 | 0 | 323 | 30 | 67 | 142 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 66 | 47 | 30 | 0 | 0 | 0 | 6541 | 926 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1320.54 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 15 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 378 | 0 | 0 | 142 | 0 | 109 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 115 | 220 | 0 | 307 | 960 | 17 | 5490.54 | 12031.54 | 107.31
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 35 | 102 | 90 | 45 | 15 | 55 | 51 | 0 | 350 | 143 | 490 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 17 | 0 | 25 | 0 | 1 | 50 | 46 | 0 | 0 | 0 | 0 | 220 | 32 | 25 | 285 | 33 | 0 | 26 | 8 | 88 | 199 | 0 | 0 | 0 | 1156 | 0 | 51 | 50 | 0 | 415 | 0 | 330 | 3 | 117 | 5 | 71 | 105 | 49 | 9 | 17 | 0 | 64 | 0 | 0 | 23 | 310 | 0 | 320 | 30 | 67 | 155 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 66 | 47 | 30 | 0 | 0 | 0 | 7050 | 925 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 37 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 344 | 0 | 0 | 140 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 306 | 1096 | 17 | 5730 | 12780 | 107.31
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 35 | 101 | 90 | 45 | 15 | 35 | 52 | 0 | 350 | 145 | 500 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 20 | 0 | 0 | 15 | 0 | 25 | 0 | 2 | 50 | 46 | 0 | 0 | 0 | 0 | 220 | 31 | 28 | 285 | 32 | 0 | 26 | 8 | 87 | 199 | 0 | 0 | 0 | 1166 | 0 | 51 | 50 | 0 | 415 | 0 | 330 | 3 | 126 | 5 | 72 | 105 | 50 | 9 | 17 | 0 | 66 | 0 | 0 | 23 | 315 | 0 | 336 | 30 | 67 | 152 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 66 | 47 | 30 | 0 | 0 | 0 | 7114 | 927 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1283.72 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 37 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 356 | 0 | 0 | 139 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 306 | 1100 | 17 | 5711.72 | 12825.72
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 35 | 101 | 90 | 45 | 15 | 35 | 52 | 0 | 350 | 151 | 500 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 13 | 0 | 24 | 0 | 0 | 50 | 46 | 0 | 0 | 0 | 0 | 221 | 33 | 20 | 285 | 35 | 0 | 26 | 8 | 89 | 199 | 0 | 0 | 0 | 1176 | 0 | 51 | 50 | 0 | 415 | 0 | 330 | 3 | 205 | 5 | 72 | 105 | 48 | 9 | 17 | 0 | 64 | 0 | 0 | 23 | 310 | 0 | 353 | 30 | 67 | 155 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 67 | 47 | 34 | 0 | 0 | 0 | 7215 | 920 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1272.24 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 383 | 0 | 0 | 140 | 0 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 115 | 220 | 0 | 307 | 1098 | 17 | 5719.24 | 12934.24 | 107.31
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 17 | 100 | 90 | 45 | 15 | 0 | 50 | 0 | 350 | 142 | 495 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 16 | 0 | 24 | 0 | 1 | 50 | 46 | 0 | 0 | 0 | 0 | 222 | 43 | 20 | 285 | 30 | 0 | 26 | 8 | 87 | 199 | 0 | 0 | 0 | 1130 | 0 | 51 | 50 | 0 | 405 | 0 | 330 | 5 | 186 | 5 | 72 | 105 | 56 | 8 | 17 | 0 | 68 | 0 | 0 | 23 | 315 | 0 | 308 | 30 | 67 | 154 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 67 | 48 | 35 | 0 | 0 | 0 | 7055 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1313.15 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 401 | 0 | 0 | 140 | 20 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 115 | 220 | 0 | 306 | 1160 | 17 | 5830.15 | 12885.15 | 107.31
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 18 | 17 | 101 | 90 | 45 | 15 | 0 | 48 | 0 | 350 | 145 | 480 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 13 | 0 | 5 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 222 | 67 | 23 | 285 | 30 | 0 | 15 | 8 | 88 | 187 | 0 | 0 | 0 | 1161 | 0 | 51 | 50 | 0 | 340 | 0 | 330 | 5 | 192 | 5 | 54 | 105 | 93 | 0 | 17 | 0 | 72 | 0 | 0 | 20 | 300 | 0 | 326 | 30 | 67 | 141 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 35 | 0 | 0 | 0 | 6911 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1319.09 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 38 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 347 | 0 | 0 | 144 | 45 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 307 | 1222 | 17 | 5874.09 | 12785.09 | 107.31
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 18 | 17 | 100 | 60 | 45 | 15 | 0 | 48 | 0 | 350 | 145 | 490 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 17 | 22 | 0 | 0 | 13 | 0 | 24 | 0 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 222 | 66 | 28 | 285 | 30 | 0 | 24 | 8 | 89 | 163 | 0 | 0 | 0 | 1155 | 0 | 51 | 50 | 0 | 335 | 0 | 330 | 5 | 192 | 5 | 17 | 105 | 95 | 0 | 17 | 0 | 74 | 0 | 0 | 23 | 310 | 0 | 328 | 30 | 68 | 143 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 35 | 0 | 0 | 0 | 6895 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1320.75 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 37 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 345 | 0 | 0 | 142 | 45 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 307 | 1222 | 17 | 5875.75 | 12770.75 | 107.31
Total KWH | 0 | 2012160 | 272160 | 0 | 0 | 0 | 0 | 0 | 8488800 | 0 | 0 | 259560 | 311400 | 1819152 | 1063680 | 1265335 | 219856 | 267354 | 797760 | 0 | 8455000 | 3455185 | 11789379 | 0 | 210232 | 7766476 | 0 | 0 | 100786 | 2078400 | 433800 | 402840 | 0 | 0 | 313636 | 163091 | 421440 | 0 | 36960 | 384629 | 754704 | 137837 | 0 | 0 | 19078 | 4631782 | 909126 | 553440 | 6829090.91 | 326182 | 0 | 529440 | 101611.8 | 1378327 | 4343538 | 0 | 0 | 0 | 25887271 | 103680 | 1224212 | 978545 | 0 | 8064000 | 0 | 7786000 | 71040 | 2987000 | 220968 | 560640 | 2492910 | 1342080 | 42840 | 236310 | 31920 | 1554240 | 7392 | 456236 | 336336 | 7469000 | 0 | 8165000 | 717000 | 1593720 | 3660136 | 192216 | 0 | 1933440 | 715008 | 0 | 397000 | 1652820 | 73800 | 1584000 | 1164000 | 271680 | 11050 | 224470 | 30000 | 157541187.71 | 22125818 | 0 | 0 | 10560 | 22272 | 912000 | 0 | 0 | 0 | 0 | 0 | 494640 | 8843636 | 0 | 29957838 | 0 | 84823 | 0 | 96672 | 242400 | 0 | 728992 | 299090 | 0 | 226572 | 572425 | 94798 | 0 | 346496 | 0 | 0 | 4569809 | 0 | 0 | 0 | 8706546 | 0 | 28740 | 3490000 | 772800 | 1266130 | 186455 | 1027977 | 0 | 0 | 0 | 40099.92 | 1167120 | 3583 | 12384 | 5694000 | 2711000 | 5322000 | 0 | 7396363.63 | 26309818.18 | 207600 | 133971457.73 | 291512645.44

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-10-2025 | during | 11-10-2025 | during | 11-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174 | 174 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 343 | 351 | 0 | 0 | 367 | 367 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 151 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 90 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 17 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 12 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 26 | 101 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 55 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 52 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 545 | 500 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 1986 | 2379 | 5419.65 | 5387.65 | 3876.56 | 3938.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 98 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 202 | 199 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 2 | 89 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 46 | 40 | 70 | 68 | 68 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 17 | 20 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 16 | 24 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.02 | 0 | 3.78 | 0 | 3.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 13 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 35 | 144 | 144 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1152 | 1176 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 3 | 0 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1850.02 | 2225 | 3225.64 | 3255.86 | 2991.64 | 2991.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 127 | 205 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 295 | 415 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 5 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 2 | 3 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 101 | 105 | 163 | 163 | 108 | 108 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 48 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 64 | 160 | 160 | 78 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 72 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 52 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1044 | 1397 | 2823.86 | 2763.86 | 2470.86 | 2419.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-10-2025 | during | 11-10-2025 | during | 11-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 34 | 157.5 | 157.5 | 31 | 31 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 48 | 48 | 45 | 45 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.43 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 168.43 | 165 | 389 | 349 | 206 | 166
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 7 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 340 | 353 | 365 | 365 | 357 | 357 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1040 | 1049 | 1098 | 1098 | 1071 | 1071
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 937 | 920 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 118 | 118 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.38 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 364 | 365 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1433.38 | 1323 | 2780 | 2688 | 2291 | 2199
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 307 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1054 | 1098 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 269 | 279 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.8 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1925.8 | 2036 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 51.98 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 196 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 383 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 22 | 22 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.59 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1177 | 1272.24 | 1435.88 | 1435.88 | 1435 | 1435 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.62 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 77 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1985.19 | 1997.24 | 3185.57 | 3018.87 | 3117.31 | 2950.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 0 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 141 | 140 | 150 | 150 | 145 | 145 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 189 | 0 | 175.18 | 0 | 175.18 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 399.4 | 363 | 659.18 | 448 | 654.18 | 443
System Total |  |  |  |  | 28823.2 | 28365.955 | 11832.22 | 12934.24 | 21727.9 | 21155.24 | 18642.55 | 18142.89
Forecast Scenario (11-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12720 |  | 0 |  | 12720
|  |  |  | 1:00 | 12240 |  | 0 |  | 12240
|  |  |  | 2:00 | 11740 |  | 0 |  | 11740
|  |  |  | 3:00 | 11430 |  | 0 |  | 11430
|  |  |  | 4:00 | 10890 |  | 0 |  | 10890
|  |  |  | 5:00 | 10630 |  | 0 |  | 10630
|  |  |  | 6:00 | 10260 |  | 0 |  | 10260
|  |  |  | 7:00 | 10180 |  | 0 |  | 10180
|  |  |  | 8:00 | 10040 |  | 0 |  | 10040
|  |  |  | 9:00 | 9950 |  | 0 |  | 9950
|  |  |  | 10:00 | 10050 |  | 0 |  | 10050
|  |  |  | 11:00 | 10250 |  | 0 |  | 10250
|  |  |  | 12:00 | 10660 |  | 0 |  | 10660
|  |  |  | 13:00 | 11190 |  | 0 |  | 11190
|  |  |  | 14:00 | 11500 |  | 0 |  | 11500
|  |  |  | 15:00 | 11570 |  | 0 |  | 11570
|  |  |  | 16:00 | 11440 |  | 0 |  | 11440
|  |  |  | 17:00 | 11000 |  | 0 |  | 11000
|  |  |  | 18:00 | 11750 |  | 0 |  | 11750
|  |  |  | 18:30 | 12300 |  | 0 |  | 12300
|  |  |  | 19:00 | 13200 |  | 0 |  | 13200
|  |  |  | 19:30 | 13270 |  | 0 |  | 13270
|  |  |  | 20:00 | 13320 |  | 0 |  | 13320
|  |  |  | 21:00 | 13390 |  | 0 |  | 13390
|  |  |  | 22:00 | 13320 |  | 0 |  | 13320
|  |  |  | 23:00 | 13280 |  | 0 |  | 13280
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10660.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13390.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13390.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 276.00 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:08 hrs on 11-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11832.22 | MW | 12:00 Hr. | Energy Generated |  |  | 291.5126 |  | MKWHr.
| Day Peak Demand |  |  | 11832.22 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.127 |  | MKWHr.
| Evening Peak Generation |  |  | 12934.24 | MW | 20:00 Hr. | Energy Demand |  |  | 291.6396 |  | MKWHr.
| Evening Peak Demand |  |  | 12960.37 | MW | 20:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 10472.51 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 850.04 |  | MMCFD
| Maximum Generation of the Day |  |  | 14100.69 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.092 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.7915 | 0 | 10.577 | 0 | 0 | 0.10079 | 0 | 0 | 51.4693 | Gas | 116.8473 | Gas | 416976961.27
| Chattogram Zone |  |  | 4.897 | 32.7164 | 5.42 | 0 | 4.6318 | 0.12276 | 0 | 0.03696 | 47.8249 | Coal | 85.223 | Coal | 490831729.0658
| Cumilla Zone |  |  | 23.0824 | 0 | 3.2998 | 0 | 0 | 0.45624 | 1.5542 | 0 | 28.3927 | HFO | 26.2423 | HFO | 484682672.734
| Mymensingh Zone |  |  | 0.27168 | 0 | 2.8518 | 0 | 0 | 0.23552 | 0 | 0 | 3.359 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.4953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.4953 | Hydro | 4.6318 | Hydro | 463178.2
| Khulna Zone |  |  | 0 | 8.8436 | 0.032832 | 0 | 0 | 0.49464 | 23.0378 | 0 | 32.4089 | Solar | 3.9814 | Solar | 61023410.0132
| Barishal Zone |  |  | 8.033 | 39.4002 | 0.21998 | 0 | 0 | 0.003583 | 0 | 0 | 47.6567 | Import | 54.5499 | Import | 321366782.52
| Rajshahi Zone |  |  | 13.2764 | 0 | 1.5468 | 0 | 0 | 1.1742 | 29.9578 | 0 | 45.9552 | Wind | 0.03696 | Wind | 544790.4
| Rangpur Zone |  |  | 0 | 4.2628 | 2.2941 | 0 | 0 | 1.3937 | 0 | 0 | 7.9506
| Total |  |  | 116.8473 | 85.223 | 26.2423 | 0 | 4.6318 | 3.9814 | 54.5499 | 0.03696 | 291.5126
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416976961.27 |  | Hydro | 463178.2
|  |  |  | Coal | 490831729.0658 |  | Solar | 61023410.0132
|  |  |  | HFO | 484682672.734 |  | Import | 321366782.52
|  |  |  | HSD | 0 |  | Wind | 544790.4
[5 empty] | Total: | 177,58,89,524 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1258 | Peak Hr Flow | 920.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29244173.14 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.9578 | Peak Hr Flow | 1272.24 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1522 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5542 | Peak Hr Flow | 64.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2189 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.6379 | Peak Hr Flow | 2256.24 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4258
|  |  |  | Chattogram |  | 0 |  | 1322
|  |  |  | Cumilla |  | 0 |  | 1299
|  |  |  | Mymensingh |  | 25 |  | 1079
|  |  |  | Sylhet |  | 0 |  | 619
|  |  |  | Khulna |  | 0 |  | 1420
|  |  |  | Barishal |  | 0 |  | 412
|  |  |  | Rajshahi |  | 0 |  | 1261
|  |  |  | Rangpur |  | 0 |  | 890
|  |  |  | Total |  | 25 |  | 12560
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 531 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 531
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:02 | Jashore 132/33kV S/S T-3 HT is restored.
|  | 08:02 | Jashore 132/33kV S/S T-3 LT is restored.
| 08:08 | 11:11 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Project Work S/D Due to To remove T
connection between juldha and khulshi-3 ckt.at 4 circuit tower at cepz end
| 08:10 | 12:05 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Protection
Settings Reshaple at halishahar S/S
| 08:20 | 11:20 | Mirpur 132/33kV S/S Main Bus Project Work S/D Due to 132/33KV NewT3 Transformer
(80/120MVA) loop connecting works.
| 08:20 | 11:20 | Mirpur 132/33kV S/S Main Bus Project Work S/D Due to 132/33KV NewT3 Transformer
(80/120MVA) loop connecting works.
| 08:20 | 12:27 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33 kv DS Y phase Loop change. | [7 empty] | 42.0MW load
interrup.
| 08:21 | 12:25 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 kv DS Y phase loop change | [7 empty] | 42.0MW load
interrup.
| 08:38 | 17:52 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to OPGw installation
in 132 KV line
| 10:42 | 12:33 | Chandraghona-Kaptai 132 kV Ckt-2 Tripped from Chandraghona 132/33kV end showing REL670
relays.
| 10:42 |  | Kaptai-1,2 & 3 tripped
|  | 11:26 | Meghnaghat 400/230kV S/S ATR-1 HT is restored.
| 11:59 |  | Kaptai-1 was sync.
| 12:48 |  | Kaptai-2 was sync.
| 14:34 | 16:49 | Aminbazar-Mirpur 132kV Ckt-2 Forced S/D from Mirpur 132/33kV end Due to Red Hot
maintenance work Main Bus loop Y Phase .
| 14:53 | 19:42 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Junction
point temperature imcrease
| 15:04 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing Distance
protechtion, Zone-1, Location-10.45km, Phase-A,B relays. and from Naogaon 132/33kV end
showing Distance relay. relays Due to Unknown.
| 15:09 | 17:37 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Red hot | [7 empty] | 27.0MW load
|  |  | manintenance | [7 empty] | interrup.
| 15:10 | 17:32 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Maintenance | [7 empty] | 27.0MW load
interrup.
|  | 15:40 | Hathazari 230/132/33kV S/S 132KV MAIN BUS-01 is restored.
|  | 15:42 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 15:42 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 15:44 | Hathazari 230/132/33kV S/S MT-04 HT is restored.
|  | 15:46 | Hathazari 230/132/33kV S/S MT-04 LT is restored.
|  | 15:49 | Hathazari-Madunaghat 132kV Ckt-1 is restored.
|  | 15:49 | Hathazari-Madunaghat 132kV Ckt-2 is restored.
| 16:54 | 17:19 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Lockout Relay-K861 | [7 empty] | 52.0MW load
|  |  | Lockout Relay-K862 relays Due to Due to Bandarban 33kv Feeder | [7 empty] | interrup.
| 17:30 | 21:09 | Mirpur 132/33kV S/S Reserve Bus Project Work S/D
| 17:57 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 18:20 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Forced S/D from Bogura 230/132kV end Due to Repair &
Maintenance of Conductor. and from Naogaon 132/33kV end Due to wire disconnected
| 18:23 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 20:00 |  | Evening Peak Generation is 12934 MW
| 21:13 | 22:22 | Bakulia-Sikalbaha 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Distance Relay
relays Due to Thundering
| 21:13 |  | Bakulia-Sikalbaha 132 kV Ckt-1 Tripped from Bakulia 132/33kV end showing Distance Relay
relays Due to Thundering and from Shikalbaha 230/132kV end showing ABB REL670 relays.
| 06:00 |  | Minimum Generation is 10736 MW.
| 06:15 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Scheduled S/D Due to Project work
| 06:32 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 06:43 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 06:58 |  | BIPTC S/S 10CF15 Tripped showing 87.1 Differential relay relays Due to Tripped by C1
unbalance 60/61 CPR04
| 07:24 |  | Keranigonj 230/132/33kV S/S ATR-2 LT Scheduled S/D Due to High maintenance work at cse
pot.
| 07:24 |  | Keranigonj 230/132/33kV S/S ATR-2 HT Scheduled S/D Due to High maintenance work at cse
pot.
| 08:00 |  | Kachua 230/132/33kV S/S TR-1 HT Forced S/D Due to for maintenance work | [7 empty] | 15.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 351 | 8488800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8455000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 151 | 3455185 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 219856 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7766476 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 259560 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 90 | 1063680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 267354 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 210232 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 433800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 402840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 272160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 1265335 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 101 | 1819152 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2012160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 52 | 797760 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 100786 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 311400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 500 | 11789379 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 2078400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2379 | 51469315
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 101611.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 103680 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 529440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 4631782 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 199 | 4343538 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 89 | 1378327 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 754704 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 384629 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 553440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 421440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19078 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 163091 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 137837 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 909126 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 313636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 35 | 326182 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1176 | 25887271 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 36960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6829090.91 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2225 | 47824863.71
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 205 | 2987000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7786000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 415 | 8064000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 5 | 220968 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 3 | 71040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1224212 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 978545 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 336336 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2492910 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 48 | 1342080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1554240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 7392 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 236310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 31920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 42840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 560640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456236 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1397 | 28392669
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 271680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1164000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1584000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 224470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 30000 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 73800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 165 | 3359000
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1593720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3660136 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715008 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1933440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1652820 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 397000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 192216 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7469000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 353 | 8165000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1049 | 26495340
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 920 | 22125818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 10560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 22272 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 494640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 365 | 8843636 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1323 | 32408926
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 7396363.63 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 12384 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2711000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1098 | 26309818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5322000 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 207600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 5694000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3583 | -
Barishal Area Total |  |  |  |  | 2858 | 2036 | 47656748.81
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 226572 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 84823 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 299090 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4569809 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 383 | 8706546 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 94798 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 728992 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 242400 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 96672 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1272.24 | 29957838 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 346496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 572425 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1997.24 | 45955201
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 772800 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3490000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1027977 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40099.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1266130 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186455 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1167120 | -
Rangpur Area Total |  |  |  |  | 950 | 363 | 7950581.92
Eastern Grid Total |  |  |  |  | 17385.715 | 7215 | 157541187.71
Western Grid Total |  |  |  |  | 10980.24 | 5719.24 | 133971457.73
National Grid Total |  |  |  |  | 28365.955 | 12934.24 | 291512645.44
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-10-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8551.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3982.6 | MW
i) Dhaka area |  |  | 4257.58 |  | MW | i) Khulna area |  |  |  | 1420 | MW
ii) Chattogram area |  |  | 1322 |  | MW | ii) Barishal area |  |  |  | 412 | MW
iii) Cumilla area |  |  | 1298.73 |  | MW | iii) Rajshahi area |  |  |  | 1260.6 | MW
iv) Mymensingh area |  |  | 1054 |  | MW | iv) Rangpur area |  |  |  | 890 | MW
v) Sylhet area |  |  | 619 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12533.91 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 81 | 00:00 | 133 | Niamatpur | 68 | 22:00
2 | AKSML | 120.7 | 07:00 | 68 | Ishurdi | 57 | 13:00 | 134 | Noapara | 35 | 00:00
3 | Aftabnagar | 34 | 00:00 | 69 | Jaldhaka | 81 | 18:30 | 135 | PHP | 6 | 01:00
4 | Agargaon | 111 | 13:00 | 70 | Jamalpur | 111 | 17:00 | 136 | Pabna | 94 | 00:00
5 | Agrabad | 80 | 18:00 | 71 | Jashore | 124 | 13:00 | 137 | Palashbari | 104 | 00:00
6 | Amnura | 27 | 00:00 | 72 | Jhenaidah | 103 | 00:00 | 138 | Panchagarh | 59 | 18:30
7 | Ashuganj | 87 | 13:00 | 73 | Joydebpur | 139 | 01:00 | 139 | Patiya | 11 | 00:00
8 | BSRM | 116 | 22:00 | 74 | Joypurhat | 55 | 00:00 | 140 | Patuakhali | 64.5 | 22:00
9 | Bagerhat | 71 | 18:00 | 75 | Juldah | 14 | 00:00 | 141 | Payra | 28 | 00:00
10 | Bajitpur | 87 | 19:00 | 76 | KSRM | 26 | 08:00 | 142 | Postogola | 64 | 00:00
11 | Bakulia | 76 | 21:00 | 77 | Kabirpur | 219 | 00:00 | 143 | Purbachal | 20 | 00:00
12 | Banani | 30 | 18:30 | 78 | Kachua | 88 | 20:00 | 144 | Purbasadipur | 113 | 18:30
13 | Bangabhaban | 5 | 10:00 | 79 | Kallyanpur | 96 | 00:00 | 145 | Rahanpur | 36 | 00:00
14 | Barapukuria | 59 | 18:30 | 80 | Kalurghat | 44 | 02:00 | 146 | Rahim | 25 | 01:00
15 | Barguna | 20 | 21:00 | 81 | Kamrangirchar | 68 | 00:00 | 147 | Rajbari | 68 | 00:00
16 | Barishal | 103 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 120 | 00:00
17 | Barishal-230 | 88 | 18:00 | 83 | Kasba | 35 | 21:00 | 149 | Rajshahi | 96 | 00:00
18 | Baroaulia | 55 | 00:00 | 84 | Kazla | 93 | 00:00 | 150 | Rajshahi-230 | 88 | 13:00
19 | Baroirhat | 58 | 00:00 | 85 | Keranigonj | 83 | 00:00 | 151 | Ramganj | 106 | 21:00
20 | Bashundhara | 168 | 12:00 | 86 | Khagrachori | 28 | 19:30 | 152 | Rampur | 42 | 00:00
21 | BashundharaCement | 5 | 00:00 | 87 | Khulna | 62 | 13:00 | 153 | Rangamati | 17 | 18:00
22 | Beanibazar | 76 | 20:00 | 88 | Khulshi | 187 | 00:00 | 154 | Rangpur | 130 | 18:30
23 | Benapole | 62 | 19:30 | 89 | Kishoreganj | 120 | 00:00 | 155 | Ruppur | 7.4 | 10:00
24 | Bhaluka | 135 | 00:00 | 90 | Kodda | 268 | 00:00 | 156 | SSM | 1 | 06:00
25 | Bhandaria | 45 | 00:00 | 91 | Kulaura | 52 | 18:00 | 157 | Saidpur | 88 | 09:00
26 | Bhangura | 32 | 18:00 | 92 | Kurigram | 65 | 18:30 | 158 | Satkhira | 107 | 00:00
27 | Bheramara(GK) | 57 | 00:00 | 93 | Kushtia | 145 | 00:00 | 159 | Satmasjid | 86 | 13:00
28 | Bhulta | 199 | 01:00 | 94 | Laksam | 33 | 00:00 | 160 | Savar | 184 | 00:00
29 | Bog-Sherpur | 70 | 00:00 | 95 | Lakshmipur | 31 | 21:00 | 161 | SevenRings | 15.69 | 00:00
30 | Bogura | 146 | 01:00 | 96 | Lalbag | 56 | 00:00 | 162 | ShahCement | 30 | 04:00
31 | Borhanuddin | 91 | 23:00 | 97 | Lalmonirhat | 60 | 18:30 | 163 | Shahjadpur | 73 | 00:00
32 | Brahmanbaria | 129 | 21:00 | 98 | MI_Cement | 16.1 | 12:00 | 164 | Shahjibazar | 124 | 22:00
33 | Cantonment | 120 | 12:00 | 99 | Madanganj | 38 | 11:00 | 165 | Shahmirpur | 46 | 00:00
34 | Chandina | 19.29 | 15:00 | 100 | Madaripur | 97 | 00:00 | 166 | Shariatpur | 81 | 00:00
35 | Chandpur | 75 | 21:00 | 101 | Madartek | 83 | 00:00 | 167 | Sherpur | 124 | 18:30
36 | Chandraghona | 37 | 18:00 | 102 | Madunaghat | 52 | 00:00 | 168 | Shikalbaha | 23 | 00:00
37 | Chapai | 64 | 19:30 | 103 | Magura | 53 | 18:00 | 169 | Shitalakhya | 62.4 | 00:00
38 | Charsaidpur | 39 | 01:00 | 104 | Mahasthangarh | 70 | 00:00 | 170 | Sholosohor | 40 | 00:00
39 | Chauddagram | 65 | 00:00 | 105 | Maijdee | 21 | 23:00 | 171 | Shyampur | 100 | 02:00
40 | Chhatak | 41 | 20:00 | 106 | Manikganj | 120 | 00:00 | 172 | Siddhirganj | 103 | 00:00
41 | Chowmuhani | 173 | 18:00 | 107 | Maniknagar | 58 | 00:00 | 173 | Sirajganj | 88 | 00:00
42 | Chuadanga | 100 | 00:00 | 108 | Matarbari | 52 | 21:00 | 174 | Sonargaon | 131 | 00:00
43 | Coxsbazar | 134 | 18:00 | 109 | Matuail | 62 | 00:00 | 175 | Sreemongol | 83 | 18:00
44 | Cumilla(N) | 134 | 00:00 | 110 | Metrorail_Motijheel | 21 | 16:00 | 176 | Sreepur | 87 | 01:00
45 | Cumilla(S) | 137 | 00:00 | 111 | Metrorail_Uttara | 5 | 18:00 | 177 | Srinagar | 42.63 | 21:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 107 | 00:00 | 178 | Sunamganj | 60 | 00:00
47 | Daudkandi | 146 | 00:00 | 113 | Mirpur | 109 | 13:00 | 179 | Sylhet | 52 | 18:00
48 | DhakaUniversity | 40 | 11:00 | 114 | Mirsorai | 10 | 15:00 | 180 | Sylhet-132 | 106 | 13:00
49 | Dhamrai | 124 | 00:00 | 115 | Mirzapur | 37 | 00:00 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 100 | 18:00 | 116 | Mithapukur | 65 | 18:30 | 182 | Tangail | 162 | 21:00
51 | Dohazari | 95 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 21 | 00:00
52 | Faridpur | 142 | 02:00 | 118 | Mogbazar | 72.3 | 13:00 | 184 | Thakurgaon | 98 | 19:00
53 | Fatullah | 91 | 00:00 | 119 | Mongla | 26 | 18:00 | 185 | Tongi | 99 | 11:00
54 | Fenchuganj | 42 | 18:00 | 120 | Motijheel | 37 | 13:00 | 186 | Ullahpara | 35 | 18:00
55 | Feni | 107 | 00:00 | 121 | Muktagacha | 35 | 18:00 | 187 | Ullon | 59 | 14:00
56 | GPH | 6 | 18:00 | 122 | Munshiganj | 103 | 00:00 | 188 | Uttara | 60 | 12:00
57 | Ghatail | 76 | 18:00 | 123 | Muradnagar | 40 | 21:00 | 189 | UttaraNew | 69 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 181 | 21:00 | 190 | Zigatola | 64 | 12:00
59 | Ghorashal-230 | 100 | 00:00 | 125 | Naogaon | 115 | 00:00
60 | Goalpara | 24 | 00:00 | 126 | Narail | 48 | 19:30
61 | Gollamari | 96 | 13:00 | 127 | Narinda | 40 | 00:00
62 | Gopalganj | 93 | 19:00 | 128 | Narshingdi | 178 | 00:00
63 | Gulshan | 82 | 12:00 | 129 | Natore | 133 | 00:00
64 | Halishahar | 41 | 00:00 | 130 | Nawabganj | 42 | 00:00
65 | HaripurSBU | 140 | 01:00 | 131 | Netrakona | 142 | 18:00
66 | Hasnabad | 77 | 00:00 | 132 | New | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14100.69 | 30 |  | 14132.04
1:00 | 13616.39 | 29 |  | 13646.7
2:00 | 13161.36 | 0 |  | 13161.36
3:00 | 12629.1 | 0 |  | 12629.1
4:00 | 12330.37 | 0 |  | 12330.37
5:00 | 11965.56 | 0 |  | 11965.56
6:00 | 11391.33 | 0 |  | 11391.33
7:00 | 11117.42 | 0 |  | 11117.42
8:00 | 11139.92 | 0 |  | 11139.92
9:00 | 10883.64 | 0 |  | 10883.64
10:00 | 10936.42 | 0 |  | 10936.42
11:00 | 11168.7 | 0 |  | 11168.7
12:00 | 11832.22 | 0 |  | 11832.22
13:00 | 12396.81 | 0 |  | 12396.81
14:00 | 11438.94 | 0 |  | 11438.94
15:00 | 11121.78 | 0 |  | 11121.78
16:00 | 10545.08 | 0 |  | 10545.08
17:00 | 10472.51 | 0 |  | 10472.51
18:00 | 12031.54 | 0 |  | 12031.54
19:00 | 12780 | 19 |  | 12799.86
19:30 | 12825.72 | 19 |  | 12845.58
20:00 | 12934.24 | 25 |  | 12960.37
21:00 | 12885.15 | 24 |  | 12910.23
22:00 | 12785.09 | 0 |  | 12785.09
23:00 | 12770.75 | 0 |  | 12770.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8085.36 | 6015.33 | 14100.69 | DAILY GENERATION CURVE
00:30 | 7889.76 | 5968.78 | 13858.54
01:00 | 7694.16 | 5922.23 | 13616.39 | 10-10-2025
01:30 | 7558.86 | 5830.015 | 13388.875
02:00 | 7423.56 | 5737.8 | 13161.36
02:30 | 7242.88 | 5652.35 | 12895.23
03:00 | 7062.2 | 5566.9 | 12629.1
03:30 | 6966.2 | 5513.535 | 12479.735
04:00 | 6870.2 | 5460.17 | 12330.37
04:30 | 6717.2 | 5430.765 | 12147.965
05:00 | 6564.2 | 5401.36 | 11965.56
05:30 | 6323.11 | 5355.335 | 11678.445
06:00 | 6082.02 | 5309.31 | 11391.33
06:30 | 5964.385 | 5289.99 | 11254.375
07:00 | 5846.75 | 5270.67 | 11117.42
07:30 | 5825.065 | 5303.605 | 11128.67
08:00 | 5803.38 | 5336.54 | 11139.92
08:30 | 5748.66 | 5263.12 | 11011.78
09:00 | 5693.94 | 5189.7 | 10883.64
09:30 | 5676.585 | 5233.445 | 10910.03
10:00 | 5659.23 | 5277.19 | 10936.42
10:30 | 5709.75 | 5342.81 | 11052.56
11:00 | 5760.27 | 5408.43 | 11168.7
11:30 | 5924.36 | 5576.1 | 11500.46
12:00 | 6088.45 | 5743.77 | 11832.22
12:30 | 6277.81 | 5836.705 | 12114.515
13:00 | 6467.17 | 5929.64 | 12396.81
13:30 | 6253.395 | 5664.48 | 11917.875
14:00 | 6039.62 | 5399.32 | 11438.94
14:30 | 5957.52 | 5322.84 | 11280.36
15:00 | 5875.42 | 5246.36 | 11121.78
15:30 | 5821.63 | 5011.8 | 10833.43
16:00 | 5767.84 | 4777.24 | 10545.08
16:30 | 5733.465 | 4775.33 | 10508.795
17:00 | 5699.09 | 4773.42 | 10472.51
17:30 | 6120.045 | 5131.98 | 11252.025
18:00 | 6541 | 5490.54 | 12031.54
18:30 | 6795.5 | 5610.27 | 12405.77
19:00 | 7050 | 5730 | 12780
19:30 | 7114 | 5711.72 | 12825.72
20:00 | 7215 | 5719.24 | 12934.24
20:30 | 7135 | 5774.695 | 12909.695 |  | Executive Engineer
21:00 | 7055 | 5830.15 | 12885.15 |  | Network Operation Division
21:30 | 6983 | 5852.12 | 12835.12
22:00 | 6911 | 5874.09 | 12785.09
22:30 | 6903 | 5874.92 | 12777.92
23:00 | 6895 | 5875.75 | 12770.75

## En-Curve
QF-LDC-12
Date | 10-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2957 | 1957.5 | 900 | 38 | 78 | 1364.33 | 222 | 3642 | 0 | 767 | 2174.86 | 0 | 0 | 0 | 30 | DAILY ENERGY CURVE
00:30 | 2960.5 | 1919.15 | 900 | 38 | 75 | 1364.28 | 222 | 3635.5 | 0 | 698.5 | 2045.11 | 0 | 0 | 0.5 | 29.5 | 10-10-2025
01:00 | 2964 | 1880.8 | 900 | 38 | 72 | 1364.23 | 222 | 3629 | 0 | 630 | 1915.36 | 0 | 0 | 1 | 29
01:30 | 2962.5 | 1874.5 | 900.5 | 38 | 73 | 1363.015 | 221 | 3639.5 | 0 | 575 | 1741.36 | 0 | 0 | 0.5 | 14.5 | Energy Generated | 291.5126 |  | MKWHr
02:00 | 2961 | 1868.2 | 901 | 38 | 74 | 1361.8 | 220 | 3650 | 0 | 520 | 1567.36 | 0 | 0 | 0 | 0 | Energy not Served | 0.127 |  | MKWHr
02:30 | 2976.5 | 1881.7 | 901 | 38 | 68 | 1363.85 | 219.5 | 3667 | 0 | 428.5 | 1351.18 | 0 | 0 | 0 | 0 | Total Energy Requirement | 291.6396 |  | MKWHr
03:00 | 2992 | 1895.2 | 901 | 38 | 62 | 1365.9 | 219 | 3684 | 0 | 337 | 1135 | 0 | 0 | 0 | 0
03:30 | 2998.5 | 1899.7 | 901 | 38 | 64 | 1365.535 | 218.5 | 3689.5 | 0 | 295.5 | 1009.5 | 0 | 0 | 0 | 0
04:00 | 3005 | 1904.2 | 901 | 38 | 66 | 1365.17 | 218 | 3695 | 0 | 254 | 884 | 0 | 0 | 0 | 0
04:30 | 3008.5 | 1893.2 | 901.5 | 38 | 64 | 1363.265 | 218 | 3685.5 | 0 | 254 | 722 | 0 | 0 | 0 | 0
05:00 | 3012 | 1882.2 | 902 | 38 | 62 | 1361.36 | 218 | 3676 | 0 | 254 | 560 | 0 | 0 | 0 | 0
05:30 | 3000.5 | 1882.6 | 902.5 | 38 | 62 | 1337.335 | 198 | 3634 | 0.51 | 216 | 407 | 0 | 0 | 0 | 0
06:00 | 2989 | 1883 | 903 | 38 | 62 | 1313.31 | 178 | 3592 | 1.02 | 178 | 254 | 0 | 0 | 0 | 0
06:30 | 2939.5 | 1903 | 903 | 38 | 62 | 1265.365 | 178.5 | 3548 | 37.01 | 178 | 201 | 0 | 0 | 1 | 0
07:00 | 2890 | 1923 | 903 | 38 | 62 | 1217.42 | 179 | 3504 | 73 | 178 | 148 | 0 | 0 | 2 | 0
07:30 | 2859 | 1908.5 | 903 | 38 | 60 | 1216.21 | 179.5 | 3482 | 144.96 | 178 | 158.5 | 0 | 0 | 1 | 0
08:00 | 2828 | 1894 | 903 | 38 | 58 | 1215 | 180 | 3460 | 216.92 | 178 | 169 | 0 | 0 | 0 | 0
08:30 | 2807 | 1864 | 903 | 38 | 56 | 1164.5 | 180 | 3346 | 327.78 | 141.5 | 180 | 0 | 0 | 4 | 0
09:00 | 2786 | 1834 | 903 | 38 | 54 | 1114 | 180 | 3232 | 438.64 | 105 | 191 | 0 | 0 | 8 | 0
09:30 | 2822 | 1839.5 | 915 | 38 | 55 | 1068.5 | 180.5 | 3205.5 | 502.53 | 87 | 190 | 0 | 0 | 6.5 | 0
10:00 | 2858 | 1845 | 927 | 38 | 56 | 1023 | 181 | 3179 | 566.42 | 69 | 189 | 0 | 0 | 5 | 0
10:30 | 2901.5 | 1854 | 926.5 | 38 | 60 | 1018.5 | 130.5 | 3240 | 595.56 | 88 | 197.5 | 0 | 0 | 2.5 | 0
11:00 | 2945 | 1863 | 926 | 38 | 64 | 1014 | 80 | 3301 | 624.7 | 107 | 206 | 0 | 0 | 0 | 0
11:30 | 2946.5 | 1875 | 931.5 | 38 | 67 | 1095.5 | 89 | 3461 | 620.46 | 152.5 | 224 | 0 | 0 | 0 | 0
12:00 | 2948 | 1887 | 937 | 38 | 70 | 1177 | 98 | 3621 | 616.22 | 198 | 242 | 0 | 0 | 0 | 0
12:30 | 2906 | 1938 | 931.5 | 38 | 72 | 1247.5 | 127 | 3622.5 | 632.015 | 236 | 364 | 0 | 0 | 0 | 0
13:00 | 2864 | 1989 | 926 | 38 | 74 | 1318 | 156 | 3624 | 647.81 | 274 | 486 | 0 | 0 | 0 | 0
13:30 | 2805.5 | 1868 | 926.5 | 38 | 68 | 1264.5 | 164 | 3482.5 | 532.875 | 244 | 523.5 | 0 | 0 | 0.5 | 0
14:00 | 2747 | 1747 | 927 | 38 | 62 | 1211 | 172 | 3341 | 417.94 | 214 | 561 | 0 | 0 | 1 | 0
14:30 | 2731 | 1752.5 | 926.5 | 38 | 62 | 1215.87 | 172 | 3342 | 342.49 | 188.5 | 509 | 0 | 0 | 0.5 | 0
15:00 | 2715 | 1758 | 926 | 38 | 62 | 1220.74 | 172 | 3343 | 267.04 | 163 | 457 | 0 | 0 | 0 | 0
15:30 | 2767.5 | 1762.5 | 926 | 38 | 61 | 1120.515 | 195 | 3210 | 188.915 | 163 | 398.5 | 0 | 0 | 2.5 | 0
16:00 | 2820 | 1767 | 926 | 38 | 60 | 1020.29 | 218 | 3077 | 110.79 | 163 | 340 | 0 | 0 | 5 | 0
16:30 | 2790.5 | 1739 | 926.5 | 38 | 58 | 1053.31 | 218 | 3107.5 | 69.985 | 163 | 341 | 0 | 0 | 4 | 0
17:00 | 2761 | 1711 | 927 | 38 | 56 | 1086.33 | 218 | 3138 | 29.18 | 163 | 342 | 0 | 0 | 3 | 0
17:30 | 2843 | 1698.5 | 926.5 | 38 | 61 | 1203.435 | 218.5 | 3241.5 | 14.59 | 352 | 653 | 0 | 0 | 2 | 0
18:00 | 2925 | 1686 | 926 | 38 | 66 | 1320.54 | 219 | 3345 | 0 | 541 | 964 | 0 | 0 | 1 | 0
18:30 | 2958.5 | 1781 | 925.5 | 38 | 65 | 1319.27 | 219.5 | 3483.5 | 0 | 574.5 | 1040 | 0 | 0 | 1 | 9.5
19:00 | 2992 | 1876 | 925 | 38 | 64 | 1318 | 220 | 3622 | 0 | 608 | 1116 | 0 | 0 | 1 | 19
19:30 | 3045 | 1906 | 927 | 38 | 66 | 1283.72 | 220 | 3637 | 0 | 608 | 1093 | 0 | 0 | 2 | 19
20:00 | 3169 | 1904 | 920 | 38 | 64 | 1272.24 | 221 | 3650 | 0 | 601 | 1095 | 0 | 0 | 0 | 25
20:30 | 3143.5 | 1900 | 910.5 | 38 | 66 | 1292.695 | 221.5 | 3662.5 | 0 | 601 | 1073.5 | 0 | 0 | 0.5 | 24.5
21:00 | 3118 | 1896 | 901 | 38 | 68 | 1313.15 | 222 | 3675 | 0 | 601 | 1052 | 0 | 0 | 1 | 24
21:30 | 3050 | 1877.5 | 901 | 38 | 70 | 1316.12 | 222 | 3740.5 | 0 | 575 | 1044.5 | 0 | 0 | 0.5 | 12
22:00 | 2982 | 1859 | 901 | 38 | 72 | 1319.09 | 222 | 3806 | 0 | 549 | 1037 | 0 | 0 | 0 | 0
22:30 | 2977.5 | 1872.5 | 900.5 | 38 | 73 | 1319.92 | 222 | 3802 | 0 | 535 | 1033.5 | 0 | 0 | 4 | 0
23:00 | 2973 | 1886 | 900 | 38 | 74 | 1320.75 | 222 | 3798 | 0 | 521 | 1030 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 13:00 | 378 | 12:00 | Payra | 412 | 17:00 | 408 | 00:00
Ashuganj | 403 | 14:00 | 385 | 12:00 | Rahanpur | 406 | 16:00 | 395 | 03:00
Bhulta | 400 | 14:00 | 382 | 12:00 | Rampal | 406 | 16:00 | 392 | 00:00
Bibiana | 392 | 16:00 | 384 | 12:00
BIPTC | 403 | 05:00 | 394 | 12:00
Bogura | 395 | 16:00 | 381 | 18:30
Gopalganj | 400 | 16:00 | 390 | 01:00
Kaliakoir | 383 | 14:00 | 369 | 12:00
Madunaghat | 395 | 00:00 | 389 | 12:00
Meghnaghat | 392 | 09:00 | 384 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 16:00 | 225 | 12:00 | Kaliakoir | 239 | 14:00 | 223 | 12:00
AKSML | 235 | 00:00 | 229 | 05:00 | Keranigonj | 230 | 14:00 | 223 | 12:00
Aminbazar | 233 | 17:00 | 227 | 00:00 | Khulna(S) | 233 | 16:00 | 222 | 00:00
Ashuganj | 232 | 17:00 | 225 | 12:00 | Madunaghat | 235 | 21:00 | 229 | 11:00
Ashuganj-400 | 232 | 17:00 | 225 | 12:00 | Madunaghat-400 | 236 | 01:00 | 230 | 12:00
Baghabari | 234 | 13:00 | 225 | 00:00 | Maniknagar | 225 | 14:00 | 220 | 00:00
Barapukuria | 222 | 11:00 | 216 | 18:30 | Meghnaghat | 233 | 17:00 | 227 | 07:00
Barapukuria-230 | 222 | 11:00 | 216 | 18:30 | Meghnaghat-400 | 229 | 14:00 | 224 | 00:00
Barishal | 237 | 17:00 | 230 | 00:00 | Mirsorai | 231 | 19:00 | 225 | 12:00
Bheramara | 235 | 14:00 | 222 | 18:00 | Rajshahi | 232 | 14:00 | 220 | 18:00
Bhulta | 231 | 14:00 | 219 | 12:00 | Rampal | 232 | 09:00 | 222 | 00:00
Bibiana | 231 | 07:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 14:00 | 222 | 18:00 | Rampura | 229 | 14:00 | 217 | 12:00
Bogura | 236 | 16:00 | 227 | 18:30 | Shikalbaha | 234 | 00:00 | 227 | 13:00
Bogura-400 | 235 | 09:00 | 227 | 18:30 | Shyampur | 229 | 17:00 | 222 | 12:00
Borhanuddin | 239 | 16:00 | 234 | 00:00 | Siddhirganj | 229 | 18:00 | 222 | 00:00
BSRM | 230 | 00:00 | 225 | 12:00 | Sirajgonj | 239 | 14:00 | 233 | 18:30
Cumilla(N) | 228 | 14:00 | 222 | 12:00 | Sreepur | 229 | 16:00 | 222 | 12:00
Faridpur | 235 | 16:00 | 227 | 01:00 | Tongi | 230 | 01:00 | 222 | 11:00
Fenchuganj | 232 | 09:00 | 225 | 22:00
Ghorashal | 235 | 14:00 | 225 | 09:00
Ghorashal-230 | 230 | 14:00 | 220 | 12:00
Gopalganj | 235 | 16:00 | 229 | 00:00
GPH | 233 | 17:00 | 228 | 06:00
Haripur | 227 | 17:00 | 221 | 00:00
Hasnabad | 229 | 13:00 | 223 | 11:00
Hathazari | 233 | 18:00 | 225 | 11:00
Ishurdi | 237 | 14:00 | 223 | 00:00
Jhenaidah | 234 | 16:00 | 220 | 00:00
Kachua | 215 | 00:00 | 210 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 130 | 12:00 | Lalmonirhat | 127 | 23:00 | 120 | 18:30
Agargaon | 137 | 17:00 | 132 | 12:00 | Madanganj | 132 | 17:00 | 128 | 00:00
Agrabad | 134 | 00:00 | 130 | 03:00 | Madaripur | 138 | 16:00 | 133 | 00:00
AKS | 132 | 16:00 | 129 | 07:00 | Madartek | 136 | 14:00 | 130 | 12:00
Aminbazar | 138 | 13:00 | 133 | 10:00 | Madunaghat | 137 | 21:00 | 132 | 07:00
Amnura | 138 | 17:00 | 128 | 02:00 | Magura | 137 | 06:00 | 128 | 18:00
Ashuganj | 140 | 07:00 | 137 | 00:00 | Mahasthangarh | 131 | 11:00 | 125 | 18:30
Bagerhat | 135 | 09:00 | 122 | 00:00 | Maijdee | 132 | 17:00 | 127 | 23:00
Bajitpur | 131 | 17:00 | 125 | 00:00 | Manikganj | 132 | 17:00 | 125 | 09:00
Bakulia | 135 | 00:00 | 131 | 12:00 | Maniknagar | 137 | 14:00 | 133 | 00:00
Banani | 137 | 14:00 | 130 | 12:00 | Matarbari | 119 | 09:00 | 113 | 18:00
Bangabhaban | 136 | 14:00 | 133 | 00:00 | Matuail | 132 | 14:00 | 126.6 | 07:00
Barapukuria | 136 | 16:00 | 128 | 05:00 | Metrorail_Motijheel | 137 | 14:00 | 130 | 01:00
Barguna | 136 | 17:00 | 133 | 12:00 | Metrorail_Uttara | 137 | 14:00 | 131 | 12:00
Barishal | 137 | 17:00 | 132 | 00:00 | Millgate | 138 | 14:00 | 128 | 12:00
Barishal-230 | 137 | 17:00 | 132 | 00:00 | Mirpur | 137 | 14:00 | 131 | 11:00
Baroaulia | 135 | 00:00 | 131 | 12:00 | Mirzapur | 133 | 14:00 | 126 | 12:00
Baroirhat | 131 | 17:00 | 127 | 01:00 | Mithapukur | 130 | 02:00 | 125 | 04:00
Bashundhara | 136 | 01:00 | 129 | 12:00 | MI_Cement | 133 | 16:00 | 129 | 00:00
BashundharaCement | 138 | 01:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 07:00 | 120 | 22:00 | Mogbazar | 137 | 03:00 | 130 | 12:00
Benapole | 135 | 09:00 | 123 | 23:00 | Mongla | 135 | 09:00 | 124 | 00:00
Bhaluka | 132 | 16:00 | 126 | 00:00 | Motijheel | 136 | 14:00 | 133 | 00:00
Bhandaria | 135 | 09:00 | 118 | 00:00 | Muktagacha | 128 | 09:00 | 118 | 01:00
Bhangura | 134 | 16:00 | 128 | 01:00 | Munshiganj | 132 | 17:00 | 127 | 07:00
Bheramara | 136 | 14:00 | 128 | 00:00 | Muradnagar | 132 | 16:00 | 126 | 00:00
Bheramara(GK) | 136 | 14:00 | 128 | 00:00 | Mymensingh | 128 | 09:00 | 115 | 01:00
Bhulta | 130 | 14:00 | 126 | 07:00 | Naogaon | 129 | 10:00 | 117 | 22:00
Bog-Sherpur | 132 | 09:00 | 126 | 18:30 | Narail | 137 | 06:00 | 128 | 00:00
Bogura | 134 | 16:00 | 129 | 03:00 | Narinda | 137 | 14:00 | 133 | 00:00
Bogura-230 | 134 | 10:00 | 128 | 18:30 | Narshingdi | 135 | 17:00 | 122 | 00:00
Brahmanbaria | 136 | 17:00 | 129 | 00:00 | Natore | 133 | 09:00 | 126 | 00:00
Cantonment | 136 | 14:00 | 131 | 12:00 | Nawabganj | 137 | 14:00 | 131 | 00:00
Chandina | 134 | 16:00 | 129 | 12:00 | Netrakona | 123 | 14:00 | 116 | 01:00
Chandpur | 138 | 02:00 | 132 | 10:00 | New | 134 | 13:00 | 129 | 12:00
Chandraghona | 136 | 00:00 | 133 | 07:00 | Niamatpur | 138 | 16:00 | 133 | 18:00
Chapai | 136 | 14:00 | 132 | 20:00 | Noapara | 137 | 08:00 | 127 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 17:00 | 129 | 00:00 | Pabna | 136 | 16:00 | 128 | 00:00
Chauddagram | 133 | 17:00 | 128 | 11:00 | Palashbari | 128 | 04:00 | 121 | 18:30
Chhatak | 128 | 10:00 | 117 | 22:00 | Panchagarh | 136 | 02:00 | 123 | 15:00
Chowmuhani | 131 | 17:00 | 128 | 00:00 | Patiya | 134 | 17:00 | 129 | 07:00
Chuadanga | 137 | 18:00 | 126 | 00:00 | Patuakhali | 137 | 17:00 | 134 | 05:00
Coxsbazar | 122 | 17:00 | 114 | 18:00 | Payra | 137 | 09:00 | 135 | 00:00
Cumilla(N) | 133 | 16:00 | 129 | 12:00 | PHP | 130 | 16:00 | 126 | 13:00
Cumilla(S) | 134 | 16:00 | 127 | 13:00 | Postogola | 136 | 17:00 | 132 | 00:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 137 | 02:00 | 129 | 12:00
Daudkandi | 130 | 16:00 | 123 | 01:00 | Purbasadipur | 132 | 02:00 | 121 | 15:00
DhakaUniversity | 137 | 06:00 | 130 | 12:00 | Rahanpur | 139 | 10:00 | 134 | 00:00
Dhamrai | 140 | 14:00 | 130 | 12:00 | Rahanpur-400 | 139 | 07:00 | 135 | 01:00
Dhanmondi | 137 | 05:00 | 130 | 12:00 | Rahim | 132 | 14:00 | 128 | 00:00
Dohazari | 131 | 23:00 | 125 | 05:00 | Rajbari | 138 | 16:00 | 132 | 00:00
Faridpur | 138 | 16:00 | 134 | 13:00 | Rajendrapur | 139 | 14:00 | 125 | 00:00
Fatullah | 139 | 14:00 | 135 | 00:00 | Rajshahi | 133 | 08:00 | 127 | 00:00
Fenchuganj | 136 | 08:00 | 131 | 22:00 | Rajshahi-230 | 133 | 14:00 | 126 | 18:00
Feni | 131 | 19:00 | 127 | 23:00 | Ramganj | 133 | 17:00 | 129 | 11:00
Ghatail | 127 | 09:00 | 118 | 01:00 | Rampur | 133 | 00:00 | 129 | 12:00
Ghorashal | 140 | 14:00 | 132 | 11:00 | Rampura | 137 | 14:00 | 130 | 12:00
Goalpara | 139 | 08:00 | 130 | 00:00 | Rangamati | 135 | 17:00 | 131 | 12:00
Gollamari | 139 | 08:00 | 131 | 00:00 | Rangpur | 131 | 03:00 | 126 | 12:00
Gopalganj | 137 | 09:00 | 130 | 01:00 | Ruppur | 137 | 09:00 | 130 | 00:00
Gopalganj-400 | 139 | 16:00 | 134 | 00:00 | Saidpur | 132 | 01:00 | 124 | 08:00
Gulshan | 136 | 04:00 | 130 | 12:00 | Satkhira | 136 | 10:00 | 126 | 00:00
Halishahar | 134 | 00:00 | 129 | 12:00 | Satmasjid | 137 | 16:00 | 131 | 12:00
Haripur | 133 | 16:00 | 129 | 00:00 | Savar | 137 | 14:00 | 130 | 12:00
HaripurSBU | 133 | 16:00 | 129 | 00:00 | SevenRings | 140 | 14:00 | 132 | 12:00
Hasnabad | 136 | 15:00 | 132 | 00:00 | ShahCement | 133 | 17:00 | 129 | 00:00
Hathazari | 135 | 00:00 | 133 | 01:00 | Shahjadpur | 136 | 09:00 | 131 | 21:00
Ishurdi | 138 | 14:00 | 130 | 00:00 | Shahjibazar | 135 | 08:00 | 129 | 00:00
Jaldhaka | 128 | 22:00 | 122 | 18:30 | Shahmirpur | 135 | 00:00 | 131 | 13:00
Jamalpur | 127 | 09:00 | 116 | 13:00 | Shariatpur | 138 | 17:00 | 131 | 00:00
Jashore | 139 | 08:00 | 126 | 18:30 | Sherpur | 126 | 06:00 | 112 | 01:00
Jhenaidah | 138 | 06:00 | 120 | 00:00 | Shikalbaha | 125 | 00:00 | 120 | 07:00
Jhenaidah-230 | 140 | 08:00 | 130 | 00:00 | Shikalbaha-230 | 136 | 00:00 | 132 | 07:00
Joydebpur | 140 | 01:00 | 127 | 10:00 | Shitalakhya | 133 | 16:00 | 129 | 00:00
Joypurhat | 128 | 09:00 | 114 | 22:00 | Sholosohor | 135 | 00:00 | 132 | 12:00
Juldah | 134 | 00:00 | 132 | 02:00 | Shyampur | 140 | 18:00 | 135 | 00:00
Kabirpur | 140 | 14:00 | 128 | 12:00 | Shyampur-230 | 139 | 14:00 | 135 | 00:00
Kachua | 138 | 15:00 | 134 | 11:00 | Siddhirganj | 133 | 14:00 | 129 | 00:00
Kaliakoir | 141 | 14:00 | 131 | 12:00 | Sirajganj | 132 | 09:00 | 125 | 18:30
Kallyanpur | 137 | 14:00 | 132 | 12:00 | Sonargaon | 137 | 15:00 | 127 | 00:00
Kalurghat | 136 | 00:00 | 132 | 12:00 | Sreemongol | 134 | 09:00 | 128 | 00:00
Kamrangirchar | 137 | 16:00 | 131 | 00:00 | Sreepur | 134 | 16:00 | 128 | 01:00
Kaptai | 137 | 1:00 | 135 | 7:00 | Srinagar | 137 | 16:00 | 132 | 00:00
Kasba | 131 | 16:00 | 125 | 00:00 | SSM | 139 | 00:00 | 134 | 06:00
Kazla | 136 | 15:00 | 132 | 06:00 | Sunamganj | 125 | 06:00 | 114 | 22:00
Keranigonj | 136 | 14:00 | 132 | 00:00 | Sylhet | 129 | 06:00 | 122 | 22:00
Khagrachori | 134 | 01:00 | 130 | 12:00 | Sylhet-132 | 130 | 07:00 | 124 | 20:00
Khulna | 138 | 09:00 | 129 | 00:00 | Tangail | 128 | 07:00 | 122 | 00:00
Khulna(S) | 139 | 08:00 | 130 | 22:00 | Taraganj | 130 | 22:00 | 124 | 05:00
Khulshi | 132 | 00:00 | 128 | 12:00 | Thakurgaon | 135 | 02:00 | 120 | 15:00
Kishoreganj | 130 | 14:00 | 123 | 00:00 | TK | 135 | 00:00 | 132 | 12:00
Kodda | 138 | 14:00 | 128 | 11:00 | Tongi | 136 | 01:00 | 132 | 11:00
KSRM | 135 | 13:00 | 131 | 12:00 | Ullahpara | 134 | 09:00 | 128 | 00:00
Kulaura | 135 | 09:00 | 130 | 22:00 | Ullon | 136 | 02:00 | 129 | 12:00
Kurigram | 128 | 22:00 | 121 | 18:00 | Uttara | 136 | 14:00 | 130 | 10:00
Kushtia | 134 | 16:00 | 123 | 00:00 | UttaraNew | 137 | 14:00 | 131 | 11:00
Laksam | 138 | 17:00 | 133 | 12:00 | Zigatola | 137 | 17:00 | 132 | 00:00
Lakshmipur | 132 | 17:00 | 126 | 22:00
Lalbag | 137 | 17:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division