## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-10-2025 | during | 12-10-2025 | during | 12-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174 | 174 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 365 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 0 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 100 | 100 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 96 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 21 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 149 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 72 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 18 | 0 | 12 | 0 | 12 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 3 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 569 | 540 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 22 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 1884.5 | 2522 | 5504.65 | 5492.65 | 3697.69 | 3779.69
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 48 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 180 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 205 | 187 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 88 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 62 | 40 | 70 | 68 | 68 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 26 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 40 | 89 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.92 | 0 | 3.92 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 96 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 58 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 140 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1120 | 1224 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1878 | 2657.5 | 3239.64 | 3255.72 | 2989.78 | 2975.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 187 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 89 | 95 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 10 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 125 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 26 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 105 | 163 | 163 | 108 | 108 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 128 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 68 | 160 | 160 | 78 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 37 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 94 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 2 | 7 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 69 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 15 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1107 | 1367 | 2823.86 | 2763.86 | 2470.86 | 2419.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-10-2025 | during | 12-10-2025 | during | 12-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 44 | 42 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 47 | 48 | 48 | 45 | 45 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.16 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 200.16 | 156 | 391.9 | 349 | 335.4 | 292.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 68 | 70 | 70 | 70 | 70 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 157 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 329 | 365 | 365 | 357 | 357 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1035 | 1034 | 1123 | 1123 | 1050 | 1050
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 901 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 410 | 410 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 365 | 362 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1359 | 1301 | 2778 | 2688 | 2015 | 1925
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 307 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 25 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1076 | 1222 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 234 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1952.73 | 2213 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 67.4 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 11 | 190 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 197 | 130 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 351 | 336 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.94 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1157 | 1356.7 | 748 | 748 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.48 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 121 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1966.82 | 2440.7 | 2493.59 | 2328.99 | 3094.09 | 2929.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 46 | 48 | 48 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 140 | 146 | 150 | 150 | 145 | 145 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 174 | 0 | 182.7 | 0 | 182.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 400.7 | 411 | 664.7 | 446 | 641.7 | 423
System Total |  |  |  |  | 28823.2 | 28365.955 | 11783.91 | 14102.2 | 21166.34 | 20593.22 | 18258.52 | 17758.4
Forecast Scenario (12-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13400 |  | 0 |  | 13400
|  |  |  | 1:00 | 12940 |  | 0 |  | 12940
|  |  |  | 2:00 | 12390 |  | 0 |  | 12390
|  |  |  | 3:00 | 12160 |  | 0 |  | 12160
|  |  |  | 4:00 | 11800 |  | 0 |  | 11800
|  |  |  | 5:00 | 11690 |  | 0 |  | 11690
|  |  |  | 6:00 | 11420 |  | 0 |  | 11420
|  |  |  | 7:00 | 11670 |  | 0 |  | 11670
|  |  |  | 8:00 | 11820 |  | 0 |  | 11820
|  |  |  | 9:00 | 11910 |  | 0 |  | 11910
|  |  |  | 10:00 | 12280 |  | 0 |  | 12280
|  |  |  | 11:00 | 12710 |  | 0 |  | 12710
|  |  |  | 12:00 | 13110 |  | 0 |  | 13110
|  |  |  | 13:00 | 13300 |  | 0 |  | 13300
|  |  |  | 14:00 | 13070 |  | 0 |  | 13070
|  |  |  | 15:00 | 13030 |  | 0 |  | 13030
|  |  |  | 16:00 | 12650 |  | 0 |  | 12650
|  |  |  | 17:00 | 12480 |  | 0 |  | 12480
|  |  |  | 18:00 | 13900 |  | 0 |  | 13900
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14470 |  | 0 |  | 14470
|  |  |  | 19:30 | 14420 |  | 0 |  | 14420
|  |  |  | 20:00 | 14220 |  | 0 |  | 14220
|  |  |  | 21:00 | 14040 |  | 0 |  | 14040
|  |  |  | 22:00 | 13850 |  | 0 |  | 13850
|  |  |  | 23:00 | 13660 |  | 0 |  | 13660
Probable Maximum Temperature: |  |  | 31.60°C
Probable Maximum Demand at Day Peak: |  |  | 13110.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14470.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14470.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 307.97 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:07 hrs on 12-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-10-2025 | [28 empty] | Date: | 11-10-2025 | [28 empty] | Date: | 11-10-2025 | [28 empty] | Date: | 11-10-2025 | [28 empty] | Date: | 11-10-2025 | [14 empty] | Date: | 11-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 100 | 45 | 45 | 15 | 0 | 17 | 0 | 350 | 143 | 485 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 17 | 22 | 0 | 0 | 13 | 0 | 24 | 0 | 6 | 16 | 46 | 0 | 0 | 0 | 0 | 222 | 66 | 29 | 285 | 30 | 0 | 26 | 8 | 90 | 161 | 0 | 0 | 0 | 1135 | 0 | 51 | 50 | 0 | 335 | 0 | 330 | 5 | 183 | 5 | 17 | 105 | 95 | 0 | 17 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 326 | 30 | 67 | 147 | 7 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 35 | 0 | 0 | 0 | 6715 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1315.51 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 37 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 394 | 0 | 0 | 144 | 50 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 115 | 220 | 0 | 307 | 1222 | 17 | 5912.51 | 12627.51 | 107.31
01:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 100 | 30 | 15 | 0 | 0 | 17 | 0 | 350 | 147 | 480 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 46 | 0 | 0 | 0 | 0 | 222 | 67 | 29 | 285 | 0 | 0 | 26 | 0 | 90 | 161 | 0 | 0 | 0 | 1155 | 0 | 51 | 50 | 0 | 283 | 0 | 330 | 5 | 195 | 5 | 17 | 105 | 91 | 0 | 17 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 330 | 30 | 68 | 148 | 7 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 35 | 0 | 0 | 0 | 6484 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1309.73 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 144 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 307 | 1216 | 17 | 5874.73 | 12358.73 | 107.3
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 17 | 0 | 350 | 144 | 500 | 0 | 17 | 335 | 0 | 0 | 0 | 70 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 10 | 0 | 0 | 0 | 0 | 222 | 67 | 34 | 285 | 0 | 0 | 26 | 0 | 89 | 158 | 0 | 0 | 0 | 1135 | 0 | 51 | 50 | 55 | 0 | 0 | 330 | 11 | 188 | 35 | 17 | 105 | 95 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 310 | 30 | 68 | 144 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 35 | 0 | 0 | 0 | 6169 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1314.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 404 | 0 | 0 | 145 | 47 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 307 | 1220 | 17 | 5688.6 | 11857.6 | 107.3
03:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 146 | 500 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 220 | 33 | 29 | 285 | 0 | 0 | 26 | 0 | 70 | 153 | 0 | 0 | 0 | 1070 | 0 | 51 | 0 | 107 | 0 | 0 | 330 | 37 | 192 | 35 | 17 | 105 | 68 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 331 | 30 | 68 | 141 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 69 | 0 | 0 | 0 | 5984 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1226.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 408 | 0 | 0 | 144 | 47 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 115 | 220 | 0 | 307 | 1220 | 0 | 5455.57 | 11439.57 | 107.3
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 143 | 510 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 218 | 17 | 29 | 285 | 0 | 0 | 26 | 0 | 36 | 151 | 0 | 0 | 0 | 1029 | 0 | 51 | 0 | 162 | 0 | 0 | 330 | 41 | 188 | 35 | 17 | 105 | 63 | 0 | 17 | 0 | 64 | 0 | 0 | 0 | 310 | 0 | 309 | 30 | 68 | 143 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 70 | 0 | 0 | 3 | 5875 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1219.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 367 | 0 | 0 | 145 | 45 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 115 | 220 | 0 | 308 | 1220 | 0 | 5322.45 | 11197.45 | 107.3
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 151 | 520 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1061 | 0 | 51 | 0 | 182 | 0 | 0 | 330 | 40 | 202 | 31 | 0 | 105 | 0 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 315 | 0 | 336 | 30 | 68 | 153 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 16 | 70 | 0 | 0 | 6 | 5745 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1126.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 389 | 0 | 0 | 145 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 115 | 220 | 0 | 310 | 1124 | 0 | 5150.21 | 10895.21 | 107.3
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 144 | 515 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.06 | 218 | 0 | 29 | 285 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 182 | 0 | 0 | 330 | 41 | 190 | 31 | 0 | 106 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 320 | 0 | 309 | 30 | 68 | 149 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 16 | 70 | 0 | 0 | 6 | 5672.06 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 1114.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 346 | 0 | 0 | 143 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 115 | 220 | 0 | 308 | 1104 | 0 | 5064.29 | 10736.35 | 107.3
07:00 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 146 | 540 | 0 | 0 | 335 | 86 | 0 | 1 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 220 | 0 | 19 | 285 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1130 | 6 | 51 | 0 | 172 | 0 | 0 | 300 | 42 | 189 | 33 | 0 | 106 | 0 | 0 | 17 | 0 | 52 | 0 | 11 | 0 | 315 | 0 | 310 | 30 | 68 | 156 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 32 | 70 | 0 | 0.32 | 6 | 5591.82 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 367 | 0 | 1168.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 5 | 0 | 0 | 0.33 | 0 | 0 | 196 | 0 | 0 | 0 | 373 | 0 | 0 | 144 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 44 | 0.12 | 0 | 217 | 115 | 220 | 0 | 307 | 1104 | 0 | 5256.77 | 10848.59 | 107.3
08:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 146 | 490 | 0 | 0 | 335 | 135 | 0 | 3 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.63 | 180 | 0 | 2 | 285 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 1135 | 12 | 51 | 0 | 170 | 0 | 0 | 280 | 41 | 188 | 35 | 0 | 104 | 0 | 0 | 17 | 0 | 56 | 0 | 40 | 0 | 300 | 0 | 320 | 30 | 67 | 149 | 6 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 67 | 32 | 67 | 0 | 1.07 | 6 | 5545.7 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 367 | 0 | 1165.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.75 | 38 | 0 | 0 | 1.95 | 0 | 0 | 182 | 0 | 0 | 0 | 340 | 0 | 0.19 | 141 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 2.8 | 52 | 0.06 | 0 | 217 | 100 | 180 | 0 | 308 | 1052 | 0 | 5185.91 | 10731.61 | 107.3
09:00 | 0 | 48 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 30 | 0 | 0 | 0 | 0 | 0 | 450 | 147 | 477 | 0 | 0 | 335 | 75 | 0 | 7 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.57 | 180 | 0 | 2 | 285 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 1045 | 16 | 51 | 0 | 172 | 0 | 0 | 280 | 41 | 189 | 37 | 0 | 104 | 0 | 0 | 17 | 0 | 62 | 0 | 50 | 0 | 300 | 0 | 331 | 30 | 67 | 149 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 60 | 1 | 3.34 | 6 | 5566.91 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 367 | 0 | 1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.25 | 31 | 0 | 0 | 0.4 | 0 | 0 | 187 | 0 | 0 | 0 | 320 | 0 | 0.13 | 142 | 48 | 0 | 22 | 0 | 0 | 0 | 0 | 4.6 | 105 | 0.14 | 0 | 174 | 100 | 180 | 0 | 307 | 1015 | 0 | 5158.52 | 10725.43 | 107.3
10:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 15 | 0 | 0 | 0 | 17 | 0 | 450 | 150 | 451 | 0 | 0 | 335 | 75 | 0 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 0 | 16 | 0 | 0 | 0 | 3.39 | 180 | 0 | 2 | 285 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 940 | 17 | 51 | 0 | 182 | 0 | 0 | 280 | 41 | 193 | 38 | 0 | 104 | 0 | 0 | 17 | 0 | 56 | 0 | 53 | 0 | 305 | 0 | 331 | 30 | 67 | 145 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 3 | 67 | 47 | 50 | 0 | 2.13 | 6 | 5566.52 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76 | 366 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.79 | 54 | 0 | 0 | 14.89 | 0 | 0 | 193 | 0 | 0 | 0 | 365 | 0 | 1.29 | 141 | 46 | 0 | 30 | 0 | 0 | 0 | 0 | 6 | 133 | 0.38 | 0 | 168 | 115 | 220 | 0 | 306 | 950 | 0 | 5228.35 | 10794.87 | 107.3
11:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 15 | 0 | 0 | 0 | 16 | 0 | 450 | 150 | 526 | 0 | 0 | 335 | 99 | 0 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 4.37 | 180 | 0 | 2 | 285 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 990 | 19 | 51 | 0 | 182 | 0 | 72 | 330 | 41 | 196 | 38 | 0 | 105 | 0 | 0 | 0 | 0 | 56 | 0 | 3 | 0 | 315 | 0 | 351 | 30 | 67 | 158 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 67 | 24 | 45 | 1 | 26.41 | 6 | 5811.78 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 365 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.02 | 103 | 0 | 0 | 20.03 | 0 | 0 | 202 | 0 | 0 | 0 | 362 | 0 | 1.73 | 142 | 48 | 0 | 37 | 0 | 0 | 0 | 0 | 2.3 | 114 | 0.46 | 0 | 172 | 115 | 220 | 0 | 307 | 976 | 0 | 5312.54 | 11124.32 | 107.3
12:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 52 | 15 | 0 | 0 | 0 | 45 | 0 | 450 | 151 | 569 | 0 | 0 | 335 | 100 | 0 | 18 | 22 | 19.5 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 1 | 0 | 25 | 0 | 0 | 0 | 0 | 180 | 0 | 7 | 285 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 1120 | 15 | 51 | 0 | 182 | 0 | 89 | 330 | 41 | 187 | 38 | 1 | 105 | 0 | 2 | 12 | 0 | 54 | 0 | 15 | 0 | 310 | 0 | 336 | 30 | 67 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 67 | 24 | 44 | 2 | 40.16 | 6 | 6104.66 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 365 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4 | 121 | 0 | 0 | 56.48 | 11 | 0 | 197 | 0 | 0 | 0 | 351 | 0 | 5.94 | 140 | 46 | 0 | 36 | 0 | 0 | 0 | 0 | 4.7 | 174 | 0.73 | 0 | 234 | 115 | 220 | 0 | 307 | 1076 | 0 | 5679.25 | 11783.91 | 107.3
13:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 52 | 15 | 0 | 0 | 0 | 48 | 0 | 450 | 150 | 526 | 0 | 0 | 335 | 100 | 0 | 29 | 35 | 19.5 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 0 | 40 | 0 | 0 | 0 | 0 | 180 | 0 | 10 | 285 | 0 | 0 | 0 | 0 | 29 | 205 | 0 | 0 | 0 | 1140 | 19 | 51 | 41 | 138 | 0 | 23 | 330 | 36 | 158 | 38 | 28 | 106 | 41 | 8 | 15 | 0 | 58 | 0 | 18 | 0 | 305 | 0 | 343 | 30 | 67 | 153 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 67 | 24 | 44 | 2 | 18.33 | 6 | 6152.83 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 366 | 0 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.66 | 72 | 0 | 0 | 52.58 | 25 | 0 | 191 | 0 | 0 | 0 | 351 | 0 | 3.17 | 140 | 46 | 0 | 33 | 0 | 0 | 0 | 0 | 6.7 | 165 | 0.71 | 0 | 277 | 115 | 220 | 0 | 307 | 1105 | 0 | 5801.82 | 11954.65 | 107.3
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 52 | 15 | 0 | 0 | 17 | 49 | 0 | 450 | 151 | 525 | 0 | 0 | 335 | 100 | 0 | 20 | 35 | 19 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 0 | 40 | 0 | 0 | 0 | 0 | 180 | 0 | 9 | 285 | 0 | 0 | 0 | 0 | 31 | 202 | 0 | 0 | 0 | 1150 | 18 | 51 | 80 | 8 | 0 | 19 | 330 | 10 | 182 | 10 | 34 | 105 | 34 | 9 | 15 | 0 | 60 | 0 | 19 | 0 | 300 | 0 | 356 | 30 | 68 | 152 | 9 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 67 | 24 | 45 | 2 | 18.15 | 6 | 6061.15 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 365 | 0 | 1266.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.41 | 89 | 0 | 0 | 48.55 | 13 | 0 | 190 | 0 | 0 | 0 | 351 | 0 | 4.35 | 141 | 46 | 0 | 8 | 0 | 0 | 0 | 0 | 5.8 | 149 | 0.08 | 0 | 276 | 115 | 220 | 0 | 305 | 1105 | 0 | 5720.77 | 11781.92 | 107.3
15:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 52 | 15 | 0 | 0 | 35 | 51 | 0 | 450 | 151 | 546 | 0 | 0 | 335 | 98 | 0 | 16 | 35 | 20 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 32 | 0 | 0 | 0 | 0 | 182 | 0 | 9 | 285 | 0 | 0 | 0 | 0 | 33 | 202 | 0 | 0 | 0 | 1155 | 0 | 51 | 80 | 8 | 0 | 11 | 330 | 10 | 212 | 10 | 34 | 106 | 34 | 0 | 15 | 0 | 66 | 0 | 10 | 0 | 310 | 0 | 380 | 30 | 68 | 160 | 10 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 67 | 45 | 45 | 1 | 18.28 | 6 | 6142.28 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 365 | 0 | 1262.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.5 | 39 | 0 | 0 | 38.88 | 29 | 0 | 202 | 0 | 0 | 0 | 395 | 0 | 2.77 | 146 | 45 | 0 | 21 | 0 | 0 | 0 | 0 | 4.4 | 114 | 0.05 | 0 | 283 | 115 | 220 | 0 | 307 | 1102 | 0 | 5679.35 | 11821.63 | 107.3
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 52 | 15 | 95 | 0 | 35 | 54 | 0 | 450 | 50 | 496 | 0 | 17 | 335 | 99 | 0 | 11 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 32 | 0 | 0 | 0 | 0 | 180 | 0 | 7 | 285 | 0 | 0 | 5 | 0 | 34 | 202 | 0 | 0 | 0 | 1150 | 3 | 51 | 80 | 8 | 0 | 14 | 330 | 10 | 200 | 10 | 34 | 104 | 60 | 0 | 15 | 0 | 52 | 0 | 8 | 0 | 320 | 0 | 375 | 30 | 68 | 159 | 0 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 67 | 45 | 45 | 0 | 16.78 | 6 | 6087.78 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 365 | 0 | 1261.94 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21.27 | 37 | 0 | 0 | 16.95 | 66 | 0 | 202 | 0 | 0 | 0 | 368 | 0 | 0.98 | 145 | 45 | 35 | 8 | 18 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 278 | 115 | 220 | 0 | 307 | 1104 | 0 | 5640.14 | 11727.92 | 107.3
17:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 52 | 53 | 145 | 0 | 35 | 54 | 0 | 450 | 0 | 495 | 0 | 35 | 335 | 99 | 0 | 3 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 8 | 32 | 0 | 0 | 0 | 0.12 | 218 | 0 | 10 | 285 | 15 | 0 | 27 | 1 | 34 | 202 | 0 | 0 | 0 | 1170 | 1 | 51 | 80 | 8 | 0 | 15 | 330 | 10 | 193 | 10 | 34 | 106 | 68 | 0 | 15 | 0 | 60 | 0 | 1 | 0 | 315 | 0 | 360 | 30 | 68 | 159 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 45 | 0 | 3.92 | 6 | 6215.04 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 364 | 0 | 1268.53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 4 | 7 | 0 | 0 | 4.21 | 138 | 0 | 130 | 0 | 0 | 0 | 361 | 0 | 0.35 | 146 | 45 | 35 | 3 | 34 | 0 | 0 | 0 | 0.4 | 9 | 0 | 0 | 278 | 115 | 220 | 0 | 307 | 1104 | 17 | 5567.49 | 11782.53 | 107.3
18:00 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 128 | 96 | 277 | 35 | 55 | 72 | 0 | 450 | 0 | 486 | 0 | 35 | 335 | 99 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 7 | 5 | 74 | 0 | 0 | 48 | 62 | 1 | 0 | 0 | 0 | 218 | 29 | 16 | 285 | 60 | 0 | 37 | 10 | 42 | 187 | 0 | 0 | 0 | 1185 | 0 | 51 | 90 | 8 | 0 | 68 | 330 | 10 | 212 | 10 | 40 | 105 | 66 | 0 | 15 | 55 | 70 | 8 | 0 | 4 | 310 | 0 | 391 | 30 | 68 | 155 | 8 | 0 | 83 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 42 | 0 | 0 | 6 | 7054 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1358.7 | 0 | 28 | 0 | 70 | 55 | 0 | 95 | 14 | 8 | 0 | 0 | 22 | 0 | 0 | 199 | 0 | 130 | 0 | 0 | 0 | 405 | 0 | 0 | 147 | 45 | 109 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 307 | 1120 | 17 | 6181.7 | 13235.7 | 107.3
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 96 | 277 | 55 | 55 | 72 | 0 | 450 | 0 | 540 | 0 | 35 | 335 | 100 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 58 | 45 | 89 | 0 | 0 | 49 | 62 | 17 | 0 | 0 | 0 | 218 | 96 | 26 | 285 | 140 | 0 | 48 | 25.5 | 88 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 8 | 0 | 95 | 330 | 10 | 186 | 10 | 69 | 105 | 128 | 7 | 18 | 94 | 68 | 37 | 0 | 26 | 315 | 0 | 329 | 30 | 68 | 157 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 42 | 0 | 0 | 0 | 7736.5 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 1356.7 | 0 | 40 | 0 | 100 | 111 | 0 | 95 | 35 | 25 | 0 | 0 | 22 | 0 | 0 | 190 | 0 | 130 | 0 | 0 | 0 | 336 | 0 | 0 | 146 | 46 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 307 | 115 | 220 | 0 | 307 | 1222 | 17 | 6365.7 | 14102.2 | 107.3
19:30 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 96 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 515 | 0 | 35 | 335 | 100 | 0 | 0 | 90 | 21 | 22 | 0 | 0 | 92 | 45 | 97 | 0 | 0 | 49 | 62 | 17 | 0 | 0 | 0 | 218 | 97 | 29 | 285 | 85 | 0 | 48 | 25.5 | 87 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 136 | 8 | 0 | 103 | 330 | 10 | 194 | 10 | 69 | 105 | 128 | 9 | 18 | 33 | 60 | 8 | 0 | 30 | 312 | 0 | 347 | 30 | 68 | 150 | 8 | 0 | 83 | 30 | 0 | 16 | 0 | 0 | 67 | 47 | 45 | 0 | 0 | 0 | 7569.5 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 1365.32 | 0 | 40 | 0 | 70 | 113 | 0 | 96 | 37 | 8 | 0 | 0 | 22 | 0 | 0 | 183 | 0 | 130 | 0 | 0 | 0 | 349 | 0 | 0 | 145 | 46 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 306 | 1222 | 17 | 6375.32 | 13944.82
20:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 96 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 520 | 0 | 35 | 335 | 100 | 0 | 0 | 90 | 21 | 22 | 0 | 0 | 84 | 45 | 98 | 0 | 0 | 49 | 62 | 17 | 0 | 0 | 0 | 220 | 98 | 19 | 285 | 82 | 0 | 50 | 25.5 | 90 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 8 | 0 | 123 | 330 | 10 | 193 | 10 | 69 | 106 | 123 | 9 | 18 | 33 | 66 | 8 | 0 | 29 | 305 | 0 | 325 | 30 | 68 | 152 | 8 | 0 | 84 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 45 | 0 | 0 | 0 | 7556.5 | 835 | 38 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 1359.44 | 0 | 40 | 0 | 50 | 113 | 0 | 96 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 186 | 0 | 130 | 0 | 0 | 0 | 345 | 0 | 0 | 143 | 45 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 307 | 1222 | 17 | 6326.44 | 13882.94 | 107.3
21:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 96 | 277 | 30 | 0 | 72 | 0 | 450 | 0 | 475 | 0 | 35 | 335 | 100 | 0 | 0 | 70 | 21.5 | 22 | 0 | 0 | 86 | 45 | 98 | 0 | 4 | 49 | 62 | 17 | 0 | 0 | 0 | 220 | 101 | 21 | 285 | 30 | 0 | 50 | 25.5 | 88 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 136 | 8 | 0 | 152 | 330 | 10 | 189 | 10 | 58 | 106 | 124 | 9 | 18 | 0 | 66 | 0 | 0 | 29 | 310 | 0 | 349 | 30 | 68 | 153 | 8 | 0 | 84 | 30 | 0 | 16 | 0 | 0 | 67 | 48 | 45 | 0 | 0 | 0 | 7394 | 902 | 39 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1352.58 | 0 | 40 | 0 | 50 | 50 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 188 | 0 | 130 | 0 | 0 | 0 | 354 | 0 | 0 | 145 | 46 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 307 | 1222 | 17 | 6299.58 | 13693.58 | 107.3
22:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 96 | 195 | 30 | 0 | 54 | 0 | 450 | 0 | 480 | 0 | 35 | 335 | 100 | 0 | 0 | 70 | 21.5 | 22 | 0 | 0 | 55 | 45 | 98 | 0 | 6 | 49 | 62 | 17 | 0 | 0 | 0 | 220 | 106 | 16 | 285 | 30 | 0 | 50 | 17 | 89 | 181 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 8 | 0 | 254 | 330 | 10 | 199 | 10 | 43 | 106 | 129 | 8 | 18 | 0 | 62 | 0 | 0 | 29 | 310 | 0 | 360 | 30 | 68 | 157 | 8 | 0 | 84 | 30 | 0 | 16 | 0 | 0 | 68 | 48 | 42 | 0 | 0 | 1 | 7340.5 | 901 | 35 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 1361.35 | 0 | 40 | 0 | 0 | 50 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 194 | 0 | 130 | 0 | 0 | 0 | 368 | 0 | 0 | 143 | 45 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 307 | 1222 | 17 | 6237.35 | 13577.85 | 107.3
23:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 96 | 195 | 30 | 0 | 35 | 0 | 450 | 0 | 470 | 0 | 0 | 335 | 100 | 0 | 0 | 70 | 21 | 22 | 0 | 0 | 43 | 45 | 100 | 0 | 8 | 49 | 61 | 17 | 0 | 0 | 0 | 220 | 106 | 18 | 285 | 30 | 0 | 50 | 17 | 87 | 167 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 8 | 0 | 354 | 330 | 10 | 193 | 10 | 17 | 106 | 126 | 0 | 18 | 0 | 64 | 0 | 0 | 29 | 305 | 0 | 356 | 30 | 68 | 154 | 8 | 0 | 84 | 30 | 0 | 16 | 0 | 0 | 68 | 48 | 42 | 0 | 0 | 6 | 7307 | 901 | 35 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 1349.78 | 0 | 32 | 0 | 0 | 50 | 0 | 96 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 190 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 142 | 49 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 115 | 220 | 0 | 307 | 1222 | 17 | 6198.78 | 13505.78 | 107.3
Total KWH | 0 | 1487040 | 208800 | 0 | 0 | 0 | 0 | 0 | 2196000 | 0 | 0 | 259200 | 301680 | 1758960 | 858720 | 1832389 | 268363 | 266048 | 804960 | 0 | 10140500 | 2323753 | 12168984 | 0 | 268629 | 8076976 | 1838000 | 0 | 127863 | 1088400 | 386400 | 532080 | 0 | 0 | 392673 | 270982 | 962880 | 0 | 174240 | 382547 | 714912 | 108861 | 0 | 0 | 12480 | 4996509 | 884036 | 425760 | 6843636.36 | 362982 | 0 | 475200 | 140893.2 | 1046291 | 4283567 | 0 | 0 | 0 | 27179997 | 128250 | 1242104 | 1423490 | 1973818 | 0 | 1568700 | 7836000 | 569760 | 4709000 | 542808 | 563520 | 2517630 | 1422720 | 61320 | 356150 | 143640 | 1487040 | 69994 | 241918 | 163168 | 7542500 | 0 | 8529000 | 716000 | 1621800 | 3673309 | 167352 | 0 | 1911360 | 715680 | 0 | 395000 | 0 | 112680 | 1590000 | 988800 | 1176960 | 9350 | 143470 | 106320 | 153272802.56 | 21741090 | 199296 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 372960 | 8814545 | 0 | 29322909 | 0 | 228703 | 0 | 290688 | 559872 | 0 | 741584 | 223550 | 36106 | 362660 | 574532 | 148416 | 0 | 250496 | 1660182 | 0 | 4391209 | 0 | 0 | 0 | 8965818 | 0 | 20580 | 3546000 | 1043781 | 1092165 | 201202 | 1041638 | 0 | 0 | 0 | 40965.6 | 1090080 | 2157 | 150144 | 6022000 | 1726000 | 5453500 | 0 | 7381818.18 | 28062545.45 | 172800 | 136843992.23 | 290116794.79

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11783.91 | MW | 12:00 Hr. | Energy Generated |  |  | 290.1168 |  | MKWHr.
| Day Peak Demand |  |  | 11783.91 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.112 |  | MKWHr.
| Evening Peak Generation |  |  | 14102.2 | MW | 19:00 Hr. | Energy Demand |  |  | 290.2288 |  | MKWHr.
| Evening Peak Demand |  |  | 14151.2 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.7 |  | °C
| Minimum Generation of the Day |  |  | 10725.43 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 879.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 14102.2 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.1522 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.6627 | 0 | 9.4032 | 0 | 0 | 0.12786 | 0 | 0 | 47.1937 | Gas | 112.533 | Gas | 410071220.5
| Chattogram Zone |  |  | 4.7093 | 34.0236 | 5.7423 | 0 | 4.9965 | 0.14073 | 0 | 0.17424 | 49.7867 | Coal | 88.8943 | Coal | 514142972.9637
| Cumilla Zone |  |  | 21.316 | 0 | 3.8479 | 0 | 0 | 0.24192 | 1.487 | 0 | 26.8928 | HFO | 26.4768 | HFO | 489505545.856
| Mymensingh Zone |  |  | 1.177 | 0 | 2.7978 | 0 | 0 | 0.15282 | 0 | 0 | 4.1276 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.272 | Hydro | 4.9965 | Hydro | 499650.9
| Khulna Zone |  |  | 0.1993 | 8.8145 | 0 | 0 | 0 | 0.37296 | 22.6531 | 0 | 32.0399 | Solar | 3.579 | Solar | 53292574.696
| Barishal Zone |  |  | 7.1795 | 41.4664 | 0.32294 | 0 | 0 | 0.002157 | 0 | 0 | 48.971 | Import | 53.463 | Import | 314787699.27
| Rajshahi Zone |  |  | 15.0172 | 0 | 2.2289 | 0 | 0 | 1.2083 | 29.3229 | 0 | 47.7773 | Wind | 0.17424 | Wind | 2568297.6
| Rangpur Zone |  |  | 0 | 4.5898 | 2.1338 | 0 | 0 | 1.3322 | 0 | 0 | 8.0558
| Total |  |  | 112.533 | 88.8943 | 26.4768 | 0 | 4.9965 | 3.579 | 53.463 | 0.17424 | 290.1168
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 410071220.5 |  | Hydro | 499650.9
|  |  |  | Coal | 514142972.9637 |  | Solar | 53292574.696
|  |  |  | HFO | 489505545.856 |  | Import | 314787699.27
|  |  |  | HSD | 0 |  | Wind | 2568297.6
[5 empty] | Total: | 178,48,67,961 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7411 | Peak Hr Flow | 901.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41680896.05 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.3229 | Peak Hr Flow | 1356.70 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1766 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.487 | Peak Hr Flow | 68.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2411 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.551 | Peak Hr Flow | 2325.70 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 17 |  | 4887
|  |  |  | Chattogram |  | 0 |  | 1477
|  |  |  | Cumilla |  | 0 |  | 1269
|  |  |  | Mymensingh |  | 30 |  | 1054
|  |  |  | Sylhet |  | 0 |  | 544
|  |  |  | Khulna |  | 0 |  | 1659
|  |  |  | Barishal |  | 0 |  | 394
|  |  |  | Rajshahi |  | 0 |  | 1386
|  |  |  | Rangpur |  | 0 |  | 955
|  |  |  | Total |  | 47 |  | 13625
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 531 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 931
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 11:00 | Kachua 230/132/33kV S/S TR-1 HT Forced S/D Due to for maintenance work | [7 empty] | 15.0MW load
interrup.
| 08:02 | 14:09 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintence.
| 08:03 | 14:08 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintence.
| 08:18 | 16:00 | Hathazari 230/132/33kV S/S 132KV MAIN BUS-01 Project Work S/D Due to Project Work
Shutdown
| 08:18 | 16:04 | Panchagarh 132/33kV S/S T-1(407T) LT Scheduled S/D Due to Annual Maintenance work
| 08:18 | 16:02 | Panchagarh 132/33kV S/S T-1(407T) HT Scheduled S/D Due to Annual Maintenance work
| 08:20 | 16:00 | Hathazari 230/132/33kV S/S MT-04 HT Project Work S/D Due to Project Work Shutdown
| 08:20 | 16:00 | Hathazari 230/132/33kV S/S MT-04 LT Project Work S/D Due to Project Work Shutdown
| 08:24 | 12:08 | Mirpur 132/33kV S/S Reserve Bus Project Work S/D Due to Project development work
| 08:27 | 17:34 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 08:27 | 17:34 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to Bus Upgradation work | [7 empty] | 20.0MW load
interrup.
| 08:31 | 16:12 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to Annual Maintenance
| 08:31 | 16:12 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to Annual Maintenance
| 08:39 | 06:06 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Shutdown
taken by SDE NLDC
| 08:39 | 15:10 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to
Annual Bay Maintenance. and from Chandraghona 132/33kV end Due to Annual Maintenance
| 08:40 | 19:14 | Kamrangirchar-Keraniganj 132kV Ckt Scheduled S/D from Keranigonj 230/132/33kV end Due to
High temperature maintenance work
| 08:48 | 14:10 | Jaldhaka 132/33kV S/S Capacitor Bank Outdoor (22.5 MVAR) Scheduled S/D Due to Anual
Maintenance.
| 08:48 | 15:45 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to For annual maintenance
| 08:49 | 15:44 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to for annual maintenance
| 08:50 | 04:37 | Kabirpur -Tongi 132kV Ckt-1 Project Work S/D from Tongi 230/132/33kV end.
| 08:58 | 11:38 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Due
to high temperature maintenance and from Gopalganj 400/132kVend.
|  | 09:33 | Keranigonj 230/132/33kV S/S ATR-2 LT is restored.
|  | 09:33 | Keranigonj 230/132/33kV S/S ATR-2 HT is restored.
| 09:35 | 15:57 | Mahasthangarh 132/33kV S/S 132KV Main bus 1 Scheduled S/D Due to Annual Maintenance Work
| 09:40 | 14:51 | Daudkandi 132/33kV S/S Transformer-1 LT Tripped showing Overcurrent relay relays Due to | [7 empty] | 30.0MW load
|  |  | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) | [7 empty] | interrup.
| 09:40 | 10:11 | Daudkandi 132/33kV S/S Transformer-2 LT Tripped showing Overcurrent relay relays Due to | [7 empty] | 30.0MW load
|  |  | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) | [7 empty] | interrup.
| 09:40 | 10:10 | Daudkandi 132/33kV S/S Transformer-3 LT Tripped showing Overcurrent relay relays Due to | [7 empty] | 30.0MW load
|  |  | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) | [7 empty] | interrup.
| 09:42 | 16:46 | BIPTC S/S 10CF15 Scheduled S/D Due to C1 unbalane 60/61 CPR04
| 09:55 | 19:39 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to CNTIC project work
| 09:58 | 19:21 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to The
shutdown has been taken at 09:00 for project work.
| 10:03 | 17:12 | Maniknagar 132/33kV S/S Motijheel Ckt-1 Scheduled S/D Due to Winter Maintenance by DPDC
| 10:31 | 19:27 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to CNTIC
project work and from Daganbhuiyan 132/33kV end Due to CNTIC project work
| 10:33 | 19:18 | Daganbhuiyan 132/33kV S/S Main Bus 1&2 Project Work S/D Due to CNTIC project work
| 10:36 | 12:39 | Ghatail 132/33kV S/S T-1 LT Forced S/D Due to Remove of Red hot in 33 kV Tarakandi feeder | [7 empty] | 25.0MW load
|  |  | Bus raiser in bus section -1. | [7 empty] | interrup.
| 10:37 | 12:38 | Ghatail 132/33kV S/S T-1 HT Forced S/D Due to Remove of Red hot in 33 kV Tarakandi feeder | [7 empty] | 25.0MW load
|  |  | Bus raiser in bus section -1. | [7 empty] | interrup.
| 10:41 | 12:32 | Ghatail 132/33kV S/S Bus-1 Forced S/D Due to Remove of Red hot in 33 kV Tarakandi feeder | [7 empty] | 25.0MW load
|  |  | Bus raiser in bus section -1. | [7 empty] | interrup.
| 10:44 |  | Ashuganj North CCPP GT was synchronized.
| 10:44 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 10:59 |  | Siddhirganj 2x120 MW GT-1 was shutdown.
| 11:11 | 14:27 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Scheduled S/D Due to auxiliary transformer
installation
| 11:11 | 14:27 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Scheduled S/D Due to auxiliary transformer
installation
| 11:20 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 11:20 |  | Sirajganj 225 MW CCPP Unit-1 GT was sync.
| 11:34 | 13:16 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Shutdown for T-3 GCB hydraulic oil
leakage problem.
| 12:00 |  | Day Peak Generation is 11780 MW.
| 12:38 | 14:50 | Daudkandi 132/33kV S/S Transformer-1 HT Forced S/D Due to Flushing occurred at 33KV | [7 empty] | 30.0MW load
|  |  | switchyard (PBS-3). Need maintenance | [7 empty] | interrup.
| 13:45 | 16:58 | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Transformer T-2 shutdown for tap changer
maintenance purpose.
| 14:31 |  | Sirajganj 225 MW CCPP Unit-1 ST was sync.
| 14:31 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 14:42 | 18:35 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by pbs
| 14:43 | 15:04 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Forced S/D Due to LT side breaker problem
| 14:44 | 18:35 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by pbs
|  | 15:15 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
| 15:42 | 17:03 | BIPTC S/S 20DF12 Tripped showing C1 unbalance 60/61 instant L3 relays Due to Dead bird
has been found inside the fence.
| 16:00 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- ST
|  | 16:03 | Hathazari-Madunaghat 132kV Ckt-2 is restored.
|  | 16:03 | Hathazari-Madunaghat 132kV Ckt-1 is restored.
| 16:05 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- Shutdown as per NLDC (Gas shortage)
| 16:05 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
| 16:06 |  | Meghnaghat CCPP(Summit) ST Shutdown with remarks:- Shutdown as per NLDC (Gas
shortage) ST shutdown at 16:00
| 16:06 |  | Meghnaghat CCPP(Summit) GT-1 Ready with remarks:- None
| 16:07 |  | Meghnaghat CCPP(Summit) ST Ready with remarks:- ST ready at 16:01
| 16:11 | 17:03 | BIPTC S/S 20DF12 Scheduled S/D Due to Tripped by 60/61 C1 unbalane 60/61 instant L3
| 16:46 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- st
|  | 18:51 | Baroirhat-Hathazari 132 kV Ckt-1 is restored.
|  | 18:52 | Baroirhat-Hathazari 132 kV Ckt-2 is restored.
| 19:36 |  | Bheramara 410 MW CCPP Synchronized with remarks:- GT
| 19:50 | 20:52 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to 33kv bus high temperature | [7 empty] | 70.0MW load
interrup.
| 19:52 | 20:56 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kv bus high temperature | [7 empty] | 70.0MW load
interrup.
| 19:56 | 20:56 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to 33kv bus high temperature | [7 empty] | 70.0MW load
interrup.
| 19:56 | 20:54 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kv bus high temperature | [7 empty] | 70.0MW load
interrup.
| 00:21 |  | Bheramara 410 MW CCPP Synchronized with remarks:- ST
06:00
| 06:00 |  | Minimum Generation is 10917 MW.
| 07:11 |  | Kalurghat 132/33kV S/S TRFO-01(506T) HT Forced S/D Due to Due to high temp DS (Y &B ph
and 33 KV cable connector) maintenance.
| 07:43 |  | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
| 07:44 |  | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance
| 07:49 |  | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
Annual Maintenance and deadline checking.
| 07:49 |  | Adani Power Jharkhand Ltd. Unit-2 was shutdown at 07:49 hrs. due to condenser I/L CW duct
bellow leakage.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 2196000 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10140500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 2323753 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 268363 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 1838000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 8076976 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 259200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 96 | 858720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 266048 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 268629 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 386400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 532080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 208800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 1832389 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1758960 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1487040 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 804960 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 127863 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 301680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 540 | 12168984 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1088400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2522 | 47193745
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 140893.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128250 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 475200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 4996509 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4283567 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 1046291 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 714912 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 382547 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 425760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 962880 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 12480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 270982 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 108861 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 96 | 884036 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 58 | 392673 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 140 | 362982 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27179997 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 174240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6843636.36 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2657.5 | 49786696.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 186 | 4709000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 95 | 1568700 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7836000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 542808 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 569760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1973818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1242104 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1423490 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 26 | 163168 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2517630 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 128 | 1422720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1487040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 37 | 69994 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 356150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 94 | 143640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 7 | 61320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 563520 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 241918 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1367 | 26892780
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 42 | 1176960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 988800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1590000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 143470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 106320 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 112680 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 156 | 4127580
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1621800 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3673309 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715680 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1911360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 395000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 167352 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7542500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 329 | 8529000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1034 | 25272001
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 901 | 21741090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 199296 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 372960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 362 | 8814545 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1301 | 32039891
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 7381818.18 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 25 | 150144 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 1726000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 28062545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5453500 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 172800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6022000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2157 | -
Barishal Area Total |  |  |  |  | 2858 | 2213 | 48970964.63
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 362660 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 228703 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 223550 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 1660182 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 4391209 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 336 | 8965818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 148416 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 36106 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 741584 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 559872 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 100 | 290688 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1356.7 | 29322909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 250496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 574532 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2440.7 | 47777305
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1043781 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 146 | 3546000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1041638 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40965.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1092165 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201202 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1090080 | -
Rangpur Area Total |  |  |  |  | 950 | 411 | 8055831.6
Eastern Grid Total |  |  |  |  | 17385.715 | 7736.5 | 153272802.56
Western Grid Total |  |  |  |  | 10980.24 | 6365.7 | 136843992.23
National Grid Total |  |  |  |  | 28365.955 | 14102.2 | 290116794.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9184.71 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4393.3 | MW
i) Dhaka area |  |  | 4870.5 |  | MW | i) Khulna area |  |  |  | 1659 | MW
ii) Chattogram area |  |  | 1477 |  | MW | ii) Barishal area |  |  |  | 393.5 | MW
iii) Cumilla area |  |  | 1269.21 |  | MW | iii) Rajshahi area |  |  |  | 1385.8 | MW
iv) Mymensingh area |  |  | 1024 |  | MW | iv) Rangpur area |  |  |  | 955 | MW
v) Sylhet area |  |  | 544 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13578.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 18:00 | 133 | Niamatpur | 68 | 21:00
2 | AKSML | 123 | 04:00 | 68 | Ishurdi | 64 | 21:00 | 134 | Noapara | 40 | 14:00
3 | Aftabnagar | 34 | 18:00 | 69 | Jaldhaka | 84 | 18:30 | 135 | PHP | 8 | 10:00
4 | Agargaon | 107 | 19:00 | 70 | Jamalpur | 113 | 22:00 | 136 | Pabna | 107 | 18:30
5 | Agrabad | 84 | 11:00 | 71 | Jashore | 138 | 19:00 | 137 | Palashbari | 105 | 20:00
6 | Amnura | 27 | 00:00 | 72 | Jhenaidah | 126 | 18:30 | 138 | Panchagarh | 61 | 18:30
7 | Ashuganj | 78 | 00:00 | 73 | Joydebpur | 152 | 18:30 | 139 | Patiya | 11 | 00:00
8 | BSRM | 114 | 18:30 | 74 | Joypurhat | 52 | 00:00 | 140 | Patuakhali | 61 | 00:00
9 | Bagerhat | 80 | 18:30 | 75 | Juldah | 15.5 | 11:00 | 141 | Payra | 26 | 00:00
10 | Bajitpur | 80 | 00:00 | 76 | KSRM | 28 | 23:00 | 142 | Postogola | 60 | 11:00
11 | Bakulia | 86 | 18:30 | 77 | Kabirpur | 225 | 11:00 | 143 | Purbachal | 19 | 18:30
12 | Banani | 33.6 | 11:00 | 78 | Kachua | 82 | 00:00 | 144 | Purbasadipur | 115 | 18:00
13 | Bangabhaban | 7 | 10:00 | 79 | Kallyanpur | 96 | 18:00 | 145 | Rahanpur | 34 | 21:00
14 | Barapukuria | 67 | 18:30 | 80 | Kalurghat | 48 | 12:00 | 146 | Rahim | 29 | 15:00
15 | Barguna | 18 | 00:00 | 81 | Kamrangirchar | 66 | 19:30 | 147 | Rajbari | 76 | 18:30
16 | Barishal | 109 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 122 | 18:30
17 | Barishal-230 | 78 | 00:00 | 83 | Kasba | 32 | 00:00 | 149 | Rajshahi | 92 | 19:00
18 | Baroaulia | 61 | 11:00 | 84 | Kazla | 94 | 13:00 | 150 | Rajshahi-230 | 98 | 20:00
19 | Baroirhat | 59 | 18:30 | 85 | Keranigonj | 88 | 19:00 | 151 | Ramganj | 102 | 01:00
20 | Bashundhara | 169 | 18:00 | 86 | Khagrachori | 30 | 18:00 | 152 | Rampur | 41 | 18:30
21 | BashundharaCement | 2 | 15:00 | 87 | Khulna | 72 | 13:00 | 153 | Rangamati | 16 | 18:00
22 | Beanibazar | 74 | 18:00 | 88 | Khulshi | 190 | 19:00 | 154 | Rangpur | 146 | 18:30
23 | Benapole | 58 | 18:30 | 89 | Kishoreganj | 111 | 18:30 | 155 | Ruppur | 5.4 | 11:00
24 | Bhaluka | 132 | 21:00 | 90 | Kodda | 287 | 18:30 | 156 | SSM | 9 | 23:00
25 | Bhandaria | 46 | 20:00 | 91 | Kulaura | 45 | 18:00 | 157 | Saidpur | 104 | 19:00
26 | Bhangura | 35 | 21:00 | 92 | Kurigram | 62 | 19:00 | 158 | Satkhira | 118 | 19:00
27 | Bheramara(GK) | 65 | 18:00 | 93 | Kushtia | 149 | 18:30 | 159 | Satmasjid | 94 | 14:00
28 | Bhulta | 207 | 16:00 | 94 | Laksam | 36 | 19:30 | 160 | Savar | 207 | 19:00
29 | Bog-Sherpur | 72 | 18:00 | 95 | Lakshmipur | 29 | 00:00 | 161 | SevenRings | 14.48 | 19:00
30 | Bogura | 160 | 19:30 | 96 | Lalbag | 58 | 12:00 | 162 | ShahCement | 30 | 23:00
31 | Borhanuddin | 90 | 00:00 | 97 | Lalmonirhat | 60 | 18:00 | 163 | Shahjadpur | 77 | 18:00
32 | Brahmanbaria | 130 | 01:00 | 98 | MI_Cement | 11.8 | 15:00 | 164 | Shahjibazar | 120 | 00:00
33 | Cantonment | 138 | 18:00 | 99 | Madanganj | 37 | 00:00 | 165 | Shahmirpur | 53 | 19:30
34 | Chandina | 12.95 | 12:00 | 100 | Madaripur | 93 | 19:00 | 166 | Shariatpur | 71 | 00:00
35 | Chandpur | 72 | 00:00 | 101 | Madartek | 80 | 00:00 | 167 | Sherpur | 132 | 20:00
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 56 | 18:30 | 168 | Shikalbaha | 27 | 18:00
37 | Chapai | 62 | 00:00 | 103 | Magura | 61 | 16:00 | 169 | Shitalakhya | 77.7 | 16:00
38 | Charsaidpur | 35 | 19:00 | 104 | Mahasthangarh | 76 | 19:30 | 170 | Sholosohor | 47 | 18:00
39 | Chauddagram | 61 | 18:00 | 105 | Maijdee | 21 | 00:00 | 171 | Shyampur | 92 | 00:00
40 | Chhatak | 38 | 00:00 | 106 | Manikganj | 105 | 00:00 | 172 | Siddhirganj | 109 | 14:00
41 | Chowmuhani | 164 | 00:00 | 107 | Maniknagar | 54 | 13:00 | 173 | Sirajganj | 102 | 19:00
42 | Chuadanga | 111 | 18:30 | 108 | Matarbari | 56 | 20:00 | 174 | Sonargaon | 133 | 19:00
43 | Coxsbazar | 140 | 18:00 | 109 | Matuail | 66 | 10:00 | 175 | Sreemongol | 82 | 18:30
44 | Cumilla(N) | 134 | 19:30 | 110 | Metrorail_Motijheel | 21 | 11:00 | 176 | Sreepur | 88 | 18:30
45 | Cumilla(S) | 135 | 18:00 | 111 | Metrorail_Uttara | 6 | 13:00 | 177 | Srinagar | 39.65 | 00:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 121 | 12:00 | 178 | Sunamganj | 60 | 00:00
47 | Daudkandi | 134 | 01:00 | 113 | Mirpur | 112 | 18:00 | 179 | Sylhet | 48 | 18:30
48 | DhakaUniversity | 70 | 13:00 | 114 | Mirsorai | 11 | 09:00 | 180 | Sylhet-132 | 108 | 18:00
49 | Dhamrai | 128 | 18:00 | 115 | Mirzapur | 46 | 18:00 | 181 | TK | 24 | 21:00
50 | Dhanmondi | 110 | 13:00 | 116 | Mithapukur | 68 | 18:00 | 182 | Tangail | 158 | 18:30
51 | Dohazari | 101 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 23 | 19:00
52 | Faridpur | 153 | 18:30 | 118 | Mogbazar | 74.3 | 13:00 | 184 | Thakurgaon | 98 | 19:00
53 | Fatullah | 101 | 12:00 | 119 | Mongla | 29 | 11:00 | 185 | Tongi | 121 | 11:00
54 | Fenchuganj | 44 | 00:00 | 120 | Motijheel | 39 | 18:30 | 186 | Ullahpara | 36 | 18:30
55 | Feni | 108 | 19:00 | 121 | Muktagacha | 33 | 18:00 | 187 | Ullon | 55 | 13:00
56 | GPH | 80 | 16:00 | 122 | Munshiganj | 100 | 00:00 | 188 | Uttara | 58 | 13:00
57 | Ghatail | 80 | 18:00 | 123 | Muradnagar | 38 | 11:00 | 189 | UttaraNew | 65 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 173 | 00:00 | 190 | Zigatola | 64 | 20:00
59 | Ghorashal-230 | 94 | 18:30 | 125 | Naogaon | 117 | 20:00
60 | Goalpara | 24 | 18:30 | 126 | Narail | 54 | 18:30
61 | Gollamari | 86 | 13:00 | 127 | Narinda | 54 | 13:00
62 | Gopalganj | 96 | 18:30 | 128 | Narshingdi | 162 | 00:00
63 | Gulshan | 88 | 13:00 | 129 | Natore | 153 | 18:30
64 | Halishahar | 82 | 15:00 | 130 | Nawabganj | 42.4 | 21:00
65 | HaripurSBU | 129 | 12:00 | 131 | Netrakona | 124 | 00:00
66 | Hasnabad | 72 | 11:00 | 132 | New | 51.4 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12627.51 | 0 |  | 12627.51
1:00 | 12358.73 | 0 |  | 12358.73
2:00 | 11857.6 | 0 |  | 11857.6
3:00 | 11439.57 | 0 |  | 11439.57
4:00 | 11197.45 | 0 |  | 11197.45
5:00 | 10895.21 | 0 |  | 10895.21
6:00 | 10736.35 | 0 |  | 10736.35
7:00 | 10848.59 | 0 |  | 10848.59
8:00 | 10731.61 | 0 |  | 10731.61
9:00 | 10725.43 | 0 |  | 10725.43
10:00 | 10794.87 | 0 |  | 10794.87
11:00 | 11124.32 | 0 |  | 11124.32
12:00 | 11783.91 | 0 |  | 11783.91
13:00 | 11954.65 | 0 |  | 11954.65
14:00 | 11781.92 | 0 |  | 11781.92
15:00 | 11821.63 | 0 |  | 11821.63
16:00 | 11727.92 | 0 |  | 11727.92
17:00 | 11782.53 | 0 |  | 11782.53
18:00 | 13235.7 | 38 |  | 13275.7
19:00 | 14102.2 | 47 |  | 14151.2
19:30 | 13944.82 | 34 |  | 13980.82
20:00 | 13882.94 | 27 |  | 13910.94
21:00 | 13693.58 | 0 |  | 13693.58
22:00 | 13577.85 | 0 |  | 13577.85
23:00 | 13505.78 | 0 |  | 13505.78
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6715 | 5912.51 | 12627.51 | DAILY GENERATION CURVE
00:30 | 6599.5 | 5893.62 | 12493.12
01:00 | 6484 | 5874.73 | 12358.73 | 11-10-2025
01:30 | 6326.5 | 5781.665 | 12108.165
02:00 | 6169 | 5688.6 | 11857.6
02:30 | 6076.5 | 5572.085 | 11648.585
03:00 | 5984 | 5455.57 | 11439.57
03:30 | 5929.5 | 5389.01 | 11318.51
04:00 | 5875 | 5322.45 | 11197.45
04:30 | 5810 | 5236.33 | 11046.33
05:00 | 5745 | 5150.21 | 10895.21
05:30 | 5708.53 | 5107.25 | 10815.78
06:00 | 5672.06 | 5064.29 | 10736.35
06:30 | 5631.94 | 5160.53 | 10792.47
07:00 | 5591.82 | 5256.77 | 10848.59
07:30 | 5568.76 | 5221.34 | 10790.1
08:00 | 5545.7 | 5185.91 | 10731.61
08:30 | 5556.305 | 5172.215 | 10728.52
09:00 | 5566.91 | 5158.52 | 10725.43
09:30 | 5566.715 | 5193.435 | 10760.15
10:00 | 5566.52 | 5228.35 | 10794.87
10:30 | 5689.15 | 5270.445 | 10959.595
11:00 | 5811.78 | 5312.54 | 11124.32
11:30 | 5958.22 | 5495.895 | 11454.115
12:00 | 6104.66 | 5679.25 | 11783.91
12:30 | 6128.745 | 5740.535 | 11869.28
13:00 | 6152.83 | 5801.82 | 11954.65
13:30 | 6106.99 | 5761.295 | 11868.285
14:00 | 6061.15 | 5720.77 | 11781.92
14:30 | 6101.715 | 5700.06 | 11801.775
15:00 | 6142.28 | 5679.35 | 11821.63
15:30 | 6115.03 | 5659.745 | 11774.775
16:00 | 6087.78 | 5640.14 | 11727.92
16:30 | 6151.41 | 5603.815 | 11755.225
17:00 | 6215.04 | 5567.49 | 11782.53
17:30 | 6634.52 | 5874.595 | 12509.115
18:00 | 7054 | 6181.7 | 13235.7
18:30 | 7395.25 | 6273.7 | 13668.95
19:00 | 7736.5 | 6365.7 | 14102.2
19:30 | 7569.5 | 6375.32 | 13944.82
20:00 | 7556.5 | 6326.44 | 13882.94
20:30 | 7475.25 | 6313.01 | 13788.26 |  | Executive Engineer
21:00 | 7394 | 6299.58 | 13693.58 |  | Network Operation Division
21:30 | 7367.25 | 6268.465 | 13635.715
22:00 | 7340.5 | 6237.35 | 13577.85
22:30 | 7323.75 | 6218.065 | 13541.815
23:00 | 7307 | 6198.78 | 13505.78

## En-Curve
QF-LDC-12
Date | 11-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3001 | 1884 | 901 | 38 | 76 | 1315.51 | 222 | 3779 | 0 | 422 | 983 | 0 | 0 | 6 | 0 | DAILY ENERGY CURVE
00:30 | 2986.5 | 1882.5 | 901 | 38 | 72 | 1312.62 | 222 | 3787.5 | 0 | 374.5 | 913 | 0 | 0 | 3.5 | 0 | 11-10-2025
01:00 | 2972 | 1881 | 901 | 38 | 68 | 1309.73 | 222 | 3796 | 0 | 327 | 843 | 0 | 0 | 1 | 0
01:30 | 2834.5 | 1917.5 | 900.5 | 38 | 69 | 1312.165 | 222 | 3787 | 0 | 236 | 786.5 | 0 | 0 | 5 | 0 | Energy Generated | 290.1168 |  | MKWHr
02:00 | 2697 | 1954 | 900 | 38 | 70 | 1314.6 | 222 | 3778 | 0 | 145 | 730 | 0 | 0 | 9 | 0 | Energy not Served | 0.112 |  | MKWHr
02:30 | 2719 | 1990 | 900.5 | 38 | 68 | 1270.585 | 221 | 3712.5 | 0 | 123.5 | 595.5 | 0 | 0 | 10 | 0 | Total Energy Requirement | 290.2288 |  | MKWHr
03:00 | 2741 | 2026 | 901 | 38 | 66 | 1226.57 | 220 | 3647 | 0 | 102 | 461 | 0 | 0 | 11 | 0
03:30 | 2717.5 | 2062.5 | 901 | 38 | 65 | 1223.01 | 219 | 3603.5 | 0 | 85 | 393 | 0 | 0 | 11 | 0
04:00 | 2694 | 2099 | 901 | 38 | 64 | 1219.45 | 218 | 3560 | 0 | 68 | 325 | 0 | 0 | 11 | 0
04:30 | 2734.5 | 2125 | 901 | 38 | 65 | 1172.83 | 218 | 3534 | 0 | 42.5 | 207 | 0 | 0 | 8.5 | 0
05:00 | 2775 | 2151 | 901 | 38 | 66 | 1126.21 | 218 | 3508 | 0 | 17 | 89 | 0 | 0 | 6 | 0
05:30 | 2730 | 2146 | 901 | 38 | 62 | 1120.25 | 218 | 3488 | 0.03 | 17 | 89 | 0 | 0 | 6.5 | 0
06:00 | 2685 | 2141 | 901 | 38 | 58 | 1114.29 | 218 | 3468 | 0.06 | 17 | 89 | 0 | 0 | 7 | 0
06:30 | 2546.5 | 2196 | 901 | 38 | 55 | 1141.535 | 219 | 3533.5 | 39.935 | 21 | 97 | 0 | 0 | 4 | 0
07:00 | 2408 | 2251 | 901 | 38 | 52 | 1168.78 | 220 | 3599 | 79.81 | 25 | 105 | 0 | 0 | 1 | 0
07:30 | 2396.5 | 2176.5 | 901.5 | 38 | 54 | 1166.97 | 200 | 3574.5 | 143.13 | 29.5 | 108.5 | 0 | 0 | 1 | 0
08:00 | 2385 | 2102 | 902 | 38 | 56 | 1165.16 | 180 | 3550 | 206.45 | 34 | 112 | 0 | 0 | 1 | 0
08:30 | 2373.5 | 2098.5 | 902 | 38 | 59 | 1165.58 | 180 | 3466.5 | 249.44 | 59.5 | 135.5 | 0 | 0 | 1 | 0
09:00 | 2362 | 2095 | 902 | 38 | 62 | 1166 | 180 | 3383 | 292.43 | 85 | 159 | 0 | 0 | 1 | 0
09:30 | 2392.5 | 2109 | 901.5 | 38 | 59 | 1116.5 | 180 | 3292.5 | 364.15 | 101 | 204 | 0 | 0 | 2 | 0
10:00 | 2423 | 2123 | 901 | 38 | 56 | 1067 | 180 | 3202 | 435.87 | 117 | 249 | 0 | 0 | 3 | 0
10:30 | 2510.5 | 2163.5 | 901.5 | 38 | 56 | 1067 | 180 | 3243.5 | 447.095 | 107 | 244 | 0 | 0 | 1.5 | 0
11:00 | 2598 | 2204 | 902 | 38 | 56 | 1067 | 180 | 3285 | 458.32 | 97 | 239 | 0 | 0 | 0 | 0
11:30 | 2592 | 2242.25 | 901.5 | 38 | 55 | 1112 | 180 | 3429 | 534.865 | 112.5 | 256.5 | 0 | 0 | 0.5 | 0
12:00 | 2586 | 2280.5 | 901 | 38 | 54 | 1157 | 180 | 3573 | 611.41 | 128 | 274 | 0 | 0 | 1 | 0
12:30 | 2546.5 | 2232.5 | 901 | 38 | 56 | 1212.5 | 180 | 3619.5 | 574.78 | 142 | 354.5 | 0 | 0 | 12 | 0
13:00 | 2507 | 2184.5 | 901 | 38 | 58 | 1268 | 180 | 3666 | 538.15 | 156 | 435 | 0 | 0 | 23 | 0
13:30 | 2502 | 2102.25 | 901.5 | 38 | 59 | 1267.29 | 180 | 3669.5 | 501.245 | 156 | 464.5 | 0 | 0 | 27 | 0
14:00 | 2497 | 2020 | 902 | 38 | 60 | 1266.58 | 180 | 3673 | 464.34 | 156 | 494 | 0 | 0 | 31 | 0
14:30 | 2555.5 | 2040.5 | 901.5 | 38 | 63 | 1264.665 | 181 | 3680.5 | 389.11 | 152 | 511 | 0 | 0 | 25 | 0
15:00 | 2614 | 2061 | 901 | 38 | 66 | 1262.75 | 182 | 3688 | 313.88 | 148 | 528 | 0 | 0 | 19 | 0
15:30 | 2611.5 | 1984.5 | 901 | 38 | 59 | 1262.345 | 181 | 3683.5 | 255.93 | 148 | 634 | 0 | 0 | 16 | 0
16:00 | 2609 | 1908 | 901 | 38 | 52 | 1261.94 | 180 | 3679 | 197.98 | 148 | 740 | 0 | 0 | 13 | 0
16:30 | 2596 | 1885.5 | 901 | 38 | 56 | 1265.235 | 199 | 3689 | 118.99 | 181 | 818 | 0 | 0 | 7.5 | 0
17:00 | 2583 | 1863 | 901 | 38 | 60 | 1268.53 | 218 | 3699 | 40 | 214 | 896 | 0 | 0 | 2 | 0
17:30 | 2677.5 | 1859 | 901.5 | 38 | 65 | 1313.615 | 218 | 3729.5 | 20 | 406.5 | 1279.5 | 0 | 0 | 1 | 19
18:00 | 2772 | 1855 | 902 | 38 | 70 | 1358.7 | 218 | 3760 | 0 | 599 | 1663 | 0 | 0 | 0 | 38
18:30 | 2703 | 1891 | 901.5 | 38 | 69 | 1357.7 | 218 | 3829.5 | 0 | 643.5 | 2017.75 | 0 | 0 | 0 | 42.5
19:00 | 2634 | 1927 | 901 | 38 | 68 | 1356.7 | 218 | 3899 | 0 | 688 | 2372.5 | 0 | 0 | 0 | 47
19:30 | 2677 | 1897 | 901 | 38 | 60 | 1365.32 | 218 | 3897 | 0 | 635 | 2256.5 | 0 | 0 | 0 | 34
20:00 | 2712 | 1888 | 835 | 38 | 66 | 1359.44 | 220 | 3896 | 0 | 638 | 2230.5 | 0 | 0 | 0 | 27
20:30 | 2742.5 | 1869.75 | 868.5 | 38 | 66 | 1356.01 | 220 | 3898 | 0 | 628 | 2099.5 | 0 | 0 | 2 | 13.5
21:00 | 2773 | 1851.5 | 902 | 38 | 66 | 1352.58 | 220 | 3900 | 0 | 618 | 1968.5 | 0 | 0 | 4 | 0
21:30 | 2838 | 1853.5 | 901.5 | 38 | 64 | 1356.965 | 220 | 3898.5 | 0 | 614 | 1846.25 | 0 | 0 | 5 | 0
22:00 | 2903 | 1855.5 | 901 | 38 | 62 | 1361.35 | 220 | 3897 | 0 | 610 | 1724 | 0 | 0 | 6 | 0
22:30 | 2930 | 1847.25 | 901 | 38 | 63 | 1355.565 | 220 | 3898 | 0 | 606 | 1676 | 0 | 0 | 7 | 0
23:00 | 2957 | 1839 | 901 | 38 | 64 | 1349.78 | 220 | 3899 | 0 | 602 | 1628 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 06:00 | 376 | 16:00 | Payra | 411 | 08:00 | 407 | 13:00
Ashuganj | 403 | 10:00 | 369 | 16:00 | Rahanpur | 404 | 10:00 | 395 | 02:00
Bhulta | 401 | 23:00 | 369 | 16:00 | Rampal | 403 | 09:00 | 390 | 18:30
Bibiana | 390 | 08:00 | 383 | 01:00
BIPTC | 403 | 05:00 | 393 | 19:00
Bogura | 394 | 10:00 | 384 | 00:00
Gopalganj | 398 | 06:00 | 387 | 18:30
Kaliakoir | 378 | 07:00 | 365 | 16:00
Madunaghat | 398 | 18:30 | 388 | 16:00
Meghnaghat | 391 | 06:00 | 379 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 06:00 | 224 | 13:00 | Kaliakoir | 235 | 05:00 | 226 | 16:00
AKSML | 233 | 19:30 | 226 | 16:00 | Keranigonj | 228 | 04:00 | 221 | 16:00
Aminbazar | 232 | 06:00 | 225 | 16:00 | Khulna(S) | 231 | 06:00 | 218 | 18:30
Ashuganj | 233 | 23:00 | 223 | 15:00 | Madunaghat | 236 | 18:30 | 228 | 15:00
Ashuganj-400 | 233 | 23:00 | 223 | 15:00 | Madunaghat-400 | 236 | 20:00 | 230 | 12:00
Baghabari | 233 | 06:00 | 224 | 12:00 | Maniknagar | 225 | 03:00 | 218 | 16:00
Barapukuria | 223 | 21:00 | 218 | 13:00 | Meghnaghat | 232 | 08:00 | 224 | 15:00
Barapukuria-230 | 223 | 21:00 | 218 | 13:00 | Meghnaghat-400 | 228 | 06:00 | 220 | 16:00
Barishal | 235 | 06:00 | 231 | 00:00 | Mirsorai | 237 | 19:00 | 224 | 15:00
Bheramara | 235 | 20:00 | 223 | 13:00 | Rajshahi | 233 | 20:00 | 219 | 13:00
Bhulta | 229 | 07:00 | 213 | 16:00 | Rampal | 231 | 09:00 | 219 | 18:30
Bibiana | 230 | 07:00 | 224 | 01:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 236 | 06:00 | 223 | 13:00 | Rampura | 230 | 23:00 | 212 | 15:00
Bogura | 236 | 10:00 | 228 | 13:00 | Shikalbaha | 235 | 19:00 | 225 | 15:00
Bogura-400 | 235 | 06:00 | 229 | 00:00 | Shyampur | 227 | 06:00 | 220 | 16:00
Borhanuddin | 238 | 06:00 | 234 | 00:00 | Siddhirganj | 225 | 04:00 | 218 | 16:00
BSRM | 234 | 19:00 | 224 | 15:00 | Sirajgonj | 239 | 06:00 | 233 | 13:00
Cumilla(N) | 228 | 07:00 | 220 | 16:00 | Sreepur | 229 | 23:00 | 221 | 16:00
Faridpur | 232 | 06:00 | 225 | 18:00 | Tongi | 231 | 23:00 | 219 | 15:00
Fenchuganj | 233 | 09:00 | 224 | 15:00
Ghorashal | 235 | 01:00 | 225 | 12:00
Ghorashal-230 | 230 | 23:00 | 216 | 13:00
Gopalganj | 238 | 12:00 | 227 | 18:30
GPH | 234 | 19:00 | 223 | 19:30
Haripur | 225 | 06:00 | 219 | 16:00
Hasnabad | 229 | 06:00 | 221 | 16:00
Hathazari | 233 | 18:30 | 226 | 15:00
Ishurdi | 235 | 06:00 | 225 | 13:00
Jhenaidah | 232 | 09:00 | 218 | 18:30
Kachua | 222 | 18:00 | 211 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 07:00 | 125 | 16:00 | Lalmonirhat | 130 | 17:00 | 121 | 14:00
Agargaon | 137 | 06:00 | 131 | 13:00 | Madanganj | 129 | 00:00 | 126 | 16:00
Agrabad | 134 | 21:00 | 128 | 15:00 | Madaripur | 137 | 09:00 | 133 | 00:00
AKS | 132 | 18:30 | 128 | 12:00 | Madartek | 136 | 06:00 | 124 | 16:00
Aminbazar | 137 | 04:00 | 133 | 11:00 | Madunaghat | 136 | 19:00 | 132 | 11:00
Amnura | 137 | 09:00 | 126 | 13:00 | Magura | 137 | 09:00 | 125 | 16:00
Ashuganj | 142 | 07:00 | 137 | 00:00 | Mahasthangarh | 131 | 06:00 | 126 | 13:00
Bagerhat | 134 | 09:00 | 118 | 18:30 | Maijdee | 133 | 13:00 | 127 | 00:00
Bajitpur | 133 | 07:00 | 126 | 16:00 | Manikganj | 133 | 06:00 | 121 | 16:00
Bakulia | 135 | 19:00 | 130 | 15:00 | Maniknagar | 136 | 03:00 | 131 | 13:00
Banani | 137 | 06:00 | 126 | 14:00 | Matarbari | 120 | 00:00 | 111 | 18:00
Bangabhaban | 136 | 05:00 | 131 | 16:00 | Matuail | 131 | 05:00 | 126.4 | 16:00
Barapukuria | 136 | 00:00 | 128 | 13:00 | Metrorail_Motijheel | 136 | 03:00 | 131 | 13:00
Barguna | 136 | 07:00 | 133 | 00:00 | Metrorail_Uttara | 136 | 04:00 | 124 | 16:00
Barishal | 136 | 19:30 | 132 | 00:00 | Millgate | 135 | 04:00 | 124 | 16:00
Barishal-230 | 136 | 06:00 | 132 | 00:00 | Mirpur | 136 | 04:00 | 131 | 12:00
Baroaulia | 134 | 00:00 | 129 | 15:00 | Mirzapur | 132 | 09:00 | 125 | 16:00
Baroirhat | 133 | 19:00 | 125 | 01:00 | Mithapukur | 130 | 01:00 | 123 | 14:00
Bashundhara | 136 | 06:00 | 126 | 14:00 | MI_Cement | 132 | 05:00 | 127 | 16:00
BashundharaCement | 129 | 00:00 | 126 | 16:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 131 | 09:00 | 124 | 00:00 | Mogbazar | 137 | 05:00 | 127 | 16:00
Benapole | 134 | 10:00 | 120 | 18:30 | Mongla | 134 | 09:00 | 120 | 18:30
Bhaluka | 130 | 07:00 | 125 | 14:00 | Motijheel | 136 | 04:00 | 131 | 16:00
Bhandaria | 133 | 09:00 | 112 | 18:30 | Muktagacha | 133 | 10:00 | 120 | 00:00
Bhangura | 133 | 06:00 | 128 | 13:00 | Munshiganj | 131 | 06:00 | 126 | 16:00
Bheramara | 136 | 09:00 | 128 | 13:00 | Muradnagar | 132 | 10:00 | 125 | 01:00
Bheramara(GK) | 136 | 09:00 | 128 | 13:00 | Mymensingh | 134 | 10:00 | 118 | 00:00
Bhulta | 129 | 05:00 | 125 | 11:00 | Naogaon | 128 | 09:00 | 118 | 00:00
Bog-Sherpur | 135 | 20:00 | 127 | 13:00 | Narail | 137 | 09:00 | 125 | 18:00
Bogura | 134 | 09:00 | 30 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
Bogura-230 | 133 | 06:00 | 129 | 00:00 | Narshingdi | 134 | 09:00 | 122 | 16:00
Brahmanbaria | 136 | 09:00 | 128 | 01:00 | Natore | 133 | 06:00 | 126 | 13:00
Cantonment | 136 | 03:00 | 131 | 13:00 | Nawabganj | 136 | 06:00 | 131 | 16:00
Chandina | 133 | 07:00 | 129 | 01:00 | Netrakona | 128 | 04:00 | 117 | 18:00
Chandpur | 140 | 13:00 | 132 | 05:00 | New | 136 | 04:00 | 126 | 15:00
Chandraghona | 136 | 18:30 | 132 | 16:00 | Niamatpur | 138 | 10:00 | 133 | 00:00
Chapai | 136 | 05:00 | 132 | 00:00 | Noapara | 136 | 09:00 | 124 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 06:00 | 127 | 13:00 | Pabna | 134 | 06:00 | 127 | 13:00
Chauddagram | 134 | 19:00 | 128 | 00:00 | Palashbari | 129 | 17:00 | 123 | 10:00
Chhatak | 130 | 09:00 | 118 | 00:00 | Panchagarh | 137 | 21:00 | 120 | 14:00
Chowmuhani | 133 | 13:00 | 128 | 00:00 | Patiya | 133 | 00:00 | 129 | 05:00
Chuadanga | 135 | 09:00 | 122 | 18:30 | Patuakhali | 137 | 17:00 | 134 | 01:00
Coxsbazar | 120 | 09:00 | 111 | 18:00 | Payra | 137 | 06:00 | 135 | 18:00
Cumilla(N) | 133 | 07:00 | 129 | 16:00 | PHP | 132 | 19:00 | 126 | 01:00
Cumilla(S) | 134 | 19:00 | 128 | 15:00 | Postogola | 135 | 05:00 | 130 | 16:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 06:00 | 126 | 14:00
Daudkandi | 129 | 09:00 | 123 | 16:00 | Purbasadipur | 132 | 01:00 | 118 | 14:00
DhakaUniversity | 136 | 06:00 | 127 | 15:00 | Rahanpur | 138 | 04:00 | 135 | 00:00
Dhamrai | 135 | 05:00 | 129 | 15:00 | Rahanpur-400 | 139 | 06:00 | 136 | 00:00
Dhanmondi | 137 | 07:00 | 128 | 13:00 | Rahim | 131 | 05:00 | 127 | 15:00
Dohazari | 130 | 19:30 | 125 | 12:00 | Rajbari | 136 | 06:00 | 130 | 18:30
Faridpur | 136 | 06:00 | 133 | 13:00 | Rajendrapur | 138 | 23:00 | 124 | 17:00
Fatullah | 139 | 06:00 | 134 | 12:00 | Rajshahi | 133 | 06:00 | 127 | 16:00
Fenchuganj | 138 | 09:00 | 132 | 01:00 | Rajshahi-230 | 133 | 09:00 | 125 | 13:00
Feni | 133 | 19:00 | 119 | 18:00 | Ramganj | 134 | 13:00 | 128 | 00:00
Ghatail | 131 | 09:00 | 120 | 00:00 | Rampur | 133 | 03:00 | 129 | 11:00
Ghorashal | 139 | 00:00 | 130 | 15:00 | Rampura | 136 | 00:00 | 126 | 15:00
Goalpara | 138 | 09:00 | 127 | 18:30 | Rangamati | 135 | 19:00 | 131 | 11:00
Gollamari | 137 | 09:00 | 128 | 18:30 | Rangpur | 131 | 20:00 | 126 | 14:00
Gopalganj | 135 | 06:00 | 128 | 18:30 | Ruppur | 137 | 08:00 | 130 | 13:00
Gopalganj-400 | 137 | 06:00 | 133 | 18:00 | Saidpur | 131 | 00:00 | 121 | 14:00
Gulshan | 136 | 03:00 | 126 | 15:00 | Satkhira | 136 | 10:00 | 121 | 18:30
Halishahar | 135 | 19:00 | 129 | 15:00 | Satmasjid | 136 | 05:00 | 130 | 13:00
Haripur | 132 | 06:00 | 127 | 16:00 | Savar | 135 | 04:00 | 130 | 11:00
HaripurSBU | 132 | 06:00 | 127 | 17:00 | SevenRings | 139 | 23:00 | 130 | 15:00
Hasnabad | 135 | 03:00 | 130 | 16:00 | ShahCement | 132 | 06:00 | 127 | 13:00
Hathazari | 137 | 18:30 | 132 | 12:00 | Shahjadpur | 137 | 06:00 | 132 | 00:00
Ishurdi | 137 | 06:00 | 130 | 13:00 | Shahjibazar | 137 | 09:00 | 129 | 00:00
Jaldhaka | 130 | 02:00 | 119 | 13:00 | Shahmirpur | 135 | 19:00 | 130 | 12:00
Jamalpur | 135 | 10:00 | 118 | 00:00 | Shariatpur | 136 | 06:00 | 131 | 18:00
Jashore | 136 | 22:00 | 122 | 18:30 | Sherpur | 133 | 10:00 | 114 | 00:00
Jhenaidah | 137 | 06:00 | 119 | 18:00 | Shikalbaha | 125 | 19:00 | 119 | 15:00
Jhenaidah-230 | 138 | 10:00 | 127 | 18:30 | Shikalbaha-230 | 136 | 19:00 | 130 | 15:00
Joydebpur | 137 | 22:00 | 125 | 16:00 | Shitalakhya | 132 | 05:00 | 127 | 16:00
Joypurhat | 126 | 10:00 | 115 | 00:00 | Sholosohor | 136 | 19:00 | 131 | 15:00
Juldah | 135 | 18:30 | 130 | 11:00 | Shyampur | 139 | 04:00 | 135 | 12:00
Kabirpur | 134 | 07:00 | 124 | 16:00 | Shyampur-230 | 138 | 04:00 | 133 | 16:00
Kachua | 140 | 12:00 | 134 | 00:00 | Siddhirganj | 132 | 07:00 | 128 | 15:00
Kaliakoir | 137 | 06:00 | 129 | 16:00 | Sirajganj | 132 | 06:00 | 126 | 13:00
Kallyanpur | 137 | 04:00 | 131 | 13:00 | Sonargaon | 130 | 06:00 | 125 | 16:00
Kalurghat | 137 | 19:00 | 132 | 11:00 | Sreemongol | 135 | 07:00 | 128 | 01:00
Kamrangirchar | 136 | 05:00 | 130 | 15:00 | Sreepur | 133 | 06:00 | 126 | 16:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 136 | 06:00 | 132 | 12:00
Kasba | 132 | 10:00 | 125 | 00:00 | SSM | 139 | 22:00 | 134 | 16:00
Kazla | 136 | 06:00 | 130 | 17:00 | Sunamganj | 129 | 10:00 | 116 | 01:00
Keranigonj | 136 | 04:00 | 132 | 13:00 | Sylhet | 132 | 09:00 | 124 | 01:00
Khagrachori | 134 | 19:00 | 130 | 11:00 | Sylhet-132 | 132 | 08:00 | 125 | 00:00
Khulna | 137 | 09:00 | 129 | 18:00 | Tangail | 131 | 09:00 | 120 | 18:30
Khulna(S) | 138 | 09:00 | 127 | 18:30 | Taraganj | 130 | 00:00 | 122 | 13:00
Khulshi | 133 | 19:00 | 128 | 11:00 | Thakurgaon | 135 | 01:00 | 117 | 14:00
Kishoreganj | 132 | 09:00 | 123 | 18:00 | TK | 136 | 18:30 | 131 | 15:00
Kodda | 137 | 22:00 | 123 | 16:00 | Tongi | 137 | 07:00 | 128 | 15:00
KSRM | 135 | 00:00 | 130 | 12:00 | Ullahpara | 134 | 06:00 | 128 | 13:00
Kulaura | 137 | 09:00 | 131 | 03:00 | Ullon | 135 | 00:00 | 126 | 15:00
Kurigram | 129 | 06:00 | 122 | 14:00 | Uttara | 134 | 04:00 | 125 | 16:00
Kushtia | 133 | 09:00 | 123 | 18:00 | UttaraNew | 136 | 03:00 | 124 | 16:00
Laksam | 138 | 09:00 | 133 | 00:00 | Zigatola | 138 | 06:00 | 130 | 15:00
Lakshmipur | 133 | 19:00 | 126 | 00:00
Lalbag | 136 | 04:00 | 131 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division