## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-10-2025 | during | 14-10-2025 | during | 14-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 46 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 36 | 97 | 208.13 | 208.13 | 100 | 100 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 51 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 92 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 17 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 277 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 145 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 555 | 550 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6657.724 | 2391 | 2642 | 5436.65 | 5403.65 | 3718.36 | 3779.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 24 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 3 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 19 | 19 | 50 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 209 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 136 | 200 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 31 | 54 | 40 | 60 | 40 | 60 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 49 | 49 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 63 | 104 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.76 | 0 | 3.11 | 0 | 3.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 16 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | 49 | 49 | FGMO
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 95 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 47 | 92 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 160 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1192 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 5 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2254.12 | 2592.86 | 3211.83 | 3222.72 | 2989.61 | 3000.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 177 | 204 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 290 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 250 | 260 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 10 | 10 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 2 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 115 | 132 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 102 | 163 | 163 | 108 | 108 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 53 | 157 | 200 | 200 | 50 | 150 | Engine Problem
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 76 | 160 | 160 | 76 | 76 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 25 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 26 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1290 | 1568 | 2828.86 | 2763.86 | 2262.16 | 2306.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-10-2025 | during | 14-10-2025 | during | 14-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 27 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.92 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 202.92 | 171 | 400.9 | 349 | 239.9 | 188
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 10 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 68 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 156 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 325 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 326 | 334 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1114 | 1148 | 1223 | 1223 | 1174 | 1174
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 162 | 145 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74.74 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 364 | 364 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1530.74 | 1523 | 2772 | 2682 | 2575 | 2485
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 308 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 1 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1150 | 1203 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2087.48 | 2298 | 2147 | 2146 | 1964 | 1963
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 50.44 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 162 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 403 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 55 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.58 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 744.14 | 757.08 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.57 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1572.73 | 1773.08 | 2498.59 | 2331.99 | 2425.21 | 2258.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 47 | 48 | 48 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 160 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 99 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 157 | 0 | 179.12 | 0 | 179.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 602.7 | 435 | 661.12 | 446 | 661.12 | 446
System Total |  |  |  |  | 28823.2 | 28365.955 | 13045.69 | 14150.94 | 21179.95 | 20568.22 | 18009.36 | 17600.63
Forecast Scenario (14-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13820 |  | 0 |  | 13820
|  |  |  | 1:00 | 13350 |  | 0 |  | 13350
|  |  |  | 2:00 | 12850 |  | 0 |  | 12850
|  |  |  | 3:00 | 12270 |  | 0 |  | 12270
|  |  |  | 4:00 | 11870 |  | 0 |  | 11870
|  |  |  | 5:00 | 11670 |  | 0 |  | 11670
|  |  |  | 6:00 | 11190 |  | 0 |  | 11190
|  |  |  | 7:00 | 11480 |  | 0 |  | 11480
|  |  |  | 8:00 | 11570 |  | 0 |  | 11570
|  |  |  | 9:00 | 11690 |  | 0 |  | 11690
|  |  |  | 10:00 | 12060 |  | 0 |  | 12060
|  |  |  | 11:00 | 12500 |  | 0 |  | 12500
|  |  |  | 12:00 | 13140 |  | 0 |  | 13140
|  |  |  | 13:00 | 13480 |  | 0 |  | 13480
|  |  |  | 14:00 | 13490 |  | 0 |  | 13490
|  |  |  | 15:00 | 13680 |  | 0 |  | 13680
|  |  |  | 16:00 | 13440 |  | 0 |  | 13440
|  |  |  | 17:00 | 13170 |  | 0 |  | 13170
|  |  |  | 18:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14250 |  | 0 |  | 14250
|  |  |  | 19:30 | 14550 |  | 0 |  | 14550
|  |  |  | 20:00 | 14500 |  | 0 |  | 14500
|  |  |  | 21:00 | 14400 |  | 0 |  | 14400
|  |  |  | 22:00 | 14200 |  | 0 |  | 14200
|  |  |  | 23:00 | 14100 |  | 0 |  | 14100
Probable Maximum Temperature: |  |  | 33.50°C
Probable Maximum Demand at Day Peak: |  |  | 13140.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.27 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:26 hrs on 14-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-10-2025 | [28 empty] | Date: | 13-10-2025 | [28 empty] | Date: | 13-10-2025 | [28 empty] | Date: | 13-10-2025 | [28 empty] | Date: | 13-10-2025 | [14 empty] | Date: | 13-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 127 | 277 | 55 | 0 | 54 | 0 | 450 | 0 | 530 | 0 | 0 | 335 | 99 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 90 | 52 | 105 | 0 | 0 | 50 | 61 | 54.36 | 0 | 0 | 0 | 219 | 94 | 12 | 285 | 17 | 0 | 19 | 25.5 | 0 | 104 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 290 | 250 | 0 | 179 | 0 | 34 | 105 | 105 | 0 | 16 | 103 | 68 | 43 | 0 | 29 | 310 | 0 | 341 | 30 | 68 | 158 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 57 | 33 | 0 | 0 | 6 | 7550.36 | 902 | 168 | 0 | 31 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 767.16 | 0 | 40 | 0 | 113 | 113 | 0 | 89 | 37 | 0 | 0 | 0 | 26 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 146 | 45 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 308 | 1227 | 35 | 6080.16 | 13630.52 | 107.25
01:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 90 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 525 | 0 | 35 | 335 | 99 | 0 | 0 | 125 | 21.5 | 22 | 0 | 0 | 91 | 16 | 104 | 0 | 0 | 50 | 61 | 54.36 | 0 | 0 | 0 | 220 | 95 | 12 | 285 | 17 | 0 | 19 | 25.5 | 0 | 104 | 0 | 0 | 0 | 1155 | 0 | 51 | 137 | 0 | 0 | 290 | 250 | 0 | 187 | 0 | 34 | 105 | 82 | 0 | 16 | 75 | 66 | 43 | 0 | 29 | 310 | 0 | 338 | 30 | 68 | 157 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 48 | 33 | 0 | 0 | 6 | 7331.36 | 894 | 168 | 0 | 19 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 757.1 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 148 | 46 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 277 | 115 | 220 | 0 | 308 | 1222 | 35 | 5921.1 | 13252.46 | 107.24
02:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 60 | 277 | 30 | 0 | 35 | 0 | 450 | 0 | 510 | 0 | 35 | 335 | 99 | 0 | 0 | 108 | 21.5 | 22 | 0 | 0 | 84 | 16 | 94 | 0 | 0 | 50 | 61 | 17 | 0 | 0 | 0 | 220 | 93 | 15 | 285 | 17 | 0 | 19 | 8 | 0 | 104 | 0 | 0 | 0 | 1145 | 0 | 51 | 135 | 0 | 0 | 290 | 250 | 0 | 186 | 0 | 34 | 105 | 52 | 0 | 16 | 49 | 70 | 25 | 0 | 29 | 305 | 0 | 320 | 30 | 68 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 48 | 34 | 0 | 0 | 6 | 7061.5 | 894 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 742 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 147 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 273 | 115 | 220 | 0 | 308 | 1218 | 35 | 5690 | 12751.5 | 107.24
03:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 121 | 15 | 195 | 15 | 0 | 35 | 0 | 450 | 0 | 520 | 0 | 35 | 335 | 99 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 30 | 16 | 50 | 0 | 0 | 50 | 61 | 17 | 0 | 0 | 0 | 218 | 94 | 25 | 285 | 0 | 0 | 19 | 0 | 0 | 104 | 0 | 0 | 0 | 1160 | 0 | 51 | 130 | 0 | 0 | 290 | 250 | 0 | 195 | 0 | 45 | 105 | 51 | 0 | 16 | 0 | 68 | 0 | 0 | 29 | 305 | 0 | 328 | 30 | 68 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 48 | 34 | 0 | 0 | 0 | 6655.5 | 894 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 742 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 47 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 308 | 1219 | 35 | 5515 | 12170.5 | 107.24
04:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 195 | 15 | 0 | 35 | 0 | 450 | 0 | 520 | 0 | 35 | 335 | 100 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 218 | 95 | 25 | 285 | 0 | 0 | 19 | 0 | 0 | 110 | 0 | 0 | 0 | 1150 | 0 | 51 | 133 | 0 | 0 | 290 | 250 | 0 | 195 | 0 | 51 | 104 | 51 | 0 | 16 | 0 | 64 | 0 | 0 | 0 | 315 | 0 | 338 | 30 | 68 | 155 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 34 | 0 | 0 | 0 | 6446.5 | 894 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 47 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 308 | 1219 | 35 | 5325 | 11771.5 | 107.23
05:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 195 | 0 | 0 | 35 | 0 | 450 | 0 | 525 | 0 | 0 | 335 | 99 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 218 | 94 | 25 | 285 | 0 | 0 | 19 | 0 | 0 | 110 | 0 | 0 | 0 | 1155 | 0 | 51 | 138 | 0 | 0 | 290 | 250 | 0 | 201 | 0 | 38 | 105 | 51 | 0 | 16 | 0 | 60 | 0 | 0 | 0 | 310 | 0 | 334 | 30 | 68 | 156 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 49 | 0 | 0 | 0 | 6378.5 | 894 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 748.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 47 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 309 | 1120 | 35 | 5200.56 | 11579.06 | 107.23
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 45 | 0 | 0 | 35 | 0 | 450 | 0 | 500 | 0 | 0 | 335 | 100 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 32 | 6 | 0 | 0 | 0.03 | 218 | 66 | 26 | 285 | 0 | 0 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 1102 | 0 | 51 | 40 | 0 | 0 | 290 | 250 | 0 | 201 | 0 | 34 | 105 | 51 | 0 | 16 | 0 | 58 | 0 | 0 | 0 | 315 | 0 | 320 | 30 | 68 | 158 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 49 | 0 | 0.11 | 0 | 5964.64 | 894 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.68 | 366 | 0 | 747.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 151 | 47 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 115 | 220 | 0 | 309 | 1100 | 35 | 5133.05 | 11097.69 | 107.23
07:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 15 | 45 | 0 | 0 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 335 | 99 | 0 | 5 | 108 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 32 | 54.36 | 0 | 0 | 0.55 | 218 | 65 | 30 | 285 | 0 | 0 | 19 | 0 | 0 | 63 | 0 | 0 | 0 | 1163 | 5 | 51 | 40 | 0 | 0 | 290 | 250 | 0 | 193 | 0 | 34 | 104 | 52 | 0 | 16 | 0 | 50 | 0 | 15 | 0 | 310 | 0 | 340 | 30 | 68 | 160 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 48 | 31 | 0 | 8.02 | 0 | 6156.93 | 894 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 366 | 0 | 746.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.11 | 15 | 0 | 0 | 5.1 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.49 | 153 | 47 | 35 | 4 | 0 | 0 | 0 | 0 | 0.8 | 30 | 0.08 | 0 | 278 | 115 | 220 | 0 | 308 | 1130 | 35 | 5223.51 | 11380.44 | 107.22
08:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 15 | 45 | 0 | 0 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 331 | 97 | 0 | 14 | 108 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 32 | 54.36 | 0 | 0 | 1.07 | 220 | 64 | 11 | 285 | 0 | 0 | 19 | 0 | 0 | 63 | 0 | 0 | 0 | 1150 | 11 | 51 | 40 | 0 | 0 | 290 | 250 | 0 | 185 | 0 | 32 | 103 | 51 | 0 | 16 | 0 | 56 | 0 | 37 | 0 | 305 | 0 | 312 | 30 | 68 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 31 | 1 | 21.38 | 0 | 6147.81 | 891 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 366 | 0 | 748.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.94 | 44 | 0 | 0 | 24.87 | 195 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 2.17 | 155 | 47 | 70 | 14 | 0 | 0 | 0 | 0 | 2.7 | 76 | 0.23 | 0 | 256 | 115 | 180 | 0 | 308 | 1180 | 35 | 5322.68 | 11470.49 | 107.22
09:00 | 0 | 70 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 15 | 45 | 0 | 8 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 330 | 97 | 0 | 22 | 108 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 32 | 54.36 | 0 | 0 | 2.54 | 220 | 32 | 5 | 285 | 0 | 0 | 19 | 0 | 0 | 61 | 0 | 0 | 0 | 1160 | 16 | 51 | 40 | 0 | 0 | 290 | 250 | 0 | 188 | 0 | 33 | 102 | 52 | 0 | 16 | 0 | 56 | 0 | 55 | 0 | 310 | 0 | 313 | 30 | 68 | 143 | 6 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 31 | 2 | 33.83 | 0 | 6157.73 | 892 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 366 | 0 | 748.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.89 | 76 | 0 | 0 | 44.27 | 175 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 3.92 | 153 | 47 | 70 | 23 | 0 | 0 | 0 | 0 | 4.2 | 133 | 0.21 | 0 | 238 | 115 | 180 | 0 | 308 | 1161 | 35 | 5432.01 | 11589.74 | 107.22
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 15 | 95 | 4 | 17 | 54 | 0 | 450 | 0 | 530 | 0 | 0 | 330 | 96 | 0 | 20 | 108 | 20 | 22 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 49 | 31 | 54.36 | 0 | 0 | 3.19 | 220 | 39 | 5 | 285 | 17 | 0 | 19 | 1 | 0 | 61 | 0 | 0 | 0 | 1160 | 19 | 51 | 50 | 0 | 0 | 290 | 250 | 0 | 191 | 0 | 34 | 102 | 53 | 0 | 16 | 0 | 54 | 0 | 65 | 0 | 315 | 0 | 335 | 30 | 68 | 156 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 49 | 31 | 2 | 45.12 | 0 | 6368.67 | 892 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 364 | 0 | 745.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.96 | 96 | 0 | 0 | 57.16 | 160 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 4.99 | 154 | 47 | 110 | 22 | 0 | 0 | 0 | 0 | 5.9 | 166 | 0.29 | 0 | 276 | 115 | 220 | 0 | 308 | 1148 | 35 | 5600 | 11968.67 | 107.21
11:00 | 0 | 72 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 90 | 25 | 190 | 17 | 35 | 72 | 0 | 450 | 0 | 550 | 0 | 0 | 329 | 36 | 0 | 25 | 125 | 20 | 14 | 0 | 0 | 22 | 5 | 30 | 0 | 0 | 49 | 22 | 54.36 | 0 | 0 | 3.57 | 218 | 71 | 5 | 285 | 17 | 0 | 19 | 8 | 0 | 80 | 0 | 0 | 0 | 1175 | 12 | 51 | 88 | 0 | 0 | 290 | 250 | 0 | 182 | 0 | 36 | 102 | 53 | 4 | 16 | 0 | 56 | 0 | 54 | 0 | 315 | 0 | 336 | 10 | 68 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 49 | 31 | 2 | 46.03 | 2 | 6681.96 | 892 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 365 | 0 | 742.57 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 56.24 | 105 | 0 | 0 | 64.72 | 160 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 5.46 | 158 | 47 | 115 | 37 | 15 | 0 | 0 | 0 | 7.2 | 189 | 0.3 | 0 | 280 | 115 | 220 | 0 | 308 | 1148 | 17 | 5727.49 | 12409.45 | 107.21
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 145 | 92 | 277 | 46 | 35 | 72 | 0 | 450 | 0 | 555 | 0 | 0 | 329 | 36 | 0 | 31 | 142 | 20 | 14 | 0 | 0 | 47 | 45 | 63 | 0 | 0 | 49 | 31 | 54.36 | 0 | 0 | 1.76 | 218 | 95 | 6 | 285 | 17 | 0 | 19 | 24 | 0 | 136 | 0 | 0 | 0 | 1160 | 3 | 51 | 115 | 0 | 0 | 290 | 250 | 0 | 177 | 0 | 34 | 100 | 53 | 9 | 16 | 26 | 62 | 34 | 73 | 0 | 315 | 0 | 326 | 10 | 68 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 30 | 2 | 48.92 | 6 | 7252.04 | 892 | 162 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74.74 | 364 | 0 | 744.14 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 0 | 0 | 50.44 | 97 | 0 | 0 | 65.57 | 160 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 5.58 | 157 | 48 | 115 | 21 | 99 | 0 | 0 | 0 | 5.7 | 157 | 0.48 | 1 | 277 | 115 | 220 | 0 | 307 | 1150 | 17 | 5793.65 | 13045.69 | 107.21
13:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 124 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 550 | 0 | 17 | 327 | 37 | 0 | 32 | 52 | 20 | 14 | 0 | 0 | 77 | 65 | 102 | 0 | 0 | 33 | 30 | 54.36 | 0 | 0 | 2.01 | 218 | 97 | 6 | 285 | 17 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1130 | 18 | 51 | 122 | 0 | 0 | 290 | 250 | 0 | 209 | 0 | 49 | 100 | 53 | 8 | 16 | 53 | 66 | 34 | 69 | 21 | 310 | 0 | 320 | 30 | 68 | 155 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 27 | 2 | 22.98 | 5 | 7420.85 | 891 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.07 | 365 | 0 | 745.81 | 0 | 0 | 0 | 113 | 102 | 0 | 0 | 0 | 8 | 48.48 | 106 | 0 | 0 | 63.6 | 160 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 5.37 | 155 | 48 | 115 | 34 | 106 | 0 | 0 | 0 | 2.3 | 174 | 0 | 21 | 271 | 115 | 220 | 0 | 307 | 1150 | 17 | 5960.63 | 13381.48 | 107.21
14:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 107 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 535 | 0 | 17 | 322 | 36 | 0 | 26 | 52 | 20 | 14 | 0 | 0 | 92 | 32 | 102 | 0 | 4 | 33 | 30 | 54.36 | 0 | 0 | 2.7 | 218 | 93 | 9 | 285 | 17 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1160 | 16 | 51 | 122 | 0 | 0 | 310 | 250 | 0 | 207 | 0 | 51 | 100 | 53 | 9 | 16 | 80 | 64 | 34 | 59 | 21 | 315 | 0 | 356 | 30 | 68 | 150 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 27 | 1 | 12.17 | 0 | 7445.73 | 892 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56.24 | 365 | 0 | 749.85 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 16 | 44.63 | 86 | 0 | 0 | 31.28 | 160 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 4.53 | 150 | 48 | 115 | 28 | 108 | 0 | 0 | 0 | 5.6 | 158 | 0.15 | 49 | 276 | 115 | 220 | 0 | 307 | 1155 | 17 | 5952.28 | 13398.01 | 107.2
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 107 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 560 | 0 | 35 | 322 | 38 | 0 | 19 | 52 | 20 | 14 | 0 | 0 | 100 | 49 | 102 | 0 | 18 | 49 | 29 | 54.36 | 0 | 0 | 2.28 | 219 | 80 | 7 | 285 | 17 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1160 | 12 | 51 | 115 | 0 | 0 | 330 | 300 | 0 | 199 | 0 | 51 | 100 | 52 | 0 | 16 | 79 | 66 | 43 | 44 | 33 | 325 | 0 | 346 | 30 | 68 | 155 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 28 | 1 | 26.19 | 2 | 7593.33 | 891 | 151 | 0 | 0 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 51.36 | 365 | 0 | 763.08 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 16 | 32.73 | 64 | 0 | 0 | 33.42 | 160 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 3.53 | 158 | 48 | 115 | 20 | 106 | 0 | 0 | 0 | 4 | 121 | 0.37 | 74 | 307 | 115 | 220 | 0 | 307 | 1192 | 17 | 5989.49 | 13582.82 | 107.2
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 149 | 111 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 550 | 0 | 35 | 325 | 38 | 0 | 9 | 52 | 20 | 14 | 0 | 0 | 94 | 49 | 99 | 0 | 7 | 49 | 45 | 54.36 | 0 | 0 | 0.92 | 219 | 86 | 5 | 285 | 17 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1150 | 7 | 51 | 113 | 0 | 0 | 330 | 300 | 0 | 183 | 0 | 50 | 100 | 52 | 0 | 16 | 98 | 70 | 43 | 23 | 34 | 315 | 0 | 310 | 30 | 68 | 153 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 28 | 1 | 13.29 | 6 | 7484.07 | 891 | 150 | 0 | 7 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 365 | 0 | 763.01 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 16 | 18.12 | 34 | 25 | 0 | 20.37 | 160 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 1.7 | 156 | 48 | 115 | 10 | 106 | 0 | 0 | 0 | 1.9 | 57 | 0.17 | 105 | 289 | 115 | 220 | 0 | 307 | 1205 | 17 | 5862.27 | 13346.34 | 107.2
17:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 19 | 149 | 123 | 277 | 55 | 35 | 90 | 0 | 450 | 0 | 550 | 0 | 35 | 326 | 95 | 0 | 2 | 52 | 20 | 10 | 0 | 0 | 91 | 16 | 90 | 0 | 3 | 49 | 46 | 54.36 | 0 | 0 | 0.1 | 219 | 94 | 10 | 285 | 17 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1135 | 1 | 51 | 113 | 0 | 0 | 280 | 250 | 1 | 208 | 0 | 50 | 100 | 51 | 0 | 19 | 97 | 64 | 43 | 4 | 34 | 310 | 0 | 314 | 30 | 68 | 147 | 10 | 0 | 81 | 30 | 0 | 16 | 100 | 1 | 68 | 48 | 27 | 0 | 2.47 | 6 | 7433.43 | 892 | 148 | 0 | 28 | 18 | 38 | 0 | 0 | 0 | 0 | 0 | 6.51 | 366 | 0 | 763.69 | 0 | 0 | 0 | 113 | 113 | 0 | 27 | 0 | 16 | 3.37 | 8 | 25 | 0 | 2.95 | 160 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.24 | 155 | 48 | 115 | 2 | 106 | 0 | 0 | 0 | 0.4 | 11 | 0.03 | 103 | 272 | 115 | 220 | 0 | 307 | 1105 | 17 | 5645.19 | 13078.62 | 107.2
18:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 149 | 124 | 277 | 41 | 35 | 108 | 0 | 450 | 0 | 520 | 0 | 55 | 330 | 95 | 0 | 0 | 130 | 20 | 16 | 0 | 0 | 91 | 45 | 94 | 0 | 0 | 49 | 46 | 54.36 | 0 | 0 | 0 | 218 | 100 | 16 | 285 | 90 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1190 | 0 | 51 | 123 | 8 | 0 | 300 | 260 | 5 | 207 | 0 | 50 | 102 | 120 | 0 | 19 | 97 | 72 | 43 | 0 | 35 | 315 | 0 | 314 | 30 | 68 | 146 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 27 | 0 | 0 | 11 | 7844.86 | 891 | 128 | 0 | 33 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 767.08 | 0 | 0 | 0 | 113 | 113 | 0 | 96 | 20 | 25 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 130 | 47 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 115 | 220 | 0 | 308 | 1106 | 35 | 5773.08 | 13617.94 | 107.19
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7 | 35 | 149 | 125 | 277 | 50 | 55 | 108 | 0 | 450 | 0 | 520 | 0 | 55 | 327 | 37 | 0 | 0 | 142 | 20 | 14 | 0 | 0 | 86 | 49 | 100 | 0 | 5 | 49 | 61 | 54.36 | 0 | 0 | 0 | 217 | 110 | 15 | 285 | 160 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1155 | 0 | 51 | 132 | 8 | 0 | 300 | 260 | 2 | 194 | 0 | 66 | 103 | 156 | 0 | 19 | 98 | 74 | 43 | 0 | 35 | 310 | 0 | 332 | 30 | 68 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 68 | 48 | 27 | 0 | 0 | 12 | 7968.56 | 890 | 135 | 0 | 42 | 61 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 751.44 | 0 | 32 | 0 | 113 | 113 | 0 | 96 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 152 | 47 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 277 | 115 | 220 | 0 | 307 | 1190 | 35 | 5887.44 | 13856 | 107.19
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 35 | 149 | 125 | 277 | 55 | 55 | 108 | 0 | 450 | 0 | 550 | 0 | 55 | 326 | 97 | 0 | 0 | 142 | 20 | 17 | 0 | 0 | 92 | 16 | 104 | 0 | 5 | 49 | 54 | 54.36 | 0 | 0 | 0 | 209 | 110 | 18 | 285 | 160 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1192 | 0 | 51 | 132 | 8 | 0 | 300 | 260 | 2 | 204 | 0 | 90 | 102 | 157 | 9 | 19 | 98 | 76 | 25 | 0 | 35 | 325 | 0 | 334 | 30 | 68 | 156 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 27 | 0 | 0 | 12 | 8121.86 | 891 | 145 | 0 | 35 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 757.08 | 0 | 41 | 0 | 113 | 113 | 0 | 96 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 160 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 308 | 1203 | 35 | 6029.08 | 14150.94
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2 | 35 | 149 | 125 | 277 | 55 | 55 | 108 | 0 | 450 | 0 | 555 | 0 | 55 | 327 | 97 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 92 | 16 | 103 | 0 | 8 | 49 | 61 | 54.36 | 0 | 0 | 0 | 218 | 110 | 23 | 285 | 53 | 0 | 19 | 25.5 | 0 | 200 | 0 | 0 | 0 | 1219 | 0 | 51 | 133 | 8 | 0 | 300 | 280 | 2 | 196 | 0 | 89 | 103 | 160 | 8 | 19 | 97 | 66 | 25 | 0 | 35 | 315 | 0 | 334 | 30 | 68 | 157 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 27 | 0 | 0 | 12 | 8070.06 | 891 | 147 | 0 | 35 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 754.32 | 0 | 41 | 0 | 113 | 113 | 0 | 96 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 47 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 115 | 220 | 0 | 307 | 1202 | 35 | 6037.32 | 14107.38 | 107.19
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.6 | 17 | 149 | 125 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 560 | 0 | 35 | 327 | 96 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 96 | 16 | 104 | 0 | 10 | 49 | 61 | 54.36 | 0 | 0 | 0 | 218 | 110 | 20 | 285 | 17 | 0 | 19 | 25.5 | 0 | 182 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 8 | 0 | 300 | 280 | 2 | 204 | 0 | 77 | 102 | 139 | 9 | 19 | 98 | 66 | 25 | 0 | 37 | 320 | 0 | 338 | 30 | 68 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 68 | 48 | 27 | 0 | 0 | 12 | 7961.46 | 891 | 145 | 0 | 35 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 769 | 0 | 41 | 0 | 113 | 113 | 0 | 88 | 38 | 25 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 115 | 220 | 0 | 307 | 1214 | 35 | 6080 | 14041.46 | 107.18
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.9 | 17 | 149 | 125 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 555 | 0 | 35 | 330 | 97 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 92 | 16 | 104 | 0 | 11 | 49 | 61 | 54.36 | 0 | 0 | 0 | 219 | 110 | 23 | 285 | 17 | 0 | 19 | 25.5 | 0 | 182 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 8 | 0 | 320 | 300 | 2 | 183 | 0 | 55 | 103 | 139 | 0 | 19 | 97 | 74 | 16 | 0 | 37 | 310 | 0 | 307 | 30 | 68 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 28 | 0 | 0 | 12 | 7886.76 | 891 | 143 | 0 | 35 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 769 | 0 | 41 | 0 | 113 | 113 | 0 | 88 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 158 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 307 | 115 | 220 | 0 | 307 | 1224 | 35 | 6051 | 13937.76 | 107.18
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.1 | 17 | 149 | 125 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 566 | 0 | 0 | 326 | 36 | 0 | 0 | 52 | 21.2 | 22 | 0 | 0 | 95 | 16 | 105 | 0 | 2 | 49 | 61 | 54.36 | 0 | 0 | 0 | 220 | 108 | 24 | 285 | 17 | 0 | 19 | 25.5 | 0 | 182 | 0 | 0 | 0 | 1180 | 0 | 51 | 133 | 8 | 0 | 320 | 300 | 0 | 183 | 0 | 40 | 102 | 138 | 0 | 19 | 97 | 74 | 43 | 0 | 37 | 315 | 0 | 352 | 30 | 68 | 156 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 10 | 68 | 48 | 28 | 0 | 0 | 12 | 7692.16 | 891 | 137 | 0 | 35 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 760 | 0 | 41 | 0 | 113 | 113 | 0 | 88 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 160 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 115 | 220 | 0 | 307 | 1200 | 35 | 5989 | 13681.16 | 107.17
Total KWH | 0 | 2025600 | 527040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517320 | 300240 | 3033648 | 1795680 | 5203353 | 854366 | 530208 | 1571040 | 0 | 10527000 | 0 | 12969827 | 0 | 532911 | 7867885 | 1964000 | 0 | 195776 | 2270400 | 488400 | 457200 | 0 | 0 | 1446491 | 471709 | 1557120 | 0 | 87840 | 1133882 | 932400 | 1175584 | 0 | 0 | 22559 | 5194755 | 2218036 | 362400 | 6821818.18 | 548655 | 0 | 475200 | 367484.4 | 0 | 3164109 | 0 | 0 | 0 | 28079997 | 127710 | 1226392 | 2689745 | 50182 | 0 | 7620700 | 6466000 | 19680 | 4702000 | 0 | 1114560 | 2446020 | 1916640 | 54600 | 399100 | 1304160 | 1566720 | 515707 | 484882 | 486384 | 7643000 | 0 | 8386000 | 673000 | 1598160 | 3710945 | 209880 | 0 | 1950720 | 711744 | 0 | 392000 | 2399440 | 103320 | 1618800 | 1159200 | 717120 | 14650 | 307720 | 132240 | 172611054.58 | 21610181 | 3908448 | 0 | 273120 | 360576 | 912000 | 0 | 0 | 0 | 0 | 0 | 570240 | 8836364 | 0 | 18190909 | 0 | 376484 | 0 | 1534272 | 1735104 | 0 | 680880 | 302030 | 192326 | 366858 | 746060 | 292400 | 0 | 423744 | 4487091 | 0 | 0 | 0 | 0 | 0 | 9405745 | 0 | 36900 | 3735000 | 1073891 | 2383673 | 227269 | 1868227 | 0 | 0 | 0 | 42029.76 | 1270800 | 3334 | 1302240 | 6786000 | 2760000 | 5429160 | 0 | 7389090.91 | 28830545.45 | 748800 | 139091792.12 | 311702846.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13045.69 | MW | 12:00 Hr. | Energy Generated |  |  | 311.7028 |  | MKWHr.
| Day Peak Demand |  |  | 13045.69 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.742 |  | MKWHr.
| Evening Peak Generation |  |  | 14150.94 | MW | 19:30 Hr. | Energy Demand |  |  | 313.4448 |  | MKWHr.
| Evening Peak Demand |  |  | 14449.94 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.1 |  | °C
| Minimum Generation of the Day |  |  | 11097.69 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 878.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 14150.94 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.213 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.2743 | 0 | 19.1618 | 0 | 0 | 0.19578 | 0 | 0 | 53.6319 | Gas | 115.1133 | Gas | 412544233.52
| Chattogram Zone |  |  | 3.5265 | 34.9018 | 10.3266 | 0 | 5.1948 | 0.15027 | 0 | 0.08784 | 54.1877 | Coal | 91.5527 | Coal | 531658843.5701
| Cumilla Zone |  |  | 22.9301 | 0 | 8.0818 | 0 | 0 | 0.48488 | 1.5667 | 0 | 33.0635 | HFO | 52.6339 | HFO | 987166054.252
| Mymensingh Zone |  |  | 0.71712 | 0 | 3.0136 | 0 | 0 | 0.32237 | 0 | 0 | 4.053 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.6749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.6749 | Hydro | 5.1948 | Hydro | 519475.5
| Khulna Zone |  |  | 3.9084 | 8.8364 | 0.6337 | 0 | 0 | 0.57024 | 22.5222 | 0 | 36.4709 | Solar | 4.8405 | Solar | 72907109.9696
| Barishal Zone |  |  | 8.1892 | 43.0056 | 2.051 | 0 | 0 | 0.003334 | 0 | 0 | 53.2492 | Import | 42.2798 | Import | 242215401.08
| Rajshahi Zone |  |  | 13.8928 | 0 | 5.1135 | 0 | 0 | 1.5736 | 18.1909 | 0 | 38.7708 | Wind | 0.08784 | Wind | 1294761.6
| Rangpur Zone |  |  | 0 | 4.8089 | 4.2519 | 0 | 0 | 1.5401 | 0 | 0 | 10.6009
| Total |  |  | 115.1133 | 91.5527 | 52.6339 | 0 | 5.1948 | 4.8405 | 42.2798 | 0.08784 | 311.7028
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 412544233.52 |  | Hydro | 519475.5
|  |  |  | Coal | 531658843.5701 |  | Solar | 72907109.9696
|  |  |  | HFO | 987166054.252 |  | Import | 242215401.08
|  |  |  | HSD | 0 |  | Wind | 1294761.6
[5 empty] | Total: | 224,83,05,879 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6102 | Peak Hr Flow | 891.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40884984.06 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.1909 | Peak Hr Flow | 757.08 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1861 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5667 | Peak Hr Flow | 76.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2332 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.3678 | Peak Hr Flow | 1724.08 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 6 |  | 5208
|  |  |  | Chattogram |  | 0 |  | 1497
|  |  |  | Cumilla |  | 35 |  | 1329
|  |  |  | Mymensingh |  | 67 |  | 1058
|  |  |  | Sylhet |  | 0 |  | 646
|  |  |  | Khulna |  | 66 |  | 1612
|  |  |  | Barishal |  | 0 |  | 446
|  |  |  | Rajshahi |  | 65 |  | 1311
|  |  |  | Rangpur |  | 47 |  | 790
|  |  |  | Total |  | 286 |  | 13897
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 531 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 531
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:06 | 16:01 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Annual Maintenance Work.
| 08:07 | 16:00 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Annual Maintenance Work.
| 08:30 |  | Bog-Sherpur 132/33kV S/S Main Bus-1 Scheduled S/D Due to Annual maintenance
| 08:50 | 09:56 | Shyampur 132/33kV S/S Bus-2 Scheduled S/D Due to Being a red hood in the isolator will
work and reserves on Bus-2 will work.
|  | 09:05 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 is restored.
|  | 09:07 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 is restored.
| 09:14 | 12:41 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to internal wiring Cable checking
| 09:15 | 12:41 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to internal wiring cable Checking
| 09:22 | 20:22 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to CNTIC project work
| 09:35 | 19:58 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to Project
work in Dagonvhuyan S/s
| 09:37 | 15:48 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Dead line checking
| 09:43 | 19:38 | Daganbhuiyan 132/33kV S/S Main Bus 1&2 Project Work S/D Due to CNTIC project work
| 09:49 | 19:57 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to CNTIC
project work and from Daganbhuiyan 132/33kV end Due to CNTIC project work
| 09:50 | 16:38 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Annual maintenance
| 09:50 | 14:16 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Broken
132 KV disc insulator Change.
| 09:55 | 13:25 | BIPTC S/S 10CF15 Scheduled S/D Due to for corrective maintenance
| 09:55 | 14:24 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Orion
plant Maintenance Work.
|  | 10:56 | Bhaluka 132/33kV S/S 03. Transformer-03 HT is restored.
|  | 10:58 | Bhaluka 132/33kV S/S 03. Transformer-03 LT is restored.
| 11:06 | 15:49 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to T-3 ট্রান্সফরমারের Self
Protection চেক by SPMD Rangpur.
| 11:06 | 15:48 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to T-3 ট্রান্সফরমারের Self
Protection চেক by SPMD Rangpur.
| 12:00 |  | Day peak generation 13040 MW
|  | 12:05 | Bajitpur 132/33kV S/S Tr-1(404T) LT is restored.
| 12:16 | 15:20 | Bajitpur 132/33kV S/S Tr-2(414T) HT Project Work S/D
| 13:08 |  | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D Due to Red hot maintenance work.
| 14:01 | 17:17 | Bogura 400/230kV S/S ATR-03 LT Scheduled S/D Due to ATR-03 Shutdown due to internal
wiring cable checking.
| 14:01 | 17:17 | Bogura 400/230kV S/S ATR-03 HT Scheduled S/D Due to ATR-03 Shutdown due to internal
wiring cable checking.
|  | 14:44 | Rajbari 132/33kV S/S Transformer-2 HT is restored.
|  | 14:45 | Rajbari 132/33kV S/S Transformer-2 LT is restored.
|  | 14:57 | Bogura 132/33kV S/S Transformer-3 HT is restored.
|  | 14:58 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 15:40 | 18:59 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Underground cable leakage
removing
| 15:40 | 18:59 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Underground cable leakage
removing
|  | 15:57 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 15:58 | Khulna (C) S/S Tr-2 415 T LT is restored.
|  | 16:47 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 16:48 | Hathazari-Madunaghat 132kV Ckt-2 is restored.
|  | 16:48 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
|  | 17:23 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 17:24 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 18:16 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
| 18:59 |  | Chandpur 132/33kV S/S 402T (T-01) LT Scheduled S/D
|  | 19:03 | Shyampur-Shyampur(New) 132kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation: 14150 MW.
| 06:00 |  | Minimum Generation is 11167 MW.
| 07:17 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Shutdown for | [7 empty] | 10.0MW load
|  |  | Red hot maintenance. | [7 empty] | interrup. Chhatak
132/33kV end
| 07:25 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Annual maintenance
| 07:26 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Annual maintenance
| 07:43 |  | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
| 07:44 |  | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance
| 07:45 |  | Rajbari 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance.
| 07:46 |  | Rajbari 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10527000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 854366 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1964000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7867885 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 51 | 517320 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1795680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 530208 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 532911 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 488400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 457200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 527040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 5203353 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3033648 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2025600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1571040 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 195776 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 300240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 12969827 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2270400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6657.724 | 2642 | 53631894
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 367484.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127710 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 475200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 209 | 5194755 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 200 | 3164109 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 932400 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 1133882 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 362400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 104 | 1557120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 471709 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1175584 | FGMO
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2218036 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1446491 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 548655 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1192 | 28079997 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 87840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6821818.18 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2592.86 | 54187749.58
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 204 | 4702000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 7620700 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 260 | 6466000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 2 | 19680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 50182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1226392 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 2689745 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 486384 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2446020 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 157 | 1916640 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1566720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 515707 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 399100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1304160 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 54600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1114560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 484882 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1568 | 33063472
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 27 | 717120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1159200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1618800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 307720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 132240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 103320 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 171 | 4053050
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 673000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1598160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3710945 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711744 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1950720 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2399440 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 209880 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7643000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 334 | 8386000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1148 | 27674889
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21610181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 273120 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 360576 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 145 | 3908448 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 570240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 364 | 8836364 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1523 | 36470929
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 308 | 7389090.91 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1302240 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2760000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1203 | 28830545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5429160 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 748800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6786000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3334 | -
Barishal Area Total |  |  |  |  | 2858 | 2298 | 53249170.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 366858 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 376484 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 302030 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 162 | 4487091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 403 | 9405745 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 292400 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 192326 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 680880 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1735104 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1534272 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36900 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 757.08 | 18190909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 423744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 746060 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1773.08 | 38770803
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1073891 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3735000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1868227 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42029.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2383673 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 227269 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1270800 | -
Rangpur Area Total |  |  |  |  | 950 | 435 | 10600889.76
Eastern Grid Total |  |  |  |  | 17385.715 | 8121.86 | 172611054.58
Western Grid Total |  |  |  |  | 10980.24 | 6029.08 | 139091792.12
National Grid Total |  |  |  |  | 28365.955 | 14150.94 | 311702846.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-10-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9630.19 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3981.1 | MW
i) Dhaka area |  |  | 5202.01 |  | MW | i) Khulna area |  |  |  | 1546 | MW
ii) Chattogram area |  |  | 1497.2 |  | MW | ii) Barishal area |  |  |  | 446.5 | MW
iii) Cumilla area |  |  | 1293.98 |  | MW | iii) Rajshahi area |  |  |  | 1245.6 | MW
iv) Mymensingh area |  |  | 991 |  | MW | iv) Rangpur area |  |  |  | 743 | MW
v) Sylhet area |  |  | 646 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13611.29 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 79 | 19:30 | 133 | Niamatpur | 60 | 18:00
2 | AKSML | 119 | 23:00 | 68 | Ishurdi | 62 | 18:00 | 134 | Noapara | 37 | 20:00
3 | Aftabnagar | 38 | 18:00 | 69 | Jaldhaka | 61 | 00:00 | 135 | PHP | 9 | 03:00
4 | Agargaon | 130 | 13:00 | 70 | Jamalpur | 114 | 23:00 | 136 | Pabna | 106 | 18:30
5 | Agrabad | 92 | 19:00 | 71 | Jashore | 133 | 18:00 | 137 | Palashbari | 103 | 21:00
6 | Amnura | 23 | 14:00 | 72 | Jhenaidah | 111 | 00:00 | 138 | Panchagarh | 43 | 00:00
7 | Ashuganj | 86 | 23:00 | 73 | Joydebpur | 160 | 15:00 | 139 | Patiya | 11 | 00:00
8 | BSRM | 118 | 22:00 | 74 | Joypurhat | 46 | 00:00 | 140 | Patuakhali | 66 | 22:00
9 | Bagerhat | 74 | 23:00 | 75 | Juldah | 16 | 15:00 | 141 | Payra | 30 | 00:00
10 | Bajitpur | 78 | 00:00 | 76 | KSRM | 38 | 10:00 | 142 | Postogola | 65 | 12:00
11 | Bakulia | 89 | 19:00 | 77 | Kabirpur | 242 | 21:00 | 143 | Purbachal | 21 | 20:00
12 | Banani | 47.2 | 13:00 | 78 | Kachua | 82 | 00:00 | 144 | Purbasadipur | 102 | 00:00
13 | Bangabhaban | 22 | 10:00 | 79 | Kallyanpur | 102 | 18:00 | 145 | Rahanpur | 30 | 00:00
14 | Barapukuria | 56 | 00:00 | 80 | Kalurghat | 52 | 15:00 | 146 | Rahim | 26 | 12:00
15 | Barguna | 20 | 19:30 | 81 | Kamrangirchar | 78 | 18:00 | 147 | Rajbari | 66 | 01:00
16 | Barishal | 113 | 19:30 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 125 | 21:00
17 | Barishal-230 | 98 | 19:30 | 83 | Kasba | 32 | 01:00 | 149 | Rajshahi | 93 | 00:00
18 | Baroaulia | 68 | 11:00 | 84 | Kazla | 104 | 18:30 | 150 | Rajshahi-230 | 90 | 13:00
19 | Baroirhat | 63 | 19:30 | 85 | Keranigonj | 95 | 19:00 | 151 | Ramganj | 102 | 00:00
20 | Bashundhara | 193 | 13:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 43 | 23:00
21 | BashundharaCement | 8 | 18:00 | 87 | Khulna | 64 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 80 | 19:00 | 88 | Khulshi | 203 | 19:00 | 154 | Rangpur | 131 | 13:00
23 | Benapole | 54 | 00:00 | 89 | Kishoreganj | 106 | 01:00 | 155 | Ruppur | 7.8 | 15:00
24 | Bhaluka | 133 | 14:00 | 90 | Kodda | 313 | 18:30 | 156 | SSM | 13 | 01:00
25 | Bhandaria | 52 | 22:00 | 91 | Kulaura | 48 | 19:00 | 157 | Saidpur | 93 | 15:00
26 | Bhangura | 31 | 14:00 | 92 | Kurigram | 48 | 00:00 | 158 | Satkhira | 120 | 21:00
27 | Bheramara(GK) | 56 | 21:00 | 93 | Kushtia | 138 | 20:00 | 159 | Satmasjid | 101 | 13:00
28 | Bhulta | 214 | 20:00 | 94 | Laksam | 32 | 00:00 | 160 | Savar | 234 | 15:00
29 | Bog-Sherpur | 68 | 01:00 | 95 | Lakshmipur | 36 | 19:30 | 161 | SevenRings | 16.42 | 12:00
30 | Bogura | 200 | 14:00 | 96 | Lalbag | 62 | 12:00 | 162 | ShahCement | 26 | 18:00
31 | Borhanuddin | 93 | 23:00 | 97 | Lalmonirhat | 48 | 18:00 | 163 | Shahjadpur | 73 | 12:00
32 | Brahmanbaria | 123 | 00:00 | 98 | MI_Cement | 11 | 21:00 | 164 | Shahjibazar | 124 | 22:00
33 | Cantonment | 138 | 13:00 | 99 | Madanganj | 43 | 18:30 | 165 | Shahmirpur | 58 | 02:00
34 | Chandina | 14.13 | 18:30 | 100 | Madaripur | 106 | 01:00 | 166 | Shariatpur | 77 | 23:00
35 | Chandpur | 72 | 00:00 | 101 | Madartek | 84 | 00:00 | 167 | Sherpur | 130 | 23:00
36 | Chandraghona | 38 | 19:00 | 102 | Madunaghat | 62 | 19:30 | 168 | Shikalbaha | 28 | 22:00
37 | Chapai | 59 | 22:00 | 103 | Magura | 56 | 18:00 | 169 | Shitalakhya | 85.8 | 12:00
38 | Charsaidpur | 38 | 05:00 | 104 | Mahasthangarh | 68 | 02:00 | 170 | Sholosohor | 49 | 16:00
39 | Chauddagram | 70 | 19:00 | 105 | Maijdee | 19 | 02:00 | 171 | Shyampur | 98 | 12:00
40 | Chhatak | 38 | 19:30 | 106 | Manikganj | 124 | 21:00 | 172 | Siddhirganj | 121 | 12:00
41 | Chowmuhani | 169 | 00:00 | 107 | Maniknagar | 64 | 13:00 | 173 | Sirajganj | 111 | 18:30
42 | Chuadanga | 104 | 18:00 | 108 | Matarbari | 50 | 00:00 | 174 | Sonargaon | 111 | 04:00
43 | Coxsbazar | 132 | 19:00 | 109 | Matuail | 68 | 11:00 | 175 | Sreemongol | 82 | 19:30
44 | Cumilla(N) | 129 | 18:00 | 110 | Metrorail_Motijheel | 28 | 19:00 | 176 | Sreepur | 105 | 18:30
45 | Cumilla(S) | 145 | 18:00 | 111 | Metrorail_Uttara | 8 | 09:00 | 177 | Srinagar | 45.36 | 22:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 127 | 15:00 | 178 | Sunamganj | 64 | 20:00
47 | Daudkandi | 138 | 01:00 | 113 | Mirpur | 126 | 18:00 | 179 | Sylhet | 55 | 20:00
48 | DhakaUniversity | 88 | 13:00 | 114 | Mirsorai | 12 | 15:00 | 180 | Sylhet-132 | 124 | 15:00
49 | Dhamrai | 124 | 17:00 | 115 | Mirzapur | 49 | 13:00 | 181 | TK | 24.4 | 19:00
50 | Dhanmondi | 131 | 13:00 | 116 | Mithapukur | 56 | 00:00 | 182 | Tangail | 164 | 18:00
51 | Dohazari | 100 | 19:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 23 | 18:00
52 | Faridpur | 156 | 18:30 | 118 | Mogbazar | 95.8 | 15:00 | 184 | Thakurgaon | 80 | 15:00
53 | Fatullah | 101 | 10:00 | 119 | Mongla | 43 | 12:00 | 185 | Tongi | 128 | 11:00
54 | Fenchuganj | 40 | 20:00 | 120 | Motijheel | 48 | 13:00 | 186 | Ullahpara | 34 | 18:00
55 | Feni | 108 | 19:00 | 121 | Muktagacha | 30 | 21:00 | 187 | Ullon | 62 | 18:00
56 | GPH | 76 | 03:00 | 122 | Munshiganj | 109 | 22:00 | 188 | Uttara | 66 | 13:00
57 | Ghatail | 70 | 19:00 | 123 | Muradnagar | 40 | 18:00 | 189 | UttaraNew | 76 | 18:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 181 | 21:00 | 190 | Zigatola | 70 | 19:00
59 | Ghorashal-230 | 98 | 22:00 | 125 | Naogaon | 112 | 18:30
60 | Goalpara | 30 | 18:00 | 126 | Narail | 53 | 21:00
61 | Gollamari | 98 | 13:00 | 127 | Narinda | 66 | 13:00
62 | Gopalganj | 91 | 21:00 | 128 | Narshingdi | 170 | 19:00
63 | Gulshan | 122 | 13:00 | 129 | Natore | 140 | 18:30
64 | Halishahar | 82 | 15:00 | 130 | Nawabganj | 45 | 22:00
65 | HaripurSBU | 152 | 16:00 | 131 | Netrakona | 114 | 00:00
66 | Hasnabad | 84 | 18:30 | 132 | New | 59 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13630.52 | 102 |  | 13737.11
1:00 | 13252.46 | 0 |  | 13252.46
2:00 | 12751.5 | 0 |  | 12751.5
3:00 | 12170.5 | 0 |  | 12170.5
4:00 | 11771.5 | 0 |  | 11771.5
5:00 | 11579.06 | 0 |  | 11579.06
6:00 | 11097.69 | 0 |  | 11097.69
7:00 | 11380.44 | 0 |  | 11380.44
8:00 | 11470.49 | 0 |  | 11470.49
9:00 | 11589.74 | 0 |  | 11589.74
10:00 | 11968.67 | 0 |  | 11968.67
11:00 | 12409.45 | 0 |  | 12409.45
12:00 | 13045.69 | 0 |  | 13045.69
13:00 | 13381.48 | 0 |  | 13381.48
14:00 | 13398.01 | 0 |  | 13398.01
15:00 | 13582.82 | 0 |  | 13582.82
16:00 | 13346.34 | 0 |  | 13346.34
17:00 | 13078.62 | 0 |  | 13078.62
18:00 | 13617.94 | 366 |  | 14000.41
19:00 | 13856 | 283 |  | 14152
19:30 | 14150.94 | 286 |  | 14449.94
20:00 | 14107.38 | 281 |  | 14401.38
21:00 | 14041.46 | 248 |  | 14300.46
22:00 | 13937.76 | 252 |  | 14200.76
23:00 | 13681.16 | 210 |  | 13900.16
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7550.36 | 6080.16 | 13630.52 | DAILY GENERATION CURVE
00:30 | 7440.86 | 6000.63 | 13441.49
01:00 | 7331.36 | 5921.1 | 13252.46 | 13-10-2025
01:30 | 7196.43 | 5805.55 | 13001.98
02:00 | 7061.5 | 5690 | 12751.5
02:30 | 6858.5 | 5602.5 | 12461
03:00 | 6655.5 | 5515 | 12170.5
03:30 | 6551 | 5420 | 11971
04:00 | 6446.5 | 5325 | 11771.5
04:30 | 6412.5 | 5262.78 | 11675.28
05:00 | 6378.5 | 5200.56 | 11579.06
05:30 | 6171.57 | 5166.805 | 11338.375
06:00 | 5964.64 | 5133.05 | 11097.69
06:30 | 6060.785 | 5178.28 | 11239.065
07:00 | 6156.93 | 5223.51 | 11380.44
07:30 | 6152.37 | 5273.095 | 11425.465
08:00 | 6147.81 | 5322.68 | 11470.49
08:30 | 6152.77 | 5377.345 | 11530.115
09:00 | 6157.73 | 5432.01 | 11589.74
09:30 | 6263.2 | 5516.005 | 11779.205
10:00 | 6368.67 | 5600 | 11968.67
10:30 | 6525.315 | 5663.745 | 12189.06
11:00 | 6681.96 | 5727.49 | 12409.45
11:30 | 6967 | 5760.57 | 12727.57
12:00 | 7252.04 | 5793.65 | 13045.69
12:30 | 7336.445 | 5877.14 | 13213.585
13:00 | 7420.85 | 5960.63 | 13381.48
13:30 | 7433.29 | 5956.455 | 13389.745
14:00 | 7445.73 | 5952.28 | 13398.01
14:30 | 7519.53 | 5970.885 | 13490.415
15:00 | 7593.33 | 5989.49 | 13582.82
15:30 | 7538.7 | 5925.88 | 13464.58
16:00 | 7484.07 | 5862.27 | 13346.34
16:30 | 7458.75 | 5753.73 | 13212.48
17:00 | 7433.43 | 5645.19 | 13078.62
17:30 | 7639.145 | 5709.135 | 13348.28
18:00 | 7844.86 | 5773.08 | 13617.94
18:30 | 7906.71 | 5830.26 | 13736.97
19:00 | 7968.56 | 5887.44 | 13856
19:30 | 8121.86 | 6029.08 | 14150.94
20:00 | 8070.06 | 6037.32 | 14107.38
20:30 | 8015.76 | 6058.66 | 14074.42 |  | Executive Engineer
21:00 | 7961.46 | 6080 | 14041.46 |  | Network Operation Division
21:30 | 7924.11 | 6065.5 | 13989.61
22:00 | 7886.76 | 6051 | 13937.76
22:30 | 7789.46 | 6020 | 13809.46
23:00 | 7692.16 | 5989 | 13681.16

## En-Curve
QF-LDC-12
Date | 13-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2878 | 1879.5 | 902 | 38 | 68 | 767.16 | 219 | 3907 | 0 | 803 | 2168.86 | 0 | 0 | 0 | 102 | DAILY ENERGY CURVE
00:30 | 2879.5 | 1876.5 | 898 | 38 | 67 | 762.13 | 219.5 | 3857 | 0 | 722 | 2121.86 | 0 | 0 | 0 | 51 | 13-10-2025
01:00 | 2881 | 1873.5 | 894 | 38 | 66 | 757.1 | 220 | 3807 | 0 | 641 | 2074.86 | 0 | 0 | 0 | 0
01:30 | 2868.5 | 1861.5 | 894 | 38 | 68 | 749.55 | 220 | 3797.5 | 0 | 587.5 | 1917.43 | 0 | 0 | 0 | 0 | Energy Generated | 311.7028 |  | MKWHr
02:00 | 2856 | 1849.5 | 894 | 38 | 70 | 742 | 220 | 3788 | 0 | 534 | 1760 | 0 | 0 | 0 | 0 | Energy not Served | 1.742 |  | MKWHr
02:30 | 2868 | 1861.5 | 894 | 38 | 69 | 742 | 219 | 3800 | 0 | 466 | 1503.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 313.4448 |  | MKWHr
03:00 | 2880 | 1873.5 | 894 | 38 | 68 | 742 | 218 | 3812 | 0 | 398 | 1247 | 0 | 0 | 0 | 0
03:30 | 2887.5 | 1878 | 894 | 38 | 66 | 740.5 | 218 | 3805.5 | 0 | 309 | 1134.5 | 0 | 0 | 0 | 0
04:00 | 2895 | 1882.5 | 894 | 38 | 64 | 739 | 218 | 3799 | 0 | 220 | 1022 | 0 | 0 | 0 | 0
04:30 | 2903 | 1883 | 894 | 38 | 62 | 743.78 | 218 | 3753 | 0 | 206 | 974.5 | 0 | 0 | 0 | 0
05:00 | 2911 | 1883.5 | 894 | 38 | 60 | 748.56 | 218 | 3707 | 0 | 192 | 927 | 0 | 0 | 0 | 0
05:30 | 2890 | 1872 | 894 | 38 | 59 | 747.94 | 218 | 3664 | 0.435 | 184 | 769 | 0 | 0 | 2 | 0
06:00 | 2869 | 1860.5 | 894 | 38 | 58 | 747.32 | 218 | 3621 | 0.87 | 176 | 611 | 0 | 0 | 4 | 0
06:30 | 2857 | 1871.25 | 894 | 38 | 54 | 747.125 | 218 | 3675.5 | 55.51 | 219.5 | 605.18 | 0 | 0 | 4 | 0
07:00 | 2845 | 1882 | 894 | 38 | 50 | 746.93 | 218 | 3730 | 110.15 | 263 | 599.36 | 0 | 0 | 4 | 0
07:30 | 2786 | 1845.5 | 892.5 | 38 | 53 | 747.85 | 219 | 3738.5 | 211.255 | 273 | 615.36 | 0 | 0 | 5.5 | 0
08:00 | 2727 | 1809 | 891 | 38 | 56 | 748.77 | 220 | 3747 | 312.36 | 283 | 631.36 | 0 | 0 | 7 | 0
08:30 | 2721.5 | 1804.5 | 891.5 | 38 | 56 | 748.645 | 220 | 3732.5 | 414.61 | 283.5 | 611.86 | 0 | 0 | 7.5 | 0
09:00 | 2716 | 1800 | 892 | 38 | 56 | 748.52 | 220 | 3718 | 516.86 | 284 | 592.36 | 0 | 0 | 8 | 0
09:30 | 2729.5 | 1838 | 892 | 38 | 55 | 747.11 | 220 | 3730 | 560.235 | 291 | 673.86 | 0 | 0 | 4.5 | 0
10:00 | 2743 | 1876 | 892 | 38 | 54 | 745.7 | 220 | 3742 | 603.61 | 298 | 755.36 | 0 | 0 | 1 | 0
10:30 | 2713.5 | 1883 | 892 | 38 | 55 | 744.135 | 219 | 3754 | 651.565 | 308 | 930.36 | 0 | 0 | 0.5 | 0
11:00 | 2684 | 1890 | 892 | 38 | 56 | 742.57 | 218 | 3766 | 699.52 | 318 | 1105.36 | 0 | 0 | 0 | 0
11:30 | 2689.5 | 1893 | 892 | 38 | 59 | 743.355 | 218 | 3757 | 668.355 | 372.5 | 1396.86 | 0 | 0 | 0 | 0
12:00 | 2695 | 1896 | 892 | 38 | 62 | 744.14 | 218 | 3748 | 637.19 | 427 | 1688.36 | 0 | 0 | 0 | 0
12:30 | 2735.5 | 1889.5 | 891.5 | 38 | 64 | 744.975 | 218 | 3729.5 | 649.5 | 400 | 1853.11 | 0 | 0 | 0 | 0
13:00 | 2776 | 1883 | 891 | 38 | 66 | 745.81 | 218 | 3711 | 661.81 | 373 | 2017.86 | 0 | 0 | 0 | 0
13:30 | 2817 | 1877 | 891.5 | 38 | 65 | 747.83 | 218 | 3728.5 | 596.555 | 364.5 | 2043.86 | 0 | 0 | 2 | 0
14:00 | 2858 | 1871 | 892 | 38 | 64 | 749.85 | 218 | 3746 | 531.3 | 356 | 2069.86 | 0 | 0 | 4 | 0
14:30 | 2885.5 | 1890 | 891.5 | 38 | 65 | 756.465 | 218.5 | 3784 | 483.09 | 374.5 | 2092.86 | 0 | 0 | 11 | 0
15:00 | 2913 | 1909 | 891 | 38 | 66 | 763.08 | 219 | 3822 | 434.88 | 393 | 2115.86 | 0 | 0 | 18 | 0
15:30 | 2872.5 | 1897 | 891 | 38 | 68 | 763.045 | 219 | 3813.5 | 329.175 | 424.5 | 2136.36 | 0 | 0 | 12.5 | 0
16:00 | 2832 | 1885 | 891 | 38 | 70 | 763.01 | 219 | 3805 | 223.47 | 456 | 2156.86 | 0 | 0 | 7 | 0
16:30 | 2819.5 | 1882 | 891.5 | 38 | 67 | 763.35 | 219 | 3739 | 133.77 | 485.5 | 2168.86 | 0 | 0 | 5 | 0
17:00 | 2807 | 1879 | 892 | 38 | 64 | 763.69 | 219 | 3673 | 44.07 | 515 | 2180.86 | 0 | 0 | 3 | 0
17:30 | 2836.5 | 1877 | 891.5 | 38 | 68 | 765.385 | 218.5 | 3705.5 | 22.035 | 606 | 2318.36 | 0 | 0 | 1.5 | 183
18:00 | 2866 | 1875 | 891 | 38 | 72 | 767.08 | 218 | 3738 | 0 | 697 | 2455.86 | 0 | 0 | 0 | 366
18:30 | 2819.5 | 1871 | 890.5 | 38 | 73 | 759.26 | 217.5 | 3757.5 | 0 | 766.5 | 2541.71 | 0 | 0 | 2.5 | 324.5
19:00 | 2773 | 1867 | 890 | 38 | 74 | 751.44 | 217 | 3777 | 0 | 836 | 2627.56 | 0 | 0 | 5 | 283
19:30 | 2919 | 1925 | 891 | 38 | 76 | 757.08 | 209 | 3866 | 0 | 820 | 2644.86 | 0 | 0 | 5 | 286
20:00 | 2966 | 1932 | 891 | 38 | 66 | 754.32 | 218 | 3888 | 0 | 812 | 2534.06 | 0 | 0 | 8 | 281
20:30 | 2970 | 1936.5 | 891 | 38 | 66 | 761.66 | 218 | 3897 | 0 | 812 | 2475.26 | 0 | 0 | 9 | 264.5
21:00 | 2974 | 1941 | 891 | 38 | 66 | 769 | 218 | 3906 | 0 | 812 | 2416.46 | 0 | 0 | 10 | 248
21:30 | 2959 | 1933 | 891 | 38 | 70 | 769 | 218.5 | 3911.5 | 0 | 813.5 | 2375.61 | 0 | 0 | 10.5 | 250
22:00 | 2944 | 1925 | 891 | 38 | 74 | 769 | 219 | 3917 | 0 | 815 | 2334.76 | 0 | 0 | 11 | 252
22:30 | 2930.5 | 1933.1 | 891 | 38 | 74 | 764.5 | 219.5 | 3870 | 0 | 770 | 2312.36 | 0 | 0 | 6.5 | 231
23:00 | 2917 | 1941.2 | 891 | 38 | 74 | 760 | 220 | 3823 | 0 | 725 | 2289.96 | 0 | 0 | 2 | 210
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 05:00 | 377 | 10:00 | Payra | 412 | 05:00 | 408 | 11:00
Ashuganj | 408 | 5:00 | 384 | 10:00 | Rahanpur | 405 | 17:00 | 399 | 07:00
Bhulta | 404 | 02:00 | 384 | 14:00 | Rampal | 402 | 05:00 | 393 | 11:00
Bibiana | 391 | 04:00 | 385 | 10:00
BIPTC | 403 | 05:00 | 392 | 18:30
Bogura | 399 | 17:00 | 391 | 07:00
Gopalganj | 398 | 05:00 | 391 | 10:00
Kaliakoir | 381 | 02:00 | 369 | 10:00
Madunaghat | 397 | 19:00 | 390 | 11:00
Meghnaghat | 391 | 06:00 | 381 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 05:00 | 223 | 10:00 | Kaliakoir | 238 | 01:00 | 229 | 10:00
AKSML | 238 | 18:00 | 230 | 04:00 | Keranigonj | 230 | 05:00 | 221 | 10:00
Aminbazar | 232 | 02:00 | 225 | 10:00 | Khulna(S) | 231 | 06:00 | 224 | 16:00
Ashuganj | 235 | 03:00 | 227 | 09:00 | Madunaghat | 237 | 18:00 | 232 | 08:00
Ashuganj-400 | 235 | 03:00 | 227 | 09:00 | Madunaghat-400 | 238 | 19:00 | 232 | 10:00
Baghabari | 235 | 05:00 | 229 | 15:00 | Maniknagar | 222 | 03:00 | 215 | 10:00
Barapukuria | 227 | 18:00 | 220 | 07:00 | Meghnaghat | 230 | 00:00 | 224 | 10:00
Barapukuria-230 | 227 | 18:00 | 220 | 07:00 | Meghnaghat-400 | 227 | 05:00 | 219 | 10:00
Barishal | 237 | 22:00 | 232 | 11:00 | Mirsorai | 238 | 18:30 | 227 | 11:00
Bheramara | 234 | 06:00 | 228 | 15:00 | Rajshahi | 233 | 18:00 | 226 | 15:00
Bhulta | 233 | 02:00 | 215 | 10:00 | Rampal | 230 | 05:00 | 224 | 00:00
Bibiana | 230 | 04:00 | 226 | 09:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 228 | 15:00 | Rampura | 233 | 05:00 | 215 | 10:00
Bogura | 239 | 18:00 | 233 | 07:00 | Shikalbaha | 235 | 01:00 | 229 | 10:00
Bogura-400 | 238 | 17:00 | 233 | 07:00 | Shyampur | 227 | 02:00 | 219 | 10:00
Borhanuddin | 239 | 17:00 | 236 | 00:00 | Siddhirganj | 224 | 04:00 | 217 | 11:00
BSRM | 236 | 18:30 | 227 | 10:00 | Sirajgonj | 241 | 18:00 | 236 | 11:00
Cumilla(N) | 229 | 18:30 | 222 | 10:00 | Sreepur | 231 | 18:00 | 222 | 15:00
Faridpur | 233 | 06:00 | 228 | 09:00 | Tongi | 233 | 00:00 | 225 | 09:00
Fenchuganj | 234 | 06:00 | 229 | 00:00
Ghorashal | 236 | 22:00 | 225 | 18:30
Ghorashal-230 | 232 | 04:00 | 219 | 10:00
Gopalganj | 234 | 05:00 | 230 | 10:00
GPH | 233 | 01:00 | 229 | 10:00
Haripur | 223 | 02:00 | 217 | 19:00
Hasnabad | 228 | 01:00 | 220 | 09:00
Hathazari | 233 | 18:30 | 227 | 15:00
Ishurdi | 237 | 06:00 | 230 | 15:00
Jhenaidah | 231 | 08:00 | 224 | 14:00
Kachua | 233 | 18:00 | 225 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 01:00 | 124 | 10:00 | Lalmonirhat | 131 | 18:00 | 123 | 07:00
Agargaon | 137 | 05:00 | 130 | 10:00 | Madanganj | 129 | 18:00 | 124 | 09:00
Agrabad | 137 | 18:00 | 129 | 10:00 | Madaripur | 136 | 05:00 | 134 | 01:00
AKS | 134 | 18:00 | 129 | 10:00 | Madartek | 135 | 02:00 | 125 | 14:00
Aminbazar | 137 | 04:00 | 132 | 10:00 | Madunaghat | 138 | 18:00 | 133 | 10:00
Amnura | 137 | 18:00 | 130 | 13:00 | Magura | 135 | 05:00 | 130 | 00:00
Ashuganj | 142 | 05:00 | 137 | 21:00 | Mahasthangarh | 135 | 18:00 | 129 | 07:00
Bagerhat | 132 | 06:00 | 121 | 13:00 | Maijdee | 135 | 18:30 | 131 | 00:00
Bajitpur | 133 | 18:00 | 126 | 13:00 | Manikganj | 131 | 02:00 | 124 | 15:00
Bakulia | 137 | 18:30 | 132 | 10:00 | Maniknagar | 135 | 04:00 | 129 | 10:00
Banani | 136 | 02:00 | 126 | 15:00 | Matarbari | 124 | 18:30 | 113 | 23:00
Bangabhaban | 134 | 02:00 | 128 | 11:00 | Matuail | 129.5 | 05:00 | 124 | 10:00
Barapukuria | 139 | 18:00 | 130 | 07:00 | Metrorail_Motijheel | 135 | 04:00 | 129 | 10:00
Barguna | 137 | 04:00 | 134 | 12:00 | Metrorail_Uttara | 137 | 04:00 | 130 | 10:00
Barishal | 139 | 18:00 | 131 | 14:00 | Millgate | 136 | 01:00 | 127 | 10:00
Barishal-230 | 137 | 17:00 | 133 | 11:00 | Mirpur | 137 | 05:00 | 131 | 10:00
Baroaulia | 135 | 18:30 | 132 | 14:00 | Mirzapur | 132 | 05:00 | 128 | 07:00
Baroirhat | 135 | 18:00 | 131 | 10:00 | Mithapukur | 135 | 18:00 | 127 | 07:00
Bashundhara | 136 | 01:00 | 124 | 10:00 | MI_Cement | 134 | 01:00 | 127 | 10:00
BashundharaCement | 129 | 18:00 | 124 | 09:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 130 | 08:00 | 124 | 19:30 | Mogbazar | 137 | 02:00 | 125 | 11:00
Benapole | 133 | 05:00 | 126 | 00:00 | Mongla | 132 | 06:00 | 122 | 13:00
Bhaluka | 133 | 18:00 | 124 | 14:00 | Motijheel | 134 | 02:00 | 128 | 11:00
Bhandaria | 129 | 08:00 | 117 | 22:00 | Muktagacha | 157 | 20:00 | 123 | 19:00
Bhangura | 134 | 03:00 | 131 | 13:00 | Munshiganj | 130 | 18:00 | 122 | 10:00
Bheramara | 137 | 05:00 | 134 | 15:00 | Muradnagar | 130 | 17:00 | 125 | 11:00
Bheramara(GK) | 137 | 04:00 | 134 | 14:00 | Mymensingh | 132 | 06:00 | 116 | 14:00
Bhulta | 127 | 18:00 | 123 | 11:00 | Naogaon | 132 | 17:00 | 126 | 07:00
Bog-Sherpur | 136 | 18:00 | 131 | 07:00 | Narail | 137 | 06:00 | 129 | 22:00
Bogura | 138 | 18:00 | 132 | 07:00 | Narinda | 135 | 04:00 | 129 | 10:00
Bogura-230 | 137 | 17:00 | 132 | 07:00 | Narshingdi | 134 | 05:00 | 119 | 10:00
Brahmanbaria | 136 | 18:00 | 130 | 15:00 | Natore | 134 | 05:00 | 132 | 00:00
Cantonment | 137 | 05:00 | 130 | 10:00 | Nawabganj | 136 | 05:00 | 130 | 10:00
Chandina | 134 | 18:30 | 129 | 10:00 | Netrakona | 126 | 06:00 | 115 | 19:30
Chandpur | 140 | 18:30 | 136 | 01:00 | New | 135 | 00:00 | 128 | 10:00
Chandraghona | 137 | 18:00 | 134 | 10:00 | Niamatpur | 138 | 17:00 | 136 | 00:00
Chapai | 138 | 17:00 | 134 | 15:00 | Noapara | 136 | 06:00 | 129 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:00 | 123 | 10:00 | Pabna | 136 | 06:00 | 132 | 13:00
Chauddagram | 136 | 18:00 | 130 | 10:00 | Palashbari | 132 | 17:00 | 127 | 10:00
Chhatak | 130 | 07:00 | 122 | 23:00 | Panchagarh | 134 | 02:00 | 124 | 07:00
Chowmuhani | 134 | 18:00 | 130 | 15:00 | Patiya | 136 | 18:30 | 130 | 02:00
Chuadanga | 134 | 06:00 | 127 | 21:00 | Patuakhali | 137 | 06:00 | 135 | 00:00
Coxsbazar | 122 | 09:00 | 113 | 23:00 | Payra | 137 | 05:00 | 136 | 00:00
Cumilla(N) | 134 | 17:00 | 130 | 09:00 | PHP | 135 | 18:30 | 130 | 11:00
Cumilla(S) | 135 | 18:00 | 126 | 13:00 | Postogola | 136 | 01:00 | 130 | 10:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 02:00 | 124 | 10:00
Daudkandi | 128 | 18:00 | 121 | 11:00 | Purbasadipur | 133 | 02:00 | 125 | 07:00
DhakaUniversity | 136 | 02:00 | 125 | 10:00 | Rahanpur | 139 | 17:00 | 137 | 00:00
Dhamrai | 137 | 02:00 | 128 | 10:00 | Rahanpur-400 | 139 | 17:00 | 137 | 00:00
Dhanmondi | 136.6 | 05:00 | 124 | 10:00 | Rahim | 130 | 18:00 | 124 | 10:00
Dohazari | 133 | 18:00 | 127 | 20:00 | Rajbari | 136 | 04:00 | 133 | 00:00
Faridpur | 138 | 02:00 | 134 | 13:00 | Rajendrapur | 140 | 18:00 | 124 | 14:00
Fatullah | 138 | 04:00 | 132 | 10:00 | Rajshahi | 134 | 19:30 | 130 | 13:00
Fenchuganj | 137 | 06:00 | 134 | 14:00 | Rajshahi-230 | 134 | 18:00 | 130 | 12:00
Feni | 135 | 18:30 | 128 | 10:00 | Ramganj | 135 | 18:00 | 131 | 01:00
Ghatail | 129 | 05:00 | 123 | 19:30 | Rampur | 135 | 18:00 | 131 | 09:00
Ghorashal | 139 | 00:00 | 133 | 11:00 | Rampura | 136 | 02:00 | 124 | 10:00
Goalpara | 138 | 06:00 | 130 | 22:00 | Rangamati | 136 | 18:30 | 133 | 10:00
Gollamari | 137 | 06:00 | 132 | 01:00 | Rangpur | 135 | 18:00 | 128 | 08:00
Gopalganj | 136 | 05:00 | 132 | 12:00 | Ruppur | 137 | 03:00 | 135 | 00:00
Gopalganj-400 | 137 | 05:00 | 135 | 00:00 | Saidpur | 137 | 18:00 | 125 | 07:00
Gulshan | 135 | 03:00 | 126 | 11:00 | Satkhira | 135 | 06:00 | 127 | 22:00
Halishahar | 135 | 01:00 | 131 | 10:00 | Satmasjid | 136 | 02:00 | 130 | 06:00
Haripur | 130 | 06:00 | 124 | 10:00 | Savar | 137 | 18:00 | 130 | 10:00
HaripurSBU | 130 | 06:00 | 124 | 10:00 | SevenRings | 140 | 02:00 | 132 | 10:00
Hasnabad | 136 | 04:00 | 130 | 10:00 | ShahCement | 130 | 18:00 | 123 | 10:00
Hathazari | 137 | 18:30 | 134 | 07:00 | Shahjadpur | 136 | 04:00 | 135 | 00:00
Ishurdi | 138 | 05:00 | 136 | 00:00 | Shahjibazar | 136 | 18:00 | 131 | 19:30
Jaldhaka | 132 | 16:00 | 123 | 07:00 | Shahmirpur | 136 | 18:00 | 131 | 10:00
Jamalpur | 132 | 05:00 | 121 | 19:30 | Shariatpur | 136 | 05:00 | 133 | 00:00
Jashore | 133 | 06:00 | 126 | 13:00 | Sherpur | 130 | 06:00 | 116 | 19:30
Jhenaidah | 137 | 05:00 | 127 | 00:00 | Shikalbaha | 126 | 00:00 | 118 | 01:00
Jhenaidah-230 | 138 | 06:00 | 132 | 00:00 | Shikalbaha-230 | 138 | 18:00 | 133 | 10:00
Joydebpur | 140 | 01:00 | 131 | 15:00 | Shitalakhya | 134 | 01:00 | 127 | 10:00
Joypurhat | 130 | 17:00 | 124 | 00:00 | Sholosohor | 136 | 01:00 | 133 | 10:00
Juldah | 136 | 18:00 | 131 | 10:00 | Shyampur | 137 | 00:00 | 135 | 09:00
Kabirpur | 136 | 13:00 | 125 | 15:00 | Shyampur-230 | 138 | 02:00 | 132 | 10:00
Kachua | 139 | 18:30 | 135 | 01:00 | Siddhirganj | 130 | 02:00 | 125 | 10:00
Kaliakoir | 139 | 02:00 | 131 | 10:00 | Sirajganj | 132 | 02:00 | 130 | 06:00
Kallyanpur | 137 | 00:00 | 132 | 10:00 | Sonargaon | 127 | 06:00 | 123 | 11:00
Kalurghat | 138 | 18:30 | 134 | 04:00 | Sreemongol | 135 | 08:00 | 130 | 15:00
Kamrangirchar | 136 | 02:00 | 129 | 10:00 | Sreepur | 135 | 08:00 | 127 | 14:00
Kaptai | 134 | 19:00 | 127 | 12:00 | Srinagar | 136 | 04:00 | 130 | 10:00
Kasba | 130 | 17:00 | 124 | 11:00 | SSM | 139 | 00:00 | 136 | 10:00
Kazla | 134 | 08:00 | 128 | 11:00 | Sunamganj | 128 | 12:00 | 119 | 19:30
Keranigonj | 137 | 05:00 | 130 | 10:00 | Sylhet | 131 | 07:00 | 127 | 19:30
Khagrachori | 135 | 18:30 | 132 | 10:00 | Sylhet-132 | 131 | 07:00 | 128 | 15:00
Khulna | 137 | 09:00 | 131 | 23:00 | Tangail | 129 | 06:00 | 124 | 14:00
Khulna(S) | 138 | 06:00 | 132 | 22:00 | Taraganj | 134 | 18:00 | 128 | 07:00
Khulshi | 134 | 18:00 | 129 | 10:00 | Thakurgaon | 135 | 02:00 | 124 | 07:00
Kishoreganj | 131 | 05:00 | 123 | 14:00 | TK | 137 | 18:00 | 133 | 10:00
Kodda | 139 | 18:00 | 126 | 09:00 | Tongi | 137 | 04:00 | 131 | 15:00
KSRM | 136 | 18:00 | 131 | 10:00 | Ullahpara | 134 | 03:00 | 131 | 10:00
Kulaura | 136 | 06:00 | 133 | 14:00 | Ullon | 136 | 02:00 | 126 | 09:00
Kurigram | 132 | 18:00 | 121 | 07:00 | Uttara | 135 | 01:00 | 127 | 10:00
Kushtia | 134 | 03:00 | 131 | 00:00 | UttaraNew | 137 | 04:00 | 129 | 09:00
Laksam | 138 | 18:30 | 133 | 13:00 | Zigatola | 136 | 04:00 | 130 | 10:00
Lakshmipur | 134 | 08:00 | 131 | 03:00
Lalbag | 136 | 04:00 | 129 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division