## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-10-2025 | during | 15-10-2025 | during | 15-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 94 | 96 | 208.13 | 208.13 | 100 | 100 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 46.8 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 92 | 138 | 149.36 | 149.36 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20.5 | 24.75 | 24.75 | 24.75 | 24.75 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 260 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 126 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 475 | 495 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 2281 | 2601.3 | 5428.4 | 5395.4 | 3693.75 | 3754.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 19 | 19 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 183 | 183 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 52 | 40 | 70 | 40 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 11 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 44 | 44 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.47 | 0 | 1.76 | 0 | 1.76 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 49 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 94 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 15 | 90 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 160 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1152 | 1217 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 285 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2040.97 | 2551.86 | 3237.48 | 3265.72 | 2958.62 | 2986.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 177 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 300 | 300 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 2 | 2 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 112 | 130 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 2 | 29 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 102 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 104 | 200 | 200 | 50 | 150 | Engine Problem
| Import (Tripura) | Import | Import |  | 160 | 160 | 48 | 80 | 160 | 160 | 76 | 76 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 16 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 38 | 68 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1446 | 1492 | 2828.86 | 2763.86 | 2249.16 | 2293.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-10-2025 | during | 15-10-2025 | during | 15-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 12 | 157.5 | 157.5 | 49 | 49 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 47 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.87 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 187.87 | 138 | 400.9 | 349 | 238.9 | 187
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 151 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 84 | 152 | 160 | 160 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 10 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 333 | 300 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1115 | 1147 | 1255 | 1255 | 1191 | 1191
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 893 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 63 | 50 | 60 | 50 | 60 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 147 | 114 | 410 | 410 | 169 | 169 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 365 | 365 | 370 | 370 | 370 | 370 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1530 | 1512 | 2768 | 2698 | 1764 | 1694
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 307 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 28 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1210 | 1194 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 275 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2172.66 | 2270 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 59.56 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 205 | 200 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 408 | 390 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 25 | 25 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 80 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.84 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 756 | 762.93 | 748 | 748 | 748 | 748 | Unit-2 Under Shutdown
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.49 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1779.89 | 1777.93 | 2498.64 | 2331.99 | 2398.06 | 2231.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 0 | 0 | 47 | 47 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 161 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 112 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 194 | 0 | 182.7 | 0 | 182.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 625.8 | 434 | 616.7 | 398 | 663.7 | 445
System Total |  |  |  |  | 28823.2 | 28364.092 | 13179.19 | 13924.09 | 21180.98 | 20602.97 | 17171.19 | 16796.18
Forecast Scenario (15-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13700 |  | 0 |  | 13700
|  |  |  | 1:00 | 13460 |  | 0 |  | 13460
|  |  |  | 2:00 | 12850 |  | 0 |  | 12850
|  |  |  | 3:00 | 12160 |  | 0 |  | 12160
|  |  |  | 4:00 | 11890 |  | 0 |  | 11890
|  |  |  | 5:00 | 11520 |  | 0 |  | 11520
|  |  |  | 6:00 | 11160 |  | 0 |  | 11160
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11470 |  | 0 |  | 11470
|  |  |  | 9:00 | 11700 |  | 0 |  | 11700
|  |  |  | 10:00 | 12070 |  | 0 |  | 12070
|  |  |  | 11:00 | 12720 |  | 0 |  | 12720
|  |  |  | 12:00 | 13190 |  | 0 |  | 13190
|  |  |  | 13:00 | 13580 |  | 0 |  | 13580
|  |  |  | 14:00 | 13700 |  | 0 |  | 13700
|  |  |  | 15:00 | 13740 |  | 0 |  | 13740
|  |  |  | 16:00 | 13450 |  | 0 |  | 13450
|  |  |  | 17:00 | 13330 |  | 0 |  | 13330
|  |  |  | 18:00 | 14000 |  | 0 |  | 14000
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14370 |  | 0 |  | 14370
|  |  |  | 19:30 | 14400 |  | 0 |  | 14400
|  |  |  | 20:00 | 14380 |  | 0 |  | 14380
|  |  |  | 21:00 | 14300 |  | 0 |  | 14300
|  |  |  | 22:00 | 14000 |  | 0 |  | 14000
|  |  |  | 23:00 | 13900 |  | 0 |  | 13900
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 13190.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.04 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:35 hrs on 15-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-10-2025 | [28 empty] | Date: | 14-10-2025 | [28 empty] | Date: | 14-10-2025 | [28 empty] | Date: | 14-10-2025 | [28 empty] | Date: | 14-10-2025 | [14 empty] | Date: | 14-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 17 | 149 | 125 | 277 | 55 | 0 | 72 | 0 | 450 | 0 | 574 | 0 | 0 | 329 | 36 | 0 | 0 | 52 | 21 | 22 | 0 | 0 | 102 | 16 | 101 | 0 | 0 | 49 | 60 | 54.36 | 0 | 0 | 0 | 220 | 110 | 26 | 285 | 17 | 0 | 19 | 25.5 | 0 | 182 | 0 | 0 | 0 | 1185 | 0 | 51 | 135 | 0 | 0 | 320 | 300 | 0 | 173 | 0 | 33 | 102 | 139 | 0 | 19 | 97 | 74 | 43 | 0 | 37 | 325 | 0 | 346 | 30 | 68 | 160 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 34 | 0 | 0 | 12 | 7664.86 | 891 | 136 | 0 | 31 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 763 | 0 | 41 | 0 | 113 | 113 | 0 | 88 | 37 | 8 | 0 | 0 | 25 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 158 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 278 | 115 | 220 | 0 | 308 | 1200 | 35 | 5964 | 13628.86 | 107.17
01:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 149 | 125 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 563 | 0 | 35 | 331 | 36 | 0 | 0 | 17 | 21 | 22 | 0 | 0 | 97 | 16 | 104 | 0 | 5 | 49 | 60 | 54.36 | 0 | 0 | 0 | 221 | 104 | 25 | 285 | 17 | 0 | 19 | 25.5 | 0 | 182 | 0 | 0 | 0 | 1150 | 0 | 51 | 135 | 0 | 0 | 320 | 300 | 0 | 172 | 0 | 34 | 103 | 93 | 0 | 19 | 97 | 70 | 43 | 0 | 37 | 315 | 0 | 302 | 30 | 68 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 34 | 0 | 0 | 8 | 7438.86 | 891 | 142 | 0 | 19 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 763 | 0 | 41 | 0 | 113 | 113 | 0 | 0 | 37 | 8 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 115 | 220 | 0 | 308 | 1200 | 35 | 5906 | 13344.86 | 107.16
02:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 135 | 15 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 540 | 0 | 35 | 332 | 35 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 0 | 16 | 69 | 0 | 6 | 49 | 60 | 54.36 | 0 | 0 | 0 | 219 | 98 | 25 | 285 | 17 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1157 | 0 | 51 | 132 | 0 | 0 | 320 | 300 | 0 | 172 | 0 | 34 | 103 | 51 | 0 | 19 | 13 | 62 | 0 | 0 | 37 | 305 | 0 | 332 | 30 | 68 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 17 | 67 | 48 | 34 | 0 | 0 | 12 | 6965.86 | 892 | 140 | 0 | 11 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 753 | 0 | 41 | 0 | 113 | 113 | 0 | 0 | 37 | 8 | 0 | 0 | 25 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 115 | 220 | 0 | 308 | 1200 | 35 | 5786 | 12751.86 | 107.16
03:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 131 | 0 | 277 | 0 | 0 | 35 | 0 | 450 | 0 | 548 | 0 | 35 | 332 | 36 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 45 | 60 | 17 | 0 | 0 | 0 | 219 | 93 | 26 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1156 | 0 | 51 | 132 | 0 | 0 | 320 | 300 | 0 | 172 | 0 | 34 | 104 | 52 | 0 | 19 | 0 | 62 | 0 | 0 | 37 | 305 | 0 | 312 | 30 | 68 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 67 | 48 | 34 | 0 | 0 | 12 | 6663.5 | 891 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 115 | 220 | 0 | 308 | 1200 | 35 | 5465 | 12128.5 | 107.15
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 245 | 0 | 0 | 35 | 0 | 450 | 0 | 555 | 0 | 35 | 333 | 36 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 31 | 0 | 0 | 0 | 0 | 219 | 95 | 26 | 285 | 0 | 0 | 19 | 0 | 0 | 181 | 0 | 0 | 0 | 1160 | 0 | 51 | 137 | 0 | 0 | 320 | 300 | 0 | 180 | 0 | 34 | 105 | 51 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 333 | 30 | 68 | 157 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 34 | 0 | 0 | 12 | 6529.5 | 891 | 141 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 165 | 47 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 309 | 1200 | 35 | 5364 | 11893.5 | 107.15
05:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 145 | 0 | 0 | 35 | 0 | 450 | 0 | 549 | 0 | 0 | 333 | 36 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 4 | 16 | 31 | 0 | 0 | 0 | 0 | 219 | 94 | 27 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1163 | 0 | 51 | 80 | 0 | 0 | 320 | 300 | 0 | 184 | 0 | 34 | 105 | 51 | 0 | 13 | 0 | 66 | 0 | 0 | 0 | 315 | 0 | 333 | 30 | 68 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 69 | 48 | 34 | 0 | 0 | 12 | 6305.5 | 891 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 165 | 47 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 115 | 220 | 0 | 309 | 1120 | 35 | 5216 | 11521.5 | 107.14
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 45 | 0 | 0 | 35 | 0 | 450 | 0 | 552 | 0 | 0 | 335 | 36 | 0 | 0 | 17 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 31 | 0 | 0 | 0 | 0.01 | 219 | 51 | 27 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 0 | 0 | 320 | 300 | 0 | 187 | 0 | 34 | 105 | 52 | 0 | 13 | 0 | 58 | 0 | 0 | 0 | 310 | 0 | 300 | 30 | 68 | 156 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 69 | 48 | 34 | 0 | 0.13 | 12 | 6010.34 | 891 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.5 | 366 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 160 | 45 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 115 | 220 | 0 | 309 | 1090 | 35 | 5157.55 | 11167.89 | 107.14
07:00 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 45 | 0 | 0 | 35 | 0 | 450 | 0 | 565 | 0 | 0 | 331 | 36 | 0 | 6 | 17 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 31 | 0 | 0 | 0 | 0.37 | 219 | 51 | 30 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1168 | 5 | 51 | 50 | 0 | 0 | 320 | 300 | 0 | 184 | 0 | 34 | 105 | 52 | 0 | 13 | 0 | 48 | 0 | 15 | 0 | 315 | 0 | 350 | 30 | 68 | 158 | 8 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 34 | 0 | 8.1 | 12 | 6109.97 | 891 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 366 | 0 | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.84 | 17 | 0 | 0 | 9.75 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.18 | 160 | 46 | 50 | 5 | 49 | 0 | 0 | 0 | 0.8 | 30 | 0.08 | 0 | 279 | 115 | 220 | 0 | 309 | 1110 | 35 | 5290.65 | 11400.62 | 107.13
08:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 95 | 7 | 0 | 35 | 0 | 450 | 0 | 527 | 0 | 0 | 333 | 36 | 0 | 16 | 17 | 21.5 | 22 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.76 | 219 | 51 | 2 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1160 | 11 | 51 | 78 | 0 | 0 | 280 | 250 | 0 | 207 | 0 | 34 | 104 | 52 | 0 | 13 | 0 | 38 | 0 | 36 | 0 | 310 | 0 | 320 | 30 | 68 | 148 | 8 | 0 | 81 | 30 | 0 | 16 | 35 | 0 | 69 | 49 | 27 | 1 | 22.75 | 12 | 6066.01 | 891 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 366 | 0 | 758 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 29.51 | 50 | 0 | 0 | 28.76 | 180 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 2.42 | 158 | 47 | 50 | 14 | 49 | 0 | 0 | 0 | 2.8 | 79 | 0.25 | 0 | 274 | 115 | 180 | 0 | 308 | 1195 | 35 | 5412.74 | 11478.75 | 107.13
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 95 | 15 | 17 | 35 | 0 | 450 | 0 | 490 | 0 | 0 | 333 | 37 | 0 | 24 | 52 | 21 | 22 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 2.62 | 219 | 50 | 4 | 285 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 1120 | 15 | 51 | 80 | 0 | 0 | 280 | 250 | 0 | 201 | 0 | 35 | 103 | 51 | 0 | 13 | 0 | 32 | 0 | 54 | 0 | 320 | 0 | 333 | 30 | 68 | 145 | 8 | 0 | 81 | 30 | 0 | 16 | 35 | 0 | 69 | 49 | 28 | 2 | 36.36 | 12 | 6130.98 | 891 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 366 | 0 | 761 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 45.63 | 80 | 0 | 0 | 46.81 | 170 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 4.01 | 157 | 47 | 50 | 23 | 49 | 0 | 0 | 0 | 4.7 | 131 | 0.43 | 0 | 272 | 115 | 220 | 0 | 308 | 1178 | 35 | 5576.58 | 11707.56 | 107.12
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 96 | 25 | 95 | 15 | 17 | 54 | 0 | 450 | 0 | 505 | 0 | 0 | 330 | 95 | 0 | 29 | 52 | 21 | 22 | 0 | 0 | 13 | 15 | 12 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2.41 | 219 | 51 | 5 | 285 | 0 | 0 | 8 | 0 | 0 | 183 | 0 | 0 | 0 | 1165 | 18 | 51 | 98 | 0 | 0 | 280 | 250 | 0 | 198 | 0 | 34 | 100 | 51 | 0 | 13 | 0 | 52 | 0 | 64 | 0 | 315 | 0 | 331 | 30 | 68 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 57 | 0 | 69 | 48 | 28 | 2 | 45.93 | 12 | 6365.34 | 891 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 365 | 0 | 763 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 56.05 | 101 | 0 | 0 | 58.52 | 170 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 5.05 | 159 | 48 | 50 | 31 | 49 | 0 | 0 | 0 | 6 | 167 | 0.56 | 0 | 277 | 115 | 220 | 0 | 308 | 1181 | 35 | 5713.18 | 12078.52 | 107.12
11:00 | 0 | 55 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 132 | 50 | 277 | 25 | 35 | 54 | 0 | 450 | 0 | 510 | 0 | 0 | 328 | 95 | 0 | 32 | 90 | 20 | 22 | 0 | 0 | 13 | 15 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3.45 | 219 | 51 | 2 | 285 | 17 | 0 | 0 | 13 | 0 | 183 | 0 | 0 | 0 | 1110 | 16 | 51 | 108 | 0 | 0 | 320 | 300 | 2 | 190 | 0 | 34 | 100 | 51 | 4 | 13 | 60 | 54 | 4 | 74 | 0 | 320 | 0 | 313 | 30 | 68 | 159 | 12 | 0 | 81 | 30 | 0 | 16 | 65 | 0 | 68 | 48 | 11 | 2 | 49.94 | 12 | 6848.39 | 893 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 365 | 0 | 760 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 60.25 | 110 | 0 | 0 | 65.11 | 188 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 5.66 | 157 | 48 | 75 | 35 | 49 | 0 | 0 | 0 | 6 | 177 | 0.25 | 1 | 271 | 115 | 220 | 0 | 308 | 1181 | 17 | 5851.27 | 12699.66 | 107.11
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 92 | 260 | 55 | 35 | 54 | 0 | 450 | 0 | 475 | 0 | 0 | 326 | 94 | 0 | 34 | 90 | 20 | 0 | 0 | 0 | 15 | 15 | 44 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3.47 | 219 | 54 | 5 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1152 | 15 | 51 | 112 | 0 | 0 | 343 | 300 | 2 | 202 | 0 | 38 | 100 | 52 | 9 | 13 | 80 | 48 | 34 | 60 | 2 | 315 | 0 | 333 | 30 | 67 | 147 | 12 | 0 | 81 | 30 | 0 | 16 | 84 | 0 | 68 | 49 | 10 | 2 | 46.87 | 12 | 7070.84 | 893 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 365 | 0 | 756 | 0 | 0 | 0 | 90 | 80 | 0 | 0 | 0 | 0 | 59.56 | 110 | 0 | 0 | 65.49 | 205 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 5.84 | 157 | 47 | 115 | 36 | 70 | 0 | 0 | 0 | 6.8 | 194 | 0.66 | 28 | 275 | 115 | 220 | 0 | 307 | 1210 | 17 | 6108.35 | 13179.19 | 107.11
13:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 92 | 260 | 55 | 35 | 54 | 0 | 450 | 0 | 495 | 0 | 17 | 324 | 93 | 0 | 33 | 90 | 19 | 0 | 0 | 0 | 26 | 16 | 45 | 0 | 0 | 0 | 8 | 1 | 0 | 0 | 3.24 | 219 | 86 | 12 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1165 | 19 | 51 | 108 | 0 | 0 | 338 | 330 | 2 | 205 | 0 | 50 | 99 | 51 | 8 | 13 | 80 | 78 | 34 | 68 | 33 | 315 | 0 | 359 | 30 | 67 | 153 | 10 | 0 | 81 | 30 | 0 | 16 | 95 | 0 | 68 | 48 | 10 | 2 | 44.54 | 12 | 7312.28 | 893 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 364 | 0 | 754 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 58.13 | 107 | 0 | 0 | 61.83 | 204 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.6 | 157 | 47 | 115 | 36 | 113 | 0 | 0 | 0 | 6.4 | 177 | 0.66 | 76 | 307 | 115 | 220 | 0 | 307 | 1210 | 17 | 6256.62 | 13568.9 | 107.1
14:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31 | 149 | 92 | 277 | 55 | 35 | 54 | 0 | 450 | 0 | 530 | 0 | 35 | 323 | 92 | 0 | 26 | 90 | 19.2 | 22 | 0 | 0 | 97 | 16 | 44 | 0 | 5 | 0 | 8 | 54.36 | 0 | 0 | 2.7 | 219 | 94 | 5 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 16 | 51 | 107 | 0 | 0 | 320 | 300 | 2 | 172 | 0 | 51 | 99 | 51 | 0 | 18 | 96 | 76 | 34 | 56 | 35 | 310 | 0 | 340 | 30 | 68 | 154 | 10 | 0 | 80 | 30 | 0 | 16 | 100 | 0 | 68 | 48 | 10 | 2 | 41.79 | 8 | 7489.55 | 892 | 128 | 0 | 7 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75 | 365 | 0 | 757 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 50.88 | 94 | 0 | 0 | 53.98 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.71 | 160 | 47 | 115 | 11 | 113 | 0 | 0 | 0 | 5.5 | 149 | 0.55 | 100 | 307 | 115 | 220 | 0 | 307 | 1202 | 17 | 6179.62 | 13669.17 | 107.1
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 92 | 277 | 55 | 35 | 54 | 0 | 450 | 0 | 520 | 0 | 35 | 322 | 94 | 0 | 20 | 52 | 19.5 | 21 | 0 | 0 | 109 | 16 | 45 | 0 | 6 | 0 | 35 | 54.36 | 0 | 0 | 1.88 | 221 | 106 | 0 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 12 | 51 | 105 | 0 | 0 | 320 | 300 | 2 | 175 | 0 | 51 | 99 | 51 | 0 | 18 | 96 | 84 | 43 | 41 | 34 | 320 | 0 | 322 | 30 | 68 | 153 | 12 | 0 | 80 | 30 | 0 | 16 | 116 | 0 | 67 | 48 | 11 | 1 | 30.52 | 12 | 7487.76 | 892 | 128 | 0 | 18 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 365 | 0 | 770.94 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 38.27 | 66 | 0 | 0 | 37.01 | 205 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 3.3 | 161 | 46 | 115 | 22 | 113 | 0 | 0 | 0 | 3.9 | 109 | 0.44 | 110 | 307 | 115 | 220 | 0 | 308 | 1190 | 17 | 6076.86 | 13564.62 | 107.09
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 149 | 92 | 277 | 55 | 35 | 72 | 0 | 450 | 0 | 495 | 0 | 35 | 321 | 93 | 0 | 10 | 52 | 19 | 21 | 0 | 0 | 92 | 16 | 43 | 0 | 4 | 48 | 35 | 54.36 | 0 | 0 | 0.89 | 221 | 108 | 0 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 7 | 51 | 105 | 0 | 0 | 300 | 300 | 2 | 169 | 0 | 51 | 100 | 58 | 0 | 13 | 114 | 78 | 16 | 21 | 37 | 310 | 0 | 321 | 30 | 68 | 152 | 12 | 0 | 80 | 30 | 0 | 16 | 132 | 0 | 67 | 48 | 11 | 1 | 15.48 | 12 | 7425.23 | 892 | 125 | 0 | 21 | 12 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 366 | 0 | 764.54 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 20.97 | 39 | 0 | 0 | 19.73 | 205 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 1.8 | 161 | 46 | 115 | 10 | 113 | 0 | 0 | 0 | 2.1 | 54 | 0.18 | 110 | 307 | 115 | 220 | 0 | 307 | 1184 | 17 | 5874.32 | 13299.55 | 107.09
17:00 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2 | 17 | 149 | 122 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 500 | 0 | 35 | 321 | 39 | 0 | 2 | 52 | 19 | 21 | 0 | 0 | 92 | 16 | 38 | 0 | 0 | 65 | 37 | 54.36 | 0 | 0 | 0.07 | 221 | 97 | 4 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 1 | 51 | 117 | 0 | 0 | 300 | 300 | 2 | 174 | 0 | 50 | 100 | 57 | 0 | 19 | 114 | 66 | 16 | 3 | 27 | 315 | 0 | 290 | 30 | 68 | 153 | 12 | 0 | 80 | 30 | 0 | 16 | 148 | 0 | 67 | 48 | 11 | 0 | 2.55 | 12 | 7390.68 | 892 | 125 | 0 | 34 | 33 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 366 | 0 | 765.08 | 0 | 40 | 0 | 113 | 113 | 0 | 7.3 | 14 | 0 | 3.2 | 9 | 6 | 0 | 3.22 | 205 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0.26 | 158 | 45 | 115 | 2 | 109 | 0 | 0 | 0 | 0.5 | 8 | 0.38 | 110 | 307 | 115 | 220 | 0 | 307 | 1188 | 17 | 5808.94 | 13199.62 | 107.08
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.9 | 17 | 149 | 138 | 277 | 55 | 35 | 126 | 0 | 420 | 0 | 460 | 0 | 55 | 322 | 94 | 0 | 0 | 142 | 20 | 21 | 0 | 0 | 94 | 18 | 43 | 0 | 0 | 66 | 52 | 54.36 | 0 | 0 | 0 | 221 | 98 | 2 | 285 | 72 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1197 | 0 | 51 | 117 | 0 | 0 | 300 | 300 | 2 | 175 | 0 | 51 | 102 | 88 | 0 | 19 | 114 | 82 | 16 | 0 | 27 | 315 | 0 | 318 | 30 | 67 | 152 | 10 | 0 | 81 | 30 | 0 | 16 | 152 | 0 | 67 | 48 | 11 | 0 | 0 | 12 | 7673.76 | 891 | 120 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 758.54 | 0 | 40 | 0 | 113 | 113 | 0 | 85 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 159 | 46 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 307 | 1180 | 17 | 5943.54 | 13617.3 | 107.08
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.8 | 17 | 149 | 138 | 277 | 55 | 55 | 126 | 0 | 450 | 0 | 495 | 0 | 55 | 328 | 96 | 0 | 0 | 142 | 20.5 | 21 | 0 | 0 | 90 | 49 | 44 | 0 | 0 | 66 | 52 | 54.36 | 0 | 0 | 0 | 221 | 94 | 11 | 285 | 160 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1217 | 0 | 51 | 130 | 0 | 0 | 300 | 300 | 2 | 177 | 0 | 68 | 102 | 104 | 0 | 19 | 114 | 80 | 16 | 0 | 29 | 310 | 0 | 300 | 30 | 67 | 151 | 10 | 0 | 81 | 30 | 0 | 16 | 152 | 0 | 67 | 47 | 12 | 0 | 0 | 12 | 7930.16 | 891 | 114 | 0 | 41 | 63 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 762.93 | 0 | 40 | 0 | 113 | 113 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 161 | 46 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 307 | 1194 | 17 | 5993.93 | 13924.09 | 107.08
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 17 | 149 | 139 | 277 | 55 | 55 | 126 | 0 | 450 | 0 | 540 | 0 | 55 | 321 | 36 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 92 | 49 | 44 | 0 | 0 | 66 | 52 | 54.36 | 0 | 0 | 0 | 220 | 94 | 13 | 285 | 40 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 0 | 51 | 134 | 0 | 0 | 300 | 300 | 2 | 176 | 0 | 90 | 103 | 103 | 9 | 19 | 114 | 84 | 16 | 0 | 35 | 320 | 0 | 322 | 30 | 67 | 152 | 10 | 0 | 81 | 30 | 0 | 16 | 152 | 0 | 67 | 48 | 12 | 0 | 0 | 12 | 7879.36 | 891 | 113 | 0 | 37 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 752.97 | 0 | 40 | 0 | 113 | 113 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 43 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 307 | 1220 | 17 | 6010.97 | 13890.33 | 107.07
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 149 | 139 | 277 | 55 | 55 | 126 | 0 | 450 | 0 | 520 | 0 | 55 | 327 | 96 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 89 | 52 | 41 | 0 | 4 | 66 | 52 | 54.36 | 0 | 0 | 0 | 220 | 100 | 15 | 285 | 17 | 0 | 0 | 25.5 | 0 | 183 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 172 | 0 | 90 | 102 | 105 | 8 | 19 | 114 | 84 | 16 | 0 | 36 | 310 | 0 | 322 | 30 | 67 | 153 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 67 | 48 | 12 | 0 | 0 | 12 | 7906.36 | 891 | 108 | 0 | 37 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 760.35 | 0 | 40 | 0 | 113 | 113 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 157 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 307 | 1220 | 17 | 6008.35 | 13914.71 | 107.07
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 149 | 140 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 547 | 0 | 55 | 327 | 96 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 87 | 52 | 18 | 0 | 0 | 66 | 52 | 54.36 | 0 | 0 | 0 | 219 | 106 | 10 | 285 | 17 | 0 | 0 | 25.5 | 0 | 137 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 176 | 0 | 82 | 102 | 103 | 9 | 19 | 97 | 74 | 16 | 0 | 36 | 305 | 0 | 363 | 30 | 67 | 153 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 12 | 0 | 0 | 12 | 7826.36 | 891 | 107 | 0 | 37 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 763.44 | 0 | 40 | 0 | 113 | 113 | 0 | 96 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 115 | 220 | 0 | 307 | 1220 | 17 | 5971.44 | 13797.8 | 107.07
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.7 | 17 | 149 | 140 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 567 | 0 | 35 | 328 | 36 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 96 | 16 | 14 | 0 | 8 | 66 | 44 | 54.36 | 0 | 0 | 0 | 219 | 108 | 15 | 285 | 17 | 0 | 0 | 25.5 | 0 | 175 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 179 | 0 | 71 | 102 | 103 | 10 | 19 | 97 | 82 | 16 | 0 | 36 | 300 | 0 | 356 | 30 | 67 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 12 | 0 | 0 | 12 | 7780.06 | 891 | 104 | 0 | 37 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 765.78 | 0 | 40 | 0 | 113 | 113 | 0 | 97 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 115 | 220 | 0 | 307 | 1221 | 17 | 5949.78 | 13729.84 | 107.07
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2 | 17 | 149 | 140 | 277 | 55 | 35 | 108 | 0 | 450 | 0 | 548 | 0 | 0 | 328 | 96 | 0 | 0 | 52 | 19.5 | 22 | 0 | 0 | 95 | 16 | 12 | 0 | 5 | 66 | 44 | 54.36 | 0 | 0 | 0 | 219 | 106 | 16 | 285 | 17 | 0 | 0 | 25.5 | 0 | 175 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 175 | 0 | 39 | 103 | 104 | 0 | 19 | 97 | 82 | 43 | 0 | 36 | 310 | 0 | 356 | 30 | 67 | 154 | 10 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 23 | 0 | 0 | 12 | 7686.56 | 890 | 103 | 0 | 37 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 759.34 | 0 | 40 | 0 | 113 | 113 | 0 | 97 | 37 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 158 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 307 | 1222 | 17 | 5890.34 | 13576.9 | 107.06
Total KWH | 0 | 1885440 | 497280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518760 | 309240 | 3171456 | 1719360 | 5410855 | 938470 | 529175 | 1576800 | 0 | 10498500 | 0 | 12603636 | 0 | 532525 | 7862031 | 1711000 | 0 | 227280 | 1610400 | 487800 | 464760 | 0 | 0 | 1363691 | 426545 | 669120 | 0 | 84960 | 720054 | 863904 | 790409 | 0 | 0 | 22043 | 5212650 | 2140245 | 319680 | 6814545.46 | 458327 | 0 | 190560 | 366305.4 | 9199 | 4325847 | 0 | 0 | 0 | 28319997 | 131760 | 1238468 | 2793454 | 0 | 0 | 7828500 | 7220000 | 36000 | 4449000 | 0 | 1114560 | 2426440 | 1651680 | 54600 | 381160 | 1485420 | 1601280 | 399024 | 478505 | 503840 | 7601000 | 0 | 8371000 | 718000 | 1592880 | 3692127 | 242088 | 0 | 1927680 | 719328 | 0 | 393000 | 2905200 | 37800 | 1638000 | 1159200 | 464640 | 14150 | 322940 | 290640 | 171536213.86 | 21586181 | 3361536 | 0 | 345120 | 419200 | 912000 | 0 | 0 | 0 | 0 | 0 | 628560 | 8843636 | 0 | 18327273 | 0 | 429765 | 0 | 1709280 | 1926144 | 0 | 626672 | 330290 | 20285 | 436198 | 809110 | 243850 | 0 | 445504 | 4767273 | 0 | 0 | 0 | 0 | 0 | 9651636 | 0 | 39300 | 3931000 | 1073890 | 2387132 | 222345 | 2216736 | 0 | 0 | 0 | 45341.52 | 1247760 | 4078 | 1512384 | 6960000 | 2743000 | 5437000 | 0 | 7389090.91 | 28602181.82 | 616800 | 140247552.25 | 311783766.11

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13179.19 | MW | 12:00 Hr. | Energy Generated |  |  | 311.7838 |  | MKWHr.
| Day Peak Demand |  |  | 13194.87 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.676 |  | MKWHr.
| Evening Peak Generation |  |  | 13924.09 | MW | 19:00 Hr. | Energy Demand |  |  | 314.4598 |  | MKWHr.
| Evening Peak Demand |  |  | 14272.08 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 11167.89 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 865.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 13924.09 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 7.1173 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.6277 | 0 | 18.6998 | 0 | 0 | 0.22728 | 0 | 0 | 52.5548 | Gas | 116.4402 | Gas | 416431273.84
| Chattogram Zone |  |  | 4.6455 | 35.1345 | 7.9984 | 0 | 5.2127 | 0.1538 | 0 | 0.08496 | 53.2298 | Coal | 91.9343 | Coal | 534491039.6966
| Cumilla Zone |  |  | 23.5796 | 0 | 8.0026 | 0 | 0 | 0.47851 | 1.6013 | 0 | 33.6619 | HFO | 50.61 | HFO | 947530570.402
| Mymensingh Zone |  |  | 0.46464 | 0 | 3.1256 | 0 | 0 | 0.33709 | 0 | 0 | 3.9274 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1623 | Hydro | 5.2127 | Hydro | 521265
| Khulna Zone |  |  | 3.3615 | 8.8436 | 0.76432 | 0 | 0 | 0.62856 | 22.4982 | 0 | 36.0962 | Solar | 5.0749 | Solar | 75510189.0092
| Barishal Zone |  |  | 8.18 | 42.9513 | 2.1292 | 0 | 0 | 0.004078 | 0 | 0 | 53.2645 | Import | 42.4267 | Import | 243312152.4
| Rajshahi Zone |  |  | 14.4189 | 0 | 5.2863 | 0 | 0 | 1.7301 | 18.3273 | 0 | 39.7626 | Wind | 0.08496 | Wind | 1252310.4
| Rangpur Zone |  |  | 0 | 5.0049 | 4.6039 | 0 | 0 | 1.5154 | 0 | 0 | 11.1242
| Total |  |  | 116.4402 | 91.9343 | 50.61 | 0 | 5.2127 | 5.0749 | 42.4267 | 0.08496 | 311.7838
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416431273.84 |  | Hydro | 521265
|  |  |  | Coal | 534491039.6966 |  | Solar | 75510189.0092
|  |  |  | HFO | 947530570.402 |  | Import | 243312152.4
|  |  |  | HSD | 0 |  | Wind | 1252310.4
[5 empty] | Total: | 221,90,48,800 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5862 | Peak Hr Flow | 891.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44438145.51 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.3273 | Peak Hr Flow | 762.93 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1996 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6013 | Peak Hr Flow | 80.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2540 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.5147 | Peak Hr Flow | 1733.93 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 65 |  | 5228
|  |  |  | Chattogram |  | 15 |  | 1505
|  |  |  | Cumilla |  | 40 |  | 1396
|  |  |  | Mymensingh |  | 55 |  | 1032
|  |  |  | Sylhet |  | 20 |  | 597
|  |  |  | Khulna |  | 45 |  | 1487
|  |  |  | Barishal |  | 0 |  | 452
|  |  |  | Rajshahi |  | 55 |  | 1248
|  |  |  | Rangpur |  | 38 |  | 787
|  |  |  | Total |  | 333 |  | 13732
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 | 15:54 | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to For annual maintenance
| 08:05 | 15:53 | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to for annual maintenance
| 08:16 | 17:34 | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end. and from
Chandraghona 132/33kV end Due to Annual maintenance
| 08:29 | 16:45 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to OPGW work
|  | 08:35 | Bog-Sherpur 132/33kV S/S Main Bus-1 is restored.
| 08:36 | 15:33 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Annual Maintenance Work.
| 08:37 | 15:32 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Annual Maintenance Work.
| 09:02 | 12:44 | Bogura 230/132kV S/S 132KV Main 1 Scheduled S/D Due to Annual Maintenance work
| 09:07 | 16:43 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Deadline checking
| 09:12 |  | Bog-Sherpur 132/33kV S/S Main Bus-2 Scheduled S/D Due to Annual maintenance
| 09:20 | 15:07 | Meghnaghat 400/230kV S/S 230kV BUS Section 01 Scheduled S/D Due to 230 kV Bus Section- 1
shutdown instructed by NLDC.
| 09:22 | 16:36 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to annual maintenance
| 09:30 | 20:02 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to CNTIC project work
| 09:43 | 19:55 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to For
Project work.
| 09:50 | 19:54 | Daganbhuiyan 132/33kV S/S Main Bus 1&2 Project Work S/D Due to CNTIC project work
| 09:54 |  | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Annual maintenance
| 10:05 | 19:56 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to CNTIC
project work and from Daganbhuiyan 132/33kV end Due to CNTIC project work
| 12:00 |  | Day peak generation 13174 MW
|  | 12:39 | Chattak-Sylhet 132 kV Ckt-2 is restored.
|  | 13:54 | Rajbari 132/33kV S/S Transformer-2 HT is restored.
|  | 13:55 | Rajbari 132/33kV S/S Transformer-2 LT is restored.
| 14:21 | 14:25 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Over current relays Due to 33 kv | [7 empty] | 40.0MW load
|  |  | kasipur feeder fault. | [7 empty] | interrup.
|  | 16:57 | Siddhirganj 132/33kV S/S T-1 HT is restored.
|  | 16:58 | Siddhirganj 132/33kV S/S T-1 LT is restored.
|  | 17:21 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 17:23 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 17:42 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
|  | 17:42 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
| 20:57 |  | Ruppur-Baghabari 230 kV ckt-1 and ckt-2 charged from Baghabari end.
| 21:00 | 21:07 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent Protection P142. relays Due to
For 33 kv pbs agla feeder.
| 00:05 |  | Fenchuganj CCPP-1 was shutdown.
| 03:25 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- ST
| 03:26 |  | Bibiyana-3 400 MW CCPP ST tripped.
| 03:26 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT (False)
| 03:26 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 04:34 |  | Siddhirganj 2x120 MW GT-2 tripped.
| 06:00 |  | Minimum Generation is 11479 MW.
| 06:50 |  | Siddhirganj 2x120 MW GT-1 was sync.
| 07:27 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to annual maintenance works
| 07:28 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Annual maintenance works
| 07:33 |  | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
annual deadline checking
| 07:47 |  | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10498500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 938470 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 96 | 1711000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7862031 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46.8 | 518760 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 138 | 1719360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 529175 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 532525 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 487800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 464760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 497280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 5410855 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3171456 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1885440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1576800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 227280 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 309240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 495 | 12603636 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1610400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2601.3 | 52554768
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 366305.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131760 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 190560 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5212650 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 183 | 4325847 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 9199 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 863904 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 720054 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 319680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 669120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22043 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 426545 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 790409 | FGMO
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 94 | 2140245 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 1363691 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 458327 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1217 | 28319997 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 84960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 285 | 6814545.46 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2551.86 | 53229841.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 177 | 4449000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 7828500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 300 | 7220000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 2 | 36000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1238468 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 2793454 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 503840 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2426440 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1651680 | Engine Problem
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1601280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 399024 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 381160 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1485420 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 54600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 1114560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 478505 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1492 | 33661931
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 464640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1159200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1638000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 322940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290640 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 37800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 138 | 3927370
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 718000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1592880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3692127 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719328 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1927680 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 152 | 2905200 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 393000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 242088 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7601000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 300 | 8371000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1147 | 28162303
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21586181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 345120 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 419200 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 114 | 3361536 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 628560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 365 | 8843636 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1512 | 36096233
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 7389090.91 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1512384 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2743000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1194 | 28602181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5437000 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 616800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6960000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4078 | -
Barishal Area Total |  |  |  |  | 2858 | 2270 | 53264534.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 436198 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 429765 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 330290 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 200 | 4767273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 390 | 9651636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 243850 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 20285 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 626672 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1926144 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1709280 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 762.93 | 18327273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 445504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 809110 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1777.93 | 39762580
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1073890 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3931000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 112 | 2216736 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45341.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2387132 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 222345 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1247760 | -
Rangpur Area Total |  |  |  |  | 950 | 434 | 11124204.52
Eastern Grid Total |  |  |  |  | 17383.852 | 7930.16 | 171536213.86
Western Grid Total |  |  |  |  | 10980.24 | 5993.93 | 140247552.25
National Grid Total |  |  |  |  | 28364.092 | 13924.09 | 311783766.11
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9564.2 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3835.2 | MW
i) Dhaka area |  |  | 5163.31 |  | MW | i) Khulna area |  |  |  | 1441.6 | MW
ii) Chattogram area |  |  | 1490.5 |  | MW | ii) Barishal area |  |  |  | 452 | MW
iii) Cumilla area |  |  | 1356.39 |  | MW | iii) Rajshahi area |  |  |  | 1192.6 | MW
iv) Mymensingh area |  |  | 977 |  | MW | iv) Rangpur area |  |  |  | 749 | MW
v) Sylhet area |  |  | 577 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13399.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 19:00 | 133 | Niamatpur | 60 | 21:00
2 | AKSML | 143 | 03:00 | 68 | Ishurdi | 63 | 18:30 | 134 | Noapara | 40 | 18:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 60 | 18:00 | 135 | PHP | 8 | 19:00
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 111 | 00:00 | 136 | Pabna | 93 | 13:00
5 | Agrabad | 104 | 18:00 | 71 | Jashore | 132 | 18:30 | 137 | Palashbari | 96 | 19:00
6 | Amnura | 26 | 19:00 | 72 | Jhenaidah | 102 | 00:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 98 | 14:00 | 73 | Joydebpur | 161 | 19:00 | 139 | Patiya | 10.2 | 00:00
8 | BSRM | 165 | 22:00 | 74 | Joypurhat | 47 | 01:00 | 140 | Patuakhali | 63.7 | 21:00
9 | Bagerhat | 74 | 00:00 | 75 | Juldah | 15.5 | 14:00 | 141 | Payra | 32 | 18:30
10 | Bajitpur | 90 | 18:00 | 76 | KSRM | 38 | 02:00 | 142 | Postogola | 68 | 13:00
11 | Bakulia | 89 | 15:00 | 77 | Kabirpur | 255 | 11:00 | 143 | Purbachal | 22 | 18:00
12 | Banani | 51.8 | 14:00 | 78 | Kachua | 95 | 19:00 | 144 | Purbasadipur | 109 | 13:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rahanpur | 29 | 00:00
14 | Barapukuria | 59 | 01:00 | 80 | Kalurghat | 54 | 15:00 | 146 | Rahim | 23 | 12:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 76 | 12:00 | 147 | Rajbari | 64 | 22:00
16 | Barishal | 112 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 121 | 14:00
17 | Barishal-230 | 96 | 18:30 | 83 | Kasba | 34 | 01:00 | 149 | Rajshahi | 89 | 18:30
18 | Baroaulia | 68 | 03:00 | 84 | Kazla | 101 | 19:00 | 150 | Rajshahi-230 | 92 | 13:00
19 | Baroirhat | 65 | 18:30 | 85 | Keranigonj | 85 | 00:00 | 151 | Ramganj | 114 | 19:00
20 | Bashundhara | 196 | 18:00 | 86 | Khagrachori | 28 | 14:00 | 152 | Rampur | 42 | 00:00
21 | BashundharaCement | 12 | 16:00 | 87 | Khulna | 70 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 74 | 00:00 | 88 | Khulshi | 198 | 18:30 | 154 | Rangpur | 116 | 14:00
23 | Benapole | 52 | 18:30 | 89 | Kishoreganj | 117 | 01:00 | 155 | Ruppur | 8 | 11:00
24 | Bhaluka | 131 | 14:00 | 90 | Kodda | 313 | 15:00 | 156 | SSM | 6 | 05:00
25 | Bhandaria | 50 | 18:30 | 91 | Kulaura | 47 | 00:00 | 157 | Saidpur | 92 | 15:00
26 | Bhangura | 30 | 14:00 | 92 | Kurigram | 48 | 20:00 | 158 | Satkhira | 112 | 00:00
27 | Bheramara(GK) | 55 | 21:00 | 93 | Kushtia | 136 | 00:00 | 159 | Satmasjid | 102 | 18:00
28 | Bhulta | 222 | 11:00 | 94 | Laksam | 34 | 22:00 | 160 | Savar | 224 | 12:00
29 | Bog-Sherpur | 68 | 01:00 | 95 | Lakshmipur | 32 | 22:00 | 161 | SevenRings | 7.21 | 13:00
30 | Bogura | 150 | 00:00 | 96 | Lalbag | 63 | 13:00 | 162 | ShahCement | 28 | 00:00
31 | Borhanuddin | 95 | 21:00 | 97 | Lalmonirhat | 46 | 18:00 | 163 | Shahjadpur | 73 | 13:00
32 | Brahmanbaria | 119 | 00:00 | 98 | MI_Cement | 11.2 | 00:00 | 164 | Shahjibazar | 119 | 23:00
33 | Cantonment | 140 | 13:00 | 99 | Madanganj | 44 | 19:30 | 165 | Shahmirpur | 68 | 18:00
34 | Chandina | 39.03 | 22:00 | 100 | Madaripur | 104 | 01:00 | 166 | Shariatpur | 76 | 00:00
35 | Chandpur | 80 | 19:00 | 101 | Madartek | 88 | 23:00 | 167 | Sherpur | 130 | 18:00
36 | Chandraghona | 34 | 21:00 | 102 | Madunaghat | 59 | 20:00 | 168 | Shikalbaha | 25 | 00:00
37 | Chapai | 57 | 00:00 | 103 | Magura | 52 | 18:00 | 169 | Shitalakhya | 87.9 | 15:00
38 | Charsaidpur | 38 | 00:00 | 104 | Mahasthangarh | 72 | 01:00 | 170 | Sholosohor | 51 | 15:00
39 | Chauddagram | 65 | 00:00 | 105 | Maijdee | 19 | 02:00 | 171 | Shyampur | 134 | 14:00
40 | Chhatak | 36 | 00:00 | 106 | Manikganj | 115 | 21:00 | 172 | Siddhirganj | 126 | 12:00
41 | Chowmuhani | 170 | 20:00 | 107 | Maniknagar | 66 | 18:00 | 173 | Sirajganj | 100 | 19:00
42 | Chuadanga | 97 | 00:00 | 108 | Matarbari | 56 | 19:00 | 174 | Sonargaon | 129 | 06:00
43 | Coxsbazar | 142 | 18:30 | 109 | Matuail | 68 | 10:00 | 175 | Sreemongol | 80 | 23:00
44 | Cumilla(N) | 131 | 01:00 | 110 | Metrorail_Motijheel | 42 | 17:00 | 176 | Sreepur | 94 | 16:00
45 | Cumilla(S) | 155 | 18:00 | 111 | Metrorail_Uttara | 7 | 10:00 | 177 | Srinagar | 47.5 | 21:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 126 | 12:00 | 178 | Sunamganj | 59 | 01:00
47 | Daudkandi | 135 | 01:00 | 113 | Mirpur | 124 | 18:00 | 179 | Sylhet | 59 | 22:00
48 | DhakaUniversity | 94 | 13:00 | 114 | Mirsorai | 11 | 15:00 | 180 | Sylhet-132 | 154 | 19:00
49 | Dhamrai | 120 | 19:30 | 115 | Mirzapur | 44 | 00:00 | 181 | TK | 25 | 18:00
50 | Dhanmondi | 115 | 13:00 | 116 | Mithapukur | 54 | 01:00 | 182 | Tangail | 160 | 19:30
51 | Dohazari | 93 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 25 | 18:00
52 | Faridpur | 148 | 00:00 | 118 | Mogbazar | 80.9 | 11:00 | 184 | Thakurgaon | 87 | 18:30
53 | Fatullah | 107 | 12:00 | 119 | Mongla | 35 | 14:00 | 185 | Tongi | 116 | 15:00
54 | Fenchuganj | 40 | 23:00 | 120 | Motijheel | 49 | 13:00 | 186 | Ullahpara | 30 | 01:00
55 | Feni | 110 | 19:00 | 121 | Muktagacha | 34 | 01:00 | 187 | Ullon | 65 | 18:30
56 | GPH | 72 | 09:00 | 122 | Munshiganj | 107 | 18:00 | 188 | Uttara | 68 | 13:00
57 | Ghatail | 70 | 17:00 | 123 | Muradnagar | 37 | 00:00 | 189 | UttaraNew | 76 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 183 | 23:00 | 190 | Zigatola | 68 | 18:00
59 | Ghorashal-230 | 103 | 00:00 | 125 | Naogaon | 106 | 22:00
60 | Goalpara | 33 | 18:00 | 126 | Narail | 47 | 00:00
61 | Gollamari | 92 | 00:00 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 93.4 | 18:00 | 128 | Narshingdi | 183 | 22:00
63 | Gulshan | 124 | 13:00 | 129 | Natore | 136 | 18:00
64 | Halishahar | 85 | 15:00 | 130 | Nawabganj | 44.8 | 21:00
65 | HaripurSBU | 153 | 09:00 | 131 | Netrakona | 107 | 07:00
66 | Hasnabad | 86 | 18:30 | 132 | New | 57.6 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13628.86 | 164 |  | 13800.24
1:00 | 13344.86 | 63 |  | 13410.7
2:00 | 12751.86 | 47 |  | 12800.86
3:00 | 12128.5 | 35 |  | 12165.5
4:00 | 11893.5 | 0 |  | 11893.5
5:00 | 11521.5 | 0 |  | 11521.5
6:00 | 11167.89 | 0 |  | 11167.89
7:00 | 11400.62 | 0 |  | 11400.62
8:00 | 11478.75 | 0 |  | 11478.75
9:00 | 11707.56 | 0 |  | 11707.56
10:00 | 12078.52 | 0 |  | 12078.52
11:00 | 12699.66 | 22 |  | 12722.65
12:00 | 13179.19 | 15 |  | 13194.87
13:00 | 13568.9 | 14 |  | 13583.9
14:00 | 13669.17 | 35 |  | 13705.75
15:00 | 13564.62 | 168 |  | 13740.18
16:00 | 13299.55 | 149 |  | 13455.26
17:00 | 13199.62 | 128 |  | 13333.38
18:00 | 13617.3 | 368 |  | 14001.86
19:00 | 13924.09 | 333 |  | 14272.08
19:30 | 13890.33 | 298 |  | 14201.74
20:00 | 13914.71 | 255 |  | 14181.19
21:00 | 13797.8 | 290 |  | 14100.85
22:00 | 13729.84 | 299 |  | 14042.3
23:00 | 13576.9 | 291 |  | 13881
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7664.86 | 5964 | 13628.86 | DAILY GENERATION CURVE
00:30 | 7551.86 | 5935 | 13486.86
01:00 | 7438.86 | 5906 | 13344.86 | 14-10-2025
01:30 | 7202.36 | 5846 | 13048.36
02:00 | 6965.86 | 5786 | 12751.86
02:30 | 6814.68 | 5625.5 | 12440.18
03:00 | 6663.5 | 5465 | 12128.5
03:30 | 6596.5 | 5414.5 | 12011
04:00 | 6529.5 | 5364 | 11893.5
04:30 | 6417.5 | 5290 | 11707.5
05:00 | 6305.5 | 5216 | 11521.5
05:30 | 6157.92 | 5186.775 | 11344.695
06:00 | 6010.34 | 5157.55 | 11167.89
06:30 | 6060.155 | 5224.1 | 11284.255
07:00 | 6109.97 | 5290.65 | 11400.62
07:30 | 6087.99 | 5351.695 | 11439.685
08:00 | 6066.01 | 5412.74 | 11478.75
08:30 | 6098.495 | 5494.66 | 11593.155
09:00 | 6130.98 | 5576.58 | 11707.56
09:30 | 6248.16 | 5644.88 | 11893.04
10:00 | 6365.34 | 5713.18 | 12078.52
10:30 | 6606.865 | 5782.225 | 12389.09
11:00 | 6848.39 | 5851.27 | 12699.66
11:30 | 6959.615 | 5979.81 | 12939.425
12:00 | 7070.84 | 6108.35 | 13179.19
12:30 | 7191.56 | 6182.485 | 13374.045
13:00 | 7312.28 | 6256.62 | 13568.9
13:30 | 7400.915 | 6218.12 | 13619.035
14:00 | 7489.55 | 6179.62 | 13669.17
14:30 | 7488.655 | 6128.24 | 13616.895
15:00 | 7487.76 | 6076.86 | 13564.62
15:30 | 7456.495 | 5975.59 | 13432.085
16:00 | 7425.23 | 5874.32 | 13299.55
16:30 | 7407.955 | 5841.63 | 13249.585
17:00 | 7390.68 | 5808.94 | 13199.62
17:30 | 7532.22 | 5876.24 | 13408.46
18:00 | 7673.76 | 5943.54 | 13617.3
18:30 | 7801.96 | 5968.735 | 13770.695
19:00 | 7930.16 | 5993.93 | 13924.09
19:30 | 7879.36 | 6010.97 | 13890.33
20:00 | 7906.36 | 6008.35 | 13914.71
20:30 | 7866.36 | 5989.895 | 13856.255 |  | Executive Engineer
21:00 | 7826.36 | 5971.44 | 13797.8 |  | Network Operation Division
21:30 | 7803.21 | 5960.61 | 13763.82
22:00 | 7780.06 | 5949.78 | 13729.84
22:30 | 7733.31 | 5920.06 | 13653.37
23:00 | 7686.56 | 5890.34 | 13576.9

## En-Curve
QF-LDC-12
Date | 14-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2898 | 1957 | 891 | 38 | 74 | 763 | 220 | 3825 | 0 | 711 | 2251.86 | 0 | 0 | 0 | 164 | DAILY ENERGY CURVE
00:30 | 2899 | 1945.5 | 891 | 38 | 72 | 763 | 220.5 | 3806.5 | 0 | 643.5 | 2205.36 | 0 | 0 | 2.5 | 113.5 | 14-10-2025
01:00 | 2900 | 1934 | 891 | 38 | 70 | 763 | 221 | 3788 | 0 | 576 | 2158.86 | 0 | 0 | 5 | 63
01:30 | 2913.5 | 1913.75 | 891.5 | 38 | 66 | 758 | 220 | 3791.5 | 0 | 514 | 1936.61 | 0 | 0 | 5.5 | 55 | Energy Generated | 311.7838 |  | MKWHr
02:00 | 2927 | 1893.5 | 892 | 38 | 62 | 753 | 219 | 3795 | 0 | 452 | 1714.36 | 0 | 0 | 6 | 47 | Energy not Served | 2.676 |  | MKWHr
02:30 | 2919.5 | 1899.5 | 891.5 | 38 | 62 | 756 | 219 | 3796 | 0 | 369.5 | 1481.18 | 0 | 0 | 8 | 41 | Total Energy Requirement | 314.4598 |  | MKWHr
03:00 | 2912 | 1905.5 | 891 | 38 | 62 | 759 | 219 | 3797 | 0 | 287 | 1248 | 0 | 0 | 10 | 35
03:30 | 2925.5 | 1913 | 891 | 38 | 65 | 760.5 | 219 | 3801 | 0 | 200.5 | 1189 | 0 | 0 | 8.5 | 17.5
04:00 | 2939 | 1920.5 | 891 | 38 | 68 | 762 | 219 | 3805 | 0 | 114 | 1130 | 0 | 0 | 7 | 0
04:30 | 2945.5 | 1916 | 891 | 38 | 67 | 765 | 219 | 3768.5 | 0 | 106 | 986 | 0 | 0 | 5.5 | 0
05:00 | 2952 | 1911.5 | 891 | 38 | 66 | 768 | 219 | 3732 | 0 | 98 | 842 | 0 | 0 | 4 | 0
05:30 | 2932 | 1910.35 | 891 | 38 | 62 | 766.5 | 219 | 3708.5 | 0.345 | 81.5 | 732.5 | 0 | 0 | 3 | 0
06:00 | 2912 | 1909.2 | 891 | 38 | 58 | 765 | 219 | 3685 | 0.69 | 65 | 623 | 0 | 0 | 2 | 0
06:30 | 2940.5 | 1921.85 | 891 | 38 | 53 | 765.5 | 219 | 3704 | 61.905 | 66.5 | 620.5 | 0 | 0 | 2.5 | 0
07:00 | 2969 | 1934.5 | 891 | 38 | 48 | 766 | 219 | 3723 | 123.12 | 68 | 618 | 0 | 0 | 3 | 0
07:30 | 2839.5 | 1874 | 891 | 38 | 43 | 762 | 219 | 3758 | 228.685 | 91 | 694 | 0 | 0 | 1.5 | 0
08:00 | 2710 | 1813.5 | 891 | 38 | 38 | 758 | 219 | 3793 | 334.25 | 114 | 770 | 0 | 0 | 0 | 0
08:30 | 2703 | 1819.25 | 891 | 38 | 35 | 759.5 | 219 | 3763 | 433.905 | 136 | 795.5 | 0 | 0 | 0 | 0
09:00 | 2696 | 1825 | 891 | 38 | 32 | 761 | 219 | 3733 | 533.56 | 158 | 821 | 0 | 0 | 0 | 0
09:30 | 2740.5 | 1833.5 | 891 | 38 | 42 | 762 | 219 | 3760.5 | 600.04 | 159 | 847.5 | 0 | 0 | 0 | 0
10:00 | 2785 | 1842 | 891 | 38 | 52 | 763 | 219 | 3788 | 666.52 | 160 | 874 | 0 | 0 | 0 | 0
10:30 | 2841.5 | 1852 | 892 | 38 | 53 | 761.5 | 219 | 3756.5 | 696.59 | 194 | 1085 | 0 | 0 | 0 | 11
11:00 | 2898 | 1862 | 893 | 38 | 54 | 760 | 219 | 3725 | 726.66 | 228 | 1296 | 0 | 0 | 0 | 22
11:30 | 2945.5 | 1826.5 | 893 | 38 | 51 | 758 | 219 | 3761.5 | 726.675 | 266.5 | 1453.75 | 0 | 0 | 0 | 18.5
12:00 | 2993 | 1791 | 893 | 38 | 48 | 756 | 219 | 3798 | 726.69 | 305 | 1611.5 | 0 | 0 | 0 | 15
12:30 | 3023.5 | 1806 | 893 | 38 | 63 | 755 | 219 | 3820 | 717.045 | 320.5 | 1719 | 0 | 0 | 0 | 14.5
13:00 | 3054 | 1821 | 893 | 38 | 78 | 754 | 219 | 3842 | 707.4 | 336 | 1826.5 | 0 | 0 | 0 | 14
13:30 | 2999.5 | 1846.1 | 892.5 | 38 | 77 | 755.5 | 219 | 3869.5 | 648.255 | 340.5 | 1930.68 | 0 | 0 | 2.5 | 24.5
14:00 | 2945 | 1871.2 | 892 | 38 | 76 | 757 | 219 | 3897 | 589.11 | 345 | 2034.86 | 0 | 0 | 5 | 35
14:30 | 2938.5 | 1868.85 | 892 | 38 | 80 | 763.97 | 220 | 3891.5 | 514.715 | 344.5 | 2059.36 | 0 | 0 | 5.5 | 101.5
15:00 | 2932 | 1866.5 | 892 | 38 | 84 | 770.94 | 221 | 3886 | 440.32 | 344 | 2083.86 | 0 | 0 | 6 | 168
15:30 | 2902 | 1845.75 | 892 | 38 | 81 | 767.74 | 221 | 3883 | 336.235 | 377 | 2083.36 | 0 | 0 | 5 | 158.5
16:00 | 2872 | 1825 | 892 | 38 | 78 | 764.54 | 221 | 3880 | 232.15 | 410 | 2082.86 | 0 | 0 | 4 | 149
16:30 | 2830.5 | 1835.5 | 892 | 38 | 72 | 764.81 | 221 | 3880 | 136.665 | 486.15 | 2090.96 | 0 | 0 | 2 | 138.5
17:00 | 2789 | 1846 | 892 | 38 | 66 | 765.08 | 221 | 3880 | 41.18 | 562.3 | 2099.06 | 0 | 0 | 0 | 128
17:30 | 2864 | 1809.5 | 891.5 | 38 | 74 | 761.81 | 221 | 3863 | 20.59 | 687.65 | 2177.41 | 0 | 0 | 0 | 248
18:00 | 2939 | 1773 | 891 | 38 | 82 | 758.54 | 221 | 3846 | 0 | 813 | 2255.76 | 0 | 0 | 0 | 368
18:30 | 2925.5 | 1807.25 | 891 | 38 | 81 | 760.735 | 221 | 3864 | 0 | 836.5 | 2345.71 | 0 | 0 | 0 | 350.5
19:00 | 2912 | 1841.5 | 891 | 38 | 80 | 762.93 | 221 | 3882 | 0 | 860 | 2435.66 | 0 | 0 | 0 | 333
19:30 | 2890 | 1900.5 | 891 | 38 | 84 | 752.97 | 220 | 3909 | 0 | 850 | 2354.86 | 0 | 0 | 0 | 298
20:00 | 2948 | 1873.5 | 891 | 38 | 84 | 760.35 | 220 | 3910 | 0 | 851 | 2334.86 | 0 | 0 | 4 | 255
20:30 | 2930 | 1882 | 891 | 38 | 79 | 761.895 | 219.5 | 3910 | 0 | 851.5 | 2291.36 | 0 | 0 | 2 | 272.5
21:00 | 2912 | 1890.5 | 891 | 38 | 74 | 763.44 | 219 | 3910 | 0 | 852 | 2247.86 | 0 | 0 | 0 | 290
21:30 | 2883.5 | 1903 | 891 | 38 | 78 | 764.61 | 219 | 3912 | 0 | 848.5 | 2222.21 | 0 | 0 | 4 | 294.5
22:00 | 2855 | 1915.5 | 891 | 38 | 82 | 765.78 | 219 | 3914 | 0 | 845 | 2196.56 | 0 | 0 | 8 | 299
22:30 | 2863.5 | 1909 | 890.5 | 38 | 82 | 762.56 | 219 | 3913.5 | 0 | 799.5 | 2169.31 | 0 | 0 | 6.5 | 295
23:00 | 2872 | 1902.5 | 890 | 38 | 82 | 759.34 | 219 | 3913 | 0 | 754 | 2142.06 | 0 | 0 | 5 | 291
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 06:00 | 376 | 12:00 | Payra | 411 | 02:00 | 407 | 12:00
Ashuganj | 408 | 4:00 | 390 | 13:00 | Rahanpur | 405 | 02:00 | 401 | 07:00
Bhulta | 404 | 04:00 | 387 | 10:00 | Rampal | 403 | 06:00 | 394 | 12:00
Bibiana | 391 | 06:00 | 384 | 12:00
BIPTC | 403 | 06:00 | 392 | 18:30
Bogura | 399 | 02:00 | 394 | 07:00
Gopalganj | 399 | 06:00 | 390 | 12:00
Kaliakoir | 378 | 01:00 | 368 | 10:00
Madunaghat | 395 | 00:00 | 389 | 10:00
Meghnaghat | 390 | 05:00 | 381 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 04:00 | 223 | 12:00 | Kaliakoir | 237 | 01:00 | 229 | 10:00
AKSML | 234 | 01:00 | 227 | 10:00 | Keranigonj | 229 | 05:00 | 220 | 13:00
Aminbazar | 233 | 05:00 | 224 | 12:00 | Khulna(S) | 233 | 06:00 | 224 | 00:00
Ashuganj | 235 | 18:30 | 227 | 13:00 | Madunaghat | 235 | 00:00 | 229 | 12:00
Ashuganj-400 | 235 | 18:30 | 227 | 13:00 | Madunaghat-400 | 236 | 00:00 | 231 | 10:00
Baghabari | 235 | 05:00 | 230 | 13:00 | Maniknagar | 221 | 20:00 | 214 | 13:00
Barapukuria | 227 | 18:30 | 216 | 11:00 | Meghnaghat | 229 | 00:00 | 223 | 10:00
Barapukuria-230 | 227 | 18:30 | 216 | 11:00 | Meghnaghat-400 | 226 | 04:00 | 220 | 10:00
Barishal | 236 | 16:00 | 233 | 03:00 | Mirsorai | 237 | 18:30 | 227 | 03:00
Bheramara | 235 | 06:00 | 228 | 13:00 | Rajshahi | 235 | 06:00 | 225 | 13:00
Bhulta | 233 | 04:00 | 216 | 09:00 | Rampal | 231 | 06:00 | 224 | 00:00
Bibiana | 230 | 17:00 | 226 | 10:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 228 | 13:00 | Rampura | 233 | 04:00 | 218 | 13:00
Bogura | 239 | 02:00 | 235 | 07:00 | Shikalbaha | 235 | 18:00 | 226 | 11:00
Bogura-400 | 239 | 19:00 | 234 | 07:00 | Shyampur | 226 | 04:00 | 219 | 10:00
Borhanuddin | 239 | 17:00 | 236 | 02:00 | Siddhirganj | 223 | 19:00 | 217 | 10:00
BSRM | 236 | 19:00 | 226 | 10:00 | Sirajgonj | 240 | 06:00 | 236 | 13:00
Cumilla(N) | 228 | 18:30 | 222 | 10:00 | Sreepur | 232 | 18:30 | 224 | 09:00
Faridpur | 233 | 06:00 | 228 | 12:00 | Tongi | 233 | 04:00 | 223 | 10:00
Fenchuganj | 234 | 18:00 | 229 | 00:00
Ghorashal | 236 | 18:30 | 230 | 07:00
Ghorashal-230 | 233 | 22:00 | 220 | 13:00
Gopalganj | 234 | 06:00 | 230 | 12:00
GPH | 231 | 21:00 | 228 | 12:00
Haripur | 223 | 06:00 | 216 | 10:00
Hasnabad | 228 | 04:00 | 220 | 11:00
Hathazari | 233 | 18:00 | 224 | 10:00
Ishurdi | 238 | 06:00 | 230 | 13:00
Jhenaidah | 233 | 06:00 | 224 | 13:00
Kachua | 231 | 09:00 | 225 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 128 | 10:00 | Lalmonirhat | 131 | 19:00 | 127 | 10:00
Agargaon | 136 | 04:00 | 130 | 12:00 | Madanganj | 129 | 01:00 | 124 | 10:00
Agrabad | 134 | 00:00 | 128 | 10:00 | Madaripur | 136 | 05:00 | 134 | 11:00
AKS | 132 | 00:00 | 128 | 10:00 | Madartek | 137 | 23:00 | 127 | 13:00
Aminbazar | 137 | 05:00 | 132 | 09:00 | Madunaghat | 136 | 00:00 | 132 | 10:00
Amnura | 138 | 19:00 | 129 | 13:00 | Magura | 138 | 06:00 | 130 | 13:00
Ashuganj | 142 | 08:00 | 138 | 11:00 | Mahasthangarh | 135 | 02:00 | 131 | 07:00
Bagerhat | 134 | 09:00 | 123 | 00:00 | Maijdee | 134 | 00:00 | 130 | 07:00
Bajitpur | 131 | 18:30 | 127 | 14:00 | Manikganj | 130 | 22:00 | 124 | 15:00
Bakulia | 134 | 00:00 | 129 | 11:00 | Maniknagar | 134 | 06:00 | 128 | 13:00
Banani | 135 | 01:00 | 127 | 13:00 | Matarbari | 125 | 18:00 | 112 | 18:30
Bangabhaban | 134 | 04:00 | 128 | 11:00 | Matuail | 129 | 01:00 | 125 | 10:00
Barapukuria | 139 | 18:30 | 133 | 07:00 | Metrorail_Motijheel | 134 | 06:00 | 128 | 13:00
Barguna | 137 | 05:00 | 134 | 00:00 | Metrorail_Uttara | 136 | 03:00 | 130 | 12:00
Barishal | 140 | 23:00 | 134 | 05:00 | Millgate | 136 | 03:00 | 129 | 10:00
Barishal-230 | 137 | 16:00 | 134 | 02:00 | Mirpur | 136 | 04:00 | 131 | 10:00
Baroaulia | 134 | 00:00 | 130 | 10:00 | Mirzapur | 132 | 01:00 | 126 | 11:00
Baroirhat | 133 | 00:00 | 128 | 13:00 | Mithapukur | 135 | 18:30 | 130 | 07:00
Bashundhara | 137 | 05:00 | 127 | 13:00 | MI_Cement | 134 | 03:00 | 125 | 10:00
BashundharaCement | 129 | 01:00 | 124 | 12:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 130 | 18:00 | 126 | 00:00 | Mogbazar | 137 | 02:00 | 127 | 13:00
Benapole | 134 | 05:00 | 126 | 00:00 | Mongla | 134 | 09:00 | 124 | 00:00
Bhaluka | 133 | 18:30 | 120 | 11:00 | Motijheel | 134 | 04:00 | 128 | 11:00
Bhandaria | 133 | 10:00 | 119 | 00:00 | Muktagacha | 132 | 05:00 | 121 | 19:30
Bhangura | 135 | 03:00 | 131 | 13:00 | Munshiganj | 129 | 20:00 | 123 | 09:00
Bheramara | 138 | 06:00 | 134 | 14:00 | Muradnagar | 130 | 19:00 | 126 | 10:00
Bheramara(GK) | 138 | 06:00 | 134 | 13:00 | Mymensingh | 132 | 06:00 | 117 | 14:00
Bhulta | 127 | 22:00 | 123 | 10:00 | Naogaon | 132 | 18:00 | 126 | 13:00
Bog-Sherpur | 136 | 18:30 | 132 | 07:00 | Narail | 137 | 06:00 | 130 | 00:00
Bogura | 137 | 18:00 | 133 | 07:00 | Narinda | 134 | 06:00 | 128 | 13:00
Bogura-230 | 137 | 02:00 | 133 | 07:00 | Narshingdi | 133 | 19:30 | 120 | 10:00
Brahmanbaria | 135 | 18:30 | 130 | 14:00 | Natore | 135 | 05:00 | 131 | 13:00
Cantonment | 136 | 01:00 | 130 | 12:00 | Nawabganj | 136 | 05:00 | 129 | 12:00
Chandina | 133 | 00:00 | 129 | 10:00 | Netrakona | 126 | 18:30 | 116 | 00:00
Chandpur | 138 | 07:00 | 135 | 01:00 | New | 135 | 04:00 | 129 | 15:00
Chandraghona | 136 | 01:00 | 133 | 10:00 | Niamatpur | 138 | 02:00 | 136 | 13:00
Chapai | 138 | 18:00 | 135 | 17:00 | Noapara | 136 | 06:00 | 129 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 20:00 | 124 | 10:00 | Pabna | 136 | 06:00 | 132 | 13:00
Chauddagram | 134 | 18:30 | 130 | 02:00 | Palashbari | 133 | 18:30 | 127 | 07:00
Chhatak | 128 | 18:00 | 122 | 00:00 | Panchagarh | 136 | 03:00 | 125 | 10:00
Chowmuhani | 135 | 17:00 | 130 | 22:00 | Patiya | 134 | 18:00 | 128 | 11:00
Chuadanga | 135 | 05:00 | 127 | 13:00 | Patuakhali | 138 | 04:00 | 134 | 19:00
Coxsbazar | 122 | 20:00 | 110 | 18:30 | Payra | 137 | 04:00 | 135 | 13:00
Cumilla(N) | 133 | 17:00 | 129 | 10:00 | PHP | 131 | 00:00 | 129 | 11:00
Cumilla(S) | 134 | 19:00 | 127 | 15:00 | Postogola | 136 | 06:00 | 130 | 10:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 04:00 | 126 | 13:00
Daudkandi | 127 | 20:00 | 123 | 09:00 | Purbasadipur | 135 | 04:00 | 127 | 08:00
DhakaUniversity | 136 | 04:00 | 128 | 13:00 | Rahanpur | 139 | 01:00 | 137 | 11:00
Dhamrai | 135 | 04:00 | 130 | 10:00 | Rahanpur-400 | 139 | 00:00 | 137 | 19:00
Dhanmondi | 136 | 03:00 | 127 | 13:00 | Rahim | 129 | 18:30 | 125 | 09:00
Dohazari | 131 | 18:00 | 124 | 11:00 | Rajbari | 137 | 06:00 | 133 | 13:00
Faridpur | 137 | 06:00 | 134 | 13:00 | Rajendrapur | 141 | 18:30 | 125 | 14:00
Fatullah | 137 | 01:00 | 132 | 10:00 | Rajshahi | 134 | 03:00 | 130 | 13:00
Fenchuganj | 137 | 07:00 | 134 | 13:00 | Rajshahi-230 | 135 | 06:00 | 129 | 13:00
Feni | 135 | 17:00 | 130 | 02:00 | Ramganj | 135 | 00:00 | 131 | 02:00
Ghatail | 130 | 03:00 | 120 | 18:00 | Rampur | 133 | 00:00 | 128 | 10:00
Ghorashal | 139 | 00:00 | 135 | 11:00 | Rampura | 136 | 04:00 | 127 | 13:00
Goalpara | 139 | 06:00 | 131 | 00:00 | Rangamati | 135 | 00:00 | 132 | 09:00
Gollamari | 139 | 06:00 | 133 | 00:00 | Rangpur | 135 | 19:00 | 129 | 11:00
Gopalganj | 137 | 06:00 | 132 | 12:00 | Ruppur | 138 | 05:00 | 135 | 13:00
Gopalganj-400 | 138 | 06:00 | 134 | 12:00 | Saidpur | 134 | 06:00 | 128 | 10:00
Gulshan | 135 | 04:00 | 128 | 12:00 | Satkhira | 136 | 06:00 | 127 | 00:00
Halishahar | 134 | 00:00 | 129 | 11:00 | Satmasjid | 137 | 05:00 | 129 | 13:00
Haripur | 129 | 06:00 | 125 | 10:00 | Savar | 136 | 20:00 | 130 | 12:00
HaripurSBU | 129 | 06:00 | 125 | 10:00 | SevenRings | 141 | 04:00 | 134 | 13:00
Hasnabad | 136 | 03:00 | 129 | 11:00 | ShahCement | 130 | 20:00 | 124 | 10:00
Hathazari | 136 | 18:00 | 131 | 10:00 | Shahjadpur | 139 | 03:00 | 133 | 13:00
Ishurdi | 139 | 06:00 | 135 | 14:00 | Shahjibazar | 136 | 08:00 | 131 | 15:00
Jaldhaka | 133 | 04:00 | 126 | 08:00 | Shahmirpur | 134 | 00:00 | 129 | 11:00
Jamalpur | 132 | 06:00 | 120 | 22:00 | Shariatpur | 136 | 05:00 | 133 | 12:00
Jashore | 134 | 05:00 | 125 | 12:00 | Sherpur | 130 | 06:00 | 117 | 18:00
Jhenaidah | 138 | 06:00 | 127 | 13:00 | Shikalbaha | 126 | 00:00 | 120 | 08:00
Jhenaidah-230 | 138 | 06:00 | 131 | 13:00 | Shikalbaha-230 | 136 | 01:00 | 131 | 03:00
Joydebpur | 140 | 18:30 | 131 | 09:00 | Shitalakhya | 134 | 03:00 | 125 | 10:00
Joypurhat | 130 | 18:00 | 125 | 13:00 | Sholosohor | 135 | 00:00 | 132 | 10:00
Juldah | 133 | 00:00 | 129 | 10:00 | Shyampur | 135 | 00:00 | 132 | 12:00
Kabirpur | 137 | 18:30 | 126 | 09:00 | Shyampur-230 | 137 | 02:00 | 131 | 12:00
Kachua | 137 | 00:00 | 134 | 05:00 | Siddhirganj | 130 | 20:00 | 125 | 10:00
Kaliakoir | 137 | 01:00 | 131 | 09:00 | Sirajganj | 132 | 00:00 | 130 | 07:00
Kallyanpur | 137 | 06:00 | 132 | 10:00 | Sonargaon | 128 | 19:30 | 123 | 09:00
Kalurghat | 136 | 00:00 | 132 | 10:00 | Sreemongol | 134 | 07:00 | 130 | 00:00
Kamrangirchar | 136 | 05:00 | 129 | 10:00 | Sreepur | 136 | 18:30 | 129 | 00:00
Kaptai | 137 | 1:00 | 135 | 5:00 | Srinagar | 135 | 05:00 | 129 | 12:00
Kasba | 129 | 18:30 | 125 | 12:00 | SSM | 138 | 01:00 | 132 | 10:00
Kazla | 134 | 05:00 | 128 | 12:00 | Sunamganj | 127 | 08:00 | 121 | 00:00
Keranigonj | 136 | 05:00 | 129 | 13:00 | Sylhet | 131 | 08:00 | 127 | 00:00
Khagrachori | 134 | 01:00 | 131 | 10:00 | Sylhet-132 | 131 | 07:00 | 128 | 00:00
Khulna | 138 | 06:00 | 131 | 00:00 | Tangail | 130 | 04:00 | 123 | 19:30
Khulna(S) | 139 | 06:00 | 132 | 00:00 | Taraganj | 134 | 04:00 | 128 | 07:00
Khulshi | 133 | 18:00 | 128 | 10:00 | Thakurgaon | 137 | 04:00 | 126 | 08:00
Kishoreganj | 131 | 18:30 | 125 | 13:00 | TK | 136 | 18:00 | 132 | 10:00
Kodda | 138 | 00:00 | 124 | 09:00 | Tongi | 138 | 19:00 | 131 | 09:00
KSRM | 135 | 01:00 | 130 | 10:00 | Ullahpara | 135 | 06:00 | 131 | 00:00
Kulaura | 136 | 07:00 | 133 | 00:00 | Ullon | 135 | 02:00 | 127 | 12:00
Kurigram | 131 | 04:00 | 126 | 08:00 | Uttara | 135 | 03:00 | 128 | 10:00
Kushtia | 136 | 06:00 | 131 | 00:00 | UttaraNew | 136 | 03:00 | 130 | 12:00
Laksam | 136 | 00:00 | 123 | 02:00 | Zigatola | 136 | 05:00 | 129 | 13:00
Lakshmipur | 133 | 00:00 | 130 | 02:00
Lalbag | 136 | 06:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division