## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-10-2025 | [28 empty] | Date: | 15-10-2025 | [28 empty] | Date: | 15-10-2025 | [28 empty] | Date: | 15-10-2025 | [28 empty] | Date: | 15-10-2025 | [14 empty] | Date: | 15-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 149 | 140 | 277 | 55 | 0 | 72 | 0 | 450 | 0 | 517 | 0 | 0 | 329 | 97 | 0 | 0 | 52 | 13.1 | 22 | 0 | 0 | 97 | 16 | 13 | 0 | 2 | 66 | 44 | 54.36 | 0 | 0 | 0 | 219 | 100 | 18 | 285 | 17 | 0 | 0 | 25.5 | 0 | 175 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 174 | 0 | 34 | 103 | 104 | 0 | 19 | 97 | 82 | 43 | 0 | 36 | 310 | 0 | 339 | 30 | 67 | 154 | 10 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 34 | 0 | 0 | 12 | 7548.96 | 896 | 103 | 0 | 37 | 49 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 761.1 | 0 | 40 | 0 | 113 | 113 | 0 | 97 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 161 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 308 | 1222 | 17 | 5905.1 | 13454.06 | 107.06
01:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 140 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 330 | 98 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 97 | 16 | 12 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 0 | 220 | 110 | 18 | 285 | 17 | 0 | 0 | 25.5 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 177 | 0 | 33 | 103 | 65 | 0 | 19 | 97 | 78 | 43 | 0 | 36 | 310 | 0 | 310 | 0 | 67 | 156 | 10 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 35 | 0 | 0 | 12 | 7345.36 | 896 | 108 | 0 | 37 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 757.2 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 161 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 308 | 1222 | 17 | 5807.2 | 13152.56 | 107.05
02:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 107 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 503 | 0 | 0 | 329 | 91 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 91 | 16 | 13 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 0 | 220 | 110 | 18 | 285 | 17 | 0 | 0 | 25.5 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 184 | 0 | 35 | 103 | 51 | 0 | 19 | 50 | 76 | 43 | 0 | 36 | 310 | 0 | 320 | 0 | 67 | 155 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 35 | 0 | 0 | 12 | 7239.36 | 896 | 109 | 0 | 37 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 760.25 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 161 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 308 | 1222 | 17 | 5779.25 | 13018.61 | 107.04
03:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 0 | 277 | 55 | 0 | 35 | 0 | 450 | 0 | 465 | 0 | 0 | 330 | 38 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 0 | 221 | 110 | 18 | 285 | 17 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 0 | 0 | 300 | 300 | 2 | 189 | 0 | 34 | 103 | 51 | 0 | 19 | 10 | 66 | 16 | 0 | 36 | 315 | 0 | 298 | 0 | 67 | 151 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 35 | 0 | 0 | 12 | 6912.86 | 896 | 118 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 760.25 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 161 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 307 | 1204 | 17 | 5467.25 | 12380.11 | 107.03
04:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 277 | 15 | 0 | 35 | 0 | 450 | 0 | 543 | 0 | 35 | 330 | 39 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 94 | 16 | 0 | 0 | 0 | 66 | 36 | 0 | 0 | 0 | 0 | 221 | 110 | 27 | 285 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 0 | 0 | 300 | 300 | 2 | 196 | 0 | 34 | 104 | 51 | 0 | 19 | 0 | 72 | 0 | 0 | 36 | 305 | 0 | 226 | 0 | 67 | 154 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 35 | 0 | 0 | 12 | 6755.5 | 896 | 133 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 758.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 307 | 1204 | 17 | 5336.1 | 12091.6 | 107.03
05:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 95 | 15 | 0 | 35 | 0 | 420 | 0 | 540 | 0 | 35 | 333 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 66 | 36 | 0 | 0 | 0 | 0 | 221 | 110 | 28 | 285 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 0 | 0 | 300 | 300 | 2 | 199 | 0 | 34 | 104 | 51 | 0 | 19 | 0 | 64 | 0 | 0 | 36 | 310 | 0 | 262 | 0 | 67 | 151 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 33 | 0 | 0 | 12 | 6462.5 | 897 | 139 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 761.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 160 | 45 | 70 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 180 | 0 | 307 | 1204 | 17 | 5207.17 | 11669.67 | 107.01
06:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 95 | 15 | 0 | 35 | 0 | 400 | 0 | 550 | 0 | 35 | 280 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 66 | 36 | 0 | 0 | 0 | 0.01 | 221 | 110 | 28 | 285 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1166 | 0 | 51 | 137 | 0 | 0 | 300 | 300 | 2 | 204 | 0 | 34 | 104 | 52 | 0 | 19 | 0 | 62 | 0 | 0 | 36 | 305 | 0 | 262 | 0 | 67 | 155 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 33 | 0 | 0.11 | 12 | 6345.62 | 896 | 145 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 762.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 45 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 115 | 180 | 0 | 307 | 1180 | 17 | 5134.63 | 11480.25 | 107
07:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 95 | 15 | 0 | 35 | 0 | 450 | 0 | 569 | 0 | 35 | 335 | 36 | 0 | 5 | 17 | 13.5 | 22 | 0 | 0 | 100 | 16 | 0 | 0 | 0 | 66 | 36 | 8 | 0 | 0 | 0.56 | 221 | 110 | 28 | 285 | 17 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 0 | 0 | 300 | 300 | 2 | 200 | 0 | 34 | 104 | 52 | 0 | 19 | 0 | 64 | 1 | 14 | 36 | 300 | 0 | 240 | 0 | 67 | 158 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 30 | 0 | 5.54 | 12 | 6580.6 | 897 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.56 | 364 | 0 | 758.53 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 8.29 | 15 | 0 | 0 | 9.64 | 130 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0.8 | 162 | 45 | 50 | 5 | 49 | 0 | 0 | 0 | 0.9 | 30 | 0.08 | 0 | 307 | 115 | 220 | 0 | 307 | 1160 | 17 | 5265.8 | 11846.4 | 106.99
08:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 30 | 47 | 55 | 0 | 35 | 0 | 450 | 0 | 485 | 0 | 0 | 280 | 35 | 0 | 14 | 17 | 13.5 | 22 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 1.55 | 219 | 110 | 13 | 285 | 17 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1224 | 11 | 51 | 135 | 0 | 0 | 280 | 280 | 2 | 209 | 0 | 34 | 104 | 52 | 0 | 19 | 0 | 56 | 16 | 37 | 36 | 300 | 0 | 268 | 0 | 67 | 143 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 28 | 1 | 14.71 | 12 | 6493.12 | 883 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 367 | 0 | 757.83 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 26 | 44 | 0 | 0 | 28.41 | 130 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 2.41 | 161 | 46 | 50 | 15 | 49 | 0 | 0 | 0 | 2.9 | 83 | 0.24 | 16 | 274 | 100 | 180 | 0 | 306 | 1200 | 17 | 5399.79 | 11892.91 | 106.98
09:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 40 | 45 | 55 | 17 | 35 | 0 | 450 | 0 | 510 | 0 | 0 | 280 | 36 | 0 | 23 | 52 | 13.5 | 22 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 2.51 | 219 | 110 | 8 | 285 | 17 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 1202 | 15 | 51 | 133 | 0 | 0 | 280 | 280 | 2 | 209 | 0 | 34 | 103 | 51 | 0 | 19 | 0 | 58 | 16 | 48 | 36 | 295 | 0 | 266 | 0 | 67 | 139 | 7 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 28 | 2 | 23.81 | 12 | 6553.18 | 883 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 367 | 0 | 753.29 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 41.09 | 73 | 0 | 0 | 44.12 | 130 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 3.81 | 160 | 47 | 50 | 24 | 49 | 0 | 0 | 0 | 4.8 | 132 | 0.41 | 16 | 255 | 100 | 180 | 0 | 307 | 1179 | 17 | 5445.52 | 11998.7 | 106.97
10:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 30 | 45 | 55 | 17 | 35 | 0 | 450 | 0 | 520 | 0 | 0 | 326 | 36 | 0 | 29 | 52 | 13 | 21 | 0 | 0 | 66 | 16 | 0 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 3.13 | 218 | 110 | 9 | 285 | 17 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 1172 | 18 | 35 | 115 | 0 | 0 | 300 | 280 | 2 | 208 | 0 | 34 | 100 | 51 | 0 | 19 | 0 | 64 | 16 | 61 | 36 | 320 | 0 | 263 | 0 | 67 | 154 | 10 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 28 | 2 | 41.23 | 12 | 6659.72 | 883 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 370 | 0 | 750.35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 52.15 | 93 | 0 | 0 | 56.16 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.83 | 161 | 45 | 50 | 30 | 49 | 0 | 0 | 0 | 6 | 161 | 0.2 | 16 | 245 | 100 | 220 | 0 | 307 | 1178 | 17 | 5646.69 | 12306.41 | 106.96
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 35 | 123 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 575 | 0 | 0 | 326 | 93 | 0 | 32 | 52 | 13 | 21 | 0 | 0 | 81 | 16 | 8 | 0 | 0 | 66 | 36 | 54.36 | 0 | 0 | 3.44 | 218 | 0 | 3 | 285 | 17 | 0 | 0 | 1 | 0 | 175 | 0 | 0 | 0 | 1187 | 19 | 35 | 108 | 0 | 0 | 310 | 280 | 2 | 206 | 0 | 34 | 100 | 42 | 5 | 19 | 98 | 68 | 43 | 30 | 29 | 315 | 0 | 266 | 0 | 67 | 156 | 10 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 48 | 28 | 2 | 46.87 | 12 | 6997.67 | 898 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 369 | 0 | 745.72 | 0 | 0 | 0 | 35 | 40 | 0 | 0 | 0 | 0 | 60.9 | 100 | 0 | 0 | 64.07 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.46 | 164 | 46 | 113 | 34 | 80 | 0 | 0 | 0 | 6.6 | 180 | 0.48 | 16 | 280 | 115 | 220 | 0 | 307 | 1178 | 17 | 5902.23 | 12899.9 | 106.95
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 139 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 550 | 0 | 0 | 325 | 93 | 0 | 31 | 52 | 13 | 21 | 0 | 0 | 91 | 16 | 12 | 0 | 1 | 65 | 36 | 54.36 | 0 | 0 | 3.45 | 218 | 0 | 12 | 285 | 35 | 0 | 0 | 21 | 0 | 179 | 0 | 0 | 0 | 1175 | 18 | 35 | 107 | 0 | 0 | 310 | 280 | 2 | 203 | 0 | 34 | 100 | 34 | 9 | 19 | 97 | 72 | 43 | 22 | 29 | 315 | 0 | 266 | 0 | 67 | 154 | 10 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 48 | 28 | 1 | 51.39 | 12 | 7019.2 | 898 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 370 | 0 | 747.63 | 0 | 0 | 0 | 35 | 75 | 0 | 0 | 0 | 16 | 40.57 | 105 | 0 | 0 | 51.7 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.12 | 161 | 47 | 115 | 35 | 88 | 0 | 0 | 0 | 6.7 | 179 | 0.71 | 16 | 282 | 115 | 220 | 0 | 307 | 1179 | 17 | 5916.43 | 12935.63 | 106.94
13:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 139 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 545 | 0 | 17 | 325 | 94 | 0 | 32 | 52 | 12 | 21 | 0 | 0 | 94 | 32 | 23 | 0 | 0 | 64 | 36 | 42 | 0 | 0 | 3.19 | 218 | 0 | 18 | 285 | 35 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1166 | 18 | 35 | 113 | 0 | 0 | 310 | 280 | 2 | 192 | 0 | 40 | 100 | 34 | 8 | 19 | 98 | 74 | 43 | 61 | 29 | 305 | 0 | 268 | 0 | 67 | 152 | 12 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 48 | 27 | 1 | 37.19 | 12 | 7067.88 | 898 | 159 | 0 | 11 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60.65 | 370 | 0 | 753.32 | 0 | 0 | 0 | 35 | 104 | 0 | 0 | 0 | 25 | 61.44 | 85 | 0 | 0 | 40.81 | 130 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 2.59 | 164 | 47 | 115 | 23 | 96 | 0 | 0 | 0 | 6.4 | 175 | 0.31 | 16 | 277 | 115 | 180 | 0 | 307 | 1196 | 17 | 5907.52 | 12975.4 | 106.93
14:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 138 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 540 | 0 | 35 | 319 | 94 | 0 | 27 | 52 | 12 | 20 | 0 | 0 | 89 | 16 | 49 | 0 | 0 | 64 | 37 | 54.36 | 0 | 0 | 2.66 | 218 | 0 | 7 | 285 | 35 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1155 | 16 | 35 | 115 | 0 | 0 | 310 | 280 | 2 | 196 | 0 | 51 | 100 | 34 | 0 | 19 | 99 | 68 | 43 | 59 | 27 | 300 | 0 | 268 | 0 | 67 | 150 | 12 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 47 | 27 | 1 | 40.84 | 12 | 7057.36 | 899 | 160 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 370 | 0 | 753 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 52 | 52.86 | 84 | 0 | 0 | 12.42 | 140 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 1.23 | 162 | 47 | 115 | 8 | 98 | 0 | 0 | 0 | 5.3 | 152 | 0.55 | 16 | 275 | 115 | 220 | 0 | 307 | 1215 | 17 | 5905.36 | 12962.72 | 106.92
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 121 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 550 | 0 | 35 | 322 | 94 | 0 | 19 | 125 | 19.7 | 20 | 0 | 0 | 94 | 16 | 54 | 0 | 0 | 64 | 30 | 54.36 | 0 | 0 | 1.86 | 220 | 0 | 9 | 285 | 35 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1147 | 12 | 43 | 110 | 0 | 0 | 310 | 280 | 2 | 184 | 0 | 54 | 100 | 34 | 0 | 19 | 101 | 68 | 43 | 41 | 27 | 310 | 0 | 249 | 0 | 67 | 152 | 12 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 47 | 27 | 1 | 29.51 | 12 | 7079.93 | 898 | 160 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 370 | 0 | 749 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 52 | 36.9 | 64 | 0 | 0 | 40.21 | 140 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 3.69 | 157 | 47 | 115 | 21 | 102 | 0 | 0 | 0 | 3.7 | 120 | 0.37 | 16 | 270 | 115 | 220 | 0 | 306 | 1218 | 17 | 5830.87 | 12910.8 | 106.91
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.5 | 17 | 17 | 121 | 97 | 55 | 35 | 72 | 0 | 450 | 0 | 510 | 0 | 35 | 320 | 94 | 0 | 11 | 142 | 19.2 | 15 | 0 | 0 | 86 | 16 | 78 | 0 | 0 | 64 | 45 | 54.36 | 0 | 0 | 0.86 | 221 | 0 | 9 | 285 | 35 | 0 | 0 | 17 | 0 | 179 | 0 | 0 | 0 | 1163 | 7 | 51 | 110 | 0 | 0 | 310 | 280 | 2 | 186 | 0 | 50 | 100 | 34 | 0 | 19 | 98 | 68 | 43 | 8 | 27 | 310 | 0 | 268 | 0 | 67 | 141 | 12 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 67 | 47 | 27 | 1 | 15.29 | 12 | 7066.21 | 898 | 160 | 0 | 17 | 14 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 370 | 0 | 753 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 0 | 52 | 20.24 | 35 | 15 | 0 | 18.28 | 140 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 1.75 | 157 | 47 | 115 | 11 | 105 | 0 | 0 | 0 | 2.1 | 61 | 0.17 | 16 | 268 | 115 | 220 | 0 | 307 | 1190 | 17 | 5714.54 | 12780.75 | 106.9
17:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 19 | 17 | 121 | 97 | 55 | 35 | 90 | 0 | 450 | 0 | 510 | 0 | 35 | 322 | 94 | 0 | 2 | 142 | 20.2 | 15 | 0 | 0 | 86 | 16 | 92 | 0 | 0 | 64 | 45 | 54.36 | 0 | 0 | 0.06 | 221 | 0 | 13 | 285 | 35 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1152 | 1 | 51 | 118 | 0 | 0 | 310 | 280 | 2 | 193 | 0 | 49 | 100 | 43 | 0 | 19 | 97 | 68 | 43 | 1 | 34 | 310 | 0 | 256 | 0 | 67 | 142 | 12 | 0 | 80 | 30 | 0 | 16 | 159 | 14 | 67 | 47 | 27 | 0 | 2.52 | 12 | 7126.64 | 899 | 162 | 0 | 20 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 370 | 0 | 746 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 0 | 52 | 3 | 7 | 25 | 0 | 2.48 | 140 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0.21 | 158 | 47 | 115 | 2 | 105 | 0 | 0 | 0 | 0.5 | 10 | 0.34 | 16 | 269 | 115 | 220 | 0 | 305 | 1101 | 17 | 5497.53 | 12624.17 | 106.89
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8 | 35 | 17 | 121 | 114 | 55 | 35 | 108 | 0 | 450 | 0 | 520 | 0 | 55 | 322 | 94 | 0 | 0 | 142 | 20.5 | 15 | 0 | 0 | 89 | 16 | 100 | 0 | 0 | 77 | 45 | 54.36 | 0 | 0 | 0 | 222 | 0 | 13 | 285 | 72 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1182 | 0 | 51 | 115 | 0 | 0 | 310 | 280 | 2 | 186 | 0 | 50 | 100 | 85 | 0 | 19 | 105 | 76 | 43 | 0 | 35 | 305 | 0 | 250 | 0 | 67 | 146 | 10 | 0 | 80 | 30 | 0 | 16 | 158 | 17 | 67 | 48 | 27 | 0 | 0 | 12 | 7331.16 | 898 | 163 | 0 | 27 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1 | 0 | 738 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 12 | 52 | 0 | 0 | 25 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 281 | 115 | 220 | 0 | 305 | 1116 | 17 | 5961.1 | 13292.26 | 106.88
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2 | 35 | 17 | 140 | 130 | 55 | 55 | 108 | 0 | 450 | 0 | 500 | 0 | 55 | 326 | 95 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 81 | 32 | 105 | 0 | 0 | 83 | 52 | 54.36 | 0 | 0 | 0 | 222 | 0 | 6 | 285 | 160 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1139 | 0 | 51 | 113 | 0 | 0 | 310 | 280 | 2 | 181 | 0 | 65 | 100 | 106 | 0 | 19 | 98 | 78 | 43 | 0 | 36 | 305 | 0 | 256 | 0 | 67 | 149 | 10 | 0 | 80 | 30 | 0 | 16 | 159 | 17 | 67 | 47 | 27 | 0 | 0 | 12 | 7473.56 | 898 | 164 | 0 | 36 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 734 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 37 | 52 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 158 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 260 | 115 | 220 | 0 | 305 | 1180 | 17 | 5986 | 13459.56 | 106.87
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2 | 35 | 35 | 140 | 135 | 55 | 55 | 108 | 0 | 450 | 0 | 525 | 0 | 55 | 326 | 36 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 60 | 32 | 106 | 0 | 0 | 83 | 52 | 54.36 | 0 | 0 | 0 | 222 | 0 | 8 | 280 | 160 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1170 | 0 | 51 | 113 | 0 | 0 | 310 | 280 | 2 | 184 | 0 | 90 | 100 | 103 | 9 | 19 | 104 | 80 | 43 | 0 | 36 | 315 | 0 | 268 | 0 | 67 | 143 | 10 | 0 | 80 | 30 | 0 | 16 | 159 | 17 | 67 | 47 | 27 | 0 | 0 | 12 | 7528.56 | 898 | 164 | 0 | 30 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 727 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 37 | 52 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 158 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 115 | 220 | 0 | 305 | 1185 | 17 | 6025 | 13553.56 | 0
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7 | 35 | 30 | 140 | 194 | 55 | 55 | 108 | 0 | 450 | 0 | 510 | 0 | 55 | 326 | 96 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 58 | 32 | 106 | 0 | 0 | 83 | 52 | 54.36 | 0 | 0 | 0 | 222 | 0 | 15 | 280 | 160 | 0 | 0 | 25.5 | 0 | 179 | 0 | 0 | 0 | 1153 | 0 | 51 | 115 | 0 | 0 | 310 | 280 | 2 | 188 | 0 | 90 | 102 | 103 | 8 | 19 | 98 | 74 | 43 | 0 | 36 | 310 | 0 | 256 | 0 | 67 | 141 | 10 | 0 | 80 | 30 | 0 | 16 | 158 | 17 | 67 | 47 | 27 | 0 | 0 | 12 | 7592.06 | 898 | 165 | 0 | 30 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 735 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 38 | 52 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 157 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 115 | 220 | 0 | 305 | 1185 | 17 | 6040 | 13632.06 | 106.86
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.6 | 17 | 44 | 140 | 194 | 55 | 35 | 108 | 0 | 450 | 0 | 530 | 0 | 55 | 327 | 96 | 0 | 0 | 142 | 20.3 | 22 | 0 | 0 | 63 | 16 | 106 | 0 | 14 | 82 | 53 | 54.36 | 0 | 0 | 0 | 221 | 0 | 20 | 276 | 108 | 0 | 0 | 25.5 | 0 | 178 | 0 | 0 | 0 | 1165 | 0 | 51 | 117 | 0 | 0 | 310 | 280 | 2 | 173 | 0 | 90 | 103 | 104 | 9 | 19 | 106 | 84 | 43 | 0 | 36 | 310 | 0 | 260 | 0 | 67 | 154 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 17 | 67 | 47 | 28 | 0 | 0 | 12 | 7581.76 | 898 | 165 | 0 | 30 | 45 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 0 | 732.04 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 38 | 52 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 115 | 220 | 0 | 305 | 1216 | 17 | 6124.04 | 13705.8 | 106.85
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 66 | 140 | 194 | 55 | 35 | 108 | 0 | 450 | 0 | 530 | 0 | 35 | 325 | 96 | 0 | 0 | 142 | 20 | 15 | 0 | 0 | 80 | 16 | 106 | 0 | 0 | 82 | 52 | 54.36 | 0 | 0 | 0 | 221 | 0 | 22 | 279 | 17 | 0 | 0 | 25.5 | 0 | 177 | 0 | 0 | 0 | 1165 | 0 | 51 | 120 | 0 | 0 | 310 | 280 | 2 | 171 | 0 | 74 | 103 | 103 | 9 | 19 | 106 | 80 | 43 | 0 | 37 | 310 | 0 | 138 | 0 | 67 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 67 | 47 | 28 | 0 | 0 | 12 | 7303.86 | 898 | 166 | 0 | 30 | 45 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 732.51 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 38 | 52 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 47 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 278 | 115 | 220 | 0 | 305 | 1222 | 17 | 6151.51 | 13455.37 | 106.84
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 68 | 140 | 194 | 55 | 35 | 72 | 0 | 450 | 0 | 530 | 0 | 0 | 330 | 98 | 0 | 0 | 142 | 20 | 20 | 0 | 0 | 77 | 16 | 106 | 0 | 2 | 84 | 52 | 54.36 | 0 | 0 | 0 | 218 | 0 | 22 | 277 | 17 | 0 | 0 | 25.5 | 0 | 177 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 0 | 0 | 310 | 280 | 2 | 168 | 0 | 42 | 103 | 104 | 0 | 19 | 103 | 80 | 43 | 0 | 37 | 315 | 0 | 25 | 0 | 67 | 157 | 10 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 47 | 34 | 0 | 0 | 12 | 7152.86 | 898 | 161 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 732.25 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 37 | 52 | 0 | 0 | 26 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 163 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 198 | 115 | 220 | 0 | 307 | 1219 | 17 | 6067.25 | 13220.11 | 106.83
Total KWH | 0 | 2240640 | 551520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518760 | 302400 | 1342368 | 2199360 | 3512727 | 1195556 | 542492 | 1565280 | 0 | 10468000 | 0 | 12686818 | 0 | 532796 | 7740967 | 1766000 | 0 | 228867 | 1818000 | 379800 | 487080 | 0 | 0 | 2039891 | 431564 | 1082880 | 0 | 14880 | 1682477 | 862560 | 1188218 | 0 | 0 | 23039 | 5277529 | 1153340 | 404160 | 6807272.73 | 896582 | 0 | 0 | 379508.4 | 0 | 4167780 | 0 | 0 | 0 | 28505452 | 126630 | 1124916 | 2945672 | 0 | 0 | 7695100 | 7022000 | 63360 | 4647000 | 1080 | 1109760 | 2415160 | 1504800 | 53760 | 445720 | 1631340 | 1692480 | 771624 | 391105 | 810768 | 7517000 | 0 | 6247000 | 0 | 1613640 | 3635672.73 | 257664 | 0 | 1933440 | 719232 | 0 | 392000 | 3332500 | 88920 | 1611600 | 1142400 | 675840 | 12700 | 319560 | 299280 | 169247287.86 | 21699636 | 3758976 | 0 | 346080 | 425216 | 912000 | 0 | 0 | 0 | 0 | 0 | 545040 | 10334550 | 0 | 18283651 | 0 | 443356 | 0 | 947424 | 2071008 | 0 | 606864 | 267200 | 583195 | 410656 | 727080 | 245390 | 0 | 374240 | 3849364 | 0 | 0 | 0 | 0 | 0 | 9338836 | 0 | 30480 | 3941000 | 1023709 | 2399892 | 228846 | 2217216 | 0 | 0 | 0 | 45204.24 | 1238400 | 0 | 609984 | 6807000 | 2733000 | 5331530 | 0 | 7374545 | 29118545.45 | 440400 | 139709513.69 | 308956801.55

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-10-2025 | during | 16-10-2025 | during | 16-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 400.75 | 400.75 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 93 | 96 | 208.13 | 208.13 | 100 | 100 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 49.6 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 139 | 140 | 149.36 | 149.36 | 133 | 133 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 20.3 | 24.75 | 24.75 | 24.75 | 24.75 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 97 | 194 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 44 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 550 | 530 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 2097 | 2414.9 | 5828.15 | 5796.15 | 4227.45 | 4289.45
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 21 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 19 | 19 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 179 | 178 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 53 | 40 | 64 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 65 | 82 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 20 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 106 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.45 | 0 | 3.47 | 0 | 3.47 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 48 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 63 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 108 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1175 | 1165 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 14 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 285 | 276 | 285 | 285 | 285 | 285 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2221.81 | 2381.86 | 3239.19 | 3251.72 | 2676.33 | 2720.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 173 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 310 | 310 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 2 | 2 | 55 | 55 | 10 | 10 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 35 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 107 | 117 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 103 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 104 | 200 | 200 | 50 | 100 | Engine Problem
| Import (Tripura) | Import | Import |  | 160 | 160 | 72 | 84 | 160 | 160 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 97 | 106 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 39 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 22 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1396 | 1527 | 2828.86 | 2763.86 | 2217.16 | 2251.16
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-10-2025 | during | 16-10-2025 | during | 16-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 28 | 28 | 157.5 | 157.5 | 49 | 49 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.39 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 207.39 | 171 | 400.9 | 349 | 238.9 | 187
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 10 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 266 | 260 | 268 | 268 | 365 | 365 | ST tripped due to attemperation control valve
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1097 | 1087 | 1156 | 1156 | 1235 | 1235
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 50 | 50 | 50 | 60 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 160 | 165 | 410 | 410 | 169 | 169 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 370 | 614 | 617.1 | 617.1 | 617 | 617 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1532 | 1790 | 3032.1 | 2937.1 | 2028 | 1943
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 305 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1179 | 1216 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 282 | 276 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.71 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2136.71 | 2165 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 40.57 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 205 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 52 | 52.2 | 52.2 | 25 | 25 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 75 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.12 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 747.63 | 732.04 | 1435.88 | 1435.88 | 1436 | 1436 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.7 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1616.02 | 1743.04 | 3186.47 | 3019.87 | 3086.01 | 2919.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 50 | 50 | 47 | 47 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 157 | 150 | 150 | 0 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 88 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 182.71 | 0 | 182.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 631.7 | 426 | 665.71 | 448 | 512.71 | 445
System Total |  |  |  |  | 28823.2 | 28364.092 | 12935.63 | 13705.8 | 22484.38 | 21867.7 | 18235.56 | 18003.88
Forecast Scenario (16-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13760 |  | 0 |  | 13760
|  |  |  | 1:00 | 13400 |  | 0 |  | 13400
|  |  |  | 2:00 | 13120 |  | 0 |  | 13120
|  |  |  | 3:00 | 12380 |  | 0 |  | 12380
|  |  |  | 4:00 | 12090 |  | 0 |  | 12090
|  |  |  | 5:00 | 11670 |  | 0 |  | 11670
|  |  |  | 6:00 | 11480 |  | 0 |  | 11480
|  |  |  | 7:00 | 11840 |  | 0 |  | 11840
|  |  |  | 8:00 | 11890 |  | 0 |  | 11890
|  |  |  | 9:00 | 11990 |  | 0 |  | 11990
|  |  |  | 10:00 | 12300 |  | 0 |  | 12300
|  |  |  | 11:00 | 12980 |  | 0 |  | 12980
|  |  |  | 12:00 | 13140 |  | 0 |  | 13140
|  |  |  | 13:00 | 13520 |  | 0 |  | 13520
|  |  |  | 14:00 | 13550 |  | 0 |  | 13550
|  |  |  | 15:00 | 13580 |  | 0 |  | 13580
|  |  |  | 16:00 | 13450 |  | 0 |  | 13450
|  |  |  | 17:00 | 13300 |  | 0 |  | 13300
|  |  |  | 18:00 | 14000 |  | 0 |  | 14000
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14270 |  | 0 |  | 14270
|  |  |  | 19:30 | 14202 |  | 0 |  | 14202
|  |  |  | 20:00 | 14207 |  | 0 |  | 14207
|  |  |  | 21:00 | 14176 |  | 0 |  | 14176
|  |  |  | 22:00 | 13900 |  | 0 |  | 13900
|  |  |  | 23:00 | 13800 |  | 0 |  | 13800
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13140.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14270.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14270.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 313.793 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 10:59 hrs on 16-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12935.63 | MW | 12:00 Hr. | Energy Generated |  |  | 308.9568 |  | MKWHr.
| Day Peak Demand |  |  | 13144.63 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.565 |  | MKWHr.
| Evening Peak Generation |  |  | 13705.8 | MW | 21:00 Hr. | Energy Demand |  |  | 316.5218 |  | MKWHr.
| Evening Peak Demand |  |  | 14269.56 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 11480.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 860.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 13705.8 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.1256 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.5287 | 0 | 16.3219 | 0 | 0 | 0.22887 | 0 | 0 | 50.0794 | Gas | 112.8506 | Gas | 404087929.4743
| Chattogram Zone |  |  | 4.5719 | 35.3127 | 9.717 | 0 | 5.2775 | 0.14967 | 0 | 0.01488 | 55.0438 | Coal | 93.9121 | Coal | 547576497.3861
| Cumilla Zone |  |  | 23.4143 | 0 | 8.8277 | 0 | 0 | 0.3911 | 1.6925 | 0 | 34.3256 | HFO | 49.6121 | HFO | 933993177.272
| Mymensingh Zone |  |  | 0.67584 | 0 | 3.1422 | 0 | 0 | 0.33226 | 0 | 0 | 4.1503 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6481 | Hydro | 5.2775 | Hydro | 527752.9
| Khulna Zone |  |  | 3.759 | 10.3346 | 0.7713 | 0 | 0 | 0.54504 | 22.6116 | 0 | 38.0215 | Solar | 4.7018 | Solar | 70681777.1804
| Barishal Zone |  |  | 8.0645 | 43.3001 | 1.0504 | 0 | 0 | 0 | 0 | 0 | 52.415 | Import | 42.5878 | Import | 244404361.79
| Rajshahi Zone |  |  | 13.1882 | 0 | 5.1644 | 0 | 0 | 1.5425 | 18.2837 | 0 | 38.1787 | Wind | 0.01488 | Wind | 219331.2
| Rangpur Zone |  |  | 0 | 4.9647 | 4.6171 | 0 | 0 | 1.5125 | 0 | 0 | 11.0943
| Total |  |  | 112.8506 | 93.9121 | 49.6121 | 0 | 5.2775 | 4.7018 | 42.5878 | 0.01488 | 308.9568
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 404087929.4743 |  | Hydro | 527752.9
|  |  |  | Coal | 547576497.3861 |  | Solar | 70681777.1804
|  |  |  | HFO | 933993177.272 |  | Import | 244404361.79
|  |  |  | HSD | 0 |  | Wind | 219331.2
[5 empty] | Total: | 220,14,90,827 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6996 | Peak Hr Flow | 898.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44547109.15 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.2837 | Peak Hr Flow | 732.04 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2025 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6925 | Peak Hr Flow | 84.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2494 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.6758 | Peak Hr Flow | 1714.04 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 78 |  | 4986
|  |  |  | Chattogram |  | 22 |  | 1429
|  |  |  | Cumilla |  | 52 |  | 1423
|  |  |  | Mymensingh |  | 58 |  | 1096
|  |  |  | Sylhet |  | 40 |  | 588
|  |  |  | Khulna |  | 55 |  | 1599
|  |  |  | Barishal |  | 25 |  | 413
|  |  |  | Rajshahi |  | 68 |  | 1262
|  |  |  | Rangpur |  | 52 |  | 810
|  |  |  | Total |  | 450 |  | 13606
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 15:18 | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Annual Maintenance.
| 08:02 | 15:17 | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Annual Maintenance.
| 08:16 | 11:13 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to Emergency red hot | [7 empty] | 25.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 08:17 | 16:24 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to
Rangamati-Khagrachori Ckt-01 Taken shutdown due to annual maintenance. and from
Khagrachori 132/33kV end Due to Annual Maintenance
| 08:18 | 11:10 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to Emergency red hot | [7 empty] | 25.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 08:20 | 15:07 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance work
| 08:20 | 15:07 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Annual Maintenance work
| 08:23 | 14:34 | Rajbari 132/33kV S/S Transformer-3 LT Scheduled S/D
| 08:24 | 14:33 | Rajbari 132/33kV S/S Transformer-3 HT Scheduled S/D
| 08:54 | 17:30 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Annual maintenance
|  | 09:00 | Chandpur 132/33kV S/S 200KVA Aux. T-2 HT is restored.
| 09:08 |  | Bhulta 400/230/132 kV s/s 230/132 kV ATR-2 tripped showing Non-directional Earth Fault.
No interruption is occurring.
| 09:14 | 16:02 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Annual maintenance RPCL 01
| 09:14 | 16:02 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Annual maintenance RPCL 01
| 09:20 | 20:55 | Chowmuhani-Feni 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to Order by NLDC
| 09:24 | 20:40 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Project Work S/D Due to CNTIC project work
| 09:28 | 13:20 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D Due to Scada And RTU integration
| 09:29 | 13:18 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Scheduled S/D Due to Bogura -01 (230 kv ckt)
Shutdown due to SCADA and RTU upgradation at bogura 230 kv substation.
| 09:46 | 20:52 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to CNTIC
project work and from Daganbhuiyan 132/33kV end Due to CNTIC project work
| 09:52 | 19:46 | Daganbhuiyan 132/33kV S/S Main Bus 1&2 Project Work S/D Due to CNTIC project work
| 10:10 | 10:58 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to High temperature at T-5 LT CB R | [7 empty] | 5.0MW load
|  |  | phase Upper part maintenance. | [7 empty] | interrup.
| 10:11 | 10:57 | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to High temperature at T-5 LT CB R | [7 empty] | 5.0MW load
|  |  | phase Upper part maintenance. | [7 empty] | interrup.
| 10:35 | 11:17 | Bibiyana-Kaliakoir 400 kV Ckt-1 Tripped from Bibiana 400/230kV end showing Main 1, Main 2
relays Due to EF COM Trip
| 10:37 | 11:17 | Kaliakoir 400/230/132kV S/S Bibiyana1 Tripped showing REL 670 relays.
| 11:10 | 16:45 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Forced S/D Due to Auxiliary
Transfformer 2 maintenances
| 11:10 | 16:45 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Forced S/D Due to Auxiliary
Transfformer 2 maintenances
| 12:05 | 14:10 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 12:05 | 14:10 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 12:05 | 12:42 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens 7sa87
and L8b relays. and from Ghorashal 230kV end showing SIPROTEC-7SA611 relays Due to
Unknown
| 12:14 | 16:05 | Kachua 230/132/33kV S/S ATR-2 HT Project Work S/D
| 12:53 | 16:10 | Kachua 230/132/33kV S/S ATR-2 LT Project Work S/D
| 13:42 | 14:07 | Joydebpur 132/33kV S/S GT-4 HT Scheduled S/D Due to Due to replacement of faulty energy | [7 empty] | 30.0MW load
|  |  | meter of incomer. | [7 empty] | interrup.
|  | 14:31 | Bog-Sherpur 132/33kV S/S Main Bus-2 is restored.
| 14:46 | 16:29 | Bogura 230/132kV S/S Bogura (W) CKT-2 Project Work S/D Due to SCADA & RTU Integration
| 14:46 | 16:29 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Scheduled S/D Due to Bogura -02 (230 kv ckt)
Shutdown due to SCADA and RTU upgradation at bogura 230 kv substation.
|  | 16:47 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 16:49 | Barishal 230/132kV S/S T-4 LT is restored.
|  | 16:50 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 16:50 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
| 17:07 | 17:27 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Scheduled S/D Due to SCADA upgradation at Bogura
230kV Grid Sub-Station
| 17:07 | 17:27 | Bogura 230/132kV S/S Bogura (W) CKT-1 Project Work S/D Due to SCADA & RTU Integration
| 17:22 | 18:32 | Baghabari-Roppur 230kV Ckt-1 Tripped from Baghabari 230/132kV end showing Line diff
protection relay relays Due to SPMD testing work time.
|  | 17:29 | Chandraghona-Madunaghat 132 kV Ckt-2 is restored.
|  | 19:00 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation: 13704 MW.
| 00:08 |  | Adani Power Jharkhand Ltd. Unit-2 was synchronized.
| 00:49 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 00:58 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 00:59 |  | Ashuganj 225 MW was shut down due to a problem in the generator winding.
| 05:21 |  | Ashuganj 420 MW CCPP (East) GT was sync.
| 06:00 |  | Minimum Generation: 11782 MW.
| 06:13 |  | Aminbazar 400/230/132kV S/S ATR-03 LT Scheduled S/D Due to Annual maintenance
| 06:15 |  | Aminbazar 400/230/132kV S/S ATR-03 HT Scheduled S/D Due to Annual maintenance
| 06:57 |  | Khagrachari-Rangamati 132kV Ckt-2 Scheduled S/D from Khagrachori 132/33kV end Due to
Annual maintenance and from Rangamati 132/33kV end Due to Annual Bay Maintenance.
| 07:37 |  | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Annual Maintenance and deadline checking. and from Chandraghona 132/33kV end Due to
Annual Maintenance
| 07:39 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Maintenance work 2025
| 07:39 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Maintenance work 2025
| 07:40 |  | Naogaon 132/33kV S/S T-1 LT Tripped showing Inst. E/F relays Due to 33kV feeder(NESCO
Argi-Naogaon) Trip
| 07:40 |  | Naogaon 132/33kV S/S T-2 LT Tripped showing Inst. E/F relays Due to 33kV feeder(NESCO
Argi-Naogaon) Trip
| 07:49 |  | Bhandaria 132/33kV S/S Transformer-2 LT Scheduled S/D
| 07:49 |  | Bhandaria 132/33kV S/S Transformer-2 HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | Shutdown for Steam leakage & Maintenance
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10468000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1195556 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 96 | 1766000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7740967 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49.6 | 518760 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 2199360 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 542492 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 532796 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.3 | 379800 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 487080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 551520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 194 | 3512727 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 44 | 1342368 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2240640 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1565280 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 228867 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 302400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 530 | 12686818 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1818000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2414.9 | 50079431
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 379508.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126630 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5277529 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 178 | 4167780 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 53 | 862560 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 82 | 1682477 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 404160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 106 | 1082880 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 431564 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1188218 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 1153340 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 63 | 2039891 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 108 | 896582 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1165 | 28505452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 14880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 276 | 6807272.73 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2381.86 | 55043763.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 173 | 4647000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 310 | 7695100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 7022000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 1080 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 2 | 63360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1124916 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 117 | 2945672 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 810768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2415160 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1504800 | Engine Problem
| Import (Tripura) |  | Import | 0 | 160 | 84 | 1692480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 771624 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 445720 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1631340 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 53760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1109760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 391105 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1527 | 34325645
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 28 | 675840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1142400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1611600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 319560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 299280 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 88920 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 171 | 4150300
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1613640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3635672.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719232 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1933440 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3332500 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 257664 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7517000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 260 | 6247000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1087 | 25648148.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 21699636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 346080 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 425216 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 165 | 3758976 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 545040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 614 | 10334550 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1790 | 38021498
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 305 | 7374545 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 609984 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2733000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1216 | 29118545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5331530 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 440400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6807000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2858 | 2165 | 52415004.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 410656 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 443356 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 267200 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 205 | 3849364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9338836 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 245390 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 583195 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 606864 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2071008 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 947424 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 732.04 | 18283651 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 374240 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 727080 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1743.04 | 38178744
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1023709 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3941000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2217216 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45204.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2399892 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 228846 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1238400 | -
Rangpur Area Total |  |  |  |  | 950 | 426 | 11094267.24
Eastern Grid Total |  |  |  |  | 17383.852 | 7581.76 | 169247287.86
Western Grid Total |  |  |  |  | 10980.24 | 6124.04 | 139709513.69
National Grid Total |  |  |  |  | 28364.092 | 13705.8 | 308956801.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-10-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9271.12 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3883.4 | MW
i) Dhaka area |  |  | 4907.56 |  | MW | i) Khulna area |  |  |  | 1543.7 | MW
ii) Chattogram area |  |  | 1406.93 |  | MW | ii) Barishal area |  |  |  | 387.5 | MW
iii) Cumilla area |  |  | 1370.63 |  | MW | iii) Rajshahi area |  |  |  | 1194.2 | MW
iv) Mymensingh area |  |  | 1038 |  | MW | iv) Rangpur area |  |  |  | 758 | MW
v) Sylhet area |  |  | 548 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13154.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 71 | 22:00 | 133 | Niamatpur | 56 | 21:00
2 | AKSML | 126 | 02:00 | 68 | Ishurdi | 60 | 18:00 | 134 | Noapara | 40 | 19:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 58 | 19:00 | 135 | PHP | 8 | 20:00
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 110 | 02:00 | 136 | Pabna | 111 | 18:30
5 | Agrabad | 98 | 11:00 | 71 | Jashore | 126 | 22:00 | 137 | Palashbari | 96 | 00:00
6 | Amnura | 29 | 20:00 | 72 | Jhenaidah | 96 | 21:00 | 138 | Panchagarh | 40 | 18:00
7 | Ashuganj | 90 | 20:00 | 73 | Joydebpur | 150 | 21:00 | 139 | Patiya | 10 | 00:00
8 | BSRM | 191 | 18:00 | 74 | Joypurhat | 40 | 18:00 | 140 | Patuakhali | 60.5 | 20:00
9 | Bagerhat | 77 | 20:00 | 75 | Juldah | 16.5 | 12:00 | 141 | Payra | 26 | 02:00
10 | Bajitpur | 82 | 00:00 | 76 | KSRM | 25 | 06:00 | 142 | Postogola | 71 | 13:00
11 | Bakulia | 90 | 19:30 | 77 | Kabirpur | 237 | 21:00 | 143 | Purbachal | 22 | 18:00
12 | Banani | 51.6 | 13:00 | 78 | Kachua | 102 | 20:00 | 144 | Purbasadipur | 100 | 18:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kallyanpur | 108 | 15:00 | 145 | Rahanpur | 30 | 20:00
14 | Barapukuria | 44 | 19:30 | 80 | Kalurghat | 55 | 10:00 | 146 | Rahim | 20 | 07:00
15 | Barguna | 20 | 18:00 | 81 | Kamrangirchar | 79 | 13:00 | 147 | Rajbari | 74 | 21:00
16 | Barishal | 105 | 11:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 113 | 00:00
17 | Barishal-230 | 80 | 19:30 | 83 | Kasba | 41 | 21:00 | 149 | Rajshahi | 89 | 18:00
18 | Baroaulia | 70 | 12:00 | 84 | Kazla | 102 | 13:00 | 150 | Rajshahi-230 | 84 | 12:00
19 | Baroirhat | 59 | 00:00 | 85 | Keranigonj | 77 | 23:00 | 151 | Ramganj | 102 | 00:00
20 | Bashundhara | 188 | 13:00 | 86 | Khagrachori | 34 | 20:00 | 152 | Rampur | 42 | 00:00
21 | BashundharaCement | 12 | 02:00 | 87 | Khulna | 58 | 12:00 | 153 | Rangamati | 17 | 18:30
22 | Beanibazar | 70 | 03:00 | 88 | Khulshi | 188 | 20:00 | 154 | Rangpur | 143 | 18:30
23 | Benapole | 52 | 18:00 | 89 | Kishoreganj | 114 | 02:00 | 155 | Ruppur | 7.2 | 15:00
24 | Bhaluka | 124 | 11:00 | 90 | Kodda | 289 | 14:00 | 156 | SSM | 3 | 00:00
25 | Bhandaria | 48 | 02:00 | 91 | Kulaura | 46 | 01:00 | 157 | Saidpur | 96 | 14:00
26 | Bhangura | 29 | 23:00 | 92 | Kurigram | 56 | 07:00 | 158 | Satkhira | 113 | 19:00
27 | Bheramara(GK) | 53 | 20:00 | 93 | Kushtia | 136 | 20:00 | 159 | Satmasjid | 101 | 18:00
28 | Bhulta | 203 | 12:00 | 94 | Laksam | 36 | 23:00 | 160 | Savar | 213 | 19:30
29 | Bog-Sherpur | 64 | 00:00 | 95 | Lakshmipur | 32 | 18:30 | 161 | SevenRings | 17.51 | 20:00
30 | Bogura | 146 | 22:00 | 96 | Lalbag | 64 | 13:00 | 162 | ShahCement | 30 | 08:00
31 | Borhanuddin | 77 | 02:00 | 97 | Lalmonirhat | 44 | 02:00 | 163 | Shahjadpur | 72 | 21:00
32 | Brahmanbaria | 129 | 01:00 | 98 | MI_Cement | 10.7 | 07:00 | 164 | Shahjibazar | 125 | 21:00
33 | Cantonment | 140 | 13:00 | 99 | Madanganj | 42 | 14:00 | 165 | Shahmirpur | 51 | 00:00
34 | Chandina | 40.05 | 22:00 | 100 | Madaripur | 104 | 02:00 | 166 | Shariatpur | 72 | 01:00
35 | Chandpur | 84 | 20:00 | 101 | Madartek | 88 | 23:00 | 167 | Sherpur | 132 | 01:00
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 56 | 14:00 | 168 | Shikalbaha | 25 | 02:00
37 | Chapai | 53 | 11:00 | 103 | Magura | 51 | 20:00 | 169 | Shitalakhya | 87.9 | 13:00
38 | Charsaidpur | 39 | 19:00 | 104 | Mahasthangarh | 68 | 18:00 | 170 | Sholosohor | 51 | 15:00
39 | Chauddagram | 74 | 21:00 | 105 | Maijdee | 22 | 02:00 | 171 | Shyampur | 136 | 13:00
40 | Chhatak | 34 | 02:00 | 106 | Manikganj | 112 | 01:00 | 172 | Siddhirganj | 125 | 15:00
41 | Chowmuhani | 162 | 02:00 | 107 | Maniknagar | 68 | 13:00 | 173 | Sirajganj | 108 | 18:00
42 | Chuadanga | 98 | 18:00 | 108 | Matarbari | 47 | 00:00 | 174 | Sonargaon | 103 | 04:00
43 | Coxsbazar | 122 | 14:00 | 109 | Matuail | 68 | 09:00 | 175 | Sreemongol | 78 | 01:00
44 | Cumilla(N) | 113 | 21:00 | 110 | Metrorail_Motijheel | 25 | 16:00 | 176 | Sreepur | 92 | 18:30
45 | Cumilla(S) | 154 | 18:00 | 111 | Metrorail_Uttara | 10 | 19:30 | 177 | Srinagar | 48 | 19:30
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 128 | 15:00 | 178 | Sunamganj | 60 | 03:00
47 | Daudkandi | 145 | 02:00 | 113 | Mirpur | 124 | 18:00 | 179 | Sylhet | 57 | 00:00
48 | DhakaUniversity | 96 | 13:00 | 114 | Mirsorai | 11 | 10:00 | 180 | Sylhet-132 | 114 | 10:00
49 | Dhamrai | 112 | 20:00 | 115 | Mirzapur | 38 | 18:00 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 133 | 13:00 | 116 | Mithapukur | 52 | 02:00 | 182 | Tangail | 170 | 20:00
51 | Dohazari | 94 | 02:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 20 | 14:00
52 | Faridpur | 147 | 21:00 | 118 | Mogbazar | 91.6 | 15:00 | 184 | Thakurgaon | 79 | 19:30
53 | Fatullah | 92 | 00:00 | 119 | Mongla | 39 | 18:30 | 185 | Tongi | 117 | 11:00
54 | Fenchuganj | 39 | 00:00 | 120 | Motijheel | 51 | 13:00 | 186 | Ullahpara | 30 | 00:00
55 | Feni | 106 | 00:00 | 121 | Muktagacha | 31 | 00:00 | 187 | Ullon | 62 | 13:00
56 | GPH | 75 | 01:00 | 122 | Munshiganj | 99 | 03:00 | 188 | Uttara | 66 | 12:00
57 | Ghatail | 70 | 07:00 | 123 | Muradnagar | 45 | 21:00 | 189 | UttaraNew | 74 | 18:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 195 | 21:00 | 190 | Zigatola | 72 | 18:30
59 | Ghorashal-230 | 97 | 04:00 | 125 | Naogaon | 106 | 00:00
60 | Goalpara | 33 | 19:00 | 126 | Narail | 44 | 00:00
61 | Gollamari | 88 | 13:00 | 127 | Narinda | 66 | 13:00
62 | Gopalganj | 98 | 20:00 | 128 | Narshingdi | 185 | 02:00
63 | Gulshan | 124 | 13:00 | 129 | Natore | 113 | 00:00
64 | Halishahar | 79 | 16:00 | 130 | Nawabganj | 48 | 19:30
65 | HaripurSBU | 149 | 10:00 | 131 | Netrakona | 113 | 08:00
66 | Hasnabad | 92 | 19:30 | 132 | New | 56 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13454.06 | 293 |  | 13760.25
1:00 | 13152.56 | 238 |  | 13401.27
2:00 | 13018.61 | 98 |  | 13121.02
3:00 | 12380.11 | 0 |  | 12380.11
4:00 | 12091.6 | 0 |  | 12091.6
5:00 | 11669.67 | 0 |  | 11669.67
6:00 | 11480.25 | 0 |  | 11480.25
7:00 | 11846.4 | 0 |  | 11846.4
8:00 | 11892.91 | 0 |  | 11892.91
9:00 | 11998.7 | 0 |  | 11998.7
10:00 | 12306.41 | 0 |  | 12306.41
11:00 | 12899.9 | 84 |  | 12987.68
12:00 | 12935.63 | 200 |  | 13144.63
13:00 | 12975.4 | 524 |  | 13523.4
14:00 | 12962.72 | 565 |  | 13552.72
15:00 | 12910.8 | 645 |  | 13584.8
16:00 | 12780.75 | 643 |  | 13452.75
17:00 | 12624.17 | 648 |  | 13301.17
18:00 | 13292.26 | 680 |  | 14003.26
19:00 | 13459.56 | 775 |  | 14269.56
19:30 | 13553.56 | 620 |  | 14201.56
20:00 | 13632.06 | 550 |  | 14207.06
21:00 | 13705.8 | 450 |  | 14175.8
22:00 | 13455.37 | 569 |  | 14050.37
23:00 | 13220.11 | 603 |  | 13850.11
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7548.96 | 5905.1 | 13454.06 | DAILY GENERATION CURVE
00:30 | 7447.16 | 5856.15 | 13303.31
01:00 | 7345.36 | 5807.2 | 13152.56 | 15-10-2025
01:30 | 7292.36 | 5793.225 | 13085.585
02:00 | 7239.36 | 5779.25 | 13018.61
02:30 | 7076.11 | 5623.25 | 12699.36
03:00 | 6912.86 | 5467.25 | 12380.11
03:30 | 6834.18 | 5401.675 | 12235.855
04:00 | 6755.5 | 5336.1 | 12091.6
04:30 | 6609 | 5271.635 | 11880.635
05:00 | 6462.5 | 5207.17 | 11669.67
05:30 | 6404.06 | 5170.9 | 11574.96
06:00 | 6345.62 | 5134.63 | 11480.25
06:30 | 6463.11 | 5200.215 | 11663.325
07:00 | 6580.6 | 5265.8 | 11846.4
07:30 | 6536.86 | 5332.795 | 11869.655
08:00 | 6493.12 | 5399.79 | 11892.91
08:30 | 6523.15 | 5422.655 | 11945.805
09:00 | 6553.18 | 5445.52 | 11998.7
09:30 | 6606.45 | 5546.105 | 12152.555
10:00 | 6659.72 | 5646.69 | 12306.41
10:30 | 6828.695 | 5774.46 | 12603.155
11:00 | 6997.67 | 5902.23 | 12899.9
11:30 | 7008.435 | 5909.33 | 12917.765
12:00 | 7019.2 | 5916.43 | 12935.63
12:30 | 7043.54 | 5911.975 | 12955.515
13:00 | 7067.88 | 5907.52 | 12975.4
13:30 | 7062.62 | 5906.44 | 12969.06
14:00 | 7057.36 | 5905.36 | 12962.72
14:30 | 7068.645 | 5868.115 | 12936.76
15:00 | 7079.93 | 5830.87 | 12910.8
15:30 | 7073.07 | 5772.705 | 12845.775
16:00 | 7066.21 | 5714.54 | 12780.75
16:30 | 7096.425 | 5606.035 | 12702.46
17:00 | 7126.64 | 5497.53 | 12624.17
17:30 | 7228.9 | 5729.315 | 12958.215
18:00 | 7331.16 | 5961.1 | 13292.26
18:30 | 7402.36 | 5973.55 | 13375.91
19:00 | 7473.56 | 5986 | 13459.56
19:30 | 7528.56 | 6025 | 13553.56
20:00 | 7592.06 | 6040 | 13632.06
20:30 | 7586.91 | 6082.02 | 13668.93 |  | Executive Engineer
21:00 | 7581.76 | 6124.04 | 13705.8 |  | Network Operation Division
21:30 | 7442.81 | 6137.775 | 13580.585
22:00 | 7303.86 | 6151.51 | 13455.37
22:30 | 7228.36 | 6109.38 | 13337.74
23:00 | 7152.86 | 6067.25 | 13220.11

## En-Curve
QF-LDC-12
Date | 15-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2872 | 1867.1 | 896 | 38 | 82 | 761.1 | 219 | 3918 | 0 | 751 | 2047.86 | 0 | 0 | 2 | 293 | DAILY ENERGY CURVE
00:30 | 2858 | 1867.3 | 896 | 38 | 80 | 759.15 | 219.5 | 3917.5 | 0 | 670 | 1996.86 | 0 | 0 | 1 | 265.5 | 15-10-2025
01:00 | 2844 | 1867.5 | 896 | 38 | 78 | 757.2 | 220 | 3917 | 0 | 589 | 1945.86 | 0 | 0 | 0 | 238
01:30 | 2833 | 1859.5 | 896 | 38 | 77 | 758.725 | 220 | 3917 | 0 | 572.5 | 1913.86 | 0 | 0 | 0 | 168 | Energy Generated | 308.9568 |  | MKWHr
02:00 | 2822 | 1851.5 | 896 | 38 | 76 | 760.25 | 220 | 3917 | 0 | 556 | 1881.86 | 0 | 0 | 0 | 98 | Energy not Served | 7.565 |  | MKWHr
02:30 | 2802 | 1833 | 896 | 38 | 71 | 760.25 | 220.5 | 3907 | 0 | 420.5 | 1751.11 | 0 | 0 | 0 | 49 | Total Energy Requirement | 316.5218 |  | MKWHr
03:00 | 2782 | 1814.5 | 896 | 38 | 66 | 760.25 | 221 | 3897 | 0 | 285 | 1620.36 | 0 | 0 | 0 | 0
03:30 | 2776 | 1854.5 | 896 | 38 | 69 | 759.175 | 221 | 3896.5 | 0 | 276.5 | 1449.18 | 0 | 0 | 0 | 0
04:00 | 2770 | 1894.5 | 896 | 38 | 72 | 758.1 | 221 | 3896 | 0 | 268 | 1278 | 0 | 0 | 0 | 0
04:30 | 2769 | 1859.5 | 896.5 | 38 | 68 | 759.635 | 221 | 3896 | 0 | 250.5 | 1122.5 | 0 | 0 | 0 | 0
05:00 | 2768 | 1824.5 | 897 | 38 | 64 | 761.17 | 221 | 3896 | 0 | 233 | 967 | 0 | 0 | 0 | 0
05:30 | 2751.5 | 1819 | 896.5 | 38 | 63 | 761.89 | 221 | 3842.5 | 0.07 | 233 | 948.5 | 0 | 0 | 0 | 0
06:00 | 2735 | 1813.5 | 896 | 38 | 62 | 762.61 | 221 | 3789 | 0.14 | 233 | 930 | 0 | 0 | 0 | 0
06:30 | 2762.5 | 1867 | 896.5 | 38 | 63 | 760.57 | 221 | 3821.5 | 53.755 | 233 | 946.5 | 0 | 0 | 0 | 0
07:00 | 2790 | 1920.5 | 897 | 38 | 64 | 758.53 | 221 | 3854 | 107.37 | 233 | 963 | 0 | 0 | 0 | 0
07:30 | 2727 | 1843.5 | 890 | 38 | 60 | 758.18 | 220 | 3858.5 | 212.295 | 265.5 | 996.68 | 0 | 0 | 0 | 0
08:00 | 2664 | 1766.5 | 883 | 38 | 56 | 757.83 | 219 | 3863 | 317.22 | 298 | 1030.36 | 0 | 0 | 0 | 0
08:30 | 2660 | 1771.5 | 883 | 38 | 57 | 755.56 | 219 | 3832.5 | 407.385 | 320.5 | 1001.36 | 0 | 0 | 0 | 0
09:00 | 2656 | 1776.5 | 883 | 38 | 58 | 753.29 | 219 | 3802 | 497.55 | 343 | 972.36 | 0 | 0 | 0 | 0
09:30 | 2724 | 1814.75 | 883 | 38 | 61 | 751.82 | 218.5 | 3782.5 | 566.125 | 338 | 974.86 | 0 | 0 | 0 | 0
10:00 | 2792 | 1853 | 883 | 38 | 64 | 750.35 | 218 | 3763 | 634.7 | 333 | 977.36 | 0 | 0 | 0 | 0
10:30 | 2832.5 | 1876 | 890.5 | 38 | 66 | 748.035 | 218 | 3789.5 | 653.26 | 376 | 1115.36 | 0 | 0 | 0 | 42
11:00 | 2873 | 1899 | 898 | 38 | 68 | 745.72 | 218 | 3816 | 671.82 | 419 | 1253.36 | 0 | 0 | 0 | 84
11:30 | 2874 | 1890 | 898 | 38 | 70 | 746.675 | 218 | 3811 | 642.23 | 426.5 | 1302.86 | 0 | 0 | 0.5 | 142
12:00 | 2875 | 1881 | 898 | 38 | 72 | 747.63 | 218 | 3806 | 612.64 | 434 | 1352.36 | 0 | 0 | 1 | 200
12:30 | 2862.5 | 1856 | 898 | 38 | 73 | 750.475 | 218 | 3809 | 610.11 | 439 | 1400.93 | 0 | 0 | 0.5 | 362
13:00 | 2850 | 1831 | 898 | 38 | 74 | 753.32 | 218 | 3812 | 607.58 | 444 | 1449.5 | 0 | 0 | 0 | 524
13:30 | 2834 | 1839 | 898.5 | 38 | 71 | 753.16 | 218 | 3814 | 569.72 | 445 | 1488.68 | 0 | 0 | 0 | 544.5
14:00 | 2818 | 1847 | 899 | 38 | 68 | 753 | 218 | 3816 | 531.86 | 446 | 1527.86 | 0 | 0 | 0 | 565
14:30 | 2793 | 1866.85 | 898.5 | 38 | 68 | 751 | 219 | 3808 | 489.05 | 470.5 | 1534.86 | 0 | 0 | 0 | 605
15:00 | 2768 | 1886.7 | 898 | 38 | 68 | 749 | 220 | 3800 | 446.24 | 495 | 1541.86 | 0 | 0 | 0 | 645
15:30 | 2778 | 1862.45 | 898 | 38 | 68 | 751 | 220.5 | 3793.5 | 332.465 | 546.5 | 1557.36 | 0 | 0 | 0 | 644
16:00 | 2788 | 1838.2 | 898 | 38 | 68 | 753 | 221 | 3787 | 218.69 | 598 | 1572.86 | 0 | 0 | 0 | 643
16:30 | 2783 | 1841.2 | 898.5 | 38 | 68 | 749.5 | 221 | 3737 | 128.4 | 624.5 | 1613.36 | 0 | 0 | 0 | 645.5
17:00 | 2778 | 1844.2 | 899 | 38 | 68 | 746 | 221 | 3687 | 38.11 | 651 | 1653.86 | 0 | 0 | 0 | 648
17:30 | 2823.5 | 1847.85 | 898.5 | 38 | 72 | 742 | 221.5 | 3840.05 | 19.055 | 718.5 | 1737.26 | 0 | 0 | 0 | 664
18:00 | 2869 | 1851.5 | 898 | 38 | 76 | 738 | 222 | 3993.1 | 0 | 786 | 1820.66 | 0 | 0 | 0 | 680
18:30 | 2852.5 | 1843 | 898 | 38 | 77 | 736 | 222 | 3980.55 | 0 | 828 | 1900.86 | 0 | 0 | 0 | 727.5
19:00 | 2836 | 1834.5 | 898 | 38 | 78 | 734 | 222 | 3968 | 0 | 870 | 1981.06 | 0 | 0 | 0 | 775
19:30 | 2833 | 1865.5 | 898 | 38 | 80 | 727 | 222 | 4025 | 0 | 844 | 2021.06 | 0 | 0 | 0 | 620
20:00 | 2887 | 1850.5 | 898 | 38 | 74 | 735 | 222 | 4011 | 0 | 847 | 2069.56 | 0 | 0 | 0 | 550
20:30 | 2907 | 1869.4 | 898 | 38 | 79 | 733.52 | 221.5 | 4033.5 | 0 | 848.5 | 2033.51 | 0 | 0 | 7 | 500
21:00 | 2927 | 1888.3 | 898 | 38 | 84 | 732.04 | 221 | 4056 | 0 | 850 | 1997.46 | 0 | 0 | 14 | 450
21:30 | 2864 | 1888.15 | 898 | 38 | 82 | 732.275 | 221 | 4063 | 0 | 850.5 | 1936.66 | 0 | 0 | 7 | 509.5
22:00 | 2801 | 1888 | 898 | 38 | 80 | 732.51 | 221 | 4070 | 0 | 851 | 1875.86 | 0 | 0 | 0 | 569
22:30 | 2747 | 1892.5 | 898 | 38 | 80 | 732.38 | 219.5 | 4060 | 0 | 849.5 | 1819.86 | 0 | 0 | 1 | 586
23:00 | 2693 | 1897 | 898 | 38 | 80 | 732.25 | 218 | 4050 | 0 | 848 | 1763.86 | 0 | 0 | 2 | 603
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 06:00 | 373 | 11:00 | Payra | 410 | 00:00 | 407 | 13:00
Ashuganj | 405 | 3:00 | 379 | 12:00 | Rahanpur | 404 | 00:00 | 398 | 10:00
Bhulta | 403 | 04:00 | 374 | 12:00 | Rampal | 402 | 05:00 | 394 | 10:00
Bibiana | 390 | 01:00 | 381 | 10:00
BIPTC | 403 | 04:00 | 393 | 18:00
Bogura | 398 | 01:00 | 392 | 10:00
Gopalganj | 397 | 06:00 | 388 | 11:00
Kaliakoir | 378 | 03:00 | 363 | 11:00
Madunaghat | 397 | 19:00 | 392 | 09:00
Meghnaghat | 390 | 22:00 | 378 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 222 | 10:00 | Kaliakoir | 237 | 04:00 | 225 | 10:00
AKSML | 235 | 18:00 | 229 | 10:00 | Keranigonj | 228 | 05:00 | 218 | 11:00
Aminbazar | 230 | 00:00 | 224 | 10:00 | Khulna(S) | 232 | 06:00 | 225 | 20:00
Ashuganj | 234 | 05:00 | 222 | 12:00 | Madunaghat | 236 | 18:00 | 231 | 10:00
Ashuganj-400 | 234 | 05:00 | 222 | 12:00 | Madunaghat-400 | 237 | 18:00 | 232 | 12:00
Baghabari | 237 | 22:00 | 230 | 12:00 | Maniknagar | 221 | 19:00 | 213 | 11:00
Barapukuria | 227 | 13:00 | 223 | 07:00 | Meghnaghat | 229 | 19:00 | 222 | 12:00
Barapukuria-230 | 227 | 13:00 | 223 | 07:00 | Meghnaghat-400 | 226 | 22:00 | 218 | 11:00
Barishal | 235 | 02:00 | 230 | 11:00 | Mirsorai | 238 | 19:00 | 225 | 04:00
Bheramara | 234 | 06:00 | 229 | 11:00 | Rajshahi | 233 | 06:00 | 228 | 11:00
Bhulta | 232 | 03:00 | 213 | 12:00 | Rampal | 231 | 06:00 | 223 | 21:00
Bibiana | 231 | 21:00 | 224 | 13:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 229 | 11:00 | Rampura | 231 | 03:00 | 211 | 12:00
Bogura | 239 | 01:00 | 234 | 10:00 | Shikalbaha | 236 | 02:00 | 230 | 05:00
Bogura-400 | 238 | 01:00 | 234 | 10:00 | Shyampur | 226 | 05:00 | 217 | 11:00
Borhanuddin | 238 | 01:00 | 235 | 10:00 | Siddhirganj | 224 | 23:00 | 215 | 11:00
BSRM | 235 | 19:00 | 226 | 03:00 | Sirajgonj | 241 | 23:00 | 236 | 11:00
Cumilla(N) | 228 | 17:00 | 222 | 10:00 | Sreepur | 232 | 23:00 | 221 | 11:00
Faridpur | 232 | 02:00 | 227 | 11:00 | Tongi | 232 | 01:00 | 217 | 11:00
Fenchuganj | 231 | 06:00 | 228 | 10:00
Ghorashal | 236 | 03:00 | 225 | 15:00
Ghorashal-230 | 232 | 03:00 | 215 | 11:00
Gopalganj | 234 | 06:00 | 228 | 11:00
GPH | 232 | 08:00 | 228 | 22:00
Haripur | 222 | 00:00 | 215 | 11:00
Hasnabad | 228 | 23:00 | 218 | 12:00
Hathazari | 232 | 16:00 | 228 | 15:00
Ishurdi | 237 | 23:00 | 231 | 11:00
Jhenaidah | 232 | 04:00 | 225 | 12:00
Kachua | 231 | 08:00 | 227 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 121 | 12:00 | Lalmonirhat | 130 | 02:00 | 126 | 10:00
Agargaon | 136 | 02:00 | 129 | 10:00 | Madanganj | 129 | 19:00 | 124 | 10:00
Agrabad | 135 | 18:00 | 131 | 10:00 | Madaripur | 136 | 06:00 | 133 | 10:00
AKS | 133 | 17:00 | 129 | 11:00 | Madartek | 136 | 00:00 | 121 | 11:00
Aminbazar | 136 | 01:00 | 131 | 10:00 | Madunaghat | 137 | 18:00 | 133 | 10:00
Amnura | 138 | 18:30 | 131 | 12:00 | Magura | 137 | 06:00 | 130 | 21:00
Ashuganj | 141 | 19:00 | 136 | 11:00 | Mahasthangarh | 134 | 00:00 | 131 | 10:00
Bagerhat | 133 | 08:00 | 124 | 20:00 | Maijdee | 136 | 18:30 | 130 | 04:00
Bajitpur | 132 | 19:00 | 125 | 12:00 | Manikganj | 130 | 02:00 | 122 | 11:00
Bakulia | 137 | 18:00 | 132 | 01:00 | Maniknagar | 133 | 00:00 | 127 | 11:00
Banani | 135 | 04:00 | 121 | 11:00 | Matarbari | 126 | 18:00 | 115 | 00:00
Bangabhaban | 134 | 03:00 | 128 | 11:00 | Matuail | 129 | 00:00 | 123 | 11:00
Barapukuria | 139 | 01:00 | 132 | 07:00 | Metrorail_Motijheel | 134 | 00:00 | 127 | 11:00
Barguna | 136 | 00:00 | 133 | 22:00 | Metrorail_Uttara | 136 | 21:00 | 129 | 10:00
Barishal | 139 | 01:00 | 132 | 10:00 | Millgate | 136 | 02:00 | 125 | 11:00
Barishal-230 | 136 | 00:00 | 131 | 11:00 | Mirpur | 136 | 05:00 | 130 | 10:00
Baroaulia | 136 | 18:00 | 132 | 00:00 | Mirzapur | 131 | 01:00 | 127 | 10:00
Baroirhat | 135 | 17:00 | 130 | 13:00 | Mithapukur | 135 | 04:00 | 130 | 07:00
Bashundhara | 136 | 04:00 | 121 | 12:00 | MI_Cement | 133.6 | 04:00 | 126 | 11:00
BashundharaCement | 130 | 23:00 | 120 | 15:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 129 | 18:30 | 126 | 00:00 | Mogbazar | 135 | 02:00 | 124 | 11:00
Benapole | 134 | 06:00 | 127 | 20:00 | Mongla | 133 | 06:00 | 126 | 19:30
Bhaluka | 134 | 17:00 | 123 | 11:00 | Motijheel | 134 | 02:00 | 128 | 12:00
Bhandaria | 131 | 09:00 | 120 | 20:00 | Muktagacha | 130 | 04:00 | 124 | 13:00
Bhangura | 135 | 04:00 | 131 | 13:00 | Munshiganj | 129 | 18:30 | 123 | 12:00
Bheramara | 137 | 02:00 | 135 | 10:00 | Muradnagar | 131 | 17:00 | 125 | 10:00
Bheramara(GK) | 137 | 04:00 | 135 | 10:00 | Mymensingh | 130 | 06:00 | 116 | 14:00
Bhulta | 126 | 00:00 | 122 | 10:00 | Naogaon | 132 | 19:00 | 126 | 13:00
Bog-Sherpur | 136 | 01:00 | 132 | 10:00 | Narail | 138 | 06:00 | 131 | 21:00
Bogura | 136 | 00:00 | 132 | 11:00 | Narinda | 133 | 00:00 | 127 | 11:00
Bogura-230 | 137 | 01:00 | 133 | 10:00 | Narshingdi | 134 | 17:00 | 118 | 12:00
Brahmanbaria | 134 | 07:00 | 129 | 11:00 | Natore | 136 | 19:00 | 132 | 04:00
Cantonment | 136 | 04:00 | 129 | 10:00 | Nawabganj | 135 | 05:00 | 128 | 12:00
Chandina | 134 | 18:30 | 129 | 11:00 | Netrakona | 123 | 15:00 | 114 | 13:00
Chandpur | 140 | 18:00 | 134 | 04:00 | New | 136 | 05:00 | 126 | 11:00
Chandraghona | 137 | 18:00 | 133 | 11:00 | Niamatpur | 138 | 17:00 | 136 | 10:00
Chapai | 137 | 19:00 | 134 | 01:00 | Noapara | 135 | 03:00 | 131 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:00 | 123 | 11:00 | Pabna | 136 | 06:00 | 133 | 11:00
Chauddagram | 135 | 18:30 | 130 | 03:00 | Palashbari | 132 | 00:00 | 128 | 10:00
Chhatak | 128 | 04:00 | 123 | 01:00 | Panchagarh | 135 | 03:00 | 125 | 10:00
Chowmuhani | 134 | 17:00 | 130 | 02:00 | Patiya | 137 | 23:00 | 131 | 00:00
Chuadanga | 135 | 06:00 | 128 | 21:00 | Patuakhali | 136 | 09:00 | 134 | 01:00
Coxsbazar | 123 | 18:00 | 115 | 00:00 | Payra | 137 | 06:00 | 135 | 10:00
Cumilla(N) | 133 | 17:00 | 130 | 01:00 | PHP | 134 | 18:00 | 130 | 00:00
Cumilla(S) | 135 | 18:30 | 126 | 10:00 | Postogola | 135 | 03:00 | 129 | 10:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 135 | 02:00 | 122 | 11:00
Daudkandi | 129 | 18:30 | 121 | 11:00 | Purbasadipur | 133 | 03:00 | 126 | 07:00
DhakaUniversity | 136 | 04:00 | 121 | 12:00 | Rahanpur | 138 | 00:00 | 137 | 09:00
Dhamrai | 135 | 03:00 | 128 | 10:00 | Rahanpur-400 | 139 | 00:00 | 137 | 10:00
Dhanmondi | 136 | 04:00 | 123 | 13:00 | Rahim | 129 | 19:30 | 123 | 11:00
Dohazari | 134 | 18:00 | 127 | 00:00 | Rajbari | 136 | 02:00 | 132 | 11:00
Faridpur | 136 | 00:00 | 134 | 10:00 | Rajendrapur | 138 | 03:00 | 120 | 12:00
Fatullah | 137 | 20:00 | 131 | 11:00 | Rajshahi | 135 | 20:00 | 131 | 12:00
Fenchuganj | 138 | 10:00 | 135 | 00:00 | Rajshahi-230 | 135 | 23:00 | 131 | 11:00
Feni | 135 | 18:30 | 130 | 04:00 | Ramganj | 136 | 19:00 | 130 | 11:00
Ghatail | 128 | 04:00 | 122 | 07:00 | Rampur | 136 | 19:00 | 130 | 11:00
Ghorashal | 139 | 01:00 | 130 | 13:00 | Rampura | 135 | 03:00 | 122 | 11:00
Goalpara | 139 | 06:00 | 131 | 18:00 | Rangamati | 135 | 07:00 | 132 | 11:00
Gollamari | 138 | 06:00 | 133 | 20:00 | Rangpur | 134 | 15:00 | 129 | 03:00
Gopalganj | 137 | 04:00 | 133 | 11:00 | Ruppur | 138 | 05:00 | 135 | 10:00
Gopalganj-400 | 137 | 01:00 | 134 | 10:00 | Saidpur | 134 | 01:00 | 127 | 07:00
Gulshan | 135 | 04:00 | 122 | 12:00 | Satkhira | 136 | 09:00 | 128 | 21:00
Halishahar | 136 | 19:00 | 130 | 11:00 | Satmasjid | 135 | 01:00 | 129 | 10:00
Haripur | 129 | 00:00 | 124 | 11:00 | Savar | 137 | 22:00 | 129 | 10:00
HaripurSBU | 129 | 00:00 | 124 | 11:00 | SevenRings | 139 | 01:00 | 128 | 12:00
Hasnabad | 135 | 04:00 | 129 | 10:00 | ShahCement | 129 | 18:00 | 123 | 11:00
Hathazari | 137 | 20:00 | 134 | 00:00 | Shahjadpur | 137 | 00:00 | 135 | 10:00
Ishurdi | 139 | 23:00 | 136 | 10:00 | Shahjibazar | 135 | 06:00 | 130 | 11:00
Jaldhaka | 132 | 04:00 | 127 | 07:00 | Shahmirpur | 137 | 18:00 | 131 | 03:00
Jamalpur | 132 | 18:30 | 122 | 20:00 | Shariatpur | 135 | 07:00 | 132 | 11:00
Jashore | 135 | 06:00 | 128 | 12:00 | Sherpur | 128 | 04:00 | 118 | 20:00
Jhenaidah | 138 | 05:00 | 129 | 12:00 | Shikalbaha | 127 | 19:00 | 121 | 00:00
Jhenaidah-230 | 137 | 05:00 | 133 | 12:00 | Shikalbaha-230 | 138 | 18:00 | 131 | 16:00
Joydebpur | 137 | 22:00 | 124 | 10:00 | Shitalakhya | 133.6 | 04:00 | 126 | 11:00
Joypurhat | 132 | 20:00 | 124 | 13:00 | Sholosohor | 137 | 18:00 | 133 | 10:00
Juldah | 136 | 20:00 | 131 | 11:00 | Shyampur | 137 | 22:00 | 132 | 10:00
Kabirpur | 137 | 01:00 | 123 | 11:00 | Shyampur-230 | 137 | 23:00 | 131 | 11:00
Kachua | 139 | 17:00 | 134 | 03:00 | Siddhirganj | 130 | 20:00 | 124 | 12:00
Kaliakoir | 136 | 02:00 | 130 | 10:00 | Sirajganj | 134 | 06:00 | 130 | 11:00
Kallyanpur | 137 | 05:00 | 131 | 10:00 | Sonargaon | 129 | 19:00 | 123 | 10:00
Kalurghat | 137 | 17:00 | 134 | 02:00 | Sreemongol | 134 | 06:00 | 129 | 11:00
Kamrangirchar | 135 | 05:00 | 128 | 10:00 | Sreepur | 135 | 23:00 | 127 | 13:00
Kaptai | 139 | 18:00 | 136 | 16:00 | Srinagar | 135 | 05:00 | 129 | 10:00
Kasba | 132 | 18:30 | 125 | 04:00 | SSM | 140 | 18:00 | 132 | 7:00
Kazla | 133 | 01:00 | 128 | 11:00 | Sunamganj | 127 | 15:00 | 120 | 02:00
Keranigonj | 136 | 06:00 | 128 | 11:00 | Sylhet | 130 | 07:00 | 128 | 00:00
Khagrachori | 134 | 07:00 | 131 | 09:00 | Sylhet-132 | 130 | 15:00 | 128 | 10:00
Khulna | 137 | 05:00 | 132 | 19:30 | Tangail | 128 | 01:00 | 124 | 07:00
Khulna(S) | 139 | 06:00 | 133 | 20:00 | Taraganj | 132 | 00:00 | 129 | 07:00
Khulshi | 134 | 18:00 | 129 | 11:00 | Thakurgaon | 136 | 03:00 | 126 | 08:00
Kishoreganj | 130 | 16:00 | 123 | 12:00 | TK | 137 | 19:00 | 133 | 10:00
Kodda | 137 | 01:00 | 119 | 12:00 | Tongi | 137 | 01:00 | 128 | 11:00
KSRM | 136 | 07:00 | 130 | 04:00 | Ullahpara | 134 | 00:00 | 131 | 12:00
Kulaura | 135 | 07:00 | 133 | 02:00 | Ullon | 135 | 03:00 | 122 | 11:00
Kurigram | 130 | 01:00 | 124 | 07:00 | Uttara | 136 | 04:00 | 124 | 12:00
Kushtia | 135 | 05:00 | 132 | 10:00 | UttaraNew | 135 | 04:00 | 129 | 10:00
Laksam | 138 | 18:30 | 133 | 03:00 | Zigatola | 136 | 06:00 | 128 | 11:00
Lakshmipur | 135 | 18:00 | 129 | 04:00
Lalbag | 135 | 06:00 | 128 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division