## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-10-2025 | during | 17-10-2025 | during | 17-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 3 | 347 | 400.75 | 400.75 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 340 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 36 | 0 | 208.13 | 208.13 | 100 | 100 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 135 | 135 | 149.36 | 149.36 | 140 | 140 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 20.5 | 24 | 24 | 24 | 24 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 97 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 89 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 460 | 360 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 2079 | 2183.5 | 5827.4 | 5795.4 | 4233.7 | 4295.7
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 19 | 19 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 163 | 163 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 60 | 54 | 68 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 66 | 66 | 84 | 84 | 84 | 84 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 14 | 23 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 96 | 106 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.34 | 0 | 3.71 | 0 | 3.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 48 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 36 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 90 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1164 | 1224 | 1224 | 1224 | 1175 | 1170 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 280 | 280 | 650 | 650 | 285 | 285 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2257.84 | 2527.86 | 3628.43 | 3645.72 | 2637.57 | 2691.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 265 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 240 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 115 | 160 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 35 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 39 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 92 | 110 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 102 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 144 | 200 | 200 | 100 | 100 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 86 | 160 | 160 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 97 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 9 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 25 | 51 | 115 | 115 | 39 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 11 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1315 | 1486 | 2607.86 | 2542.86 | 2153.86 | 2137.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-10-2025 | during | 17-10-2025 | during | 17-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 10 | 157.5 | 157.5 | 49 | 49 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 69 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.62 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 205.62 | 156 | 398.9 | 349 | 236.9 | 187
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 10 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 0 | 0 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 160 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 11 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 305 | 336 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1133 | 1176 | 1025 | 1025 | 1075 | 1075
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 192 | 185 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 15 | 15 | none
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87.44 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 602 | 616 | 617.1 | 617.1 | 370 | 604 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1819.44 | 1920 | 3023.1 | 2935.1 | 2579 | 2725
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 306 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 13 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1186 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 292 | 295 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.42 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2071.42 | 2171 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 57.15 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 207 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.43 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1270 | 1471.3 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.61 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 2107.19 | 2439.3 | 3188.62 | 3021.87 | 3108.04 | 2941.29
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 45 | 46 | 46 | 47 | 47 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 150 | 150 | 0 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 191 | 0 | 182.71 | 0 | 182.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 312.6 | 260 | 661.71 | 444 | 512.71 | 445
System Total |  |  |  |  | 28823.2 | 28364.092 | 13301.11 | 14319.66 | 22508.02 | 21904.95 | 18550.78 | 18511.71
Forecast Scenario (17-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | No Data |  | 0 |  | No Data
|  |  |  | 1:00 | 14000 |  | 0 |  | 14000
|  |  |  | 2:00 | 13500 |  | 0 |  | 13500
|  |  |  | 3:00 | 13000 |  | 0 |  | 13000
|  |  |  | 4:00 | 12600 |  | 0 |  | 12600
|  |  |  | 5:00 | 12200 |  | 0 |  | 12200
|  |  |  | 6:00 | 11600 |  | 0 |  | 11600
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11400 |  | 0 |  | 11400
|  |  |  | 9:00 | 11100 |  | 0 |  | 11100
|  |  |  | 10:00 | 11200 |  | 0 |  | 11200
|  |  |  | 11:00 | 11400 |  | 0 |  | 11400
|  |  |  | 12:00 | 12100 |  | 0 |  | 12100
|  |  |  | 13:00 | 12600 |  | 0 |  | 12600
|  |  |  | 14:00 | 11500 |  | 0 |  | 11500
|  |  |  | 15:00 | 11200 |  | 0 |  | 11200
|  |  |  | 16:00 | 11000 |  | 0 |  | 11000
|  |  |  | 17:00 | 10800 |  | 0 |  | 10800
|  |  |  | 18:00 | 12300 |  | 0 |  | 12300
|  |  |  | 18:30 | 13100 |  | 0 |  | 13100
|  |  |  | 19:00 | 13200 |  | 0 |  | 13200
|  |  |  | 19:30 | 13400 |  | 0 |  | 13400
|  |  |  | 20:00 | 13300 |  | 0 |  | 13300
|  |  |  | 21:00 | 13200 |  | 0 |  | 13200
|  |  |  | 22:00 | 13100 |  | 0 |  | 13100
|  |  |  | 23:00 | 12900 |  | 0 |  | 12900
Probable Maximum Temperature: |  |  | 33.30°C
Probable Maximum Demand at Day Peak: |  |  | 12100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 279.90 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:08 hrs on 17-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-10-2025 | [28 empty] | Date: | 16-10-2025 | [28 empty] | Date: | 16-10-2025 | [28 empty] | Date: | 16-10-2025 | [28 empty] | Date: | 16-10-2025 | [14 empty] | Date: | 16-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 70 | 140 | 194 | 55 | 35 | 72 | 0 | 450 | 0 | 535 | 0 | 0 | 300 | 97 | 0 | 0 | 142 | 20.5 | 22 | 0 | 0 | 84 | 16 | 104 | 0 | 0 | 84 | 52 | 54.36 | 0 | 0 | 0 | 218 | 0 | 24 | 278 | 17 | 0 | 0 | 25.5 | 0 | 177 | 0 | 0 | 0 | 1223 | 0 | 51 | 118 | 0 | 0 | 310 | 280 | 2 | 174 | 5 | 33 | 103 | 104 | 0 | 19 | 103 | 82 | 43 | 0 | 37 | 320 | 0 | 36 | 0 | 67 | 156 | 10 | 0 | 81 | 30 | 0 | 16 | 159 | 1 | 68 | 47 | 34 | 0 | 0 | 12 | 7154.36 | 898 | 163 | 0 | 29 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 715.67 | 0 | 40 | 0 | 35 | 113 | 0 | 89 | 35 | 52 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 161 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 198 | 115 | 220 | 0 | 307 | 1222 | 17 | 5856.67 | 13011.03 | 106.82
01:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 140 | 194 | 55 | 0 | 35 | 0 | 450 | 0 | 530 | 0 | 0 | 300 | 97 | 0 | 0 | 142 | 20.5 | 20 | 0 | 0 | 92 | 16 | 104 | 0 | 0 | 84 | 52 | 54.36 | 0 | 0 | 0 | 218 | 0 | 19 | 278 | 17 | 0 | 0 | 25.5 | 0 | 165 | 0 | 0 | 0 | 1224 | 0 | 51 | 115 | 0 | 0 | 310 | 280 | 5 | 0 | 29 | 34 | 103 | 72 | 0 | 19 | 103 | 74 | 43 | 0 | 37 | 320 | 0 | 66 | 0 | 67 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 17 | 68 | 47 | 34 | 0 | 0 | 12 | 6853.36 | 898 | 166 | 0 | 29 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 854.86 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 22 | 26 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 160 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 262 | 115 | 220 | 0 | 304 | 1222 | 17 | 5813.86 | 12667.22 | 106.81
02:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 140 | 194 | 55 | 0 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 300 | 98 | 0 | 0 | 142 | 20.5 | 20 | 0 | 0 | 89 | 16 | 105 | 0 | 0 | 82 | 52 | 54.36 | 0 | 0 | 0 | 218 | 0 | 21 | 278 | 17 | 0 | 0 | 25.5 | 0 | 165 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 0 | 0 | 310 | 280 | 18 | 0 | 34 | 34 | 103 | 54 | 0 | 19 | 100 | 74 | 43 | 0 | 37 | 310 | 0 | 66 | 0 | 67 | 144 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 17 | 67 | 47 | 34 | 0 | 0 | 12 | 6813.36 | 897 | 166 | 0 | 29 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 930.46 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 22 | 8 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 152 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 304 | 1222 | 17 | 5892.46 | 12705.82 | 106.8
03:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 140 | 194 | 55 | 0 | 35 | 0 | 450 | 0 | 490 | 0 | 0 | 280 | 99 | 0 | 0 | 142 | 20.5 | 20 | 0 | 0 | 85 | 16 | 105 | 0 | 0 | 82 | 52 | 54.36 | 0 | 0 | 0 | 221 | 0 | 13 | 280 | 17 | 0 | 0 | 25.5 | 0 | 165 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 0 | 0 | 310 | 280 | 28 | 0 | 34 | 33 | 103 | 52 | 0 | 19 | 95 | 76 | 43 | 0 | 37 | 300 | 0 | 66 | 0 | 67 | 142 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 17 | 68 | 47 | 34 | 0 | 0 | 12 | 6759.36 | 899 | 169 | 0 | 29 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1065.24 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 22 | 8 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 153 | 48 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 304 | 1232 | 17 | 6032.24 | 12791.6 | 106.79
04:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 194 | 30 | 0 | 35 | 0 | 420 | 0 | 480 | 0 | 0 | 300 | 99 | 0 | 0 | 125 | 20.5 | 20 | 0 | 0 | 89 | 16 | 39 | 0 | 0 | 82 | 52 | 54.36 | 0 | 0 | 0 | 221 | 0 | 8 | 281 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 0 | 0 | 310 | 280 | 34 | 0 | 35 | 34 | 103 | 52 | 0 | 19 | 10 | 74 | 0 | 0 | 37 | 310 | 0 | 66 | 0 | 67 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 17 | 68 | 48 | 49 | 0 | 0 | 0 | 6291.86 | 898 | 174 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1215.47 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 22 | 0 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 152 | 48 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 304 | 1222 | 17 | 6081.47 | 12373.33 | 106.78
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 194 | 30 | 0 | 35 | 0 | 420 | 0 | 480 | 0 | 0 | 330 | 98 | 0 | 0 | 142 | 20.5 | 20 | 0 | 0 | 89 | 16 | 0 | 0 | 2 | 82 | 52 | 34 | 0 | 0 | 0 | 221 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 1177 | 0 | 51 | 60 | 0 | 0 | 350 | 280 | 34 | 0 | 34 | 34 | 103 | 51 | 0 | 19 | 0 | 68 | 0 | 0 | 36 | 315 | 0 | 66 | 0 | 67 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 48 | 49 | 0 | 0 | 0 | 6162.5 | 898 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1386.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 150 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 115 | 220 | 0 | 304 | 1120 | 17 | 5749.06 | 11911.56 | 106.77
06:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 194 | 30 | 0 | 35 | 0 | 450 | 0 | 515 | 0 | 0 | 330 | 36 | 0 | 0 | 142 | 0 | 20 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 82 | 52 | 34 | 0 | 0 | 0 | 221 | 0 | 22 | 278 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 1149 | 0 | 51 | 50 | 0 | 8 | 355 | 300 | 34 | 0 | 34 | 33 | 103 | 51 | 0 | 19 | 0 | 70 | 0 | 0 | 37 | 315 | 0 | 66 | 0 | 67 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 48 | 49 | 0 | 0.05 | 0 | 6144.05 | 899 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1446.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 150 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 100 | 180 | 0 | 304 | 1100 | 17 | 5638.13 | 11782.18 | 106.76
07:00 | 0 | 57 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 194 | 30 | 0 | 35 | 0 | 450 | 0 | 500 | 0 | 0 | 330 | 98 | 0 | 5 | 142 | 20 | 20 | 0 | 0 | 92 | 16 | 0 | 0 | 0 | 82 | 52 | 38 | 0 | 0 | 0.71 | 221 | 0 | 23 | 280 | 17 | 0 | 0 | 1 | 0 | 165 | 0 | 0 | 0 | 1162 | 3 | 51 | 50 | 8 | 13 | 350 | 331 | 34 | 0 | 35 | 34 | 103 | 52 | 0 | 19 | 0 | 68 | 0 | 9 | 37 | 320 | 0 | 66 | 0 | 67 | 156 | 6 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 48 | 49 | 0 | 6.84 | 0 | 6442.55 | 898 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 370 | 0 | 1440.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.03 | 15 | 0 | 0 | 8.17 | 184 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0.68 | 148 | 48 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 28 | 0.81 | 0 | 276 | 115 | 220 | 0 | 307 | 1100 | 17 | 5845.2 | 12287.75 | 106.75
08:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 140 | 195 | 30 | 0 | 35 | 0 | 450 | 0 | 410 | 0 | 0 | 270 | 36 | 0 | 13 | 142 | 0 | 21 | 0 | 0 | 87 | 16 | 4 | 0 | 3 | 82 | 53 | 54.36 | 0 | 0 | 1.25 | 220 | 0 | 0 | 280 | 17 | 0 | 0 | 21 | 0 | 165 | 0 | 0 | 0 | 1084 | 13 | 51 | 50 | 16 | 24 | 280 | 305 | 38 | 0 | 36 | 33 | 103 | 51 | 0 | 19 | 16 | 62 | 16 | 28 | 37 | 305 | 0 | 66 | 0 | 68 | 149 | 6 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 48 | 44 | 1 | 19.48 | 9 | 6224.09 | 897 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 370 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.42 | 45 | 0 | 0 | 24.83 | 200 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1.98 | 152 | 46 | 26 | 15 | 0 | 0 | 0 | 0 | 2.6 | 83 | 0.23 | 0 | 239 | 115 | 220 | 0 | 307 | 1070 | 17 | 5942.06 | 12166.15 | 106.74
09:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 140 | 131 | 30 | 0 | 35 | 0 | 450 | 0 | 445 | 0 | 0 | 327 | 96 | 0 | 22 | 0 | 19.7 | 21 | 0 | 0 | 96 | 16 | 18 | 0 | 0 | 82 | 53 | 54.36 | 0 | 0 | 0.76 | 220 | 0 | 2 | 280 | 17 | 0 | 0 | 25.5 | 0 | 164 | 0 | 0 | 0 | 1052 | 15 | 51 | 50 | 8 | 10 | 280 | 280 | 41 | 0 | 36 | 34 | 102 | 51 | 0 | 12 | 35 | 62 | 16 | 48 | 28 | 320 | 0 | 66 | 0 | 68 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 68 | 48 | 44 | 2 | 32.36 | 12 | 6216.68 | 898 | 193 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 370 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.68 | 73 | 0 | 0 | 41.75 | 200 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 3.51 | 0 | 46 | 35 | 25 | 0 | 0 | 0 | 0 | 4.6 | 130 | 0.41 | 0 | 223 | 115 | 220 | 0 | 305 | 1070 | 17 | 5812.95 | 12029.63 | 106.73
10:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 17 | 140 | 137 | 30 | 17 | 72 | 0 | 450 | 0 | 460 | 0 | 0 | 327 | 95 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 101 | 16 | 41 | 0 | 0 | 80 | 53 | 54.36 | 0 | 0 | 2.66 | 220 | 23 | 2 | 280 | 17 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1081 | 15 | 51 | 71 | 8 | 59 | 280 | 280 | 44 | 0 | 36 | 34 | 102 | 51 | 0 | 12 | 98 | 70 | 16 | 43 | 28 | 320 | 0 | 91 | 0 | 68 | 159 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 31 | 2 | 40.15 | 12 | 6499.67 | 899 | 193 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 370 | 0 | 1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.46 | 93 | 0 | 0 | 53.9 | 200 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 4.74 | 0 | 46 | 35 | 31 | 0 | 0 | 0 | 0 | 5.8 | 169 | 0.54 | 0 | 278 | 115 | 220 | 0 | 304 | 1080 | 17 | 5983.44 | 12483.11 | 106.72
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 12 | 24 | 137 | 131 | 30 | 35 | 72 | 0 | 450 | 0 | 470 | 0 | 0 | 325 | 94 | 0 | 31 | 122 | 19.5 | 1 | 0 | 0 | 99 | 16 | 88 | 0 | 0 | 66 | 38 | 54.36 | 0 | 0 | 2.73 | 219 | 33 | 5 | 280 | 17 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1177 | 18 | 51 | 93 | 8 | 89 | 280 | 280 | 41 | 0 | 36 | 34 | 102 | 52 | 0 | 12 | 97 | 72 | 16 | 55 | 21 | 330 | 0 | 172 | 0 | 67 | 158 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 68 | 47 | 31 | 2 | 46.65 | 12 | 6954.24 | 898 | 177 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 385 | 0 | 1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.91 | 99 | 0 | 0 | 55.32 | 200 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 5.61 | 0 | 46 | 35 | 35 | 0 | 0 | 0 | 0 | 6.6 | 177 | 0.62 | 0 | 276 | 115 | 220 | 0 | 305 | 1112 | 17 | 5962.06 | 12916.3 | 106.71
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 17.5 | 17 | 34 | 135 | 145 | 30 | 35 | 72 | 0 | 450 | 0 | 460 | 0 | 0 | 325 | 36 | 0 | 31 | 142 | 19.5 | 14 | 0 | 0 | 90 | 16 | 96 | 0 | 0 | 66 | 38 | 17 | 0 | 0 | 1.34 | 220 | 36 | 14 | 280 | 17 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1164 | 14 | 51 | 92 | 8 | 115 | 280 | 280 | 42 | 0 | 36 | 25 | 102 | 51 | 7 | 12 | 98 | 68 | 16 | 11 | 21 | 320 | 0 | 305 | 0 | 67 | 155 | 0 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 68 | 47 | 31 | 2 | 45.62 | 12 | 6990.46 | 900 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87.44 | 602 | 0 | 1270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.15 | 100 | 0 | 0 | 60.61 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.43 | 0 | 46 | 35 | 34 | 0 | 0 | 0 | 0 | 6.6 | 191 | 0.42 | 13 | 292 | 115 | 220 | 0 | 304 | 1110 | 17 | 6310.65 | 13301.11 | 106.7
13:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17.5 | 17 | 34 | 134 | 145 | 15 | 35 | 72 | 0 | 450 | 0 | 495 | 0 | 0 | 327 | 35 | 0 | 30 | 142 | 19.2 | 14 | 0 | 0 | 96 | 32 | 96 | 0 | 1 | 66 | 53 | 17 | 0 | 0 | 2.57 | 218 | 34 | 17 | 273 | 17 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1130 | 19 | 51 | 88 | 0 | 134 | 280 | 280 | 43 | 0 | 36 | 16 | 100 | 51 | 8 | 12 | 97 | 82 | 16 | 66 | 27 | 315 | 0 | 337 | 0 | 67 | 154 | 12 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 31 | 2 | 44.64 | 12 | 7136.41 | 900 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 58 | 73.64 | 613 | 0 | 1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.71 | 105 | 0 | 0 | 54.94 | 200 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 5.24 | 0 | 46 | 35 | 35 | 0 | 0 | 0 | 0 | 6.5 | 136 | 0.59 | 16 | 307 | 115 | 220 | 0 | 305 | 1204 | 17 | 6500.62 | 13637.03 | 106.69
14:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 17.5 | 17 | 34 | 134 | 98 | 22 | 35 | 72 | 0 | 450 | 0 | 495 | 0 | 17 | 317 | 36 | 0 | 25 | 142 | 19 | 14 | 0 | 0 | 0 | 32 | 96 | 0 | 4 | 66 | 53 | 17 | 0 | 0 | 1.48 | 218 | 41 | 19 | 274 | 17 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1174 | 13 | 51 | 86 | 0 | 145 | 280 | 250 | 40 | 0 | 33 | 17 | 100 | 51 | 8 | 12 | 99 | 82 | 16 | 14 | 35 | 305 | 0 | 337 | 0 | 67 | 153 | 12 | 0 | 78 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 31 | 2 | 37.51 | 12 | 6974.99 | 900 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 68.83 | 617.1 | 0 | 1403.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.6 | 89 | 0 | 0 | 45.74 | 200 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 4.03 | 0 | 48 | 35 | 29 | 34 | 0 | 0 | 0 | 3.8 | 114 | 0.47 | 16 | 307 | 115 | 220 | 0 | 304 | 1222 | 17 | 6542.05 | 13517.04 | 106.68
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 17 | 17 | 34 | 134 | 97 | 30 | 35 | 72 | 0 | 450 | 0 | 500 | 0 | 30 | 321 | 0 | 0 | 17 | 142 | 18.2 | 0 | 0 | 0 | 48 | 32 | 96 | 0 | 2 | 66 | 44 | 17 | 0 | 0 | 2.11 | 219 | 77 | 14 | 270 | 17 | 0 | 0 | 25.5 | 0 | 164 | 0 | 0 | 0 | 1178 | 11 | 51 | 86 | 0 | 165 | 280 | 250 | 36 | 0 | 34 | 16 | 99 | 51 | 8 | 12 | 114 | 82 | 16 | 41 | 35 | 315 | 0 | 337 | 0 | 67 | 153 | 12 | 0 | 77 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 31 | 1 | 25.95 | 12 | 7105.76 | 900 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 50.05 | 616 | 0 | 1435.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.21 | 64 | 0 | 0 | 35.4 | 200 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 3.16 | 0 | 45 | 60 | 6 | 55 | 0 | 0 | 0 | 2.8 | 106 | 0.36 | 16 | 275 | 113 | 220 | 0 | 303 | 1225 | 17 | 6482.15 | 13587.91 | 106.67
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 17 | 17 | 39 | 133 | 97 | 30 | 35 | 72 | 0 | 450 | 0 | 500 | 0 | 35 | 323 | 0 | 0 | 9 | 142 | 18.2 | 12 | 0 | 0 | 90 | 16 | 90 | 0 | 1 | 66 | 38 | 17 | 0 | 0 | 0.62 | 220 | 93 | 9 | 265 | 17 | 0 | 0 | 25.5 | 0 | 161 | 0 | 0 | 0 | 1153 | 5 | 51 | 88 | 0 | 155 | 265 | 240 | 37 | 0 | 30 | 27 | 99 | 51 | 0 | 12 | 98 | 78 | 16 | 4 | 35 | 320 | 0 | 337 | 0 | 68 | 153 | 12 | 0 | 77 | 30 | 0 | 16 | 160 | 0 | 69 | 47 | 31 | 1 | 13.84 | 12 | 7117.16 | 900 | 181 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 26 | 611 | 0 | 1461.54 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 19.54 | 34 | 0 | 0 | 17.46 | 200 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 1.77 | 0 | 45 | 70 | 10 | 63 | 0 | 0 | 0 | 1.3 | 55 | 0.14 | 16 | 270 | 113 | 220 | 0 | 304 | 1195 | 17 | 6341.75 | 13458.91 | 106.66
17:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 17 | 17 | 34 | 133 | 97 | 30 | 35 | 72 | 0 | 450 | 0 | 465 | 0 | 35 | 280 | 0 | 0 | 2 | 142 | 0 | 0 | 0 | 0 | 89 | 16 | 90 | 0 | 0 | 66 | 45 | 17 | 0 | 0 | 0.05 | 218 | 96 | 15 | 265 | 72 | 0 | 0 | 25.5 | 0 | 162 | 0 | 0 | 0 | 1124 | 1 | 51 | 90 | 0 | 155 | 265 | 240 | 41 | 0 | 30 | 33 | 100 | 51 | 0 | 0 | 105 | 74 | 34 | 3 | 35 | 315 | 0 | 337 | 10 | 67 | 151 | 12 | 0 | 80 | 30 | 0 | 16 | 160 | 1 | 68 | 47 | 31 | 0 | 2.07 | 12 | 7095.62 | 900 | 181 | 0 | 4 | 10 | 38 | 0 | 0 | 0 | 0 | 105 | 5 | 587 | 0 | 1458.95 | 0 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 3.34 | 7 | 10 | 0 | 2.8 | 160 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0.22 | 0 | 47 | 70 | 2 | 72 | 0 | 0 | 0 | 0.4 | 7 | 0.03 | 16 | 231 | 113 | 180 | 0 | 305 | 1180 | 17 | 6123.74 | 13219.36 | 106.65
18:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 17 | 44 | 134 | 97 | 15 | 35 | 72 | 0 | 370 | 0 | 420 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 12 | 13 | 0 | 0 | 96 | 16 | 98 | 0 | 0 | 66 | 51 | 43 | 0 | 0 | 0 | 218 | 92 | 17 | 265 | 160 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1163 | 0 | 44 | 92 | 0 | 160 | 265 | 240 | 39 | 0 | 32 | 40 | 100 | 104 | 0 | 17 | 103 | 78 | 43 | 0 | 35 | 300 | 0 | 337 | 10 | 67 | 152 | 11 | 0 | 81 | 30 | 0 | 16 | 160 | 12 | 68 | 48 | 31 | 0 | 0 | 12 | 7427.5 | 900 | 185 | 0 | 34 | 60 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 610 | 0 | 1466.72 | 0 | 39 | 0 | 20 | 75 | 0 | 90 | 15 | 0 | 0 | 0 | 26 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 47 | 100 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 273 | 115 | 220 | 0 | 306 | 1139 | 17 | 6546.72 | 13974.22 | 106.64
19:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 17 | 30 | 89 | 134 | 97 | 15 | 35 | 72 | 0 | 340 | 0 | 345 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 19.5 | 14 | 0 | 0 | 86 | 16 | 105 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 218 | 101 | 10 | 265 | 160 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1224 | 0 | 51 | 105 | 0 | 175 | 265 | 240 | 39 | 0 | 35 | 51 | 100 | 145 | 0 | 19 | 97 | 74 | 43 | 0 | 35 | 300 | 0 | 337 | 10 | 67 | 150 | 11 | 0 | 81 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 0 | 0 | 0 | 12 | 7474.36 | 900 | 185 | 0 | 41 | 49 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 592 | 0 | 1471.53 | 0 | 40 | 0 | 35 | 110 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 45 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 253 | 100 | 180 | 0 | 305 | 1180 | 17 | 6588.53 | 14062.89 | 106.63
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 35 | 89 | 134 | 97 | 15 | 35 | 72 | 0 | 340 | 0 | 380 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 19.5 | 14 | 0 | 0 | 90 | 16 | 106 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 220 | 102 | 25 | 265 | 90 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1224 | 0 | 51 | 110 | 0 | 175 | 265 | 240 | 39 | 0 | 35 | 51 | 100 | 144 | 9 | 19 | 97 | 76 | 43 | 0 | 35 | 320 | 0 | 337 | 10 | 67 | 150 | 11 | 0 | 81 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 10 | 0 | 0 | 12 | 7557.36 | 901 | 186 | 0 | 34 | 47 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 600 | 0 | 1468.49 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 45 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 279 | 100 | 180 | 0 | 302 | 1182 | 17 | 6670.49 | 14227.85
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 35 | 89 | 135 | 97 | 15 | 35 | 72 | 0 | 340 | 0 | 360 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 20.5 | 14 | 0 | 0 | 90 | 16 | 106 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 220 | 110 | 23 | 280 | 90 | 0 | 0 | 25.5 | 0 | 163 | 0 | 0 | 0 | 1224 | 0 | 51 | 110 | 0 | 160 | 265 | 240 | 39 | 0 | 35 | 51 | 102 | 144 | 9 | 19 | 97 | 86 | 43 | 0 | 35 | 310 | 0 | 336 | 10 | 67 | 155 | 11 | 0 | 81 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 10 | 0 | 0 | 12 | 7529.36 | 900 | 185 | 0 | 34 | 42 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 616 | 0 | 1471.3 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 45 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 295 | 115 | 220 | 0 | 306 | 1186 | 17 | 6790.3 | 14319.66 | 106.62
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 35 | 89 | 135 | 97 | 15 | 35 | 17 | 0 | 340 | 0 | 370 | 0 | 55 | 280 | 0 | 0 | 0 | 142 | 20 | 18 | 0 | 0 | 95 | 16 | 107 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 220 | 110 | 20 | 298 | 17 | 0 | 0 | 25.5 | 0 | 162 | 0 | 0 | 0 | 1229 | 0 | 51 | 113 | 0 | 160 | 265 | 240 | 38 | 0 | 36 | 50 | 102 | 144 | 9 | 19 | 97 | 78 | 43 | 0 | 36 | 315 | 0 | 336 | 28 | 67 | 159 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 10 | 0 | 0 | 12 | 7437.86 | 900 | 187 | 0 | 34 | 35 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 614 | 0 | 1454.92 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 45 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 306 | 1218 | 17 | 6809.92 | 14247.78 | 106.61
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 89 | 137 | 97 | 15 | 0 | 17 | 0 | 340 | 0 | 360 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 90 | 16 | 106 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 220 | 108 | 20 | 442 | 17 | 0 | 0 | 25.5 | 0 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 0 | 160 | 265 | 240 | 37 | 0 | 36 | 51 | 103 | 144 | 0 | 19 | 97 | 78 | 43 | 0 | 36 | 305 | 0 | 336 | 28 | 67 | 154 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 18 | 0 | 0 | 12 | 7456.86 | 873 | 186 | 0 | 34 | 36 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 609 | 0 | 1460.29 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 45 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 281 | 115 | 220 | 0 | 306 | 1222 | 17 | 6703.29 | 14160.15 | 106.6
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 89 | 124 | 97 | 15 | 0 | 17 | 0 | 340 | 0 | 355 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 84 | 16 | 105 | 0 | 0 | 66 | 60 | 54.36 | 0 | 0 | 0 | 219 | 110 | 28 | 445 | 17 | 0 | 0 | 25.5 | 0 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 0 | 160 | 265 | 240 | 40 | 0 | 34 | 46 | 103 | 145 | 0 | 19 | 97 | 88 | 43 | 0 | 36 | 305 | 0 | 336 | 28 | 67 | 150 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 68 | 49 | 17 | 0 | 0 | 0 | 7427.86 | 873 | 189 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 607 | 0 | 1468.55 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 45 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 115 | 220 | 0 | 306 | 1222 | 17 | 6702.55 | 14130.41 | 106.59
Total KWH | 0 | 2198400 | 607680 | 0 | 0 | 0 | 0 | 0 | 2923200 | 0 | 0 | 243360 | 307440 | 1012608 | 2789760 | 3445484 | 712855 | 423153 | 1190880 | 0 | 9863500 | 0 | 10880000 | 0 | 396082 | 7363349 | 1244000 | 0 | 212848 | 3130800 | 380400 | 368280 | 0 | 0 | 2101364 | 426545 | 1811520 | 0 | 12000 | 1746839 | 1115040 | 1062491 | 0 | 0 | 15480 | 5215880 | 1194322 | 361440 | 7112727.27 | 739345 | 0 | 0 | 506383.2 | 0 | 3822607 | 0 | 0 | 0 | 28210906 | 132570 | 1223264 | 2276581 | 66909 | 2204500 | 7392400 | 6534000 | 864000 | 114000 | 806688 | 834240 | 2436660 | 1881120 | 54600 | 368870 | 1941420 | 1788480 | 614045 | 339355 | 793408 | 7609000 | 0 | 5364000 | 151000 | 1547760 | 3673309 | 253992 | 0 | 1907520 | 720000 | 0 | 392000 | 3335250 | 130680 | 1624800 | 1159200 | 710400 | 14050 | 315590 | 235200 | 166959829.47 | 21701090 | 4584672 | 0 | 302400 | 401408 | 912000 | 0 | 0 | 0 | 0 | 1081296 | 573840 | 11963640 | 0 | 32020696 | 0 | 504737 | 0 | 361728 | 1336800 | 0 | 629457 | 280620 | 57101 | 376108 | 711050 | 279360 | 0 | 396752 | 5014000 | 0 | 0 | 0 | 0 | 0 | 9149818 | 0 | 36060 | 1372000 | 1083927 | 1752652 | 223778 | 1376236 | 0 | 0 | 0 | 42461.04 | 1175760 | 3589 | 327840 | 6698000 | 2729000 | 5373270 | 0 | 7367272 | 28855272.73 | 428400 | 151484090.77 | 318443920.24

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13301.11 | MW | 12:00 Hr. | Energy Generated |  |  | 318.4439 |  | MKWHr.
| Day Peak Demand |  |  | 13555.11 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.575 |  | MKWHr.
| Evening Peak Generation |  |  | 14319.66 | MW | 20:00 Hr. | Energy Demand |  |  | 324.0189 |  | MKWHr.
| Evening Peak Demand |  |  | 14700.66 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 11782.18 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 866.99 |  | MMCFD
| Maximum Generation of the Day |  |  | 14319.66 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.1666 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.0227 | 0 | 16.4585 | 0 | 0 | 0.21285 | 0 | 0 | 49.6941 | Gas | 111.7331 | Gas | 401857866.33
| Chattogram Zone |  |  | 4.184 | 35.3236 | 10.7038 | 0 | 5.2159 | 0.14805 | 0 | 0.012 | 55.5875 | Coal | 92.6637 | Coal | 582692416.3665
| Cumilla Zone |  |  | 22.0113 | 0 | 8.3954 | 0 | 0 | 0.33936 | 1.7885 | 0 | 32.5345 | HFO | 47.8277 | HFO | 883006352.658
| Mymensingh Zone |  |  | 0.7104 | 0 | 3.1499 | 0 | 0 | 0.32964 | 0 | 0 | 4.1899 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9538 | Hydro | 5.2159 | Hydro | 521588
| Khulna Zone |  |  | 4.5847 | 11.9636 | 1.7851 | 0 | 0 | 0.57384 | 22.6131 | 0 | 41.5203 | Solar | 4.5693 | Solar | 73819661.4864
| Barishal Zone |  |  | 8.1023 | 42.9205 | 0.75624 | 0 | 0 | 0.003589 | 0 | 0 | 51.7826 | Import | 56.4223 | Import | 340089617.26
| Rajshahi Zone |  |  | 14.1638 | 0 | 3.4498 | 0 | 0 | 1.52 | 32.0207 | 0 | 51.1543 | Wind | 0.012 | Wind | 176520
| Rangpur Zone |  |  | 0 | 2.4559 | 3.1289 | 0 | 0 | 1.442 | 0 | 0 | 7.0268
| Total |  |  | 111.7331 | 92.6637 | 47.8277 | 0 | 5.2159 | 4.5693 | 56.4223 | 0.012 | 318.4439
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 401857866.33 |  | Hydro | 521588
|  |  |  | Coal | 582692416.3665 |  | Solar | 73819661.4864
|  |  |  | HFO | 883006352.658 |  | Import | 340089617.26
|  |  |  | HSD | 0 |  | Wind | 176520
[5 empty] | Total: | 228,21,64,022 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7011 | Peak Hr Flow | 900.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51150872.8 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.0207 | Peak Hr Flow | 1471.30 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2385 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7885 | Peak Hr Flow | 86.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2712 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.5103 | Peak Hr Flow | 2457.30 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 70 |  | 5261
|  |  |  | Chattogram |  | 0 |  | 1531
|  |  |  | Cumilla |  | 60 |  | 1393
|  |  |  | Mymensingh |  | 100 |  | 1067
|  |  |  | Sylhet |  | 20 |  | 593
|  |  |  | Khulna |  | 70 |  | 1606
|  |  |  | Barishal |  | 10 |  | 431
|  |  |  | Rajshahi |  | 25 |  | 1350
|  |  |  | Rangpur |  | 10 |  | 912
|  |  |  | Total |  | 365 |  | 14144
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Naogaon 132/33kV S/S T-2 LT is restored.
|  | 08:09 | Naogaon 132/33kV S/S T-1 LT is restored.
| 08:15 | 15:11 | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Annual maintenance
| 08:16 | 15:10 | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Annual maintenance
| 08:16 | 14:46 | Rajbari 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual maintenance
| 08:16 | 14:44 | Rajbari 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual maintenance
| 08:20 | 16:22 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance Work
| 08:21 | 16:21 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Annual Maintenance Work
| 08:32 | 14:53 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Annual maintenance
| 08:33 | 14:52 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Annual maintenance
| 08:34 | 14:29 | Ullahpara 132/33kV S/S 132 KV Bus1 Scheduled S/D Due to Annual maintenance work
| 08:36 |  | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D
| 08:42 |  | Barapukuria Unit-3 tripped.
|  | 08:56 | Aminbazar 400/230/132kV S/S ATR-03 HT is restored.
|  | 09:01 | Aminbazar 400/230/132kV S/S ATR-03 LT is restored.
| 09:03 | 12:31 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 09:03 | 12:31 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to High Tempareture Junction Point
Maintenance.
| 09:07 |  | Ashuganj 420 MW CCPP (East) ST was sync.
| 09:07 | 14:36 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Annual Maintenance
| 09:22 | 17:00 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Annual maintenance
work
| 09:47 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 09:47 |  | Bibiyana-3 400 MW CCPP ST was sync.
| 10:32 | 11:16 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
230kv Bus 1 Annual maintenance
| 10:44 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Direction By NLDC
| 11:15 | 12:59 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to Red hot Sripur end.
| 11:16 | 12:57 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Forced S/D Due to RED HOT
| 11:30 | 12:16 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
230kv Bus-1 Maintenance
| 11:50 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 11:50 |  | Haripur EGCB 412 MW CCPP GT was sync.
| 12:00 |  | Day Peak Generation is 13296 MW.
| 12:10 | 12:36 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Tripped showing SIMENS SIPROTEC, 7SJ81 Y | [7 empty] | 8.0MW load
|  |  | phase IDMT Earth Fault Trip relays Due to পিবিএস এর হাজীনগর, ফিডারের জন্য ৩৩ কেভি ট্রিপ | [7 empty] | interrup.
করে।
| 13:13 | 16:40 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to High
temperature junction point maintenance.
| 13:17 | 17:40 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D
|  | 14:09 | Khagrachari-Rangamati 132kV Ckt-2 is restored.
| 14:14 |  | Haripur 412 MW CCPP Tripped with remarks:- ST
| 14:14 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 14:41 | 20:51 | Baghabari-Roppur 230kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to S/D
taken by SPMD,Ishurdi.
| 14:41 | 20:58 | Baghabari-Roppur 230kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to S/D
taken by SPMD,Ishurdi.
| 14:52 | 17:35 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to Energy Meter Division work
| 14:52 |  | Siddhirganj 2x120 MW GT-1 was shutdown
|  | 14:58 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 is restored.
|  | 15:27 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 15:28 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
| 16:08 | 19:45 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
|  | 16:24 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 16:27 | Barishal 230/132kV S/S T-4 LT is restored.
|  | 16:44 | Chandraghona-Madunaghat 132 kV Ckt-2 is restored.
| 19:07 | 19:48 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Due to Keranihat PBS | [7 empty] | 60.0MW load
|  |  | feeder bus ds maintenance. | [7 empty] | interrup.
| 19:49 |  | Matarbari 2*600 MW (CPGCBL) Unit-2 was synchronized.
| 19:49 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U2
| 20:00 |  | Evening Peak Generation: 14318 MW
| 06:43 |  | GPH 230/33kV S/S HATHAZARI Scheduled S/D
| 06:45 |  | Barishal 230/132kV S/S T-5 LT Tripped showing No relay operate relays Due to Jhalokathi
feeder trip HV differential protection trip
| 06:45 |  | Barishal 230/132kV S/S T-5 HT Tripped showing MICOM P632 relays Due to Jhalokathi feeder
trip
| 07:00 |  | Minimum Generation is 11611 MW
| 07:06 | 07:57 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Remove
bird Nest
| 07:34 |  | GPH 230/33kV S/S Transformer-01(D05) HT Scheduled S/D Due to for checking & painting of
the tertiary compartment
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 347 | 2923200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 9863500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 712855 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 1244000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7363349 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 243360 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 135 | 2789760 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 423153 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 396082 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 380400 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 368280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 607680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 97 | 3445484 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 89 | 1012608 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2198400 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1190880 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 212848 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 307440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 360 | 10880000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3130800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2183.5 | 49694079
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 506383.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132570 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5215880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 163 | 3822607 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 1115040 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1746839 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 361440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 106 | 1811520 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 426545 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1062491 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1194322 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2101364 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 90 | 739345 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28210906 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 280 | 7112727.27 | U2 S/D 3/Oct/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.72 | 2527.86 | 55587459.47
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 114000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 265 | 7392400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 240 | 6534000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 160 | 2204500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 806688 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 39 | 864000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 66909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1223264 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 110 | 2276581 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 793408 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2436660 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 144 | 1881120 | Engine Problem
| Import (Tripura) |  | Import | 0 | 160 | 86 | 1788480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 614045 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 368870 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1941420 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 54600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 834240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 339355 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1486 | 32534540
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 710400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1159200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1624800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 315590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 235200 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 130680 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 156 | 4189920
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 10 | 151000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1547760 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3673309 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720000 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1907520 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3335250 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 11 | 253992 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7609000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 336 | 5364000 | IDCT-08, under maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1176 | 24953831
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21701090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 302400 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 401408 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 185 | 4584672 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1081296 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 573840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 616 | 11963640 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1920 | 41520346
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 306 | 7367272 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 327840 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2729000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1186 | 28855272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5373270 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 428400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 295 | 6698000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3589 | -
Barishal Area Total |  |  |  |  | 2858 | 2171 | 51782643.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 376108 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 504737 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 280620 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 207 | 5014000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9149818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 279360 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 57101 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 629457 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1336800 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 361728 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1471.3 | 32020696 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 396752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 711050 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2439.3 | 51154287
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1083927 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 1372000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 1376236 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42461.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1752652 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 223778 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1175760 | -
Rangpur Area Total |  |  |  |  | 950 | 260 | 7026814.04
Eastern Grid Total |  |  |  |  | 17383.852 | 7529.36 | 166959829.47
Western Grid Total |  |  |  |  | 10980.24 | 6790.3 | 151484090.77
National Grid Total |  |  |  |  | 28364.092 | 14319.66 | 318443920.24
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-10-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9595.37 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4184 | MW
i) Dhaka area |  |  | 5190.92 |  | MW | i) Khulna area |  |  |  | 1536 | MW
ii) Chattogram area |  |  | 1531.1 |  | MW | ii) Barishal area |  |  |  | 421 | MW
iii) Cumilla area |  |  | 1333.35 |  | MW | iii) Rajshahi area |  |  |  | 1325 | MW
iv) Mymensingh area |  |  | 967 |  | MW | iv) Rangpur area |  |  |  | 902 | MW
v) Sylhet area |  |  | 573 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13779.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 86 | 18:00 | 133 | Niamatpur | 64 | 21:00
2 | AKSML | 157 | 07:00 | 68 | Ishurdi | 71 | 13:00 | 134 | Noapara | 39 | 19:30
3 | Aftabnagar | 40 | 14:00 | 69 | Jaldhaka | 62 | 19:00 | 135 | PHP | 8 | 11:00
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 122 | 13:00 | 136 | Pabna | 97 | 18:30
5 | Agrabad | 102 | 12:00 | 71 | Jashore | 128 | 13:00 | 137 | Palashbari | 122 | 20:00
6 | Amnura | 31 | 18:00 | 72 | Jhenaidah | 100 | 21:00 | 138 | Panchagarh | 58 | 18:00
7 | Ashuganj | 91 | 19:30 | 73 | Joydebpur | 146 | 19:00 | 139 | Patiya | 10.5 | 18:00
8 | BSRM | 199 | 19:30 | 74 | Joypurhat | 55 | 20:00 | 140 | Patuakhali | 67.5 | 23:00
9 | Bagerhat | 77 | 20:00 | 75 | Juldah | 16.5 | 14:00 | 141 | Payra | 32 | 23:00
10 | Bajitpur | 72 | 04:00 | 76 | KSRM | 36 | 11:00 | 142 | Postogola | 68 | 00:00
11 | Bakulia | 90 | 19:00 | 77 | Kabirpur | 229 | 21:00 | 143 | Purbachal | 23 | 18:00
12 | Banani | 51 | 15:00 | 78 | Kachua | 77 | 03:00 | 144 | Purbasadipur | 114 | 18:00
13 | Bangabhaban | 24 | 10:00 | 79 | Kallyanpur | 102 | 18:00 | 145 | Rahanpur | 32 | 21:00
14 | Barapukuria | 56 | 19:30 | 80 | Kalurghat | 54 | 15:00 | 146 | Rahim | 32 | 07:00
15 | Barguna | 20 | 02:00 | 81 | Kamrangirchar | 79 | 18:00 | 147 | Rajbari | 74 | 19:30
16 | Barishal | 115 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 112 | 18:00
17 | Barishal-230 | 90 | 23:00 | 83 | Kasba | 35 | 03:00 | 149 | Rajshahi | 90 | 18:30
18 | Baroaulia | 66 | 16:00 | 84 | Kazla | 102 | 18:00 | 150 | Rajshahi-230 | 92 | 11:00
19 | Baroirhat | 59 | 02:00 | 85 | Keranigonj | 89 | 19:30 | 151 | Ramganj | 98 | 22:00
20 | Bashundhara | 203 | 18:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 43 | 00:00
21 | BashundharaCement | 6 | 01:00 | 87 | Khulna | 67 | 13:00 | 153 | Rangamati | 15 | 10:00
22 | Beanibazar | 78 | 23:00 | 88 | Khulshi | 190 | 20:00 | 154 | Rangpur | 144 | 19:00
23 | Benapole | 52 | 13:00 | 89 | Kishoreganj | 118 | 01:00 | 155 | Ruppur | 8.2 | 15:00
24 | Bhaluka | 145 | 21:00 | 90 | Kodda | 292 | 11:00 | 156 | SSM | 14 | 11:00
25 | Bhandaria | 50 | 03:00 | 91 | Kulaura | 53 | 23:00 | 157 | Saidpur | 96 | 18:00
26 | Bhangura | 32 | 20:00 | 92 | Kurigram | 58 | 20:00 | 158 | Satkhira | 115 | 21:00
27 | Bheramara(GK) | 56 | 19:30 | 93 | Kushtia | 140 | 19:30 | 159 | Satmasjid | 101 | 13:00
28 | Bhulta | 211 | 08:00 | 94 | Laksam | 35 | 21:00 | 160 | Savar | 214 | 14:00
29 | Bog-Sherpur | 62 | 19:30 | 95 | Lakshmipur | 31 | 23:00 | 161 | SevenRings | 21.6 | 07:00
30 | Bogura | 157 | 21:00 | 96 | Lalbag | 64 | 13:00 | 162 | ShahCement | 25 | 16:00
31 | Borhanuddin | 93 | 23:00 | 97 | Lalmonirhat | 56 | 19:00 | 163 | Shahjadpur | 76 | 18:00
32 | Brahmanbaria | 120 | 03:00 | 98 | MI_Cement | 9.2 | 00:00 | 164 | Shahjibazar | 132 | 23:00
33 | Cantonment | 140 | 13:00 | 99 | Madanganj | 44 | 20:00 | 165 | Shahmirpur | 59 | 18:00
34 | Chandina | 35.27 | 22:00 | 100 | Madaripur | 103 | 23:00 | 166 | Shariatpur | 77 | 22:00
35 | Chandpur | 75 | 03:00 | 101 | Madartek | 88 | 19:30 | 167 | Sherpur | 122 | 02:00
36 | Chandraghona | 37 | 19:00 | 102 | Madunaghat | 60 | 18:30 | 168 | Shikalbaha | 29 | 21:00
37 | Chapai | 59 | 12:00 | 103 | Magura | 48 | 18:00 | 169 | Shitalakhya | 86.6 | 12:00
38 | Charsaidpur | 41 | 15:00 | 104 | Mahasthangarh | 68 | 20:00 | 170 | Sholosohor | 52 | 11:00
39 | Chauddagram | 66 | 02:00 | 105 | Maijdee | 28 | 19:30 | 171 | Shyampur | 128 | 05:00
40 | Chhatak | 37 | 03:00 | 106 | Manikganj | 116 | 23:00 | 172 | Siddhirganj | 124 | 11:00
41 | Chowmuhani | 163 | 19:30 | 107 | Maniknagar | 68 | 13:00 | 173 | Sirajganj | 108 | 18:30
42 | Chuadanga | 96 | 20:00 | 108 | Matarbari | 56 | 18:30 | 174 | Sonargaon | 115 | 21:00
43 | Coxsbazar | 142 | 13:00 | 109 | Matuail | 64.2 | 01:00 | 175 | Sreemongol | 85 | 18:00
44 | Cumilla(N) | 123 | 22:00 | 110 | Metrorail_Motijheel | 34 | 18:00 | 176 | Sreepur | 101 | 19:30
45 | Cumilla(S) | 154 | 15:00 | 111 | Metrorail_Uttara | 12 | 15:00 | 177 | Srinagar | 47.6 | 19:30
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 126 | 15:00 | 178 | Sunamganj | 58 | 23:00
47 | Daudkandi | 142 | 03:00 | 113 | Mirpur | 120 | 18:30 | 179 | Sylhet | 58 | 23:00
48 | DhakaUniversity | 92 | 13:00 | 114 | Mirsorai | 20 | 18:30 | 180 | Sylhet-132 | 126 | 13:00
49 | Dhamrai | 118 | 19:00 | 115 | Mirzapur | 45 | 12:00 | 181 | TK | 24 | 18:00
50 | Dhanmondi | 131 | 13:00 | 116 | Mithapukur | 56 | 19:30 | 182 | Tangail | 160 | 13:00
51 | Dohazari | 100 | 20:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 21 | 19:00
52 | Faridpur | 148 | 18:00 | 118 | Mogbazar | 103.9 | 15:00 | 184 | Thakurgaon | 105 | 18:30
53 | Fatullah | 110 | 11:00 | 119 | Mongla | 42 | 14:00 | 185 | Tongi | 137 | 15:00
54 | Fenchuganj | 44 | 23:00 | 120 | Motijheel | 49 | 13:00 | 186 | Ullahpara | 36 | 20:00
55 | Feni | 110 | 20:00 | 121 | Muktagacha | 31 | 14:00 | 187 | Ullon | 57 | 19:30
56 | GPH | 72 | 01:00 | 122 | Munshiganj | 112 | 23:00 | 188 | Uttara | 70 | 15:00
57 | Ghatail | 72 | 17:00 | 123 | Muradnagar | 38 | 19:30 | 189 | UttaraNew | 78 | 18:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 200 | 18:30 | 190 | Zigatola | 72 | 14:00
59 | Ghorashal-230 | 99 | 19:30 | 125 | Naogaon | 115 | 20:00
60 | Goalpara | 36 | 19:30 | 126 | Narail | 50 | 21:00
61 | Gollamari | 92 | 13:00 | 127 | Narinda | 66 | 13:00
62 | Gopalganj | 96.2 | 21:00 | 128 | Narshingdi | 185 | 20:00
63 | Gulshan | 126 | 14:00 | 129 | Natore | 125 | 18:30
64 | Halishahar | 80 | 12:00 | 130 | Nawabganj | 47.4 | 19:30
65 | HaripurSBU | 153 | 09:00 | 131 | Netrakona | 120 | 03:00
66 | Hasnabad | 91 | 19:30 | 132 | New | 58 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13011.03 | 708 |  | 13750.89
1:00 | 12667.22 | 559 |  | 13251.22
2:00 | 12705.82 | 426 |  | 13150.82
3:00 | 12791.6 | 0 |  | 12791.6
4:00 | 12373.33 | 0 |  | 12373.33
5:00 | 11911.56 | 0 |  | 11911.56
6:00 | 11782.18 | 0 |  | 11782.18
7:00 | 12287.75 | 0 |  | 12287.75
8:00 | 12166.15 | 0 |  | 12166.15
9:00 | 12029.63 | 120 |  | 12154.63
10:00 | 12483.11 | 193 |  | 12685.11
11:00 | 12916.3 | 229 |  | 13155.3
12:00 | 13301.11 | 243 |  | 13555.11
13:00 | 13637.03 | 257 |  | 13905.6
14:00 | 13517.04 | 276 |  | 13805.46
15:00 | 13587.91 | 206 |  | 13803.18
16:00 | 13458.91 | 187 |  | 13654.33
17:00 | 13219.36 | 223 |  | 13452.4
18:00 | 13974.22 | 312 |  | 14300.22
19:00 | 14062.89 | 324 |  | 14401.89
19:30 | 14227.85 | 357 |  | 14600.85
20:00 | 14319.66 | 365 |  | 14700.66
21:00 | 14247.78 | 338 |  | 14600.78
22:00 | 14160.15 | 326 |  | 14501.15
23:00 | 14130.41 | 283 |  | 14426.41
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7154.36 | 5856.67 | 13011.03 | DAILY GENERATION CURVE
00:30 | 7003.86 | 5835.265 | 12839.125
01:00 | 6853.36 | 5813.86 | 12667.22 | 16-10-2025
01:30 | 6833.36 | 5853.16 | 12686.52
02:00 | 6813.36 | 5892.46 | 12705.82
02:30 | 6786.36 | 5962.35 | 12748.71
03:00 | 6759.36 | 6032.24 | 12791.6
03:30 | 6525.61 | 6056.855 | 12582.465
04:00 | 6291.86 | 6081.47 | 12373.33
04:30 | 6227.18 | 5915.265 | 12142.445
05:00 | 6162.5 | 5749.06 | 11911.56
05:30 | 6153.275 | 5693.595 | 11846.87
06:00 | 6144.05 | 5638.13 | 11782.18
06:30 | 6293.3 | 5741.665 | 12034.965
07:00 | 6442.55 | 5845.2 | 12287.75
07:30 | 6333.32 | 5893.63 | 12226.95
08:00 | 6224.09 | 5942.06 | 12166.15
08:30 | 6220.385 | 5877.505 | 12097.89
09:00 | 6216.68 | 5812.95 | 12029.63
09:30 | 6358.175 | 5898.195 | 12256.37
10:00 | 6499.67 | 5983.44 | 12483.11
10:30 | 6726.955 | 5972.75 | 12699.705
11:00 | 6954.24 | 5962.06 | 12916.3
11:30 | 6972.35 | 6136.355 | 13108.705
12:00 | 6990.46 | 6310.65 | 13301.11
12:30 | 7063.435 | 6405.635 | 13469.07
13:00 | 7136.41 | 6500.62 | 13637.03
13:30 | 7055.7 | 6521.335 | 13577.035
14:00 | 6974.99 | 6542.05 | 13517.04
14:30 | 7040.375 | 6512.1 | 13552.475
15:00 | 7105.76 | 6482.15 | 13587.91
15:30 | 7111.46 | 6411.95 | 13523.41
16:00 | 7117.16 | 6341.75 | 13458.91
16:30 | 7106.39 | 6232.745 | 13339.135
17:00 | 7095.62 | 6123.74 | 13219.36
17:30 | 7261.56 | 6335.23 | 13596.79
18:00 | 7427.5 | 6546.72 | 13974.22
18:30 | 7450.93 | 6567.625 | 14018.555
19:00 | 7474.36 | 6588.53 | 14062.89
19:30 | 7557.36 | 6670.49 | 14227.85
20:00 | 7529.36 | 6790.3 | 14319.66
20:30 | 7483.61 | 6800.11 | 14283.72 |  | Executive Engineer
21:00 | 7437.86 | 6809.92 | 14247.78 |  | Network Operation Division
21:30 | 7447.36 | 6756.605 | 14203.965
22:00 | 7456.86 | 6703.29 | 14160.15
22:30 | 7442.36 | 6702.92 | 14145.28
23:00 | 7427.86 | 6702.55 | 14130.41

## En-Curve
QF-LDC-12
Date | 16-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2635 | 1910.5 | 898 | 38 | 82 | 715.67 | 218 | 3926 | 0 | 843 | 1744.86 | 0 | 0 | 0 | 708 | DAILY ENERGY CURVE
00:30 | 2572 | 1902 | 898 | 38 | 78 | 785.265 | 218 | 3896.5 | 0 | 792 | 1659.36 | 0 | 0 | 0 | 633.5 | 16-10-2025
01:00 | 2509 | 1893.5 | 898 | 38 | 74 | 854.86 | 218 | 3867 | 0 | 741 | 1573.86 | 0 | 0 | 0 | 559
01:30 | 2504.5 | 1885.5 | 897.5 | 38 | 74 | 892.66 | 218 | 3885.5 | 0 | 740 | 1550.86 | 0 | 0 | 0 | 492.5 | Energy Generated | 318.4439 |  | MKWHr
02:00 | 2500 | 1877.5 | 897 | 38 | 74 | 930.46 | 218 | 3904 | 0 | 739 | 1527.86 | 0 | 0 | 0 | 426 | Energy not Served | 5.575 |  | MKWHr
02:30 | 2486 | 1860 | 898 | 38 | 75 | 997.85 | 219.5 | 3911 | 0 | 739 | 1524.36 | 0 | 0 | 0 | 213 | Total Energy Requirement | 324.0189 |  | MKWHr
03:00 | 2472 | 1842.5 | 899 | 38 | 76 | 1065.24 | 221 | 3918 | 0 | 739 | 1520.86 | 0 | 0 | 0 | 0
03:30 | 2508 | 1832 | 898.5 | 38 | 75 | 1140.355 | 221 | 3913 | 0 | 605 | 1351.61 | 0 | 0 | 0 | 0
04:00 | 2544 | 1821.5 | 898 | 38 | 74 | 1215.47 | 221 | 3908 | 0 | 471 | 1182.36 | 0 | 0 | 0 | 0
04:30 | 2589 | 1833.5 | 898 | 38 | 71 | 1300.765 | 221 | 3816.5 | 0 | 418.5 | 955.18 | 0 | 0 | 1 | 0
05:00 | 2634 | 1845.5 | 898 | 38 | 68 | 1386.06 | 221 | 3725 | 0 | 366 | 728 | 0 | 0 | 2 | 0
05:30 | 2587 | 1847.25 | 898.5 | 38 | 69 | 1416.095 | 221 | 3694 | 0.025 | 369 | 706 | 0 | 0 | 1 | 0
06:00 | 2540 | 1849 | 899 | 38 | 70 | 1446.13 | 221 | 3663 | 0.05 | 372 | 684 | 0 | 0 | 0 | 0
06:30 | 2627 | 1878.5 | 898.5 | 38 | 69 | 1443.42 | 221 | 3677 | 52.545 | 433.5 | 696.5 | 0 | 0 | 0 | 0
07:00 | 2714 | 1908 | 898 | 38 | 68 | 1440.71 | 221 | 3691 | 105.04 | 495 | 709 | 0 | 0 | 0 | 0
07:30 | 2600.5 | 1837 | 897.5 | 38 | 65 | 1441.355 | 220.5 | 3619.5 | 206.915 | 539.5 | 759.68 | 0 | 0 | 1.5 | 0
08:00 | 2487 | 1766 | 897 | 38 | 62 | 1442 | 220 | 3548 | 308.79 | 584 | 810.36 | 0 | 0 | 3 | 0
08:30 | 2533 | 1801.85 | 897.5 | 38 | 62 | 1379.5 | 220 | 3447 | 400.93 | 508.5 | 808.11 | 0 | 0 | 1.5 | 60
09:00 | 2579 | 1837.7 | 898 | 38 | 62 | 1317 | 220 | 3346 | 493.07 | 433 | 805.86 | 0 | 0 | 0 | 120
09:30 | 2603.5 | 1826.85 | 898.5 | 38 | 66 | 1321 | 220 | 3392.5 | 552.16 | 423.5 | 914.36 | 0 | 0 | 0 | 156.5
10:00 | 2628 | 1816 | 899 | 38 | 70 | 1325 | 220 | 3439 | 611.25 | 414 | 1022.86 | 0 | 0 | 0 | 193
10:30 | 2670.5 | 1835.75 | 898.5 | 38 | 71 | 1301 | 219.5 | 3510 | 625.845 | 455.5 | 1074.11 | 0 | 0 | 0 | 211
11:00 | 2713 | 1855.5 | 898 | 38 | 72 | 1277 | 219 | 3581 | 640.44 | 497 | 1125.36 | 0 | 0 | 0 | 229
11:30 | 2791.5 | 1850.5 | 899 | 38 | 70 | 1273.5 | 219.5 | 3689.5 | 644.025 | 506 | 1127.18 | 0 | 0 | 0 | 236
12:00 | 2870 | 1845.5 | 900 | 38 | 68 | 1270 | 220 | 3798 | 647.61 | 515 | 1129 | 0 | 0 | 0 | 243
12:30 | 2892 | 1863.85 | 900 | 38 | 75 | 1319.5 | 219 | 3838 | 642.22 | 554 | 1127 | 0 | 0 | 0.5 | 250
13:00 | 2914 | 1882.2 | 900 | 38 | 82 | 1369 | 218 | 3878 | 636.83 | 593 | 1125 | 0 | 0 | 1 | 257
13:30 | 2908.5 | 1875.1 | 900 | 38 | 82 | 1386.24 | 218 | 3912.05 | 566.145 | 601.5 | 1087 | 0 | 0 | 2.5 | 266.5
14:00 | 2903 | 1868 | 900 | 38 | 82 | 1403.48 | 218 | 3946.1 | 495.46 | 610 | 1049 | 0 | 0 | 4 | 276
14:30 | 2915 | 1863.1 | 900 | 38 | 82 | 1419.325 | 218.5 | 3929.05 | 448.25 | 605.5 | 1130.75 | 0 | 0 | 3 | 241
15:00 | 2927 | 1858.2 | 900 | 38 | 82 | 1435.17 | 219 | 3912 | 401.04 | 601 | 1212.5 | 0 | 0 | 2 | 206
15:30 | 2956 | 1864.7 | 900 | 38 | 80 | 1448.355 | 219.5 | 3877.5 | 299.855 | 597.5 | 1240.5 | 0 | 0 | 1.5 | 196.5
16:00 | 2985 | 1871.2 | 900 | 38 | 78 | 1461.54 | 220 | 3843 | 198.67 | 594 | 1268.5 | 0 | 0 | 1 | 187
16:30 | 2925.5 | 1815.6 | 900 | 38 | 76 | 1460.245 | 219 | 3791 | 117.29 | 661 | 1335 | 0 | 0 | 0.5 | 205
17:00 | 2866 | 1760 | 900 | 38 | 74 | 1458.95 | 218 | 3739 | 35.91 | 728 | 1401.5 | 0 | 0 | 0 | 223
17:30 | 2987.5 | 1728 | 900 | 38 | 76 | 1462.835 | 218 | 3771 | 17.955 | 831.5 | 1566 | 0 | 0 | 0 | 267.5
18:00 | 3109 | 1696 | 900 | 38 | 78 | 1466.72 | 218 | 3803 | 0 | 935 | 1730.5 | 0 | 0 | 0 | 312
18:30 | 3063 | 1627.75 | 900 | 38 | 76 | 1469.125 | 218 | 3833.5 | 0 | 952 | 1841.18 | 0 | 0 | 0 | 318
19:00 | 3017 | 1559.5 | 900 | 38 | 74 | 1471.53 | 218 | 3864 | 0 | 969 | 1951.86 | 0 | 0 | 0 | 324
19:30 | 3135 | 1629.5 | 901 | 38 | 76 | 1468.49 | 220 | 3897 | 0 | 952 | 1910.86 | 0 | 0 | 0 | 357
20:00 | 3142 | 1643.5 | 900 | 38 | 86 | 1471.3 | 220 | 3952 | 0 | 948 | 1918.86 | 0 | 0 | 0 | 365
20:30 | 3157 | 1652.25 | 900 | 38 | 82 | 1463.11 | 220 | 3984.5 | 0 | 945 | 1841.86 | 0 | 0 | 0 | 351.5
21:00 | 3172 | 1661 | 900 | 38 | 78 | 1454.92 | 220 | 4017 | 0 | 942 | 1764.86 | 0 | 0 | 0 | 338
21:30 | 3134.5 | 1650 | 886.5 | 38 | 78 | 1457.605 | 220 | 4073 | 0 | 943.5 | 1722.86 | 0 | 0 | 0 | 332
22:00 | 3097 | 1639 | 873 | 38 | 78 | 1460.29 | 220 | 4129 | 0 | 945 | 1680.86 | 0 | 0 | 0 | 326
22:30 | 3096 | 1640 | 873 | 38 | 83 | 1464.42 | 219.5 | 4126.5 | 0 | 940 | 1664.86 | 0 | 0 | 0 | 304.5
23:00 | 3095 | 1641 | 873 | 38 | 88 | 1468.55 | 219 | 4124 | 0 | 935 | 1648.86 | 0 | 0 | 0 | 283
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 00:00 | 368 | 12:00 | Payra | 410 | 01:00 | 405 | 13:00
Ashuganj | 402 | 2:00 | 378 | 16:00 | Rahanpur | 408 | 01:00 | 388 | 13:00
Bhulta | 401 | 00:00 | 373 | 16:00 | Rampal | 400 | 00:00 | 388 | 12:00
Bibiana | 389 | 00:00 | 380 | 12:00
BIPTC | 403 | 03:00 | 393 | 13:00
Bogura | 400 | 01:00 | 375 | 13:00
Gopalganj | 397 | 00:00 | 383 | 13:00
Kaliakoir | 378 | 01:00 | 362 | 16:00
Madunaghat | 397 | 01:00 | 32 | 22:00
Meghnaghat | 391 | 00:00 | 376 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 00:00 | 220 | 12:00 | Kaliakoir | 235 | 01:00 | 222 | 16:00
AKSML | 236 | 17:00 | 227 | 04:00 | Keranigonj | 228 | 00:00 | 217 | 12:00
Aminbazar | 233 | 00:00 | 220 | 12:00 | Khulna(S) | 228 | 00:00 | 220 | 13:00
Ashuganj | 234 | 00:00 | 220 | 16:00 | Madunaghat | 235 | 00:00 | 230 | 12:00
Ashuganj-400 | 234 | 00:00 | 220 | 16:00 | Madunaghat-400 | 236 | 01:00 | 232 | 05:00
Baghabari | 235 | 00:00 | 224 | 15:00 | Maniknagar | 222 | 00:00 | 212 | 12:00
Barapukuria | 227 | 01:00 | 211 | 13:00 | Meghnaghat | 230 | 00:00 | 221 | 12:00
Barapukuria-230 | 227 | 01:00 | 211 | 13:00 | Meghnaghat-400 | 227 | 00:00 | 217 | 12:00
Barishal | 233 | 00:00 | 227 | 13:00 | Mirsorai | 235 | 19:00 | 224 | 04:00
Bheramara | 232 | 00:00 | 223 | 12:00 | Rajshahi | 232 | 00:00 | 220 | 12:00
Bhulta | 231 | 00:00 | 212 | 16:00 | Rampal | 228 | 00:00 | 219 | 13:00
Bibiana | 231 | 02:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 00:00 | 223 | 13:00 | Rampura | 230 | 00:00 | 209 | 16:00
Bogura | 239 | 01:00 | 227 | 07:00 | Shikalbaha | 234 | 00:00 | 228 | 14:00
Bogura-400 | 238 | 00:00 | 228 | 07:00 | Shyampur | 227 | 00:00 | 216 | 12:00
Borhanuddin | 236 | 00:00 | 233 | 14:00 | Siddhirganj | 224 | 00:00 | 217 | 08:00
BSRM | 232 | 18:00 | 223 | 04:00 | Sirajgonj | 240 | 00:00 | 233 | 10:00
Cumilla(N) | 228 | 00:00 | 219 | 14:00 | Sreepur | 232 | 00:00 | 219 | 16:00
Faridpur | 231 | 00:00 | 224 | 12:00 | Tongi | 232 | 00:00 | 217 | 15:00
Fenchuganj | 230 | 00:00 | 225 | 14:00
Ghorashal | 235 | 00:00 | 230 | 04:00
Ghorashal-230 | 231 | 00:00 | 212 | 16:00
Gopalganj | 233 | 00:00 | 225 | 13:00
GPH | 232 | 02:00 | 228 | 01:00
Haripur | 223 | 01:00 | 214 | 12:00
Hasnabad | 228 | 00:00 | 216 | 12:00
Hathazari | 233 | 00:00 | 225 | 16:00
Ishurdi | 233 | 01:00 | 225 | 15:00
Jhenaidah | 229 | 00:00 | 219 | 13:00
Kachua | 231 | 17:00 | 220 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 00:00 | 123 | 10:00 | Lalmonirhat | 127 | 00:00 | 118 | 07:00
Agargaon | 136 | 01:00 | 127 | 13:00 | Madanganj | 130 | 00:00 | 123 | 09:00
Agrabad | 134 | 00:00 | 129 | 14:00 | Madaripur | 135 | 00:00 | 131 | 13:00
AKS | 133 | 01:00 | 129 | 13:00 | Madartek | 133 | 02:00 | 122 | 10:00
Aminbazar | 138 | 00:00 | 130 | 12:00 | Madunaghat | 136 | 00:00 | 134 | 04:00
Amnura | 138 | 00:00 | 127 | 12:00 | Magura | 135 | 03:00 | 125 | 13:00
Ashuganj | 140 | 01:00 | 135 | 15:00 | Mahasthangarh | 134 | 00:00 | 125 | 07:00
Bagerhat | 131 | 06:00 | 120 | 23:00 | Maijdee | 135 | 18:00 | 129 | 04:00
Bajitpur | 131 | 00:00 | 123 | 15:00 | Manikganj | 129 | 01:00 | 120 | 15:00
Bakulia | 136 | 00:00 | 132 | 14:00 | Maniknagar | 135 | 00:00 | 126 | 12:00
Banani | 133 | 00:00 | 121 | 10:00 | Matarbari | 128 | 09:00 | 113 | 22:00
Bangabhaban | 134 | 01:00 | 126 | 12:00 | Matuail | 130 | 00:00 | 123 | 08:00
Barapukuria | 139 | 01:00 | 125 | 07:00 | Metrorail_Motijheel | 135 | 01:00 | 126 | 12:00
Barguna | 136 | 07:00 | 133 | 14:00 | Metrorail_Uttara | 135 | 00:00 | 128 | 22:00
Barishal | 134 | 00:00 | 129 | 15:00 | Millgate | 135 | 00:00 | 123 | 15:00
Barishal-230 | 134 | 00:00 | 130 | 12:00 | Mirpur | 136 | 00:00 | 128 | 22:00
Baroaulia | 135 | 00:00 | 132 | 21:00 | Mirzapur | 133 | 08:00 | 124 | 21:00
Baroirhat | 135 | 00:00 | 130 | 06:00 | Mithapukur | 134 | 00:00 | 123 | 07:00
Bashundhara | 134 | 00:00 | 123 | 14:00 | MI_Cement | 133 | 00:00 | 125.6 | 16:00
BashundharaCement | 130 | 00:00 | 123 | 09:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 129 | 00:00 | 124 | 23:00 | Mogbazar | 135 | 00:00 | 123 | 10:00
Benapole | 133 | 05:00 | 124 | 13:00 | Mongla | 131 | 05:00 | 122 | 21:00
Bhaluka | 133 | 00:00 | 122 | 10:00 | Motijheel | 134 | 01:00 | 126 | 12:00
Bhandaria | 128 | 09:00 | 117 | 21:00 | Muktagacha | 131 | 07:00 | 114 | 19:00
Bhangura | 134 | 03:00 | 127 | 13:00 | Munshiganj | 129 | 00:00 | 121 | 12:00
Bheramara | 137 | 00:00 | 132 | 13:00 | Muradnagar | 130 | 01:00 | 124 | 12:00
Bheramara(GK) | 137 | 00:00 | 132 | 13:00 | Mymensingh | 132 | 09:00 | 113 | 21:00
Bhulta | 125 | 00:00 | 120 | 12:00 | Naogaon | 132 | 00:00 | 122 | 13:00
Bog-Sherpur | 136 | 00:00 | 127 | 13:00 | Narail | 135 | 06:00 | 126 | 13:00
Bogura | 136 | 00:00 | 128 | 14:00 | Narinda | 135 | 00:00 | 126 | 12:00
Bogura-230 | 136 | 00:00 | 128 | 07:00 | Narshingdi | 136 | 00:00 | 118 | 11:00
Brahmanbaria | 136 | 00:00 | 127 | 22:00 | Natore | 135 | 00:00 | 127 | 13:00
Cantonment | 135 | 00:00 | 127 | 12:00 | Nawabganj | 134 | 00:00 | 126 | 16:00
Chandina | 134 | 00:00 | 127 | 12:00 | Netrakona | 126 | 18:00 | 116 | 16:00
Chandpur | 139 | 00:00 | 133 | 15:00 | New | 136 | 00:00 | 121 | 23:00
Chandraghona | 137 | 00:00 | 133 | 05:00 | Niamatpur | 138 | 02:00 | 131 | 13:00
Chapai | 138 | 01:00 | 130 | 16:00 | Noapara | 134 | 04:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 00:00 | 123 | 10:00 | Pabna | 135 | 00:00 | 130 | 12:00
Chauddagram | 134 | 00:00 | 129 | 12:00 | Palashbari | 132 | 00:00 | 119 | 07:00
Chhatak | 128 | 00:00 | 121 | 23:00 | Panchagarh | 136 | 04:00 | 115 | 07:00
Chowmuhani | 134 | 00:00 | 129 | 16:00 | Patiya | 135 | 00:00 | 131 | 04:00
Chuadanga | 133 | 00:00 | 123 | 16:00 | Patuakhali | 136 | 10:00 | 134 | 14:00
Coxsbazar | 127 | 09:00 | 112 | 18:00 | Payra | 137 | 00:00 | 135 | 12:00
Cumilla(N) | 133 | 00:00 | 128 | 12:00 | PHP | 134 | 00:00 | 129 | 04:00
Cumilla(S) | 134 | 00:00 | 127 | 18:00 | Postogola | 135 | 01:00 | 128 | 12:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 134 | 00:00 | 122 | 10:00
Daudkandi | 129 | 00:00 | 120 | 10:00 | Purbasadipur | 134 | 01:00 | 117 | 07:00
DhakaUniversity | 134 | 00:00 | 123 | 10:00 | Rahanpur | 138 | 00:00 | 132 | 13:00
Dhamrai | 135 | 00:00 | 126 | 16:00 | Rahanpur-400 | 140 | 01:00 | 133 | 13:00
Dhanmondi | 137 | 02:00 | 122 | 14:00 | Rahim | 130 | 00:00 | 121 | 12:00
Dohazari | 133 | 00:00 | 126 | 21:00 | Rajbari | 135 | 00:00 | 130 | 13:00
Faridpur | 135 | 00:00 | 132 | 12:00 | Rajendrapur | 137 | 00:00 | 122 | 16:00
Fatullah | 137 | 00:00 | 129 | 12:00 | Rajshahi | 135 | 00:00 | 126 | 13:00
Fenchuganj | 137 | 07:00 | 132 | 14:00 | Rajshahi-230 | 134 | 00:00 | 126 | 15:00
Feni | 135 | 00:00 | 130 | 05:00 | Ramganj | 135 | 00:00 | 129 | 05:00
Ghatail | 130 | 09:00 | 116 | 21:00 | Rampur | 135 | 00:00 | 129 | 14:00
Ghorashal | 140 | 00:00 | 129 | 12:00 | Rampura | 134 | 00:00 | 122 | 09:00
Goalpara | 136 | 09:00 | 130 | 13:00 | Rangamati | 135 | 00:00 | 132 | 12:00
Gollamari | 136 | 00:00 | 131 | 14:00 | Rangpur | 133 | 00:00 | 122 | 07:00
Gopalganj | 137 | 18:30 | 130 | 12:00 | Ruppur | 137 | 00:00 | 132 | 13:00
Gopalganj-400 | 137 | 00:00 | 132 | 12:00 | Saidpur | 133 | 01:00 | 119 | 07:00
Gulshan | 134 | 00:00 | 122 | 10:00 | Satkhira | 133 | 04:00 | 126 | 21:00
Halishahar | 135 | 00:00 | 131 | 04:00 | Satmasjid | 136 | 00:00 | 126 | 13:00
Haripur | 130 | 00:00 | 122 | 12:00 | Savar | 136 | 00:00 | 127 | 22:00
HaripurSBU | 130 | 01:00 | 123 | 10:00 | SevenRings | 139 | 00:00 | 128 | 10:00
Hasnabad | 135 | 00:00 | 127 | 12:00 | ShahCement | 130 | 00:00 | 123 | 10:00
Hathazari | 137 | 00:00 | 133 | 13:00 | Shahjadpur | 136 | 00:00 | 132 | 11:00
Ishurdi | 138 | 00:00 | 133 | 12:00 | Shahjibazar | 136 | 00:00 | 127 | 23:00
Jaldhaka | 133 | 01:00 | 119 | 13:00 | Shahmirpur | 135 | 00:00 | 131 | 13:00
Jamalpur | 131 | 09:00 | 115 | 21:00 | Shariatpur | 134 | 00:00 | 129 | 14:00
Jashore | 132 | 05:00 | 121 | 13:00 | Sherpur | 129 | 09:00 | 110 | 21:00
Jhenaidah | 135 | 00:00 | 125 | 14:00 | Shikalbaha | 126 | 00:00 | 121 | 04:00
Jhenaidah-230 | 135 | 00:00 | 128 | 13:00 | Shikalbaha-230 | 137 | 00:00 | 131 | 07:00
Joydebpur | 140 | 00:00 | 125 | 10:00 | Shitalakhya | 133 | 00:00 | 125.6 | 16:00
Joypurhat | 131 | 00:00 | 121 | 13:00 | Sholosohor | 136 | 00:00 | 133 | 04:00
Juldah | 135 | 00:00 | 131 | 13:00 | Shyampur | 136 | 00:00 | 131 | 13:00
Kabirpur | 138 | 00:00 | 121 | 15:00 | Shyampur-230 | 137 | 00:00 | 129 | 12:00
Kachua | 138 | 00:00 | 133 | 03:00 | Siddhirganj | 131 | 00:00 | 123 | 12:00
Kaliakoir | 137 | 01:00 | 130 | 23:00 | Sirajganj | 133 | 00:00 | 126 | 13:00
Kallyanpur | 138 | 01:00 | 130 | 00:00 | Sonargaon | 129 | 00:00 | 122 | 09:00
Kalurghat | 136 | 00:00 | 133 | 04:00 | Sreemongol | 135 | 00:00 | 127 | 23:00
Kamrangirchar | 135 | 00:00 | 126 | 13:00 | Sreepur | 135 | 00:00 | 127 | 10:00
Kaptai | 133 | 5:00 | 124 | 13:00 | Srinagar | 135 | 00:00 | 126 | 16:00
Kasba | 130 | 00:00 | 120 | 02:00 | SSM | 140 | 00:00 | 134 | 07:00
Kazla | 134 | 03:00 | 126 | 13:00 | Sunamganj | 127 | 01:00 | 120 | 23:00
Keranigonj | 135 | 00:00 | 127 | 12:00 | Sylhet | 130 | 00:00 | 127 | 04:00
Khagrachori | 134 | 00:00 | 129 | 14:00 | Sylhet-132 | 130 | 00:00 | 127 | 14:00
Khulna | 135 | 00:00 | 129 | 21:00 | Tangail | 130 | 09:00 | 118 | 21:00
Khulna(S) | 137 | 06:00 | 131 | 21:00 | Taraganj | 133 | 00:00 | 119 | 07:00
Khulshi | 134 | 00:00 | 129 | 14:00 | Thakurgaon | 136 | 01:00 | 113 | 07:00
Kishoreganj | 130 | 00:00 | 123 | 15:00 | TK | 136 | 00:00 | 133 | 06:00
Kodda | 138 | 00:00 | 120 | 16:00 | Tongi | 137 | 04:00 | 120 | 17:00
KSRM | 136 | 00:00 | 131 | 06:00 | Ullahpara | 134 | 00:00 | 128 | 12:00
Kulaura | 135 | 00:00 | 131 | 14:00 | Ullon | 133 | 00:00 | 122 | 10:00
Kurigram | 131 | 01:00 | 118 | 13:00 | Uttara | 135 | 06:00 | 123 | 15:00
Kushtia | 135 | 00:00 | 128 | 13:00 | UttaraNew | 136 | 00:00 | 128 | 22:00
Laksam | 138 | 00:00 | 132 | 04:00 | Zigatola | 135 | 00:00 | 127 | 16:00
Lakshmipur | 134 | 00:00 | 129 | 04:00
Lalbag | 134 | 00:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division