## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-10-2025 | during | 18-10-2025 | during | 18-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 373 | 282 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 100 | 100 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 90 | 60 | 149.36 | 149.36 | 140 | 140 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 55
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 19.5 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 88 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 74 | 110 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 390 | 410 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1842 | 2184.5 | 5827.4 | 5795.4 | 4600.7 | 4662.7
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 6 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 19 | 19 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 67 | 65 | 65 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 50 | 0 | 50 | 50 | 84 | 84 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 23 | 35 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 6 | 80 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.51 | 0 | 3.57 | 0 | 3.57 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 100 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 104 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 80 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 108 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1030 | 1143 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2180.51 | 2812.36 | 3615.29 | 3600.72 | 3345.43 | 3354.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 265 | 265 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 230 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 210 | 205 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 36 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 40 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 21 | 78 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 102 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 70 | 144 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 76 | 160 | 160 | 88 | 88 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 25 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 13 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 17 | 115 | 115 | 39 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1322 | 1331 | 2607.86 | 2542.86 | 2078.86 | 2062.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-10-2025 | during | 18-10-2025 | during | 18-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 83 | 101 | 157.5 | 157.5 | 51 | 51 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 67 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.24 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 241.24 | 233 | 400.9 | 349 | 240.9 | 189
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 81 | 81 | 81 | 81
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 161 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 50 | 300 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 324 | 348 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 922 | 1186 | 1285 | 1285 | 1269 | 1269
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 878 | 851 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 252 | 312 | 410 | 410 | 410 | 410
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 617.1 | 564 | 340 | 340 | 617 | 617 | U1 Partial load due to PA fan outage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1865.1 | 1916 | 2748 | 2658 | 2352 | 2262
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 306 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 7 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 964 | 1090 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 32 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 267 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.14 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1932.14 | 2001 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 56.03 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 47 | 47 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 202 | 162 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 328 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 18 | 52.2 | 52.2 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 42 | 113 | 113 | 113 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.15 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1030.55 | 1469 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.57 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1897.3 | 2236 | 3188.62 | 3021.87 | 2888.04 | 2721.29
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 45 | 48 | 48 | 48 | 48 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 181.28 | 0 | 181.28 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 375.7 | 250 | 512.28 | 296 | 492.28 | 276
System Total |  |  |  |  | 28823.2 | 28364.092 | 12577.99 | 14149.86 | 22332.35 | 21694.85 | 19281.21 | 18810.71
Forecast Scenario (18-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13950 |  | 0 |  | 13950
|  |  |  | 1:00 | 13570 |  | 0 |  | 13570
|  |  |  | 2:00 | 13130 |  | 0 |  | 13130
|  |  |  | 3:00 | 12560 |  | 0 |  | 12560
|  |  |  | 4:00 | 12200 |  | 0 |  | 12200
|  |  |  | 5:00 | 11930 |  | 0 |  | 11930
|  |  |  | 6:00 | 11540 |  | 0 |  | 11540
|  |  |  | 7:00 | 11520 |  | 0 |  | 11520
|  |  |  | 8:00 | 11450 |  | 0 |  | 11450
|  |  |  | 9:00 | 11620 |  | 0 |  | 11620
|  |  |  | 10:00 | 11820 |  | 0 |  | 11820
|  |  |  | 11:00 | 12130 |  | 0 |  | 12130
|  |  |  | 12:00 | 12780 |  | 0 |  | 12780
|  |  |  | 13:00 | 12990 |  | 0 |  | 12990
|  |  |  | 14:00 | 12640 |  | 0 |  | 12640
|  |  |  | 15:00 | 12520 |  | 0 |  | 12520
|  |  |  | 16:00 | 12360 |  | 0 |  | 12360
|  |  |  | 17:00 | 12020 |  | 0 |  | 12020
|  |  |  | 18:00 | 13550 |  | 0 |  | 13550
|  |  |  | 18:30 | 13850 |  | 0 |  | 13850
|  |  |  | 19:00 | 14150 |  | 0 |  | 14150
|  |  |  | 19:30 | 14120 |  | 0 |  | 14120
|  |  |  | 20:00 | 14110 |  | 0 |  | 14110
|  |  |  | 21:00 | 14079 |  | 0 |  | 14079
|  |  |  | 22:00 | 14040 |  | 0 |  | 14040
|  |  |  | 23:00 | 14030 |  | 0 |  | 14030
Probable Maximum Temperature: |  |  | 33.10°C
Probable Maximum Demand at Day Peak: |  |  | 12780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 306.689 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:00 hrs on 18-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-10-2025 | [28 empty] | Date: | 17-10-2025 | [28 empty] | Date: | 17-10-2025 | [28 empty] | Date: | 17-10-2025 | [28 empty] | Date: | 17-10-2025 | [14 empty] | Date: | 17-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 89 | 137 | 195 | 15 | 0 | 17 | 0 | 340 | 0 | 370 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 0 | 16 | 107 | 0 | 0 | 33 | 60 | 17 | 0 | 0 | 0 | 218 | 110 | 29 | 488 | 17 | 0 | 0 | 25.5 | 0 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 117 | 0 | 160 | 265 | 240 | 44 | 0 | 37 | 27 | 103 | 144 | 0 | 19 | 97 | 84 | 43 | 0 | 36 | 310 | 0 | 236 | 28 | 67 | 149 | 10 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 69 | 49 | 33 | 0 | 0 | 0 | 7330.5 | 874 | 192 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 615 | 0 | 1470.89 | 0 | 40 | 0 | 35 | 113 | 0 | 50 | 38 | 8 | 0 | 0 | 26 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 47 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 270 | 115 | 220 | 0 | 306 | 1222 | 17 | 6656.89 | 13987.39 | 106.58
01:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 35 | 137 | 195 | 15 | 0 | 17 | 0 | 340 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 0 | 16 | 105 | 0 | 0 | 50 | 60 | 17 | 0 | 0 | 0 | 218 | 101 | 29 | 577 | 17 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 1202 | 0 | 51 | 122 | 0 | 160 | 265 | 240 | 44 | 0 | 37 | 16 | 103 | 144 | 0 | 19 | 95 | 74 | 43 | 0 | 36 | 305 | 0 | 336 | 28 | 67 | 140 | 10 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 49 | 51 | 0 | 0 | 0 | 7321 | 874 | 196 | 0 | 34 | 31 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 605 | 0 | 1459.43 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 38 | 26 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 46 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 115 | 220 | 0 | 307 | 1210 | 17 | 6429.43 | 13750.43 | 106.57
02:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 107 | 195 | 15 | 0 | 17 | 0 | 340 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 0 | 16 | 76 | 0 | 1 | 50 | 60 | 17 | 0 | 0 | 0 | 219 | 100 | 31 | 577 | 17 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 1162 | 0 | 51 | 128 | 0 | 165 | 265 | 240 | 44 | 0 | 37 | 17 | 104 | 145 | 0 | 19 | 9 | 78 | 25 | 0 | 36 | 305 | 0 | 336 | 30 | 67 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 49 | 51 | 0 | 0 | 0 | 7084 | 873 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 605 | 0 | 1464.25 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 26 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 44 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 307 | 1130 | 17 | 6281.25 | 13365.25 | 106.56
03:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 75 | 30 | 15 | 0 | 17 | 0 | 340 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 20 | 22 | 0 | 0 | 10 | 0 | 29 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 220 | 99 | 39 | 645 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1162 | 0 | 51 | 133 | 0 | 185 | 265 | 240 | 44 | 0 | 37 | 17 | 104 | 144 | 0 | 19 | 0 | 72 | 0 | 0 | 15 | 300 | 0 | 336 | 30 | 67 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 49 | 51 | 0 | 0 | 0 | 6753 | 873 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 604 | 0 | 1460.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 42 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 115 | 220 | 0 | 307 | 1100 | 17 | 5960.06 | 12713.06 | 106.55
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 16 | 60 | 0 | 0 | 0 | 17 | 0 | 340 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 221 | 101 | 39 | 645 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 1161 | 0 | 51 | 80 | 0 | 195 | 265 | 240 | 44 | 0 | 37 | 17 | 103 | 142 | 0 | 19 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 336 | 30 | 67 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 51 | 0 | 0 | 0 | 6583 | 873 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 613 | 0 | 1472.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 115 | 220 | 0 | 307 | 1107 | 17 | 5882.97 | 12465.97 | 106.54
05:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 16 | 60 | 0 | 0 | 0 | 17 | 0 | 340 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 221 | 58 | 40 | 645 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 0 | 205 | 265 | 240 | 44 | 0 | 37 | 17 | 103 | 140 | 0 | 19 | 0 | 72 | 0 | 0 | 0 | 295 | 0 | 336 | 30 | 67 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 51 | 0 | 0 | 0 | 6411 | 873 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 1352.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 115 | 220 | 0 | 307 | 1096 | 0 | 5685.75 | 12096.75 | 106.53
06:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 16 | 60 | 0 | 0 | 0 | 17 | 0 | 340 | 0 | 360 | 0 | 17 | 250 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 25 | 645 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1042 | 0 | 51 | 0 | 0 | 200 | 265 | 240 | 44 | 0 | 37 | 17 | 103 | 141 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 336 | 30 | 67 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 51 | 0 | 0.01 | 3 | 6289.01 | 873 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 0 | 1322.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 115 | 220 | 0 | 306 | 1100 | 0 | 5587.35 | 11876.36 | 106.52
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 16 | 60 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 355 | 0 | 17 | 250 | 0 | 0 | 4 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0.7 | 222 | 0 | 27 | 647 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 3 | 51 | 0 | 0 | 200 | 265 | 240 | 45 | 0 | 37 | 17 | 104 | 119 | 0 | 17 | 52 | 58 | 16 | 9 | 0 | 305 | 0 | 336 | 30 | 67 | 140 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 51 | 0 | 6.83 | 6 | 6199.53 | 873 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 519 | 0 | 1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.39 | 13 | 0 | 0 | 7.5 | 214 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0.61 | 0 | 42 | 0 | 5 | 0 | 0 | 0 | 0 | 0.6 | 30 | 0.07 | 0 | 199 | 115 | 220 | 0 | 308 | 1098 | 0 | 5415.17 | 11614.7 | 106.51
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 355 | 0 | 0 | 250 | 0 | 0 | 13 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1.56 | 222 | 0 | 28 | 645 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 6 | 51 | 0 | 0 | 200 | 265 | 240 | 44 | 0 | 37 | 17 | 103 | 103 | 0 | 17 | 52 | 54 | 25 | 32 | 0 | 310 | 0 | 336 | 30 | 67 | 143 | 8 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 51 | 1 | 21.53 | 4 | 6214.09 | 899 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 485 | 0 | 1025.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.41 | 41 | 0 | 0 | 22.91 | 214 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 1.93 | 0 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 2.8 | 85 | 0.07 | 0 | 195 | 115 | 220 | 0 | 306 | 996 | 0 | 5333.81 | 11547.9 | 106.5
09:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 21 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 2.41 | 222 | 0 | 29 | 650 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 844 | 11 | 51 | 0 | 0 | 205 | 265 | 240 | 45 | 0 | 35 | 17 | 102 | 104 | 0 | 14 | 34 | 50 | 25 | 50 | 0 | 300 | 0 | 336 | 30 | 67 | 139 | 8 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 50 | 2 | 33.93 | 6 | 6094.34 | 899 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 446 | 0 | 933.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.69 | 69 | 0 | 0 | 38.27 | 178 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 3.36 | 0 | 45 | 0 | 24 | 0 | 0 | 0 | 0 | 4.6 | 129 | 0.13 | 0 | 166 | 115 | 180 | 0 | 306 | 948 | 0 | 5198.94 | 11293.28 | 106.49
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 370 | 0 | 0 | 280 | 0 | 0 | 25 | 52 | 18.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 3.06 | 222 | 0 | 29 | 650 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 825 | 18 | 51 | 0 | 0 | 210 | 265 | 240 | 44 | 0 | 34 | 17 | 100 | 68 | 0 | 19 | 17 | 50 | 8 | 62 | 0 | 315 | 0 | 323 | 30 | 67 | 150 | 0 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 54 | 2 | 43.19 | 6 | 6058.95 | 878 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 460 | 0 | 926.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.78 | 85 | 0 | 0 | 49.5 | 172 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 4.24 | 0 | 42 | 0 | 31 | 0 | 0 | 0 | 0 | 5.8 | 164 | 0.37 | 0 | 172 | 110 | 180 | 0 | 306 | 940 | 0 | 5305.61 | 11364.56 | 106.48
11:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 13 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 380 | 0 | 0 | 280 | 0 | 0 | 30 | 52 | 19 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 3.51 | 222 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 825 | 15 | 51 | 0 | 0 | 210 | 265 | 240 | 43 | 0 | 34 | 16 | 100 | 68 | 8 | 19 | 16 | 54 | 8 | 68 | 0 | 270 | 0 | 324 | 30 | 67 | 156 | 0 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 66 | 48 | 83 | 2 | 47.94 | 6 | 6139.45 | 878 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 501 | 0 | 983.88 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 56.57 | 102 | 0 | 0 | 60.46 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.01 | 0 | 45 | 18 | 34 | 49 | 0 | 0 | 0 | 6.5 | 185 | 0.38 | 0 | 211 | 110 | 220 | 0 | 306 | 946 | 0 | 5686.8 | 11826.25 | 106.47
12:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17.5 | 17 | 17 | 90 | 45 | 0 | 0 | 17 | 0 | 300 | 0 | 390 | 0 | 0 | 320 | 0 | 0 | 30 | 125 | 18.5 | 14 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 50 | 0 | 0 | 0 | 0 | 3.51 | 219 | 0 | 23 | 650 | 17 | 0 | 0 | 6 | 0 | 161 | 0 | 0 | 0 | 1030 | 13 | 51 | 21 | 0 | 210 | 265 | 240 | 42 | 0 | 34 | 17 | 99 | 70 | 9 | 19 | 80 | 58 | 43 | 64 | 0 | 50 | 0 | 324 | 30 | 67 | 156 | 8 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 83 | 1 | 36.24 | 6 | 6507.75 | 878 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 617.1 | 0 | 1030.55 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 56.03 | 102 | 0 | 0 | 52.57 | 202 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.15 | 0 | 45 | 50 | 35 | 49 | 0 | 0 | 0 | 6.7 | 190 | 0.14 | 7 | 307 | 110 | 220 | 0 | 307 | 964 | 17 | 6070.24 | 12577.99 | 106.46
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 17.5 | 17 | 17 | 90 | 95 | 7 | 0 | 17 | 0 | 300 | 0 | 405 | 0 | 0 | 323 | 0 | 0 | 28 | 142 | 18.5 | 10 | 0 | 0 | 17 | 16 | 55 | 0 | 0 | 18 | 0 | 3 | 0 | 0 | 3.14 | 218 | 43 | 32 | 650 | 17 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1156 | 0 | 51 | 50 | 0 | 210 | 265 | 240 | 42 | 0 | 33 | 16 | 99 | 68 | 9 | 19 | 88 | 64 | 43 | 59 | 0 | 200 | 0 | 324 | 30 | 67 | 154 | 8 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 78 | 1 | 44.64 | 3 | 6932.78 | 878 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 605 | 0 | 1143.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.54 | 95 | 0 | 0 | 53.71 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.08 | 0 | 45 | 35 | 25 | 39 | 0 | 0 | 0 | 6.6 | 189 | 0.59 | 16 | 275 | 110 | 220 | 0 | 307 | 966 | 22 | 6065.58 | 12998.36 | 106.45
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 17.5 | 17 | 17 | 60 | 95 | 15 | 0 | 17 | 0 | 300 | 0 | 400 | 0 | 0 | 316 | 0 | 0 | 23 | 90 | 18.5 | 10 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 218 | 51 | 38 | 650 | 0 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1157 | 8 | 51 | 10 | 0 | 210 | 265 | 240 | 35 | 0 | 34 | 16 | 98 | 69 | 9 | 19 | 0 | 62 | 0 | 57 | 0 | 315 | 0 | 324 | 30 | 67 | 153 | 8 | 0 | 80 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 78 | 2 | 18.46 | 6 | 6650.08 | 878 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 576 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.38 | 61 | 0 | 0 | 44.11 | 169 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 3.89 | 0 | 42 | 35 | 19 | 34 | 0 | 0 | 0 | 5.8 | 131 | 0.54 | 0 | 206 | 110 | 220 | 0 | 307 | 966 | 23 | 5797.72 | 12447.8 | 106.45
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 17 | 17 | 17 | 60 | 95 | 15 | 0 | 17 | 0 | 300 | 0 | 480 | 0 | 0 | 323 | 0 | 0 | 17 | 90 | 18 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 222 | 50 | 38 | 650 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 1160 | 15 | 51 | 10 | 0 | 210 | 265 | 240 | 35 | 0 | 34 | 17 | 99 | 69 | 0 | 19 | 0 | 68 | 0 | 44 | 0 | 320 | 0 | 325 | 30 | 67 | 153 | 8 | 0 | 79 | 30 | 0 | 16 | 160 | 0 | 67 | 47 | 81 | 1 | 24.75 | 6 | 6656.87 | 878 | 271 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47.06 | 585 | 0 | 1279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.01 | 59 | 0 | 0 | 33 | 176 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 2.9 | 0 | 44 | 35 | 20 | 34 | 0 | 0 | 0 | 2.4 | 110 | 0.35 | 0 | 199 | 110 | 220 | 0 | 306 | 975 | 25 | 5866.72 | 12523.59 | 106.44
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 17 | 17 | 17 | 30 | 95 | 15 | 0 | 17 | 0 | 300 | 0 | 455 | 0 | 0 | 325 | 0 | 0 | 8 | 90 | 18 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 222 | 34 | 33 | 650 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 1160 | 4 | 51 | 10 | 0 | 160 | 265 | 230 | 35 | 0 | 35 | 16 | 99 | 68 | 0 | 19 | 0 | 64 | 0 | 19 | 0 | 310 | 0 | 322 | 30 | 67 | 153 | 8 | 0 | 79 | 30 | 0 | 16 | 160 | 0 | 67 | 47 | 100 | 1 | 15.07 | 6 | 6448.29 | 888 | 279 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.43 | 576 | 0 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.35 | 33 | 0 | 0 | 17.94 | 169 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 1.6 | 0 | 44 | 0 | 10 | 0 | 0 | 0 | 0 | 2 | 55 | 0.2 | 0 | 198 | 110 | 220 | 0 | 306 | 1003 | 25 | 5639.52 | 12087.81 | 106.44
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 17 | 17 | 50 | 30 | 95 | 15 | 10 | 17 | 0 | 300 | 0 | 390 | 0 | 0 | 250 | 0 | 0 | 1 | 90 | 18 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.2 | 222 | 33 | 38 | 650 | 0 | 0 | 0 | 8 | 0 | 160 | 0 | 0 | 0 | 1160 | 1 | 51 | 10 | 0 | 165 | 265 | 230 | 35 | 0 | 35 | 17 | 98 | 69 | 0 | 19 | 0 | 60 | 0 | 2 | 0 | 305 | 0 | 324 | 30 | 67 | 144 | 8 | 0 | 79 | 30 | 0 | 16 | 160 | 0 | 67 | 47 | 100 | 0 | 1.96 | 6 | 6320.16 | 888 | 292 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.21 | 524 | 0 | 1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57 | 6 | 0 | 0 | 2.79 | 162 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.21 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 0.5 | 8 | 0.03 | 0 | 196 | 100 | 180 | 0 | 306 | 1055 | 28 | 5443.31 | 11763.47 | 106.44
18:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 17 | 30 | 76 | 100 | 185 | 15 | 17 | 35 | 0 | 300 | 0 | 368 | 0 | 17 | 323 | 0 | 0 | 0 | 142 | 18 | 10 | 0 | 0 | 17 | 30 | 36 | 0 | 0 | 0 | 46 | 7 | 0 | 0 | 0 | 222 | 41 | 38 | 650 | 82 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1194 | 0 | 51 | 21 | 0 | 200 | 265 | 230 | 37 | 0 | 35 | 17 | 100 | 121 | 0 | 19 | 34 | 76 | 10 | 0 | 27 | 310 | 0 | 348 | 30 | 67 | 147 | 8 | 0 | 79 | 30 | 0 | 16 | 159 | 1 | 67 | 47 | 100 | 0 | 0 | 0 | 7177 | 850 | 300 | 0 | 26 | 7 | 38 | 0 | 0 | 0 | 0 | 21 | 0 | 565 | 0 | 1433 | 0 | 0 | 0 | 35 | 3 | 0 | 95 | 12 | 17 | 0 | 0 | 25 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 45 | 90 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 272 | 110 | 220 | 0 | 306 | 1062 | 22 | 6210 | 13387 | 106.43
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 17 | 35 | 88 | 60 | 260 | 15 | 35 | 35 | 0 | 300 | 0 | 410 | 0 | 17 | 326 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 0 | 80 | 100 | 80 | 0 | 0 | 0 | 67 | 54.36 | 0 | 0 | 0 | 222 | 104 | 35 | 650 | 108 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1143 | 0 | 51 | 78 | 0 | 205 | 265 | 230 | 40 | 0 | 36 | 17 | 102 | 144 | 0 | 19 | 13 | 76 | 25 | 0 | 30 | 300 | 0 | 348 | 30 | 67 | 147 | 8 | 0 | 80 | 30 | 0 | 16 | 160 | 17 | 67 | 48 | 101 | 0 | 0 | 0 | 7746.86 | 851 | 312 | 0 | 41 | 60 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 564 | 0 | 1469 | 0 | 32 | 0 | 35 | 42 | 0 | 95 | 30 | 18 | 0 | 0 | 25 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 45 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 267 | 110 | 180 | 0 | 306 | 1090 | 32 | 6403 | 14149.86 | 106.43
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 35 | 88 | 60 | 260 | 0 | 35 | 35 | 0 | 300 | 0 | 365 | 0 | 17 | 326 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 0 | 60 | 45 | 84 | 0 | 0 | 26 | 68 | 54.36 | 0 | 0 | 0 | 222 | 106 | 35 | 650 | 53 | 0 | 0 | 15 | 0 | 161 | 0 | 0 | 0 | 1164 | 0 | 51 | 122 | 0 | 180 | 265 | 230 | 40 | 0 | 36 | 17 | 102 | 144 | 9 | 19 | 0 | 76 | 0 | 0 | 30 | 325 | 0 | 348 | 30 | 67 | 144 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 17 | 67 | 48 | 101 | 0 | 0 | 2 | 7703.86 | 858 | 318 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 565 | 0 | 1459 | 0 | 32 | 0 | 0 | 95 | 0 | 95 | 37 | 0 | 0 | 0 | 25 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 45 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 110 | 220 | 0 | 307 | 1088 | 32 | 6400 | 14103.86
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 35 | 88 | 60 | 260 | 0 | 35 | 35 | 0 | 300 | 0 | 350 | 0 | 17 | 324 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 0 | 60 | 45 | 86 | 0 | 0 | 50 | 68 | 54.36 | 0 | 0 | 0 | 222 | 105 | 38 | 650 | 53 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1167 | 0 | 51 | 122 | 0 | 185 | 265 | 230 | 41 | 0 | 36 | 17 | 102 | 145 | 5 | 19 | 0 | 70 | 0 | 0 | 30 | 305 | 0 | 348 | 30 | 67 | 153 | 10 | 0 | 80 | 30 | 0 | 16 | 159 | 17 | 68 | 48 | 101 | 0 | 0 | 4 | 7687.86 | 858 | 322 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 576 | 0 | 1463 | 0 | 32 | 0 | 0 | 96 | 0 | 95 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 45 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 110 | 220 | 0 | 307 | 1094 | 25 | 6407 | 14094.86 | 106.43
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 17 | 108 | 60 | 260 | 0 | 35 | 17 | 0 | 300 | 0 | 350 | 0 | 17 | 322 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 0 | 63 | 50 | 91 | 0 | 0 | 18 | 68 | 54.36 | 0 | 0 | 0 | 222 | 106 | 38 | 650 | 53 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1183 | 0 | 51 | 127 | 0 | 195 | 265 | 230 | 41 | 0 | 37 | 17 | 103 | 144 | 9 | 19 | 0 | 74 | 0 | 0 | 30 | 320 | 0 | 347 | 30 | 67 | 157 | 10 | 0 | 80 | 30 | 0 | 16 | 161 | 17 | 67 | 48 | 102 | 0 | 0 | 0 | 7718.86 | 858 | 338 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 1464 | 0 | 39 | 0 | 0 | 113 | 0 | 95 | 10 | 0 | 0 | 0 | 25 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 110 | 220 | 0 | 307 | 1100 | 27 | 5915 | 13633.86 | 106.42
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 17 | 114 | 108 | 260 | 10 | 0 | 17 | 0 | 300 | 0 | 310 | 0 | 17 | 327 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 90 | 69 | 91 | 0 | 0 | 50 | 68 | 54.36 | 0 | 0 | 0 | 222 | 106 | 38 | 650 | 53 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1232 | 0 | 51 | 130 | 0 | 205 | 265 | 230 | 41 | 0 | 37 | 16 | 103 | 145 | 9 | 19 | 114 | 74 | 43 | 0 | 30 | 315 | 0 | 347 | 30 | 67 | 159 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 17 | 67 | 48 | 102 | 0 | 0 | 0 | 8019.36 | 864 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 1477 | 0 | 48 | 0 | 35 | 113 | 0 | 95 | 8 | 25 | 0 | 0 | 25 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 110 | 220 | 0 | 307 | 1180 | 35 | 6236 | 14255.36 | 106.42
23:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 17 | 114 | 108 | 275 | 15 | 0 | 17 | 0 | 300 | 0 | 330 | 0 | 0 | 330 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 99 | 70 | 91 | 0 | 0 | 50 | 68 | 54.36 | 0 | 0 | 0 | 222 | 107 | 42 | 650 | 17 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1226 | 0 | 51 | 130 | 0 | 230 | 265 | 99 | 43 | 0 | 37 | 17 | 103 | 145 | 0 | 19 | 114 | 80 | 43 | 0 | 29 | 320 | 0 | 348 | 30 | 67 | 159 | 10 | 0 | 80 | 30 | 0 | 16 | 160 | 17 | 68 | 49 | 103 | 0 | 0 | 0 | 7902.36 | 864 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 1477 | 0 | 48 | 0 | 35 | 113 | 0 | 95 | 18 | 25 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 110 | 220 | 0 | 307 | 1222 | 20 | 6273 | 14175.36 | 106.42
Total KWH | 0 | 1505280 | 405120 | 0 | 0 | 0 | 0 | 0 | 7808400 | 0 | 0 | 207360 | 301320 | 1061424 | 1702080 | 2776058 | 199373 | 132708 | 396000 | 0 | 7604000 | 0 | 8971772 | 0 | 134319 | 6994303 | 0 | 0 | 192284 | 2667600 | 463800 | 439200 | 0 | 0 | 583364 | 494291 | 965760 | 0 | 5280 | 837539 | 610656 | 403817 | 0 | 0 | 21840 | 5283285 | 1498757 | 860640 | 15410909.09 | 453309 | 0 | 0 | 175624.2 | 0 | 3775439 | 0 | 0 | 0 | 26372725 | 100845 | 1239000 | 1400072 | 0 | 4922500 | 6711000 | 5528000 | 992160 | 0 | 870840 | 408960 | 2426660 | 2737440 | 64680 | 433220 | 837900 | 1608960 | 402797 | 457491 | 278816 | 7159760 | 0 | 8355000 | 711000 | 1596840 | 3631909 | 201792 | 0 | 1912320 | 711648 | 0 | 392000 | 3764290 | 109080 | 1626000 | 1144800 | 1715520 | 11350 | 292630 | 77520 | 166550436.29 | 21170909 | 6448608 | 0 | 106560 | 103168 | 912000 | 0 | 0 | 0 | 0 | 658800 | 550800 | 11752730 | 0 | 30955080 | 0 | 352675 | 0 | 167232 | 692832 | 0 | 603136 | 192801 | 133032 | 371900 | 696983 | 210000 | 0 | 384000 | 4656455 | 0 | 0 | 0 | 0 | 0 | 8865454 | 0 | 33360 | 0 | 1023709 | 1332713 | 221159 | 1217702 | 0 | 0 | 0 | 39786 | 1241280 | 3177 | 170304 | 5957000 | 2683000 | 5347120 | 0 | 7366536 | 26080000 | 414000 | 143116001 | 309666437.29

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12577.99 | MW | 12:00 Hr. | Energy Generated |  |  | 309.6664 |  | MKWHr.
| Day Peak Demand |  |  | 12577.99 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.864 |  | MKWHr.
| Evening Peak Generation |  |  | 14149.86 | MW | 19:00 Hr. | Energy Demand |  |  | 310.5304 |  | MKWHr.
| Evening Peak Demand |  |  | 14210.47 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11293.28 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 887.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 14255.36 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.5096 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.2815 | 0 | 11.4886 | 0 | 0 | 0.19228 | 0 | 0 | 43.9624 | Gas | 118.1937 | Gas | 421385402.76
| Chattogram Zone |  |  | 4.6361 | 41.7836 | 6.0231 | 0 | 5.2833 | 0.12269 | 0 | 0.00528 | 57.8541 | Coal | 93.9636 | Coal | 589651018.1273
| Cumilla Zone |  |  | 23.1234 | 0 | 6.1307 | 0 | 0 | 0.45749 | 1.609 | 0 | 31.3205 | HFO | 32.9548 | HFO | 601441147.318
| Mymensingh Zone |  |  | 1.7155 | 0 | 2.9574 | 0 | 0 | 0.30398 | 0 | 0 | 4.9769 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4366 | Hydro | 5.2833 | Hydro | 528328.5
| Khulna Zone |  |  | 6.4486 | 11.7527 | 0.86853 | 0 | 0 | 0.5508 | 22.0829 | 0 | 41.7036 | Solar | 4.6189 | Solar | 73991878.68
| Barishal Zone |  |  | 8.0301 | 39.4035 | 0.5843 | 0 | 0 | 0.003177 | 0 | 0 | 48.0211 | Import | 54.6469 | Import | 328729084.99
| Rajshahi Zone |  |  | 13.5219 | 0 | 2.3517 | 0 | 0 | 1.4862 | 30.9551 | 0 | 48.3149 | Wind | 0.00528 | Wind | 77668.8
| Rangpur Zone |  |  | 0 | 1.0237 | 2.5504 | 0 | 0 | 1.5022 | 0 | 0 | 5.0763
| Total |  |  | 118.1937 | 93.9636 | 32.9548 | 0 | 5.2833 | 4.6189 | 54.6469 | 0.00528 | 309.6664
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 421385402.76 |  | Hydro | 528328.5
|  |  |  | Coal | 589651018.1273 |  | Solar | 73991878.68
|  |  |  | HFO | 601441147.318 |  | Import | 328729084.99
|  |  |  | HSD | 0 |  | Wind | 77668.8
[5 empty] | Total: | 201,58,04,529 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1709 | Peak Hr Flow | 851.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 332958454.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.9551 | Peak Hr Flow | 1469.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1838 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.609 | Peak Hr Flow | 76.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2395 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.7349 | Peak Hr Flow | 2396.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4563
|  |  |  | Chattogram |  | 0 |  | 1416
|  |  |  | Cumilla |  | 0 |  | 1353
|  |  |  | Mymensingh |  | 58 |  | 1210
|  |  |  | Sylhet |  | 0 |  | 645
|  |  |  | Khulna |  | 0 |  | 1628
|  |  |  | Barishal |  | 0 |  | 433
|  |  |  | Rajshahi |  | 0 |  | 1348
|  |  |  | Rangpur |  | 0 |  | 930
|  |  |  | Total |  | 58 |  | 13526
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:28 | 11:22 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Due to red hot maintenance of 33Kv bus
clamp of Khlishpur feeders.
| 09:29 | 11:21 | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Due to red hot maintenance of 33Kv bus
clamp of Khlishpur feeders.
| 09:45 | 17:39 | Rahanpur 132/33kV S/S Rahanpur-2 Forced S/D Due to রহনপুর ৪০০কেভি গ্রিড সাইডে শাটডাউন
চেয়েছে।
| 09:46 |  | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-02 Project Work S/D
|  | 10:17 | Dohazari-Sikalbaha 132 kV Ckt-2 is restored.
| 10:43 |  | Summit Bibiana-2 341MW ST tripped.
|  | 11:42 | GPH 230/33kV S/S HATHAZARI is restored.
| 11:49 |  | Summit Bibiana-2 341MW ST was sync.
| 12:00 |  | Day Peak Generation: 12574 MW.
| 12:14 | 17:08 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Tripped showing 86,86.1 relays Due to
due to faulty 21 distance zone =03 R,Y phase,IL1=5.86kA,IL2=4.88kA
| 14:35 | 16:50 | Hathazari 230/132/33kV S/S 230KV MAIN BUS-01 Project Work S/D Due to Dismantling 230kV
Conductor
|  | 16:21 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 16:23 | Barishal 230/132kV S/S T-5 LT is restored.
| 19:00 |  | Evening Peak Generation is 14149 MW.
| 20:49 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 20:49 |  | Rampal 1320 MW (BIFPCL) unit-1 tripped.
| 22:51 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- ST
| 23:24 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 23:41 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 03:01 | 05:23 | Matuail-Siddhirganj 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Due to
red hot at Matuail (DPDC) Substation Ending.
| 05:44 | 07:37 | Bagerhat 132/33kV S/S 132 kV BUS Scheduled S/D Due to 132 kV Bhandaria line bus DS B | [7 empty] | 55.0MW load
|  |  | phase red jot maintenance work | [7 empty] | interrup.
| 05:57 |  | Maniknagar-Matuail 132kV Ckt-1 Forced S/D from Maniknagar 132/33kV end Due to Red hot
at Matuail ss
| 05:58 | 07:41 | Bagerhat-Mongla 132 kV Ckt-1 Forced S/D from Mongla 132/33kV end Due to Red hot at | [7 empty] | 12.0MW load
|  |  | Bagerhat Grid | [7 empty] | interrup. Mongla
132/33kV end
| 05:59 | 07:40 | Mongla 132/33kV S/S 100MW ERBL Solar PS Forced S/D Due to Redhot maintenance at Bagerhat | [7 empty] | 1.0MW load
|  |  | grid | [7 empty] | interrup.
| 05:59 | 07:41 | Bagerhat-Mongla 132 kV Ckt-2 Forced S/D from Mongla 132/33kV end Due to Red hot | [7 empty] | 12.0MW load
|  |  | maintenance at Bagerhat Grid | [7 empty] | interrup. Mongla
132/33kV end
| 05:59 | 07:31 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to S/D TAKEN
BY ALDC KHULNA
| 06:03 |  | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Scheduled S/D Due to High Temperature
Maintenance work
| 06:14 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO on at 05:35
| 06:15 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Project Work S/D from Patuakhali | [7 empty] | 11.0MW load
|  |  | 132/33kV end Due to Stringing work of T-17/3 to T-17/4 Span (G2G project Work ) and | [7 empty] | interrup.
|  |  | from Barguna 132/33kV end Due to Barishal-Patuakhali 230kV Line stringing work. | [7 empty] | Patuakhali 132/33kV
end and 16.0MW load
interrup. Barguna
132/33kV end
| 06:35 |  | Jhenaidah 132/33kV S/S Bus-A Scheduled S/D Due to Chuadanga ckt -2 upgradation | [7 empty] | 90.0MW load
interrup.
| 06:37 |  | Jhenaidah 132/33kV S/S Bus-B Scheduled S/D | [7 empty] | 110.0MW load
interrup.
| 06:40 |  | Jhenaidah-Kushtia 132kV Ckt-1 Scheduled S/D from Kushtia 132/33kV end Due to Jhenaidah
132kv Grid Bus upgradation work
| 06:41 |  | Jhenaidah-Kushtia 132kV Ckt-2 Scheduled S/D from Kushtia 132/33kV end Due to Jhenaidah
132kv Grid Bus Upgradation work
| 06:41 |  | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-1 Project Work S/D Due to Due
to Jhenaidah 132kv ss Bus upgradation work
| 06:42 |  | Jhenaidah-Jhenaidah(New) 132kV Ckt-3 Project Work S/D from Jhenaidah 230/132kV end Due to
Due to Jhenaidah 132kv ss Bus upgradation work
| 06:42 |  | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-2 Project Work S/D Due to Due
to Jhenaidah 132kv ss Bus upgradation work
| 06:42 |  | Chuadanga 132/33kV S/S Jhenaidah-Chuadanga Ckt-2 Project Work S/D Due to Project work
| 06:43 |  | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to 132kV | [7 empty] | 21.0MW load
|  |  | Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | [7 empty] | interrup. Magura
132/33kV end
| 06:43 |  | Jhenaidah-Magura 132 kV Ckt-2 Scheduled S/D from Magura 132/33kV end Due to 132kV | [7 empty] | 21.0MW load
|  |  | Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | [7 empty] | interrup. Magura
132/33kV end
| 06:44 |  | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D | [7 empty] | 40.0MW load
interrup.
| 06:44 |  | Magura-Narail 132kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to 132kV | [7 empty] | 19.0MW load
|  |  | Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | [7 empty] | interrup. Magura
132/33kV end
| 06:45 |  | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Forced S/D Due to Red Hot Maintenance
| 06:45 |  | Magura-Narail 132kV Ckt-2 Scheduled S/D from Magura 132/33kV end Due to 132kV | [7 empty] | 19.0MW load
|  |  | Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | [7 empty] | interrup. Magura
132/33kV end
| 06:57 |  | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to Red Hot Maintenance (Bhalika-02)
| 07:14 |  | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to Dead line checking
| 07:42 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Control
Panel Change Work
| 07:46 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to For annual maintenance
| 07:47 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to For annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 282 | 7808400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7604000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 199373 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 6994303 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 207360 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 60 | 1702080 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 132708 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 134319 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19.5 | 463800 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 439200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 405120 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 2776058 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 1061424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1505280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 396000 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 192284 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 301320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 410 | 8971772 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2667600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 2184.5 | 43962401
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 175624.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 100845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5283285 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3775439 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 610656 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 837539 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 860640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 965760 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 494291 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 403817 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 104 | 1498757 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 80 | 583364 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 108 | 453309 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1143 | 26372725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 5280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15410909.09 | U-2 Under Maintenance
Chattogram Area Total |  |  |  |  | 4895.72 | 2812.36 | 57854080.29
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 265 | 6711000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 230 | 5528000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 205 | 4922500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 870840 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 992160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1239000 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 78 | 1400072 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 278816 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2426660 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 144 | 2737440 | -
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1608960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 402797 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 433220 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 13 | 837900 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 64680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 408960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 457491 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1331 | 31320496
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 101 | 1715520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1144800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1626000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 292630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 77520 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 109080 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 233 | 4976900
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 711000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1596840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3631909 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711648 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1912320 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3764290 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 201792 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7159760 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8355000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1186 | 28436559
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 851 | 21170909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 106560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 103168 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 312 | 6448608 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 658800 | none
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 550800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 564 | 11752730 | Supply disruption due to bad weather in Indonesia
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1916 | 41703575
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 306 | 7366536 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 170304 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2683000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 26080000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5347120 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 32 | 414000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 267 | 5957000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3177 | -
Barishal Area Total |  |  |  |  | 2858 | 2001 | 48021137
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 371900 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 352675 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 192801 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 162 | 4656455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 328 | 8865454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 210000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 18 | 133032 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 603136 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 42 | 692832 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 167232 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1469 | 30955080 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 384000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 696983 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2236 | 48314940
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1023709 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 1217702 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39786 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1332713 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 221159 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1241280 | -
Rangpur Area Total |  |  |  |  | 950 | 250 | 5076349
Eastern Grid Total |  |  |  |  | 17383.852 | 7746.86 | 166550436.29
Western Grid Total |  |  |  |  | 10980.24 | 6403 | 143116001
National Grid Total |  |  |  |  | 28364.092 | 14149.86 | 309666437.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9129.01 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4339.2 | MW
i) Dhaka area |  |  | 4563.1 |  | MW | i) Khulna area |  |  |  | 1628 | MW
ii) Chattogram area |  |  | 1416.1 |  | MW | ii) Barishal area |  |  |  | 433 | MW
iii) Cumilla area |  |  | 1352.81 |  | MW | iii) Rajshahi area |  |  |  | 1348.2 | MW
iv) Mymensingh area |  |  | 1152 |  | MW | iv) Rangpur area |  |  |  | 930 | MW
v) Sylhet area |  |  | 645 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13468.21 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 18:00 | 133 | Niamatpur | 70 | 18:30
2 | AKSML | 122.5 | 01:00 | 68 | Ishurdi | 69 | 18:00 | 134 | Noapara | 33 | 00:00
3 | Aftabnagar | 38 | 00:00 | 69 | Jaldhaka | 82 | 18:00 | 135 | PHP | 9 | 16:00
4 | Agargaon | 121 | 13:00 | 70 | Jamalpur | 123 | 13:00 | 136 | Pabna | 88 | 19:00
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 129 | 18:00 | 137 | Palashbari | 120 | 18:30
6 | Amnura | 32 | 18:30 | 72 | Jhenaidah | 125 | 18:30 | 138 | Panchagarh | 58 | 18:30
7 | Ashuganj | 80 | 03:00 | 73 | Joydebpur | 136 | 00:00 | 139 | Patiya | 10 | 00:00
8 | BSRM | 200 | 19:30 | 74 | Joypurhat | 60 | 21:00 | 140 | Patuakhali | 66 | 00:00
9 | Bagerhat | 77 | 20:00 | 75 | Juldah | 14.5 | 00:00 | 141 | Payra | 34 | 22:00
10 | Bajitpur | 90 | 21:00 | 76 | KSRM | 30 | 10:00 | 142 | Postogola | 68 | 00:00
11 | Bakulia | 74 | 18:00 | 77 | Kabirpur | 191 | 00:00 | 143 | Purbachal | 22 | 13:00
12 | Banani | 33.4 | 18:30 | 78 | Kachua | 97 | 22:00 | 144 | Purbasadipur | 119 | 18:30
13 | Bangabhaban | 5 | 11:00 | 79 | Kallyanpur | 102 | 13:00 | 145 | Rahanpur | 34 | 21:00
14 | Barapukuria | 61 | 21:00 | 80 | Kalurghat | 42 | 01:00 | 146 | Rahim | 7 | 00:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 71 | 00:00 | 147 | Rajbari | 75 | 18:30
16 | Barishal | 109 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 119 | 01:00
17 | Barishal-230 | 94 | 21:00 | 83 | Kasba | 37 | 20:00 | 149 | Rajshahi | 115 | 21:00
18 | Baroaulia | 59 | 19:30 | 84 | Kazla | 92 | 13:00 | 150 | Rajshahi-230 | 88 | 13:00
19 | Baroirhat | 65 | 18:00 | 85 | Keranigonj | 82 | 22:00 | 151 | Ramganj | 118 | 22:00
20 | Bashundhara | 181 | 12:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 41 | 23:00
21 | BashundharaCement | 5 | 00:00 | 87 | Khulna | 59 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 88 | 18:00 | 88 | Khulshi | 175 | 18:30 | 154 | Rangpur | 136 | 18:30
23 | Benapole | 52 | 18:30 | 89 | Kishoreganj | 127 | 22:00 | 155 | Ruppur | 8 | 15:00
24 | Bhaluka | 143 | 21:00 | 90 | Kodda | 269 | 00:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 50 | 00:00 | 91 | Kulaura | 52 | 18:00 | 157 | Saidpur | 83 | 18:30
26 | Bhangura | 36 | 18:00 | 92 | Kurigram | 63 | 18:30 | 158 | Satkhira | 120 | 22:00
27 | Bheramara(GK) | 60 | 18:00 | 93 | Kushtia | 132 | 18:30 | 159 | Satmasjid | 94 | 13:00
28 | Bhulta | 209 | 20:00 | 94 | Laksam | 36 | 02:00 | 160 | Savar | 188 | 12:00
29 | Bog-Sherpur | 60 | 00:00 | 95 | Lakshmipur | 34 | 22:00 | 161 | SevenRings | 14.26 | 12:00
30 | Bogura | 159 | 00:00 | 96 | Lalbag | 56 | 00:00 | 162 | ShahCement | 26 | 11:00
31 | Borhanuddin | 94 | 00:00 | 97 | Lalmonirhat | 60 | 19:00 | 163 | Shahjadpur | 75 | 18:30
32 | Brahmanbaria | 137 | 22:00 | 98 | MI_Cement | 8.8 | 05:00 | 164 | Shahjibazar | 131 | 00:00
33 | Cantonment | 130 | 12:00 | 99 | Madanganj | 46 | 23:00 | 165 | Shahmirpur | 48 | 00:00
34 | Chandina | 35.84 | 00:00 | 100 | Madaripur | 109 | 22:00 | 166 | Shariatpur | 89 | 22:00
35 | Chandpur | 82 | 20:00 | 101 | Madartek | 88 | 23:00 | 167 | Sherpur | 136 | 22:00
36 | Chandraghona | 36 | 18:30 | 102 | Madunaghat | 54 | 23:00 | 168 | Shikalbaha | 27 | 01:00
37 | Chapai | 66 | 22:00 | 103 | Magura | 63 | 18:30 | 169 | Shitalakhya | 63.6 | 01:00
38 | Charsaidpur | 39 | 04:00 | 104 | Mahasthangarh | 72 | 00:00 | 170 | Sholosohor | 42 | 00:00
39 | Chauddagram | 74 | 22:00 | 105 | Maijdee | 33 | 21:00 | 171 | Shyampur | 122 | 00:00
40 | Chhatak | 41 | 22:00 | 106 | Manikganj | 120 | 18:30 | 172 | Siddhirganj | 108 | 00:00
41 | Chowmuhani | 177 | 22:00 | 107 | Maniknagar | 64 | 00:00 | 173 | Sirajganj | 96 | 18:30
42 | Chuadanga | 103 | 18:30 | 108 | Matarbari | 50 | 00:00 | 174 | Sonargaon | 113 | 01:00
43 | Coxsbazar | 132 | 18:30 | 109 | Matuail | 66 | 00:00 | 175 | Sreemongol | 85 | 18:00
44 | Cumilla(N) | 145 | 18:00 | 110 | Metrorail_Motijheel | 15 | 20:00 | 176 | Sreepur | 88 | 00:00
45 | Cumilla(S) | 145 | 00:00 | 111 | Metrorail_Uttara | 7 | 16:00 | 177 | Srinagar | 47.78 | 22:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 101 | 00:00 | 178 | Sunamganj | 68 | 22:00
47 | Daudkandi | 155 | 21:00 | 113 | Mirpur | 110 | 18:30 | 179 | Sylhet | 65 | 18:00
48 | DhakaUniversity | 42 | 12:00 | 114 | Mirsorai | 17 | 00:00 | 180 | Sylhet-132 | 120 | 00:00
49 | Dhamrai | 104 | 00:00 | 115 | Mirzapur | 46 | 18:00 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 108 | 18:00 | 116 | Mithapukur | 62 | 18:00 | 182 | Tangail | 158 | 18:30
51 | Dohazari | 97 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 21 | 18:00
52 | Faridpur | 152 | 22:00 | 118 | Mogbazar | 79.3 | 13:00 | 184 | Thakurgaon | 100 | 18:30
53 | Fatullah | 100 | 00:00 | 119 | Mongla | 40 | 00:00 | 185 | Tongi | 103 | 00:00
54 | Fenchuganj | 28 | 18:00 | 120 | Motijheel | 38 | 13:00 | 186 | Ullahpara | 38 | 19:30
55 | Feni | 120 | 22:00 | 121 | Muktagacha | 36 | 18:00 | 187 | Ullon | 61 | 21:00
56 | GPH | 33 | 18:00 | 122 | Munshiganj | 112 | 00:00 | 188 | Uttara | 64 | 18:00
57 | Ghatail | 88 | 18:00 | 123 | Muradnagar | 43 | 22:00 | 189 | UttaraNew | 73 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 201 | 21:00 | 190 | Zigatola | 69 | 13:00
59 | Ghorashal-230 | 100 | 00:00 | 125 | Naogaon | 120 | 22:00
60 | Goalpara | 36 | 13:00 | 126 | Narail | 56 | 18:30
61 | Gollamari | 90 | 00:00 | 127 | Narinda | 42 | 00:00
62 | Gopalganj | 103 | 19:00 | 128 | Narshingdi | 183 | 19:30
63 | Gulshan | 88 | 12:00 | 129 | Natore | 131 | 18:30
64 | Halishahar | 52 | 10:00 | 130 | Nawabganj | 47 | 22:00
65 | HaripurSBU | 130 | 01:00 | 131 | Netrakona | 147 | 18:30
66 | Hasnabad | 87 | 00:00 | 132 | New | 43 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13987.39 | 252 |  | 14250.73
1:00 | 13750.43 | 62 |  | 13815.22
2:00 | 13365.25 | 53 |  | 13420.64
3:00 | 12713.06 | 35 |  | 12749.64
4:00 | 12465.97 | 24 |  | 12491.05
5:00 | 12096.75 | 0 |  | 12096.75
6:00 | 11876.36 | 0 |  | 11876.36
7:00 | 11614.7 | 37 |  | 11653.37
8:00 | 11547.9 | 31 |  | 11580.3
9:00 | 11293.28 | 30 |  | 11324.63
10:00 | 11364.56 | 0 |  | 11364.56
11:00 | 11826.25 | 0 |  | 11826.25
12:00 | 12577.99 | 0 |  | 12577.99
13:00 | 12998.36 | 0 |  | 12998.36
14:00 | 12447.8 | 0 |  | 12447.8
15:00 | 12523.59 | 0 |  | 12523.59
16:00 | 12087.81 | 0 |  | 12087.81
17:00 | 11763.47 | 0 |  | 11763.47
18:00 | 13387 | 36 |  | 13424.62
19:00 | 14149.86 | 58 |  | 14210.47
19:30 | 14103.86 | 54 |  | 14160.29
20:00 | 14094.86 | 53 |  | 14150.25
21:00 | 13633.86 | 59 |  | 13695.86
22:00 | 14255.36 | 43 |  | 14300.3
23:00 | 14175.36 | 91 |  | 14270.36
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7330.5 | 6656.89 | 13987.39 | DAILY GENERATION CURVE
00:30 | 7325.75 | 6543.16 | 13868.91
01:00 | 7321 | 6429.43 | 13750.43 | 17-10-2025
01:30 | 7202.5 | 6355.34 | 13557.84
02:00 | 7084 | 6281.25 | 13365.25
02:30 | 6918.5 | 6120.655 | 13039.155
03:00 | 6753 | 5960.06 | 12713.06
03:30 | 6668 | 5921.515 | 12589.515
04:00 | 6583 | 5882.97 | 12465.97
04:30 | 6497 | 5784.36 | 12281.36
05:00 | 6411 | 5685.75 | 12096.75
05:30 | 6350.005 | 5636.55 | 11986.555
06:00 | 6289.01 | 5587.35 | 11876.36
06:30 | 6244.27 | 5501.26 | 11745.53
07:00 | 6199.53 | 5415.17 | 11614.7
07:30 | 6206.81 | 5374.49 | 11581.3
08:00 | 6214.09 | 5333.81 | 11547.9
08:30 | 6154.215 | 5266.375 | 11420.59
09:00 | 6094.34 | 5198.94 | 11293.28
09:30 | 6076.645 | 5252.275 | 11328.92
10:00 | 6058.95 | 5305.61 | 11364.56
10:30 | 6099.2 | 5496.205 | 11595.405
11:00 | 6139.45 | 5686.8 | 11826.25
11:30 | 6323.6 | 5878.52 | 12202.12
12:00 | 6507.75 | 6070.24 | 12577.99
12:30 | 6720.265 | 6067.91 | 12788.175
13:00 | 6932.78 | 6065.58 | 12998.36
13:30 | 6791.43 | 5931.65 | 12723.08
14:00 | 6650.08 | 5797.72 | 12447.8
14:30 | 6653.475 | 5832.22 | 12485.695
15:00 | 6656.87 | 5866.72 | 12523.59
15:30 | 6552.58 | 5753.12 | 12305.7
16:00 | 6448.29 | 5639.52 | 12087.81
16:30 | 6384.225 | 5541.415 | 11925.64
17:00 | 6320.16 | 5443.31 | 11763.47
17:30 | 6748.58 | 5826.655 | 12575.235
18:00 | 7177 | 6210 | 13387
18:30 | 7461.93 | 6306.5 | 13768.43
19:00 | 7746.86 | 6403 | 14149.86
19:30 | 7703.86 | 6400 | 14103.86
20:00 | 7687.86 | 6407 | 14094.86
20:30 | 7703.36 | 6161 | 13864.36 |  | Executive Engineer
21:00 | 7718.86 | 5915 | 13633.86 |  | Network Operation Division
21:30 | 7869.11 | 6075.5 | 13944.61
22:00 | 8019.36 | 6236 | 14255.36
22:30 | 7960.86 | 6254.5 | 14215.36
23:00 | 7902.36 | 6273 | 14175.36

## En-Curve
QF-LDC-12
Date | 17-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3013 | 1665 | 874 | 38 | 84 | 1470.89 | 218 | 4172 | 0 | 870 | 1582.5 | 0 | 0 | 0 | 252 | DAILY ENERGY CURVE
00:30 | 3046.5 | 1648 | 874 | 38 | 79 | 1465.16 | 218 | 4191.5 | 0 | 845 | 1463.75 | 0 | 0 | 0 | 157 | 17-10-2025
01:00 | 3080 | 1631 | 874 | 38 | 74 | 1459.43 | 218 | 4211 | 0 | 820 | 1345 | 0 | 0 | 0 | 62
01:30 | 3098.5 | 1639 | 873.5 | 38 | 76 | 1461.84 | 218.5 | 4155 | 0 | 745.5 | 1251.5 | 0 | 0 | 0.5 | 57.5 | Energy Generated | 309.6664 |  | MKWHr
02:00 | 3117 | 1647 | 873 | 38 | 78 | 1464.25 | 219 | 4099 | 0 | 671 | 1158 | 0 | 0 | 1 | 53 | Energy not Served | 0.864 |  | MKWHr
02:30 | 3132 | 1646 | 873 | 38 | 75 | 1462.155 | 219.5 | 4116.5 | 0 | 523 | 953.5 | 0 | 0 | 0.5 | 44 | Total Energy Requirement | 310.5304 |  | MKWHr
03:00 | 3147 | 1645 | 873 | 38 | 72 | 1460.06 | 220 | 4134 | 0 | 375 | 749 | 0 | 0 | 0 | 35
03:30 | 3155 | 1654.5 | 873 | 38 | 73 | 1466.515 | 220.5 | 4142 | 0 | 321.5 | 645.5 | 0 | 0 | 0 | 29.5
04:00 | 3163 | 1664 | 873 | 38 | 74 | 1472.97 | 221 | 4150 | 0 | 268 | 542 | 0 | 0 | 0 | 24
04:30 | 3167.5 | 1652 | 873 | 38 | 73 | 1412.86 | 221 | 4122.5 | 0 | 268 | 453.5 | 0 | 0 | 0 | 12
05:00 | 3172 | 1640 | 873 | 38 | 72 | 1352.75 | 221 | 4095 | 0 | 268 | 365 | 0 | 0 | 0 | 0
05:30 | 3172 | 1644.5 | 873 | 38 | 70 | 1337.55 | 221.5 | 4015.5 | 0.005 | 268 | 346.5 | 0 | 0 | 0 | 0
06:00 | 3172 | 1649 | 873 | 38 | 68 | 1322.35 | 222 | 3936 | 0.01 | 268 | 328 | 0 | 0 | 0 | 0
06:30 | 3186.5 | 1620 | 873 | 38 | 63 | 1224.175 | 222 | 3849.5 | 48.855 | 268 | 352.5 | 0 | 0 | 0 | 18.5
07:00 | 3201 | 1591 | 873 | 38 | 58 | 1126 | 222 | 3763 | 97.7 | 268 | 377 | 0 | 0 | 0 | 37
07:30 | 3193.5 | 1595 | 886 | 38 | 56 | 1075.845 | 222 | 3692.5 | 198.455 | 268 | 356 | 0 | 0 | 0 | 34
08:00 | 3186 | 1599 | 899 | 38 | 54 | 1025.69 | 222 | 3622 | 299.21 | 268 | 335 | 0 | 0 | 0 | 31
08:30 | 3172 | 1568.5 | 899 | 38 | 52 | 979.79 | 222 | 3513.5 | 387.8 | 260.5 | 327.5 | 0 | 0 | 0 | 30.5
09:00 | 3158 | 1538 | 899 | 38 | 50 | 933.89 | 222 | 3405 | 476.39 | 253 | 320 | 0 | 0 | 0 | 30
09:30 | 3194 | 1558.35 | 888.5 | 38 | 50 | 930.405 | 222 | 3400 | 543.665 | 219 | 285 | 0 | 0 | 0 | 15
10:00 | 3230 | 1578.7 | 878 | 38 | 50 | 926.92 | 222 | 3395 | 610.94 | 185 | 250 | 0 | 0 | 0 | 0
10:30 | 3283.5 | 1580.35 | 878 | 38 | 52 | 955.4 | 222 | 3439.5 | 653.155 | 193 | 300.5 | 0 | 0 | 0 | 0
11:00 | 3337 | 1582 | 878 | 38 | 54 | 983.88 | 222 | 3484 | 695.37 | 201 | 351 | 0 | 0 | 0 | 0
11:30 | 3364 | 1476.75 | 878 | 38 | 56 | 1007.215 | 220.5 | 3702.05 | 685.355 | 267 | 506.25 | 0 | 0 | 1 | 0
12:00 | 3391 | 1371.5 | 878 | 38 | 58 | 1030.55 | 219 | 3920.1 | 675.34 | 333 | 661.5 | 0 | 0 | 2 | 0
12:30 | 3366 | 1455.5 | 878 | 38 | 61 | 1086.805 | 218.5 | 3962.05 | 657.32 | 316.5 | 747.5 | 0 | 0 | 1 | 0
13:00 | 3341 | 1539.5 | 878 | 38 | 64 | 1143.06 | 218 | 4004 | 639.3 | 300 | 833.5 | 0 | 0 | 0 | 0
13:30 | 3303 | 1593.5 | 878 | 38 | 63 | 1152.53 | 218 | 3954 | 564.05 | 241.5 | 717.5 | 0 | 0 | 0 | 0
14:00 | 3265 | 1647.5 | 878 | 38 | 62 | 1162 | 218 | 3904 | 488.8 | 183 | 601.5 | 0 | 0 | 0 | 0
14:30 | 3245 | 1689.25 | 878 | 38 | 65 | 1220.5 | 220 | 3911.5 | 449.195 | 183 | 586.25 | 0 | 0 | 0 | 0
15:00 | 3225 | 1731 | 878 | 38 | 68 | 1279 | 222 | 3919 | 409.59 | 183 | 571 | 0 | 0 | 0 | 0
15:30 | 3178.5 | 1711 | 883 | 38 | 66 | 1275.5 | 222 | 3928 | 308.7 | 168 | 527 | 0 | 0 | 0 | 0
16:00 | 3132 | 1691 | 888 | 38 | 64 | 1272 | 222 | 3937 | 207.81 | 153 | 483 | 0 | 0 | 0 | 0
16:30 | 3093 | 1634 | 888 | 38 | 62 | 1262.5 | 222 | 3936 | 120.64 | 163 | 506.5 | 0 | 0 | 0 | 0
17:00 | 3054 | 1577 | 888 | 38 | 60 | 1253 | 222 | 3935 | 33.47 | 173 | 530 | 0 | 0 | 0 | 0
17:30 | 3158.5 | 1591 | 869 | 38 | 68 | 1343 | 222 | 4014.5 | 16.735 | 397.5 | 857 | 0 | 0 | 0 | 18
18:00 | 3263 | 1605 | 850 | 38 | 76 | 1433 | 222 | 4094 | 0 | 622 | 1184 | 0 | 0 | 0 | 36
18:30 | 3267 | 1608.25 | 850.5 | 38 | 76 | 1451 | 222 | 4079.5 | 0 | 687.5 | 1488.68 | 0 | 0 | 0 | 47
19:00 | 3271 | 1611.5 | 851 | 38 | 76 | 1469 | 222 | 4065 | 0 | 753 | 1793.36 | 0 | 0 | 0 | 58
19:30 | 3378 | 1630.5 | 858 | 38 | 76 | 1459 | 222 | 4096 | 0 | 651 | 1695.36 | 0 | 0 | 0 | 54
20:00 | 3351 | 1608.5 | 858 | 38 | 70 | 1463 | 222 | 4114 | 0 | 676 | 1694.36 | 0 | 0 | 0 | 53
20:30 | 3399 | 1618 | 858 | 38 | 72 | 1463.5 | 222 | 3838 | 0 | 649.5 | 1706.36 | 0 | 0 | 0 | 56
21:00 | 3447 | 1627.5 | 858 | 38 | 74 | 1464 | 222 | 3562 | 0 | 623 | 1718.36 | 0 | 0 | 0 | 59
21:30 | 3482.5 | 1606.25 | 861 | 38 | 74 | 1470.5 | 222 | 3641.5 | 0 | 711.5 | 1837.36 | 0 | 0 | 0 | 51
22:00 | 3518 | 1585 | 864 | 38 | 74 | 1477 | 222 | 3721 | 0 | 800 | 1956.36 | 0 | 0 | 0 | 43
22:30 | 3467 | 1600.5 | 864 | 38 | 77 | 1477 | 222 | 3739 | 0 | 796 | 1934.86 | 0 | 0 | 0 | 67
23:00 | 3416 | 1616 | 864 | 38 | 80 | 1477 | 222 | 3757 | 0 | 792 | 1913.36 | 0 | 0 | 0 | 91
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 08:00 | 373 | 22:00 | Payra | 411 | 09:00 | 404 | 21:00
Ashuganj | 406 | 17:00 | 386 | 11:00 | Rahanpur | 402 | 09:00 | 389 | 04:00
Bhulta | 397 | 08:00 | 384 | 12:00 | Rampal | 401 | 08:00 | 378 | 22:00
Bibiana | 388 | 09:00 | 381 | 03:00
BIPTC | 404 | 06:00 | 394 | 15:00
Bogura | 391 | 09:00 | 378 | 04:00
Gopalganj | 397 | 08:00 | 382 | 21:00
Kaliakoir | 376 | 17:00 | 367 | 03:00
Madunaghat | 393 | 08:00 | 388 | 04:00
Meghnaghat | 387 | 08:00 | 378 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 08:00 | 220 | 18:30 | Kaliakoir | 234 | 17:00 | 227 | 03:00
AKSML | 234 | 18:00 | 220 | 10:00 | Keranigonj | 226 | 08:00 | 220 | 00:00
Aminbazar | 230 | 08:00 | 223 | 00:00 | Khulna(S) | 232 | 09:00 | 217 | 22:00
Ashuganj | 231 | 17:00 | 223 | 11:00 | Madunaghat | 235 | 18:30 | 229 | 16:00
Ashuganj-400 | 230 | 17:00 | 220 | 11:00 | Madunaghat-400 | 235 | 19:30 | 229 | 04:00
Baghabari | 235 | 07:00 | 228 | 00:00 | Maniknagar | 221 | 07:00 | 215 | 00:00
Barapukuria | 221 | 11:00 | 214 | 18:30 | Meghnaghat | 229 | 17:00 | 222 | 01:00
Barapukuria-230 | 221 | 11:00 | 212 | 18:00 | Meghnaghat-400 | 225 | 08:00 | 219 | 00:00
Barishal | 234 | 09:00 | 226 | 21:00 | Mirsorai | 234 | 18:30 | 220 | 03:00
Bheramara | 233 | 06:00 | 227 | 18:00 | Rajshahi | 232 | 08:00 | 225 | 13:00
Bhulta | 228 | 07:00 | 215 | 00:00 | Rampal | 231 | 08:00 | 216 | 22:00
Bibiana | 230 | 17:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 09:00 | 226 | 22:00 | Rampura | 226 | 07:00 | 216 | 12:00
Bogura | 238 | 09:00 | 230 | 03:00 | Shikalbaha | 234 | 18:30 | 226 | 06:00
Bogura-400 | 238 | 10:00 | 231 | 01:00 | Shyampur | 225 | 17:00 | 218 | 00:00
Borhanuddin | 237 | 07:00 | 231 | 21:00 | Siddhirganj | 223 | 07:00 | 217 | 01:00
BSRM | 230 | 18:30 | 220 | 03:00 | Sirajgonj | 240 | 09:00 | 235 | 01:00
Cumilla(N) | 226 | 18:30 | 221 | 00:00 | Sreepur | 228 | 07:00 | 222 | 05:00
Faridpur | 231 | 07:00 | 222 | 22:00 | Tongi | 230 | 17:00 | 222 | 00:00
Fenchuganj | 229 | 06:00 | 227 | 00:00
Ghorashal | 230 | 00:00 | 225 | 01:00
Ghorashal-230 | 225 | 07:00 | 218 | 12:00
Gopalganj | 233 | 08:00 | 224 | 21:00
GPH | 232 | 18:30 | 221 | 10:00
Haripur | 222 | 08:00 | 216 | 00:00
Hasnabad | 227 | 17:00 | 219 | 00:00
Hathazari | 233 | 18:30 | 224 | 01:00
Ishurdi | 237 | 09:00 | 229 | 19:30
Jhenaidah | 232 | 06:00 | 219 | 22:00
Kachua | 231 | 08:00 | 219 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 07:00 | 130 | 12:00 | Lalmonirhat | 128 | 21:00 | 122 | 18:30
Agargaon | 134 | 06:00 | 130 | 00:00 | Madanganj | 128 | 07:00 | 125 | 00:00
Agrabad | 133 | 18:00 | 129 | 14:00 | Madaripur | 136 | 07:00 | 129 | 22:00
AKS | 132 | 18:30 | 128 | 14:00 | Madartek | 134 | 06:00 | 128 | 12:00
Aminbazar | 137 | 18:30 | 131 | 00:00 | Madunaghat | 136 | 18:30 | 132 | 05:00
Amnura | 135 | 18:00 | 130 | 19:30 | Magura | 137 | 06:00 | 125 | 22:00
Ashuganj | 140 | 17:00 | 135 | 00:00 | Mahasthangarh | 132 | 12:00 | 127 | 18:30
Bagerhat | 135 | 10:00 | 120 | 00:00 | Maijdee | 132 | 08:00 | 130 | 16:00
Bajitpur | 128 | 06:00 | 124 | 01:00 | Manikganj | 130 | 09:00 | 130 | 09:00
Bakulia | 135 | 18:00 | 131 | 16:00 | Maniknagar | 134 | 08:00 | 129 | 00:00
Banani | 135 | 07:00 | 129 | 12:00 | Matarbari | 121 | 15:00 | 111 | 00:00
Bangabhaban | 134 | 08:00 | 130 | 00:00 | Matuail | 130 | 17:00 | 125 | 00:00
Barapukuria | 135 | 11:00 | 128 | 18:30 | Metrorail_Motijheel | 134 | 08:00 | 129 | 00:00
Barguna | 137 | 17:00 | 133 | 00:00 | Metrorail_Uttara | 135 | 19:00 | 129 | 00:00
Barishal | 134 | 08:00 | 130 | 00:00 | Millgate | 133 | 06:00 | 129 | 00:00
Barishal-230 | 135 | 07:00 | 128 | 22:00 | Mirpur | 135 | 17:00 | 129 | 00:00
Baroaulia | 134 | 07:00 | 132 | 01:00 | Mirzapur | 130 | 06:00 | 127 | 00:00
Baroirhat | 132 | 01:00 | 128 | 16:00 | Mithapukur | 132 | 21:00 | 123 | 23:00
Bashundhara | 135 | 06:00 | 128 | 12:00 | MI_Cement | 134 | 19:00 | 128 | 00:00
BashundharaCement | 128 | 07:00 | 125 | 00:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 17:00 | 123 | 22:00 | Mogbazar | 136 | 07:00 | 130 | 12:00
Benapole | 135 | 09:00 | 121 | 22:00 | Mongla | 135 | 08:00 | 122 | 21:00
Bhaluka | 130 | 07:00 | 124 | 18:30 | Motijheel | 134 | 08:00 | 130 | 00:00
Bhandaria | 131 | 09:00 | 115 | 23:00 | Muktagacha | 129 | 10:00 | 119 | 00:00
Bhangura | 134 | 04:00 | 130 | 20:00 | Munshiganj | 128 | 18:00 | 123 | 00:00
Bheramara | 138 | 06:00 | 134 | 00:00 | Muradnagar | 127 | 08:00 | 122 | 04:00
Bheramara(GK) | 137 | 06:00 | 133 | 00:00 | Mymensingh | 129 | 10:00 | 113 | 20:00
Bhulta | 128 | 13:00 | 121 | 01:00 | Naogaon | 130 | 10:00 | 126 | 01:00
Bog-Sherpur | 134 | 09:00 | 129 | 18:30 | Narail | 137 | 06:00 | 126 | 22:00
Bogura | 134 | 09:00 | 130 | 01:00 | Narinda | 134 | 8:00 | 129 | 0:00
Bogura-230 | 135 | 11:00 | 130 | 01:00 | Narshingdi | 133 | 10:00 | 119 | 00:00
Brahmanbaria | 133 | 17:00 | 126 | 19:30 | Natore | 134 | 06:00 | 130 | 00:00
Cantonment | 135 | 17:00 | 130 | 00:00 | Nawabganj | 134 | 08:00 | 129 | 00:00
Chandina | 132 | 08:00 | 127 | 02:00 | Netrakona | 122 | 06:00 | 111 | 20:00
Chandpur | 136 | 06:00 | 132 | 14:00 | New | 134 | 17:00 | 129 | 00:00
Chandraghona | 136 | 07:00 | 133 | 03:00 | Niamatpur | 136 | 09:00 | 132 | 18:00
Chapai | 134 | 09:00 | 129 | 22:00 | Noapara | 137 | 09:00 | 125 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 17:00 | 124 | 00:00 | Pabna | 136 | 07:00 | 131 | 22:00
Chauddagram | 131 | 08:00 | 126 | 03:00 | Palashbari | 129 | 11:00 | 123 | 18:30
Chhatak | 127 | 07:00 | 121 | 19:30 | Panchagarh | 136 | 02:00 | 122 | 08:00
Chowmuhani | 132 | 07:00 | 128 | 14:00 | Patiya | 133 | 08:00 | 128 | 04:00
Chuadanga | 134 | 08:00 | 122 | 22:00 | Patuakhali | 137 | 19:00 | 134 | 00:00
Coxsbazar | 120 | 15:00 | 112 | 00:00 | Payra | 137 | 09:00 | 135 | 00:00
Cumilla(N) | 132 | 18:30 | 128 | 14:00 | PHP | 131 | 07:00 | 127 | 15:00
Cumilla(S) | 131 | 05:00 | 128 | 13:00 | Postogola | 135 | 08:00 | 129 | 00:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 06:00 | 128 | 12:00
Daudkandi | 125 | 17:00 | 118 | 04:00 | Purbasadipur | 132 | 02:00 | 122 | 08:00
DhakaUniversity | 136 | 06:00 | 129 | 12:00 | Rahanpur | 137 | 07:00 | 133 | 01:00
Dhamrai | 133 | 04:00 | 129 | 00:00 | Rahanpur-400 | 138 | 09:00 | 134 | 01:00
Dhanmondi | 136 | 06:00 | 129 | 12:00 | Rahim | 129 | 16:00 | 125 | 00:00
Dohazari | 131 | 23:00 | 125 | 00:00 | Rajbari | 136 | 08:00 | 133 | 14:00
Faridpur | 136 | 08:00 | 131 | 22:00 | Rajendrapur | 136 | 19:00 | 124 | 12:00
Fatullah | 137 | 19:00 | 131 | 00:00 | Rajshahi | 134 | 06:00 | 130 | 00:00
Fenchuganj | 135 | 06:00 | 133 | 00:00 | Rajshahi-230 | 133 | 06:00 | 130 | 00:00
Feni | 132 | 18:00 | 127 | 16:00 | Ramganj | 132 | 06:00 | 128 | 03:00
Ghatail | 126 | 06:00 | 119 | 00:00 | Rampur | 132 | 08:00 | 129 | 03:00
Ghorashal | 137 | 17:00 | 131 | 11:00 | Rampura | 135 | 06:00 | 129 | 12:00
Goalpara | 137 | 09:00 | 127 | 22:00 | Rangamati | 134 | 06:00 | 132 | 14:00
Gollamari | 138 | 06:00 | 128 | 22:00 | Rangpur | 133 | 21:00 | 126 | 18:30
Gopalganj | 136 | 08:00 | 128 | 21:00 | Ruppur | 138 | 08:00 | 134 | 00:00
Gopalganj-400 | 137 | 08:00 | 131 | 21:00 | Saidpur | 131 | 21:00 | 123 | 18:30
Gulshan | 135 | 06:00 | 129 | 12:00 | Satkhira | 136 | 09:00 | 122 | 22:00
Halishahar | 134 | 21:00 | 130 | 03:00 | Satmasjid | 134 | 07:00 | 130 | 00:00
Haripur | 130 | 17:00 | 126 | 00:00 | Savar | 135 | 18:30 | 128 | 00:00
HaripurSBU | 130 | 18:00 | 126 | 00:00 | SevenRings | 138 | 21:00 | 130 | 12:00
Hasnabad | 135 | 18:00 | 130 | 00:00 | ShahCement | 130 | 17:00 | 124 | 00:00
Hathazari | 135 | 18:00 | 132 | 04:00 | Shahjadpur | 138 | 10:00 | 134 | 18:30
Ishurdi | 139 | 09:00 | 134 | 22:00 | Shahjibazar | 134 | 17:00 | 127 | 03:00
Jaldhaka | 129 | 21:00 | 121 | 18:30 | Shahmirpur | 134 | 19:00 | 132 | 00:00
Jamalpur | 128 | 10:00 | 117 | 00:00 | Shariatpur | 135 | 08:00 | 127 | 22:00
Jashore | 133 | 06:00 | 122 | 21:00 | Sherpur | 125 | 10:00 | 113 | 00:00
Jhenaidah | 137 | 05:00 | 125 | 18:00 | Shikalbaha | 124 | 18:00 | 120 | 03:00
Jhenaidah-230 | 138 | 06:00 | 128 | 22:00 | Shikalbaha-230 | 135 | 08:00 | 131 | 03:00
Joydebpur | 136 | 21:00 | 124 | 12:00 | Shitalakhya | 134 | 19:00 | 128 | 00:00
Joypurhat | 128 | 06:00 | 123 | 01:00 | Sholosohor | 135 | 18:00 | 132 | 03:00
Juldah | 134 | 18:00 | 131 | 12:00 | Shyampur | 136 | 20:00 | 132 | 00:00
Kabirpur | 136 | 18:30 | 124 | 20:00 | Shyampur-230 | 137 | 19:00 | 132 | 00:00
Kachua | 136 | 08:00 | 132 | 03:00 | Siddhirganj | 131 | 17:00 | 125 | 00:00
Kaliakoir | 136 | 17:00 | 132 | 00:00 | Sirajganj | 134 | 10:00 | 127 | 00:00
Kallyanpur | 137 | 18:30 | 130 | 00:00 | Sonargaon | 128 | 08:00 | 124 | 00:00
Kalurghat | 136 | 18:30 | 132 | 04:00 | Sreemongol | 133 | 17:00 | 127 | 00:00
Kamrangirchar | 135 | 06:00 | 129 | 00:00 | Sreepur | 133 | 07:00 | 128 | 05:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 134 | 08:00 | 129 | 00:00
Kasba | 127 | 09:00 | 121 | 04:00 | SSM | 138 | 00:00 | 132 | 02:00
Kazla | 133 | 10:00 | 130 | 00:00 | Sunamganj | 125 | 07:00 | 119 | 18:00
Keranigonj | 134 | 08:00 | 130 | 00:00 | Sylhet | 129 | 07:00 | 126 | 00:00
Khagrachori | 133 | 03:00 | 130 | 14:00 | Sylhet-132 | 129 | 00:00 | 127 | 19:30
Khulna | 137 | 09:00 | 126 | 21:00 | Tangail | 127 | 06:00 | 122 | 00:00
Khulna(S) | 139 | 09:00 | 128 | 22:00 | Taraganj | 132 | 06:00 | 125 | 07:00
Khulshi | 132 | 09:00 | 129 | 03:00 | Thakurgaon | 134 | 18:00 | 118 | 08:00
Kishoreganj | 129 | 09:00 | 119 | 20:00 | TK | 135 | 18:00 | 132 | 12:00
Kodda | 136 | 17:00 | 124 | 12:00 | Tongi | 135 | 07:00 | 130 | 13:00
KSRM | 135 | 09:00 | 130 | 05:00 | Ullahpara | 135 | 09:00 | 130 | 18:00
Kulaura | 134 | 06:00 | 132 | 00:00 | Ullon | 135 | 06:00 | 128 | 12:00
Kurigram | 131 | 21:00 | 121 | 18:30 | Uttara | 135 | 21:00 | 128 | 00:00
Kushtia | 136 | 05:00 | 130 | 00:00 | UttaraNew | 135 | 19:00 | 129 | 00:00
Laksam | 134 | 00:00 | 131 | 14:00 | Zigatola | 135 | 08:00 | 129 | 00:00
Lakshmipur | 132 | 08:00 | 127 | 02:00
Lalbag | 136 | 15:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division