## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-10-2025 | during | 20-10-2025 | during | 20-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 378 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 17.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 104 | 135 | 149.36 | 149.36 | 140 | 140 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 20 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 261 | 91 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 15 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 162 | 162 | 17 | 17 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 356 | 379 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1971.5 | 2045.5 | 5637.4 | 5605.4 | 4526.75 | 4552.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 17 | 17 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 222 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 154 | 154 | 154 | 154 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 67 | 70 | 70 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 50 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 23 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 53 | 96 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.45 | 0 | 4.1 | 0 | 4.1 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 32 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 94 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 100 | 92 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 153 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1182 | 1195 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2623.45 | 2906.36 | 3614.82 | 3606.72 | 3248.46 | 3264.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 337 | 339 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 335 | 380 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 43 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 140 | 41 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 115 | 123 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 100 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 59 | 125 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 69 | 90 | 160 | 160 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 7 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 16 | 115 | 115 | 39 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 43 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1518 | 1546 | 2289.05 | 2224.05 | 1935.05 | 1919.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-10-2025 | during | 20-10-2025 | during | 20-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 83 | 73 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 68 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.69 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 2 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 250.69 | 206 | 401.3 | 349 | 347.8 | 295.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 161 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 11 | 10 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 330 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 311 | 365 | 365 | 365 | 365 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1185 | 1195 | 1258 | 1258 | 1254 | 1254
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 873 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 352 | 349 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 83.78 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 308 | 314 | 340 | 340 | 1000 | 1000 | U1 Partial load due to PA fan outage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1654.78 | 1659 | 2743 | 2658 | 2642 | 2557
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 298 | 295 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 2 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1112 | 1170 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 266 | 281 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 2025.44 | 2085 | 2147 | 2146 | 2014 | 2013
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 62.68 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 191 | 203 | 214 | 214 | 193 | 193 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 95 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.93 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1142 | 1465.97 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 67.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 68 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1950.8 | 2447.97 | 3181.47 | 3014.87 | 3086.89 | 2920.29
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 41 | 42 | 0 | 0 | 48 | 48 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 5 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.5 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 181 | 0 | 184.49 | 0 | 184.49 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 259.5 | 264 | 468.49 | 248 | 496.49 | 276
System Total |  |  |  |  | 28823.2 | 28364.092 | 13439.16 | 14354.83 | 21740.53 | 21110.04 | 19551.44 | 19051.95
Forecast Scenario (20-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14780 |  | 0 |  | 14780
|  |  |  | 1:00 | 14150 |  | 0 |  | 14150
|  |  |  | 2:00 | 13800 |  | 0 |  | 13800
|  |  |  | 3:00 | 13407 |  | 0 |  | 13407
|  |  |  | 4:00 | 12940 |  | 0 |  | 12940
|  |  |  | 5:00 | 12490 |  | 0 |  | 12490
|  |  |  | 6:00 | 12170 |  | 0 |  | 12170
|  |  |  | 7:00 | 12220 |  | 0 |  | 12220
|  |  |  | 8:00 | 12460 |  | 0 |  | 12460
|  |  |  | 9:00 | 12540 |  | 0 |  | 12540
|  |  |  | 10:00 | 12710 |  | 0 |  | 12710
|  |  |  | 11:00 | 13130 |  | 0 |  | 13130
|  |  |  | 12:00 | 13470 |  | 0 |  | 13470
|  |  |  | 13:00 | 13580 |  | 0 |  | 13580
|  |  |  | 14:00 | 13500 |  | 0 |  | 13500
|  |  |  | 15:00 | 13490 |  | 0 |  | 13490
|  |  |  | 16:00 | 13430 |  | 0 |  | 13430
|  |  |  | 17:00 | 13280 |  | 0 |  | 13280
|  |  |  | 18:00 | 14440 |  | 0 |  | 14440
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 14750 |  | 0 |  | 14750
|  |  |  | 19:30 | 14850 |  | 0 |  | 14850
|  |  |  | 20:00 | 14800 |  | 0 |  | 14800
|  |  |  | 21:00 | 14700 |  | 0 |  | 14700
|  |  |  | 22:00 | 14600 |  | 0 |  | 14600
|  |  |  | 23:00 | 14500 |  | 0 |  | 14500
Probable Maximum Temperature: |  |  | 34.20°C
Probable Maximum Demand at Day Peak: |  |  | 13470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14850.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14850.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 325.337 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:13 hrs on 20-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-10-2025 | [28 empty] | Date: | 19-10-2025 | [28 empty] | Date: | 19-10-2025 | [28 empty] | Date: | 19-10-2025 | [28 empty] | Date: | 19-10-2025 | [14 empty] | Date: | 19-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 17 | 88 | 137 | 278 | 15 | 0 | 17 | 0 | 300 | 0 | 360 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 100 | 16 | 92 | 0 | 0 | 50 | 60 | 54.36 | 0 | 0 | 0 | 218 | 95 | 25 | 650 | 17 | 0 | 0 | 17 | 0 | 155 | 0 | 0 | 0 | 1226 | 0 | 51 | 127 | 8 | 415 | 351 | 0 | 44 | 0 | 38 | 17 | 103 | 129 | 0 | 19 | 107 | 84 | 43 | 0 | 29 | 325 | 0 | 311 | 30 | 67 | 159 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 105 | 0 | 0 | 0 | 7925.36 | 873 | 360 | 0 | 29 | 29 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 340 | 0 | 1461 | 0 | 40 | 0 | 35 | 113 | 0 | 94 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 44 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 110 | 220 | 0 | 301 | 1222 | 17 | 6690.2 | 14615.56 | 106.34
01:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 33 | 123 | 277 | 15 | 0 | 17 | 0 | 300 | 0 | 320 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 91 | 16 | 92 | 0 | 0 | 50 | 60 | 54.36 | 0 | 0 | 0 | 217 | 94 | 27 | 650 | 17 | 0 | 0 | 8 | 0 | 154 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 8 | 415 | 300 | 0 | 45 | 0 | 38 | 0 | 102 | 88 | 0 | 19 | 105 | 80 | 43 | 0 | 29 | 315 | 0 | 311 | 30 | 67 | 158 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 105 | 0 | 0 | 0 | 7586.36 | 873 | 360 | 0 | 20 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1465 | 0 | 40 | 0 | 35 | 50 | 0 | 0 | 22 | 52 | 0 | 0 | 25 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 43 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 110 | 220 | 0 | 302 | 1225 | 17 | 6413 | 13999.36 | 106.33
02:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 123 | 277 | 15 | 0 | 17 | 0 | 300 | 0 | 320 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 96 | 16 | 91 | 0 | 0 | 50 | 60 | 17 | 0 | 0 | 0 | 217 | 95 | 30 | 650 | 17 | 0 | 0 | 8 | 0 | 154 | 0 | 0 | 0 | 1164 | 0 | 51 | 128 | 8 | 415 | 300 | 0 | 44 | 0 | 38 | 0 | 103 | 70 | 0 | 19 | 106 | 74 | 43 | 0 | 29 | 315 | 0 | 311 | 30 | 67 | 159 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 105 | 0 | 0 | 0 | 7464 | 874 | 360 | 0 | 20 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1465 | 0 | 40 | 0 | 35 | 50 | 0 | 0 | 22 | 52 | 0 | 0 | 25 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 43 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 287 | 110 | 220 | 0 | 301 | 1200 | 17 | 6370 | 13834 | 106.33
03:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 17 | 90 | 277 | 15 | 0 | 17 | 0 | 300 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 92 | 16 | 92 | 0 | 0 | 50 | 60 | 17 | 0 | 0 | 0 | 216 | 94 | 41 | 650 | 17 | 0 | 0 | 8 | 0 | 154 | 0 | 0 | 0 | 1155 | 0 | 51 | 130 | 8 | 415 | 300 | 0 | 45 | 0 | 38 | 0 | 103 | 70 | 0 | 19 | 26 | 70 | 16 | 0 | 29 | 320 | 0 | 311 | 30 | 67 | 156 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 105 | 0 | 0 | 0 | 7307 | 873 | 360 | 0 | 20 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1462 | 0 | 40 | 0 | 35 | 50 | 0 | 0 | 22 | 16 | 0 | 0 | 25 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 43 | 110 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 270 | 110 | 220 | 0 | 301 | 1110 | 17 | 6200 | 13507 | 106.32
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 17 | 30 | 277 | 15 | 0 | 17 | 0 | 300 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 45 | 16 | 45 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 217 | 51 | 41 | 650 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 1162 | 0 | 51 | 133 | 8 | 415 | 300 | 0 | 45 | 0 | 38 | 0 | 104 | 70 | 0 | 19 | 0 | 70 | 0 | 0 | 29 | 310 | 0 | 312 | 30 | 67 | 155 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 106 | 0 | 0 | 0 | 7023 | 873 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1466 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 43 | 50 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 110 | 220 | 0 | 301 | 1108 | 17 | 6017 | 13040 | 106.32
05:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 17 | 30 | 145 | 15 | 0 | 17 | 0 | 300 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 42 | 16 | 24 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 217 | 49 | 41 | 650 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 1160 | 0 | 51 | 135 | 8 | 415 | 300 | 0 | 45 | 0 | 38 | 0 | 104 | 69 | 0 | 19 | 0 | 68 | 0 | 0 | 29 | 305 | 0 | 312 | 30 | 67 | 150 | 12 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 68 | 49 | 107 | 0 | 0 | 4 | 6801 | 874 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 42 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 110 | 220 | 0 | 302 | 1095 | 17 | 5795 | 12596 | 106.31
06:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 17 | 30 | 45 | 0 | 0 | 17 | 0 | 300 | 0 | 335 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 17 | 16 | 24 | 0 | 0 | 50 | 31 | 0 | 0 | 0 | 0.07 | 220 | 34 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 8 | 415 | 285 | 0 | 45 | 0 | 38 | 0 | 104 | 69 | 0 | 19 | 0 | 64 | 0 | 0 | 29 | 310 | 0 | 312 | 30 | 67 | 156 | 12 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 107 | 0 | 0 | 6 | 6556.07 | 873 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 1473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 110 | 180 | 0 | 301 | 1110 | 17 | 5714 | 12270.07 | 106.31
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 17 | 30 | 45 | 0 | 0 | 17 | 0 | 300 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 6 | 90 | 20 | 22 | 0 | 0 | 17 | 16 | 24 | 0 | 0 | 50 | 31 | 0 | 0 | 0 | 0.48 | 221 | 33 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 1180 | 6 | 51 | 35 | 8 | 415 | 280 | 0 | 45 | 0 | 38 | 0 | 104 | 69 | 0 | 19 | 0 | 64 | 0 | 5 | 29 | 320 | 0 | 312 | 30 | 67 | 159 | 12 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 107 | 0 | 8.21 | 6 | 6571.69 | 873 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 327 | 0 | 1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 14 | 0 | 0 | 10.5 | 192 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.89 | 0 | 42 | 35 | 4 | 0 | 0 | 0 | 0 | 0.7 | 27 | 0.07 | 0 | 253 | 110 | 220 | 0 | 301 | 1115 | 17 | 5750.3 | 12321.99 | 106.31
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 60 | 45 | 0 | 0 | 17 | 0 | 300 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 15 | 90 | 20 | 22 | 0 | 0 | 17 | 16 | 25 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 1.81 | 222 | 33 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 1160 | 11 | 51 | 35 | 8 | 415 | 280 | 0 | 44 | 0 | 38 | 0 | 103 | 69 | 0 | 19 | 0 | 62 | 0 | 30 | 29 | 320 | 0 | 312 | 30 | 67 | 157 | 11 | 0 | 76 | 30 | 0 | 16 | 160 | 0 | 69 | 48 | 105 | 1 | 23.66 | 6 | 6586.47 | 873 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 326 | 0 | 1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.53 | 44 | 0 | 0 | 30.36 | 191 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.59 | 0 | 42 | 50 | 13 | 0 | 0 | 0 | 0 | 2.3 | 82 | 0.22 | 0 | 265 | 110 | 220 | 0 | 301 | 1115 | 17 | 5954 | 12540.47 | 106.3
09:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 17 | 60 | 135 | 0 | 0 | 17 | 0 | 300 | 0 | 362 | 0 | 0 | 280 | 0 | 0 | 23 | 52 | 20 | 22 | 0 | 0 | 17 | 16 | 24 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 1.78 | 222 | 34 | 5 | 650 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 1160 | 16 | 51 | 48 | 50 | 410 | 343 | 0 | 42 | 0 | 38 | 9 | 103 | 69 | 0 | 19 | 0 | 56 | 0 | 26 | 29 | 315 | 0 | 312 | 30 | 67 | 159 | 11 | 0 | 78 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 94 | 2 | 35.91 | 6 | 6822.69 | 873 | 357 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 324 | 0 | 1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.28 | 73 | 0 | 0 | 47.65 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.12 | 0 | 42 | 0 | 23 | 0 | 0 | 0 | 0 | 4.2 | 130 | 0.4 | 0 | 267 | 110 | 220 | 0 | 300 | 1112 | 17 | 5782.65 | 12605.34 | 106.29
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 26 | 60 | 145 | 0 | 0 | 17 | 0 | 300 | 0 | 352 | 0 | 17 | 280 | 0 | 0 | 29 | 52 | 20 | 15 | 0 | 0 | 17 | 16 | 24 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 3.49 | 222 | 34 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 1160 | 19 | 51 | 100 | 71 | 410 | 341 | 0 | 41 | 0 | 37 | 17 | 100 | 69 | 0 | 19 | 0 | 55 | 0 | 65 | 29 | 310 | 0 | 311 | 30 | 67 | 149 | 11 | 0 | 76 | 30 | 0 | 16 | 160 | 0 | 68 | 48 | 94 | 2 | 44.13 | 6 | 6963.62 | 873 | 357 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 318 | 0 | 1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.35 | 90 | 0 | 0 | 60.38 | 183 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 5.2 | 0 | 43 | 0 | 29 | 0 | 0 | 0 | 0 | 5.6 | 164 | 0.55 | 0 | 269 | 110 | 220 | 0 | 299 | 1096 | 17 | 5828.08 | 12791.7 | 106.28
11:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 17 | 33 | 100 | 266 | 0 | 0 | 17 | 0 | 300 | 0 | 374 | 0 | 17 | 280 | 0 | 0 | 33 | 52 | 19 | 15 | 0 | 0 | 26 | 16 | 25 | 0 | 1 | 50 | 24 | 4 | 0 | 0 | 2.91 | 222 | 54 | 6 | 650 | 17 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1168 | 19 | 51 | 113 | 82 | 405 | 338 | 0 | 41 | 0 | 37 | 17 | 100 | 54 | 5 | 19 | 0 | 62 | 0 | 62 | 29 | 325 | 0 | 311 | 30 | 67 | 156 | 11 | 0 | 81 | 30 | 0 | 16 | 161 | 0 | 68 | 48 | 93 | 2 | 47.69 | 6 | 7304.6 | 873 | 353 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 313 | 0 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.65 | 93 | 0 | 0 | 66.79 | 191 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 5.78 | 0 | 41 | 0 | 35 | 0 | 0 | 0 | 0 | 6.2 | 186 | 0.65 | 0 | 271 | 110 | 220 | 0 | 299 | 1114 | 35 | 5900.07 | 13204.67 | 106.27
12:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17.5 | 17 | 33 | 104 | 261 | 0 | 0 | 17 | 0 | 300 | 0 | 356 | 0 | 0 | 300 | 0 | 0 | 34 | 52 | 19 | 15 | 0 | 0 | 100 | 16 | 53 | 0 | 0 | 50 | 45 | 17 | 0 | 0 | 3.45 | 220 | 93 | 3 | 650 | 17 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1182 | 13 | 51 | 115 | 140 | 335 | 337 | 0 | 41 | 0 | 36 | 16 | 98 | 59 | 9 | 19 | 114 | 69 | 7 | 43 | 29 | 325 | 0 | 312 | 30 | 67 | 156 | 11 | 0 | 77 | 30 | 0 | 16 | 161 | 0 | 68 | 48 | 83 | 2 | 47.69 | 2 | 7548.64 | 873 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83.78 | 308 | 0 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.68 | 68 | 0 | 0 | 67.19 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.93 | 0 | 41 | 0 | 26 | 5 | 0 | 0 | 0 | 6.5 | 181 | 0.44 | 2 | 266 | 110 | 220 | 0 | 298 | 1112 | 17 | 5890.52 | 13439.16 | 106.26
13:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17.5 | 17 | 16 | 44 | 260 | 0 | 0 | 17 | 0 | 300 | 0 | 337 | 0 | 0 | 300 | 0 | 0 | 31 | 52 | 19 | 15 | 0 | 0 | 102 | 16 | 82 | 0 | 1 | 50 | 45 | 17 | 0 | 0 | 3.25 | 220 | 95 | 12 | 650 | 17 | 0 | 0 | 1 | 0 | 160 | 0 | 0 | 0 | 1160 | 19 | 51 | 103 | 80 | 330 | 336 | 0 | 40 | 0 | 36 | 17 | 99 | 69 | 0 | 19 | 105 | 82 | 39 | 24 | 29 | 320 | 0 | 312 | 30 | 67 | 156 | 11 | 0 | 77 | 30 | 0 | 16 | 161 | 0 | 66 | 48 | 83 | 2 | 30.32 | 1 | 7413.07 | 873 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 310 | 0 | 1150 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 8 | 46.09 | 90 | 0 | 0 | 63.66 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.53 | 0 | 43 | 70 | 24 | 77 | 0 | 0 | 0 | 3.7 | 155 | 0.15 | 16 | 278 | 110 | 220 | 0 | 298 | 1112 | 17 | 6049.13 | 13462.2 | 106.25
14:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17.5 | 17 | 15 | 44 | 34 | 0 | 1 | 17 | 0 | 300 | 0 | 324 | 0 | 0 | 250 | 0 | 0 | 28 | 52 | 19 | 14 | 0 | 0 | 90 | 16 | 80 | 0 | 7 | 50 | 53 | 17 | 0 | 0 | 2.5 | 218 | 93 | 8 | 650 | 17 | 0 | 0 | 5 | 0 | 160 | 0 | 0 | 0 | 1160 | 16 | 51 | 97 | 71 | 365 | 300 | 0 | 41 | 0 | 33 | 16 | 99 | 69 | 0 | 19 | 96 | 80 | 43 | 16 | 28 | 305 | 0 | 312 | 30 | 66 | 147 | 11 | 0 | 77 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 72 | 2 | 30.5 | 6 | 7031.5 | 872 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 314 | 0 | 1137.97 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 51.52 | 91 | 0 | 0 | 55.21 | 186 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 4.87 | 0 | 43 | 115 | 30 | 95 | 0 | 0 | 0 | 5.3 | 153 | 0.56 | 16 | 270 | 100 | 180 | 0 | 298 | 1164 | 17 | 6031.43 | 13062.93 | 106.24
15:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17.5 | 17 | 15 | 44 | 34 | 0 | 17 | 17 | 0 | 300 | 0 | 333 | 0 | 0 | 300 | 0 | 0 | 20 | 52 | 19 | 14 | 0 | 0 | 91 | 16 | 88 | 0 | 6 | 50 | 51 | 17 | 0 | 0 | 2.27 | 219 | 94 | 4 | 650 | 17 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1190 | 13 | 51 | 98 | 71 | 393 | 300 | 0 | 41 | 0 | 33 | 16 | 98 | 69 | 0 | 19 | 109 | 75 | 43 | 31 | 29 | 315 | 0 | 312 | 30 | 67 | 154 | 3 | 0 | 77 | 30 | 0 | 16 | 161 | 0 | 67 | 48 | 72 | 0 | 27.67 | 6 | 7201.44 | 873 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 314 | 0 | 1161.14 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 37.58 | 64 | 0 | 0 | 41.12 | 176 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 3.71 | 0 | 43 | 115 | 22 | 92 | 0 | 0 | 0 | 3.6 | 104 | 0.37 | 16 | 275 | 110 | 180 | 0 | 298 | 1182 | 17 | 5978.52 | 13179.96 | 106.23
16:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17.5 | 17 | 15 | 44 | 37 | 0 | 17 | 17 | 0 | 300 | 0 | 323 | 0 | 0 | 300 | 0 | 0 | 11 | 52 | 19 | 21 | 0 | 0 | 87 | 16 | 94 | 0 | 2 | 48 | 51 | 17 | 0 | 0 | 0.93 | 220 | 93 | 5 | 650 | 17 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1160 | 6 | 51 | 97 | 71 | 403 | 300 | 0 | 37 | 0 | 33 | 17 | 98 | 69 | 0 | 19 | 98 | 79 | 43 | 20 | 33 | 310 | 0 | 313 | 30 | 67 | 152 | 8 | 0 | 80 | 30 | 0 | 16 | 160 | 0 | 67 | 48 | 71 | 1 | 13.42 | 6 | 7135.85 | 873 | 351 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.22 | 314 | 0 | 1393.75 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 21.02 | 33 | 0 | 0 | 22.05 | 171 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 1.97 | 0 | 43 | 115 | 10 | 96 | 0 | 0 | 0 | 1.4 | 54 | 0.18 | 16 | 273 | 110 | 180 | 0 | 298 | 1177 | 35 | 6056.59 | 13192.44 | 106.22
17:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17.5 | 17 | 15 | 44 | 37 | 4 | 35 | 17 | 0 | 300 | 0 | 325 | 0 | 0 | 250 | 0 | 0 | 2 | 52 | 19 | 0 | 0 | 0 | 90 | 16 | 88 | 0 | 0 | 50 | 58 | 17 | 0 | 0 | 0.02 | 220 | 94 | 15 | 650 | 71 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1160 | 1 | 51 | 98 | 76 | 360 | 315 | 0 | 38 | 0 | 34 | 16 | 99 | 69 | 6 | 19 | 104 | 78 | 43 | 3 | 33 | 310 | 0 | 312 | 30 | 67 | 153 | 12 | 0 | 83 | 30 | 0 | 16 | 160 | 0 | 67 | 48 | 72 | 0 | 1.96 | 6 | 7113.48 | 873 | 350 | 0 | 32 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.12 | 314 | 0 | 1449.74 | 0 | 41 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 2.7 | 6 | 20 | 0 | 3.08 | 173 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0.18 | 0 | 41 | 115 | 1 | 100 | 0 | 0 | 0 | 0.4 | 9 | 0.02 | 16 | 234 | 110 | 180 | 0 | 261 | 1152 | 35 | 5931.24 | 13044.72 | 106.21
18:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17.5 | 35 | 15 | 132 | 42 | 15 | 35 | 17 | 0 | 300 | 0 | 332 | 0 | 17 | 321 | 0 | 0 | 0 | 125 | 19 | 14 | 0 | 0 | 87 | 32 | 91 | 0 | 0 | 50 | 67 | 48 | 0 | 0 | 0 | 221 | 93 | 10 | 650 | 160 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1217 | 0 | 51 | 110 | 76 | 370 | 351 | 0 | 40 | 0 | 33 | 17 | 100 | 96 | 9 | 19 | 99 | 84 | 43 | 0 | 26 | 315 | 0 | 311 | 30 | 67 | 147 | 12 | 0 | 83 | 30 | 0 | 16 | 160 | 6 | 68 | 48 | 71 | 0 | 0 | 5 | 7725.5 | 873 | 347 | 0 | 35 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 1453.48 | 0 | 41 | 0 | 35 | 43 | 0 | 93 | 15 | 46 | 0 | 0 | 25 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 44 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 110 | 180 | 0 | 282 | 1146 | 17 | 6213.48 | 13938.98 | 106.2
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17.5 | 35 | 15 | 135 | 83 | 15 | 35 | 17 | 0 | 300 | 0 | 339 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 92 | 32 | 96 | 0 | 0 | 50 | 67 | 54.36 | 0 | 0 | 0 | 221 | 95 | 18 | 650 | 153 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1195 | 0 | 51 | 113 | 43 | 395 | 337 | 0 | 42 | 0 | 33 | 16 | 100 | 105 | 8 | 19 | 108 | 84 | 43 | 0 | 26 | 315 | 0 | 311 | 30 | 67 | 149 | 10 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 73 | 0 | 0 | 0 | 7790.86 | 873 | 348 | 0 | 40 | 61 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 1462.5 | 0 | 41 | 0 | 35 | 93 | 0 | 94 | 32 | 43 | 0 | 0 | 25 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 43 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 282 | 110 | 180 | 0 | 295 | 1170 | 17 | 6455.5 | 14246.36 | 106.19
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17.5 | 35 | 15 | 135 | 91 | 15 | 35 | 17 | 0 | 300 | 0 | 379 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 92 | 32 | 96 | 0 | 0 | 50 | 67 | 54.36 | 0 | 0 | 0 | 222 | 94 | 23 | 650 | 153 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1195 | 0 | 51 | 123 | 41 | 380 | 339 | 0 | 43 | 0 | 34 | 16 | 100 | 125 | 0 | 19 | 114 | 90 | 43 | 0 | 28 | 330 | 0 | 311 | 30 | 67 | 157 | 10 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 73 | 0 | 0 | 0 | 7898.86 | 873 | 349 | 0 | 35 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 1465.97 | 0 | 41 | 0 | 35 | 95 | 0 | 94 | 32 | 43 | 0 | 0 | 25 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 42 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 281 | 110 | 180 | 0 | 295 | 1170 | 17 | 6455.97 | 14354.83
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17.5 | 35 | 15 | 135 | 95 | 15 | 35 | 17 | 0 | 300 | 0 | 365 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 99 | 32 | 96 | 0 | 0 | 50 | 67 | 54.36 | 0 | 0 | 0 | 222 | 94 | 24 | 650 | 90 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1190 | 0 | 51 | 123 | 16 | 385 | 343 | 0 | 44 | 0 | 34 | 17 | 101 | 120 | 0 | 19 | 105 | 84 | 43 | 0 | 28 | 320 | 0 | 312 | 30 | 67 | 158 | 10 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 73 | 0 | 0 | 0 | 7788.86 | 873 | 352 | 0 | 35 | 46 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 1454.12 | 0 | 41 | 0 | 35 | 95 | 0 | 94 | 32 | 43 | 0 | 0 | 25 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 30 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 278 | 110 | 180 | 0 | 294 | 1170 | 17 | 6425.12 | 14213.98 | 106.18
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17.5 | 17 | 17 | 120 | 95 | 15 | 17 | 17 | 0 | 300 | 0 | 340 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 97 | 32 | 97 | 0 | 0 | 50 | 67 | 54.36 | 0 | 0 | 0 | 220 | 95 | 27 | 650 | 17 | 0 | 0 | 17 | 0 | 158 | 0 | 0 | 0 | 1190 | 0 | 51 | 122 | 16 | 400 | 342 | 0 | 44 | 0 | 34 | 16 | 101 | 124 | 0 | 19 | 108 | 86 | 43 | 0 | 29 | 320 | 0 | 312 | 30 | 67 | 159 | 10 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 87 | 0 | 0 | 0 | 7678.86 | 873 | 358 | 0 | 35 | 46 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 1462.4 | 0 | 41 | 0 | 35 | 95 | 0 | 94 | 30 | 43 | 0 | 0 | 25 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 279 | 110 | 180 | 0 | 294 | 1160 | 17 | 6403.4 | 14082.26 | 106.17
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 17 | 20 | 120 | 105 | 15 | 0 | 17 | 0 | 300 | 0 | 320 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 94 | 16 | 96 | 0 | 0 | 50 | 67 | 54.36 | 0 | 0 | 0 | 222 | 96 | 29 | 650 | 17 | 0 | 0 | 17 | 0 | 154 | 0 | 0 | 0 | 1185 | 0 | 51 | 123 | 16 | 410 | 349 | 0 | 44 | 0 | 35 | 17 | 102 | 126 | 0 | 19 | 98 | 88 | 43 | 0 | 29 | 310 | 0 | 312 | 30 | 67 | 157 | 10 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 87 | 0 | 0 | 0 | 7618.36 | 873 | 347 | 0 | 35 | 47 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 1462.62 | 0 | 41 | 0 | 35 | 95 | 0 | 94 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 275 | 110 | 220 | 0 | 300 | 1160 | 17 | 6431.82 | 14050.18 | 106.16
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 17 | 49 | 47 | 107 | 15 | 0 | 17 | 0 | 300 | 0 | 320 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 92 | 16 | 98 | 0 | 0 | 50 | 68 | 54.36 | 0 | 0 | 0 | 222 | 95 | 30 | 650 | 17 | 0 | 0 | 17 | 0 | 154 | 0 | 0 | 0 | 1165 | 0 | 51 | 130 | 16 | 415 | 354 | 0 | 45 | 0 | 34 | 17 | 102 | 124 | 0 | 19 | 96 | 92 | 43 | 0 | 29 | 315 | 0 | 312 | 30 | 67 | 156 | 8 | 0 | 84 | 30 | 0 | 16 | 160 | 17 | 68 | 48 | 87 | 0 | 0 | 0 | 7454.36 | 873 | 342 | 0 | 35 | 47 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 1455.73 | 0 | 41 | 0 | 35 | 95 | 0 | 94 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 110 | 220 | 0 | 292 | 1180 | 17 | 6381.93 | 13836.29 | 106.15
Total KWH | 0 | 1599360 | 407040 | 0 | 0 | 0 | 0 | 0 | 9187200 | 0 | 0 | 207360 | 331200 | 540864 | 1847520 | 3339600 | 193015 | 200922 | 420480 | 0 | 7590000 | 0 | 8266478 | 0 | 134122 | 6793785 | 0 | 0 | 224922 | 2244000 | 488400 | 454320 | 0 | 0 | 1732527 | 429055 | 1656960 | 0 | 12000 | 1170665 | 1206008 | 632349 | 0 | 0 | 20762 | 5243078 | 1932800 | 486720 | 15650909.09 | 692509 | 0 | 0 | 160063.2 | 0 | 3642501 | 0 | 0 | 0 | 28259997 | 137430 | 1147336 | 2565963 | 1003636 | 9586500 | 8038800 | 0 | 1023360 | 0 | 861408 | 264960 | 2413553 | 2002080 | 48720 | 453180 | 1647300 | 1803840 | 648394 | 384727 | 688432 | 7688500 | 0 | 7845000 | 716000 | 1577880 | 3716591 | 315864 | 0 | 1920960 | 717600 | 0 | 390000 | 3333850 | 108360 | 1626000 | 1144800 | 2080320 | 15100 | 321090 | 73920 | 175710945.29 | 21148363 | 8668800 | 0 | 324960 | 383744 | 912000 | 0 | 0 | 0 | 0 | 27792 | 504720 | 7992727 | 0 | 32181091 | 0 | 476207 | 0 | 367680 | 1013664 | 0 | 664800 | 237070 | 456989 | 404408 | 724734 | 275839 | 0 | 471008 | 4531000 | 0 | 0 | 0 | 0 | 0 | 9424145 | 0 | 40500 | 0 | 833018 | 1913191 | 215121 | 1715452 | 0 | 0 | 0 | 39972.36 | 1238400 | 3657 | 319680 | 6654000 | 2639000 | 5219400 | 0 | 7112016 | 27575272.73 | 466800 | 147177221.09 | 322888166.38

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13439.16 | MW | 12:00 Hr. | Energy Generated |  |  | 322.8882 |  | MKWHr.
| Day Peak Demand |  |  | 13575.16 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.378 |  | MKWHr.
| Evening Peak Generation |  |  | 14354.83 | MW | 19:30 Hr. | Energy Demand |  |  | 329.2662 |  | MKWHr.
| Evening Peak Demand |  |  | 14950.48 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 12270.07 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 895.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 14615.56 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.7592 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.7802 | 0 | 11.4655 | 0 | 0 | 0.22492 | 0 | 0 | 44.4706 | Gas | 122.2221 | Gas | 434114865.43
| Chattogram Zone |  |  | 4.1292 | 43.9109 | 9.6129 | 0 | 5.2431 | 0.15819 | 0 | 0.012 | 63.0663 | Coal | 94.0779 | Coal | 586662169.4219
| Cumilla Zone |  |  | 24.5278 | 0 | 7.8658 | 0 | 0 | 0.38473 | 1.8038 | 0 | 34.5822 | HFO | 40.5412 | HFO | 745859026.398
| Mymensingh Zone |  |  | 2.0803 | 0 | 2.9531 | 0 | 0 | 0.33619 | 0 | 0 | 5.3696 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2222 | Hydro | 5.2431 | Hydro | 524307.8
| Khulna Zone |  |  | 8.6688 | 7.9927 | 0.7365 | 0 | 0 | 0.50472 | 22.0604 | 0 | 39.9631 | Solar | 4.7466 | Solar | 76153228.0476
| Barishal Zone |  |  | 7.8584 | 41.3413 | 0.78648 | 0 | 0 | 0.003657 | 0 | 0 | 49.9898 | Import | 56.0453 | Import | 338965639.49
| Rajshahi Zone |  |  | 13.9551 | 0 | 3.4922 | 0 | 0 | 1.6406 | 32.1811 | 0 | 51.2691 | Wind | 0.012 | Wind | 176520
| Rangpur Zone |  |  | 0 | 0.83302 | 3.6286 | 0 | 0 | 1.4935 | 0 | 0 | 5.9552
| Total |  |  | 122.2221 | 94.0779 | 40.5412 | 0 | 5.2431 | 4.7466 | 56.0453 | 0.012 | 322.8882
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 434114865.43 |  | Hydro | 524307.8
|  |  |  | Coal | 586662169.4219 |  | Solar | 76153228.0476
|  |  |  | HFO | 745859026.398 |  | Import | 338965639.49
|  |  |  | HSD | 0 |  | Wind | 176520
[5 empty] | Total: | 218,24,55,756 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1484 | Peak Hr Flow | 873.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43003694.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.1811 | Peak Hr Flow | 1465.97 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2103 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.8038 | Peak Hr Flow | 90.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2257 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.1333 | Peak Hr Flow | 2428.97 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 120 |  | 5287
|  |  |  | Chattogram |  | 30 |  | 1374
|  |  |  | Cumilla |  | 50 |  | 1378
|  |  |  | Mymensingh |  | 85 |  | 1111
|  |  |  | Sylhet |  | 40 |  | 718
|  |  |  | Khulna |  | 65 |  | 1641
|  |  |  | Barishal |  | 20 |  | 441
|  |  |  | Rajshahi |  | 85 |  | 1429
|  |  |  | Rangpur |  | 75 |  | 875
|  |  |  | Total |  | 570 |  | 14254
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 17:27 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to Annual Maintenance Work
| 08:16 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:-
| 08:22 | 16:06 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT Scheduled S/D Due to Annual
Maintenance
| 08:24 | 16:03 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT Scheduled S/D Due to Annual
Maintenance
| 08:24 |  | Savar 132/33kV S/S Capacitor Bank-1 Scheduled S/D Due to Annual maintenance work.
| 08:24 | 15:46 | Savar 132/33kV S/S Capacitor Bank-2 Scheduled S/D Due to Annual maintenance work
| 08:24 | 15:47 | Savar 132/33kV S/S Capacitor Bank-3 Scheduled S/D Due to Annual maintenance work
| 08:25 | 15:07 | Ullahpara 132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Annual Maintenance Work
| 08:31 | 17:42 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D Due to Annual Maintenance
| 08:32 | 17:41 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D Due to Annual Maintenance
| 08:32 | 15:13 | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to QF- GMD-39 and as the
instruction of ALDC Bogura (499264)
| 08:32 | 16:45 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Yearly Maintenance
| 08:32 | 16:44 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Yearly Maintenance
| 08:32 | 16:08 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Annual Maintenance
| 08:32 | 16:10 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Annual Maintenance
| 08:33 | 15:11 | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to QF- GMD-39 and as the
instruction of ALDC Bogura (499264)
| 08:36 | 13:38 | Rajbari 132/33kV S/S 132 kV Bus-II Scheduled S/D Due to For Annual maintenance work.
| 09:22 | 17:40 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to Shutdown for annual
maintenance.
| 09:24 | 17:38 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to Shutdown for annual
maintenance.
| 09:36 | 17:17 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt Scheduled S/D Due to Due to annual maintenance
works
|  | 09:44 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
|  | 09:45 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 11:17 | GPH 230/33kV S/S Transformer-01(D05) HT is restored.
| 12:00 |  | Day Peak Generation: 13434 MW.
| 12:10 | 14:04 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to Isolator maintenance
| 13:18 | 15:46 | Baroaulia-KSRM 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing 1.P442-Distance | [7 empty] | 20.0MW load
|  |  | Realy 2.Trip-A,B,C 3.Zone-1 4.Trip relay MVAJM25(K34,K33,K32,K31) 5.DIR O/C & E/F | [7 empty] | interrup. Baroaulia
|  |  | P127 relays Due to A tree fell across the power line. | [7 empty] | 132/33kV end
| 13:20 | 15:48 | KSRM 132/33kV S/S Baraulia Main Forced S/D Due to baraulia incoming feeder trip from
baraulia S/S .
| 13:21 | 15:49 | KSRM 132/33kV S/S Transformer-01 LT Forced S/D Due to baraulia incoming feeder trip from
baraulia S/S .
| 13:23 | 15:51 | KSRM 132/33kV S/S Transformer-02 LT Forced S/D Due to baraulia incoming feeder trip from
baraulia S/S .
| 13:25 | 15:53 | KSRM 132/33kV S/S Transformer-03 LT Forced S/D Due to baraulia incoming feeder trip from
baraulia S/S .
| 13:45 | 16:07 | Rajbari 132/33kV S/S 132 kV Bus-I Scheduled S/D Due to For annual maintenance
| 14:13 | 15:46 | Baroaulia-KSRM 132 kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to A tree fell | [7 empty] | 20.0MW load
|  |  | across the power line. | [7 empty] | interrup. Baroaulia
132/33kV end
| 14:47 |  | Mogbazar 132/33kV T-1 and T-2 transformer tripped due to T-1 transformer's 132kV LA | [7 empty] | 100MW load
|  |  | burst. | [7 empty] | interrup.
|  | 16:45 | Barguna 132/33kV S/S Bus-2 is restored.
|  | 16:58 | Khulna (C) S/S Tr-3 405T HT is restored.
|  | 16:59 | Khulna (C) S/S Tr-3 405T LT is restored.
|  | 17:00 | Chandraghona-Madunaghat 132 kV Ckt-2 is restored.
| 19:30 |  | Evening Peak Generation: 14353 MW.
|  | 01:53 | Meghnaghat 230/132kV S/S Meghnaghat-Aminbazar-02 is restored.
| 04:28 |  | Patuakhali 1320 MW (RNPL) Unit-1 was sync.
| 06:00 |  | Minimum Generation: 12171 MW.
| 07:12 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33kv bus maintenance | [7 empty] | 40.0MW load
interrup.
| 07:13 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 kvbus maintenance | [7 empty] | 40.0MW load
interrup.
| 07:18 |  | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance work.
| 07:19 |  | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9187200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7590000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 193015 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6793785 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 207360 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 135 | 1847520 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 200922 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 134122 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 488400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 454320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 407040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 91 | 3339600 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 15 | 540864 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1599360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 420480 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 224922 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 331200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 379 | 8266478 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2244000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 2045.5 | 44470588
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 160063.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 137430 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5243078 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3642501 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 1206008 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1170665 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 486720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 1656960 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 429055 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 632349 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 94 | 1932800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1732527 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 153 | 692509 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1195 | 28259997 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15650909.09 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2906.36 | 63066333.29
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 339 | 8038800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 380 | 9586500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 861408 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 1023360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 41 | 1003636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1147336 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 2565963 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 688432 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2413553 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 125 | 2002080 | -
| Import (Tripura) |  | Import | 0 | 160 | 90 | 1803840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 648394 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 453180 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1647300 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 48720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 264960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 384727 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1546 | 34582189
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 2080320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1144800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1626000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 321090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 73920 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 108360 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 206 | 5369590
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1577880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3716591 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717600 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1920960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3333850 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 390000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 315864 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 7688500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 311 | 7845000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1195 | 28222245
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 21148363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 324960 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 383744 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 349 | 8668800 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 27792 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 504720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 314 | 7992727 | U1 Partial load due to PA fan outage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1659 | 39963106
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 295 | 7112016 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 319680 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2639000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 27575272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5219400 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 466800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 281 | 6654000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3657 | -
Barishal Area Total |  |  |  |  | 2858 | 2085 | 49989825.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 404408 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 476207 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 237070 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 203 | 4531000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9424145 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 275839 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 456989 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 664800 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 95 | 1013664 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 367680 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 40500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1465.97 | 32181091 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 471008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 724734 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2447.97 | 51269135
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 42 | 833018 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1715452 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39972.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1913191 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 215121 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1238400 | -
Rangpur Area Total |  |  |  |  | 950 | 264 | 5955154.36
Eastern Grid Total |  |  |  |  | 17383.852 | 7898.86 | 175710945.29
Western Grid Total |  |  |  |  | 10980.24 | 6455.97 | 147177221.09
National Grid Total |  |  |  |  | 28364.092 | 14354.83 | 322888166.38
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-10-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9543.35 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4140.7 | MW
i) Dhaka area |  |  | 5167.36 |  | MW | i) Khulna area |  |  |  | 1575.9 | MW
ii) Chattogram area |  |  | 1344 |  | MW | ii) Barishal area |  |  |  | 421 | MW
iii) Cumilla area |  |  | 1327.99 |  | MW | iii) Rajshahi area |  |  |  | 1343.8 | MW
iv) Mymensingh area |  |  | 1026 |  | MW | iv) Rangpur area |  |  |  | 800 | MW
v) Sylhet area |  |  | 678 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13684.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 23:00 | 133 | Niamatpur | 72 | 18:00
2 | AKSML | 148.8 | 03:00 | 68 | Ishurdi | 73 | 13:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 42 | 18:00 | 69 | Jaldhaka | 68 | 00:00 | 135 | PHP | 9 | 20:00
4 | Agargaon | 140 | 13:00 | 70 | Jamalpur | 114 | 00:00 | 136 | Pabna | 94 | 18:30
5 | Agrabad | 104 | 19:00 | 71 | Jashore | 142 | 13:00 | 137 | Palashbari | 120 | 18:00
6 | Amnura | 35 | 18:00 | 72 | Jhenaidah | 119 | 00:00 | 138 | Panchagarh | 60 | 18:00
7 | Ashuganj | 87 | 22:00 | 73 | Joydebpur | 144 | 00:00 | 139 | Patiya | 11 | 23:00
8 | BSRM | 204 | 19:00 | 74 | Joypurhat | 52 | 22:00 | 140 | Patuakhali | 69 | 18:30
9 | Bagerhat | 77 | 22:00 | 75 | Juldah | 18 | 16:00 | 141 | Payra | 30 | 00:00
10 | Bajitpur | 88 | 00:00 | 76 | KSRM | 45 | 00:00 | 142 | Postogola | 70 | 00:00
11 | Bakulia | 83 | 18:00 | 77 | Kabirpur | 246 | 18:30 | 143 | Purbachal | 23 | 18:00
12 | Banani | 55.4 | 13:00 | 78 | Kachua | 85 | 00:00 | 144 | Purbasadipur | 119 | 00:00
13 | Bangabhaban | 25 | 10:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rahanpur | 36 | 21:00
14 | Barapukuria | 62 | 00:00 | 80 | Kalurghat | 54 | 15:00 | 146 | Rahim | 14 | 09:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 81 | 19:00 | 147 | Rajbari | 68 | 21:00
16 | Barishal | 121 | 18:30 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 117 | 00:00
17 | Barishal-230 | 100 | 18:30 | 83 | Kasba | 37 | 19:30 | 149 | Rajshahi | 132 | 13:00
18 | Baroaulia | 65 | 16:00 | 84 | Kazla | 92 | 00:00 | 150 | Rajshahi-230 | 62 | 00:00
19 | Baroirhat | 64 | 22:00 | 85 | Keranigonj | 91 | 12:00 | 151 | Ramganj | 102 | 00:00
20 | Bashundhara | 209 | 18:30 | 86 | Khagrachori | 30 | 18:00 | 152 | Rampur | 41 | 00:00
21 | BashundharaCement | 12 | 12:00 | 87 | Khulna | 64 | 13:00 | 153 | Rangamati | 16 | 14:00
22 | Beanibazar | 86 | 19:00 | 88 | Khulshi | 179 | 18:30 | 154 | Rangpur | 136 | 13:00
23 | Benapole | 58 | 13:00 | 89 | Kishoreganj | 115 | 22:00 | 155 | Ruppur | 8 | 16:00
24 | Bhaluka | 139 | 00:00 | 90 | Kodda | 272 | 12:00 | 156 | SSM | 10 | 23:00
25 | Bhandaria | 50 | 19:00 | 91 | Kulaura | 51 | 19:30 | 157 | Saidpur | 95 | 19:00
26 | Bhangura | 32 | 23:00 | 92 | Kurigram | 54 | 07:00 | 158 | Satkhira | 122 | 18:30
27 | Bheramara(GK) | 62 | 20:00 | 93 | Kushtia | 152 | 18:30 | 159 | Satmasjid | 106 | 13:00
28 | Bhulta | 208 | 07:00 | 94 | Laksam | 36 | 00:00 | 160 | Savar | 200 | 09:00
29 | Bog-Sherpur | 56 | 20:00 | 95 | Lakshmipur | 34 | 00:00 | 161 | SevenRings | 17.44 | 00:00
30 | Bogura | 164 | 19:00 | 96 | Lalbag | 72 | 13:00 | 162 | ShahCement | 24 | 23:00
31 | Borhanuddin | 93 | 19:00 | 97 | Lalmonirhat | 51 | 18:00 | 163 | Shahjadpur | 76 | 12:00
32 | Brahmanbaria | 128 | 01:00 | 98 | MI_Cement | 15.5 | 23:00 | 164 | Shahjibazar | 128 | 19:30
33 | Cantonment | 140 | 15:00 | 99 | Madanganj | 44 | 00:00 | 165 | Shahmirpur | 47 | 23:00
34 | Chandina | 17.53 | 21:00 | 100 | Madaripur | 114 | 02:00 | 166 | Shariatpur | 88 | 00:00
35 | Chandpur | 84 | 00:00 | 101 | Madartek | 98 | 23:00 | 167 | Sherpur | 126 | 02:00
36 | Chandraghona | 35 | 00:00 | 102 | Madunaghat | 52 | 20:00 | 168 | Shikalbaha | 23 | 14:00
37 | Chapai | 81 | 13:00 | 103 | Magura | 61 | 20:00 | 169 | Shitalakhya | 83 | 16:00
38 | Charsaidpur | 35 | 00:00 | 104 | Mahasthangarh | 68 | 02:00 | 170 | Sholosohor | 46 | 11:00
39 | Chauddagram | 69 | 01:00 | 105 | Maijdee | 31 | 00:00 | 171 | Shyampur | 134 | 12:00
40 | Chhatak | 44 | 18:30 | 106 | Manikganj | 114 | 02:00 | 172 | Siddhirganj | 122 | 09:00
41 | Chowmuhani | 158 | 00:00 | 107 | Maniknagar | 66 | 11:00 | 173 | Sirajganj | 104 | 19:00
42 | Chuadanga | 113 | 21:00 | 108 | Matarbari | 47 | 02:00 | 174 | Sonargaon | 114 | 00:00
43 | Coxsbazar | 118 | 22:00 | 109 | Matuail | 74 | 10:00 | 175 | Sreemongol | 87 | 19:00
44 | Cumilla(N) | 140 | 20:00 | 110 | Metrorail_Motijheel | 37 | 18:30 | 176 | Sreepur | 97 | 16:00
45 | Cumilla(S) | 162 | 18:00 | 111 | Metrorail_Uttara | 10 | 18:30 | 177 | Srinagar | 52.12 | 19:30
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 136 | 15:00 | 178 | Sunamganj | 60 | 00:00
47 | Daudkandi | 141 | 00:00 | 113 | Mirpur | 122 | 15:00 | 179 | Sylhet | 58 | 19:30
48 | DhakaUniversity | 100 | 13:00 | 114 | Mirsorai | 12 | 15:00 | 180 | Sylhet-132 | 149 | 18:30
49 | Dhamrai | 110 | 06:00 | 115 | Mirzapur | 42 | 11:00 | 181 | TK | 23 | 02:00
50 | Dhanmondi | 137 | 14:00 | 116 | Mithapukur | 58 | 12:00 | 182 | Tangail | 166 | 18:00
51 | Dohazari | 92 | 01:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 20 | 00:00
52 | Faridpur | 155 | 00:00 | 118 | Mogbazar | 100.8 | 14:00 | 184 | Thakurgaon | 90 | 00:00
53 | Fatullah | 116 | 10:00 | 119 | Mongla | 38 | 18:30 | 185 | Tongi | 117 | 15:00
54 | Fenchuganj | 39 | 21:00 | 120 | Motijheel | 55 | 13:00 | 186 | Ullahpara | 33 | 18:30
55 | Feni | 112 | 23:00 | 121 | Muktagacha | 32 | 01:00 | 187 | Ullon | 73 | 18:00
56 | GPH | 23 | 04:00 | 122 | Munshiganj | 96 | 01:00 | 188 | Uttara | 91 | 18:00
57 | Ghatail | 74 | 00:00 | 123 | Muradnagar | 39 | 20:00 | 189 | UttaraNew | 77 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 201 | 00:00 | 190 | Zigatola | 79 | 18:00
59 | Ghorashal-230 | 108 | 00:00 | 125 | Naogaon | 128 | 19:30
60 | Goalpara | 39 | 00:00 | 126 | Narail | 55 | 02:00
61 | Gollamari | 94 | 00:00 | 127 | Narinda | 68 | 16:00
62 | Gopalganj | 99.6 | 18:00 | 128 | Narshingdi | 183 | 00:00
63 | Gulshan | 134 | 13:00 | 129 | Natore | 131 | 01:00
64 | Halishahar | 61 | 15:00 | 130 | Nawabganj | 45.2 | 18:30
65 | HaripurSBU | 153 | 09:00 | 131 | Netrakona | 128 | 01:00
66 | Hasnabad | 95 | 00:00 | 132 | New | 58.6 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14615.56 | 253 |  | 14879.95
1:00 | 13999.36 | 240 |  | 14250.16
2:00 | 13834 | 63 |  | 13899.84
3:00 | 13507 | 0 |  | 13507
4:00 | 13040 | 0 |  | 13040
5:00 | 12596 | 0 |  | 12596
6:00 | 12270.07 | 0 |  | 12270.07
7:00 | 12321.99 | 0 |  | 12321.99
8:00 | 12540.47 | 22 |  | 12563.46
9:00 | 12605.34 | 36 |  | 12642.96
10:00 | 12791.7 | 25 |  | 12817.83
11:00 | 13204.67 | 24 |  | 13229.67
12:00 | 13439.16 | 130 |  | 13575.16
13:00 | 13462.2 | 211 |  | 13682.2
14:00 | 13062.93 | 518 |  | 13604.24
15:00 | 13179.96 | 395 |  | 13592.74
16:00 | 13192.44 | 327 |  | 13534.16
17:00 | 13044.72 | 324 |  | 13383.3
18:00 | 13938.98 | 584 |  | 14549.26
19:00 | 14246.36 | 578 |  | 14850.37
19:30 | 14354.83 | 570 |  | 14950.48
20:00 | 14213.98 | 656 |  | 14899.5
21:00 | 14082.26 | 687 |  | 14800.18
22:00 | 14050.18 | 622 |  | 14700.18
23:00 | 13836.29 | 683 |  | 14550.03
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7925.36 | 6690.2 | 14615.56 | DAILY GENERATION CURVE
00:30 | 7755.86 | 6551.6 | 14307.46
01:00 | 7586.36 | 6413 | 13999.36 | 19-10-2025
01:30 | 7525.18 | 6391.5 | 13916.68
02:00 | 7464 | 6370 | 13834
02:30 | 7385.5 | 6285 | 13670.5
03:00 | 7307 | 6200 | 13507
03:30 | 7165 | 6108.5 | 13273.5
04:00 | 7023 | 6017 | 13040
04:30 | 6912 | 5906 | 12818
05:00 | 6801 | 5795 | 12596
05:30 | 6678.535 | 5754.5 | 12433.035
06:00 | 6556.07 | 5714 | 12270.07
06:30 | 6563.88 | 5732.15 | 12296.03
07:00 | 6571.69 | 5750.3 | 12321.99
07:30 | 6579.08 | 5852.15 | 12431.23
08:00 | 6586.47 | 5954 | 12540.47
08:30 | 6704.58 | 5868.325 | 12572.905
09:00 | 6822.69 | 5782.65 | 12605.34
09:30 | 6893.155 | 5805.365 | 12698.52
10:00 | 6963.62 | 5828.08 | 12791.7
10:30 | 7134.11 | 5864.075 | 12998.185
11:00 | 7304.6 | 5900.07 | 13204.67
11:30 | 7426.62 | 5895.295 | 13321.915
12:00 | 7548.64 | 5890.52 | 13439.16
12:30 | 7480.855 | 5969.825 | 13450.68
13:00 | 7413.07 | 6049.13 | 13462.2
13:30 | 7222.285 | 6040.28 | 13262.565
14:00 | 7031.5 | 6031.43 | 13062.93
14:30 | 7116.47 | 6004.975 | 13121.445
15:00 | 7201.44 | 5978.52 | 13179.96
15:30 | 7168.645 | 6017.555 | 13186.2
16:00 | 7135.85 | 6056.59 | 13192.44
16:30 | 7124.665 | 5993.915 | 13118.58
17:00 | 7113.48 | 5931.24 | 13044.72
17:30 | 7419.49 | 6072.36 | 13491.85
18:00 | 7725.5 | 6213.48 | 13938.98
18:30 | 7758.18 | 6334.49 | 14092.67
19:00 | 7790.86 | 6455.5 | 14246.36
19:30 | 7898.86 | 6455.97 | 14354.83
20:00 | 7788.86 | 6425.12 | 14213.98
20:30 | 7733.86 | 6414.26 | 14148.12 |  | Executive Engineer
21:00 | 7678.86 | 6403.4 | 14082.26 |  | Network Operation Division
21:30 | 7648.61 | 6417.61 | 14066.22
22:00 | 7618.36 | 6431.82 | 14050.18
22:30 | 7536.36 | 6406.875 | 13943.235
23:00 | 7454.36 | 6381.93 | 13836.29

## En-Curve
QF-LDC-12
Date | 19-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3510 | 1650 | 873 | 38 | 84 | 1461 | 218 | 4090 | 0 | 891 | 1800.56 | 0 | 0 | 0 | 253 | DAILY ENERGY CURVE
00:30 | 3473.5 | 1626 | 873 | 38 | 82 | 1463 | 217.5 | 4090.5 | 0 | 751 | 1692.96 | 0 | 0 | 0 | 246.5 | 19-10-2025
01:00 | 3437 | 1602 | 873 | 38 | 80 | 1465 | 217 | 4091 | 0 | 611 | 1585.36 | 0 | 0 | 0 | 240
01:30 | 3440 | 1603.5 | 873.5 | 38 | 77 | 1465 | 217 | 4038 | 0 | 611 | 1553.68 | 0 | 0 | 0 | 151.5 | Energy Generated | 322.8882 |  | MKWHr
02:00 | 3443 | 1605 | 874 | 38 | 74 | 1465 | 217 | 3985 | 0 | 611 | 1522 | 0 | 0 | 0 | 63 | Energy not Served | 6.378 |  | MKWHr
02:30 | 3429 | 1609.5 | 873.5 | 38 | 72 | 1463.5 | 216.5 | 3927 | 0 | 594.5 | 1447 | 0 | 0 | 0 | 31.5 | Total Energy Requirement | 329.2662 |  | MKWHr
03:00 | 3415 | 1614 | 873 | 38 | 70 | 1462 | 216 | 3869 | 0 | 578 | 1372 | 0 | 0 | 0 | 0
03:30 | 3415.5 | 1608.5 | 873 | 38 | 70 | 1464 | 216.5 | 3874 | 0 | 522 | 1192 | 0 | 0 | 0 | 0
04:00 | 3416 | 1603 | 873 | 38 | 70 | 1466 | 217 | 3879 | 0 | 466 | 1012 | 0 | 0 | 0 | 0
04:30 | 3404 | 1603.5 | 873.5 | 38 | 69 | 1465.5 | 217 | 3870 | 0 | 396.5 | 881 | 0 | 0 | 0 | 0
05:00 | 3392 | 1604 | 874 | 38 | 68 | 1465 | 217 | 3861 | 0 | 327 | 750 | 0 | 0 | 0 | 0
05:30 | 3391.5 | 1592.5 | 873.5 | 38 | 66 | 1469 | 218.5 | 3864.5 | 0.035 | 312.5 | 607 | 0 | 0 | 0 | 0
06:00 | 3391 | 1581 | 873 | 38 | 64 | 1473 | 220 | 3868 | 0.07 | 298 | 464 | 0 | 0 | 0 | 0
06:30 | 3350.5 | 1605 | 873 | 38 | 64 | 1472.5 | 220.5 | 3868 | 50.53 | 298 | 456 | 0 | 0 | 0 | 0
07:00 | 3310 | 1629 | 873 | 38 | 64 | 1472 | 221 | 3868 | 100.99 | 298 | 448 | 0 | 0 | 0 | 0
07:30 | 3322.5 | 1608.5 | 873 | 38 | 63 | 1469 | 221.5 | 3863.5 | 206.73 | 309.5 | 456 | 0 | 0 | 0 | 11
08:00 | 3335 | 1588 | 873 | 38 | 62 | 1466 | 222 | 3859 | 312.47 | 321 | 464 | 0 | 0 | 0 | 22
08:30 | 3408 | 1621 | 873 | 38 | 59 | 1302 | 222 | 3857 | 396.405 | 302 | 494.5 | 0 | 0 | 0 | 29
09:00 | 3481 | 1654 | 873 | 38 | 56 | 1138 | 222 | 3855 | 480.34 | 283 | 525 | 0 | 0 | 0 | 36
09:30 | 3453 | 1647.5 | 873 | 38 | 55.5 | 1140.5 | 222 | 3845 | 559.52 | 283 | 581.5 | 0 | 0 | 0 | 30.5
10:00 | 3425 | 1641 | 873 | 38 | 55 | 1143 | 222 | 3835 | 638.7 | 283 | 638 | 0 | 0 | 0 | 25
10:30 | 3440 | 1670.5 | 873 | 38 | 58.5 | 1141.5 | 222 | 3845.5 | 659.185 | 303 | 746.5 | 0 | 0 | 0.5 | 24.5
11:00 | 3455 | 1700 | 873 | 38 | 62 | 1140 | 222 | 3856 | 679.67 | 323 | 855 | 0 | 0 | 1 | 24
11:30 | 3433 | 1716.5 | 873 | 38 | 65.5 | 1141 | 221 | 3856.5 | 662.165 | 335.5 | 979.25 | 0 | 0 | 0.5 | 77
12:00 | 3411 | 1733 | 873 | 38 | 69 | 1142 | 220 | 3857 | 644.66 | 348 | 1103.5 | 0 | 0 | 0 | 130
12:30 | 3423.5 | 1695 | 873 | 38 | 75.5 | 1146 | 220 | 3854 | 598.18 | 318 | 1209 | 0 | 0 | 0.5 | 170.5
13:00 | 3436 | 1657 | 873 | 38 | 82 | 1150 | 220 | 3851 | 551.7 | 288 | 1314.5 | 0 | 0 | 1 | 211
13:30 | 3344.5 | 1612 | 872.5 | 38 | 81 | 1143.985 | 219 | 3875 | 550.08 | 291.5 | 1231 | 0 | 0 | 4 | 364.5
14:00 | 3253 | 1567 | 872 | 38 | 80 | 1137.97 | 218 | 3899 | 548.46 | 295 | 1147.5 | 0 | 0 | 7 | 518
14:30 | 3311 | 1574 | 872.5 | 38 | 77.5 | 1149.555 | 218.5 | 3925.5 | 486.39 | 294.5 | 1167.5 | 0 | 0 | 6.5 | 456.5
15:00 | 3369 | 1581 | 873 | 38 | 75 | 1161.14 | 219 | 3952 | 424.32 | 294 | 1187.5 | 0 | 0 | 6 | 395
15:30 | 3361.5 | 1578.5 | 873 | 38 | 77 | 1277.445 | 219.5 | 3933.5 | 319.755 | 309 | 1195 | 0 | 0 | 4 | 361
16:00 | 3354 | 1576 | 873 | 38 | 79 | 1393.75 | 220 | 3915 | 215.19 | 324 | 1202.5 | 0 | 0 | 2 | 327
16:30 | 3311 | 1578.5 | 873 | 38 | 78.5 | 1421.745 | 220 | 3863.5 | 124.835 | 361 | 1247.5 | 0 | 0 | 1 | 325.5
17:00 | 3268 | 1581 | 873 | 38 | 78 | 1449.74 | 220 | 3812 | 34.48 | 398 | 1292.5 | 0 | 0 | 0 | 324
17:30 | 3325.5 | 1589.5 | 873 | 38 | 81 | 1451.61 | 220.5 | 3872 | 17.24 | 581.5 | 1442 | 0 | 0 | 0 | 454
18:00 | 3383 | 1598 | 873 | 38 | 84 | 1453.48 | 221 | 3932 | 0 | 765 | 1591.5 | 0 | 0 | 0 | 584
18:30 | 3420 | 1595 | 873 | 38 | 84 | 1457.99 | 221 | 3942.5 | 0 | 799.5 | 1661.68 | 0 | 0 | 0 | 581
19:00 | 3457 | 1592 | 873 | 38 | 84 | 1462.5 | 221 | 3953 | 0 | 834 | 1731.86 | 0 | 0 | 0 | 578
19:30 | 3461 | 1659 | 873 | 38 | 90 | 1465.97 | 222 | 3947 | 0 | 820 | 1778.86 | 0 | 0 | 0 | 570
20:00 | 3474 | 1613 | 873 | 38 | 84 | 1454.12 | 222 | 3926 | 0 | 816 | 1713.86 | 0 | 0 | 0 | 656
20:30 | 3490 | 1602.5 | 873 | 38 | 85 | 1458.26 | 221 | 3907.5 | 0 | 808 | 1664.86 | 0 | 0 | 0 | 671.5
21:00 | 3506 | 1592 | 873 | 38 | 86 | 1462.4 | 220 | 3889 | 0 | 800 | 1615.86 | 0 | 0 | 0 | 687
21:30 | 3503.5 | 1597.5 | 873 | 38 | 87 | 1462.51 | 221 | 3888 | 0 | 800.5 | 1595.21 | 0 | 0 | 0 | 654.5
22:00 | 3501 | 1603 | 873 | 38 | 88 | 1462.62 | 222 | 3887 | 0 | 801 | 1574.56 | 0 | 0 | 0 | 622
22:30 | 3482 | 1605 | 873 | 38 | 90 | 1459.175 | 222 | 3885.5 | 0 | 711.5 | 1577.06 | 0 | 0 | 0 | 652.5
23:00 | 3463 | 1607 | 873 | 38 | 92 | 1455.73 | 222 | 3884 | 0 | 622 | 1579.56 | 0 | 0 | 0 | 683
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 05:00 | 365 | 16:00 | Payra | 409 | 04:00 | 405 | 15:00
Ashuganj | 406 | 4:00 | 380 | 12:00 | Rahanpur | 399 | 14:00 | 389 | 07:00
Bhulta | 400 | 04:00 | 370 | 12:00 | Rampal | 396 | 05:00 | 386 | 16:00
Bibiana | 387 | 04:00 | 379 | 16:00
BIPTC | 402 | 04:00 | 394 | 18:00
Bogura | 389 | 14:00 | 377 | 07:00
Gopalganj | 391 | 06:00 | 381 | 14:00
Kaliakoir | 373 | 04:00 | 356 | 16:00
Madunaghat | 392 | 03:00 | 386 | 11:00
Meghnaghat | 381 | 03:00 | 370 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 04:00 | 215 | 11:00 | Kaliakoir | 233 | 04:00 | 219 | 16:00
AKSML | 232 | 02:00 | 225 | 10:00 | Keranigonj | 224 | 05:00 | 212 | 12:00
Aminbazar | 227 | 04:00 | 216 | 11:00 | Khulna(S) | 227 | 05:00 | 218 | 13:00
Ashuganj | 227 | 02:00 | 217 | 11:00 | Madunaghat | 234 | 18:00 | 228 | 08:00
Ashuganj-400 | 227 | 02:00 | 217 | 11:00 | Madunaghat-400 | 234 | 19:00 | 228 | 11:00
Baghabari | 232 | 05:00 | 226 | 12:00 | Maniknagar | 217 | 05:00 | 209 | 11:00
Barapukuria | 225 | 14:00 | 213 | 12:00 | Meghnaghat | 224 | 03:00 | 219 | 11:00
Barapukuria-230 | 225 | 14:00 | 213 | 12:00 | Meghnaghat-400 | 222 | 05:00 | 214 | 11:00
Barishal | 231 | 04:00 | 226 | 13:00 | Mirsorai | 233 | 18:00 | 220 | 10:00
Bheramara | 232 | 04:00 | 225 | 12:00 | Rajshahi | 232 | 06:00 | 222 | 13:00
Bhulta | 229 | 04:00 | 210 | 11:00 | Rampal | 227 | 06:00 | 219 | 13:00
Bibiana | 228 | 03:00 | 223 | 19:30 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 235 | 06:00 | 224 | 13:00 | Rampura | 228 | 04:00 | 207 | 12:00
Bogura | 237 | 14:00 | 230 | 07:00 | Shikalbaha | 233 | 08:00 | 227 | 10:00
Bogura-400 | 238 | 14:00 | 230 | 07:00 | Shyampur | 222 | 05:00 | 212 | 12:00
Borhanuddin | 235 | 05:00 | 232 | 13:00 | Siddhirganj | 220 | 04:00 | 212 | 11:00
BSRM | 231 | 18:00 | 219 | 11:00 | Sirajgonj | 238 | 03:00 | 233 | 12:00
Cumilla(N) | 222 | 18:00 | 215 | 10:00 | Sreepur | 226 | 04:00 | 217 | 10:00
Faridpur | 228 | 06:00 | 222 | 13:00 | Tongi | 227 | 03:00 | 212 | 13:00
Fenchuganj | 230 | 06:00 | 226 | 19:00
Ghorashal | 225 | 00:00 | 220 | 10:00
Ghorashal-230 | 227 | 04:00 | 211 | 10:00
Gopalganj | 230 | 06:00 | 224 | 14:00
GPH | 233 | 18:00 | 224 | 11:00
Haripur | 219 | 05:00 | 211 | 12:00
Hasnabad | 222 | 03:00 | 212 | 11:00
Hathazari | 231 | 18:30 | 224 | 10:00
Ishurdi | 234 | 04:00 | 228 | 12:00
Jhenaidah | 228 | 06:00 | 218 | 13:00
Kachua | 230 | 18:00 | 219 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 123 | 12:00 | Lalmonirhat | 132 | 04:00 | 122 | 12:00
Agargaon | 133 | 03:00 | 124 | 11:00 | Madanganj | 128 | 17:00 | 124 | 07:00
Agrabad | 134 | 18:00 | 130 | 09:00 | Madaripur | 133 | 06:00 | 129 | 02:00
AKS | 131 | 00:00 | 126 | 10:00 | Madartek | 136 | 22:00 | 122 | 12:00
Aminbazar | 133 | 04:00 | 124 | 12:00 | Madunaghat | 136 | 18:00 | 132 | 08:00
Amnura | 136 | 00:00 | 128 | 12:00 | Magura | 133 | 06:00 | 124 | 13:00
Ashuganj | 137 | 05:00 | 132 | 22:00 | Mahasthangarh | 132 | 14:00 | 126 | 07:00
Bagerhat | 130 | 09:00 | 121 | 01:00 | Maijdee | 132 | 18:00 | 126 | 11:00
Bajitpur | 128 | 04:00 | 121 | 16:00 | Manikganj | 128 | 06:00 | 117 | 16:00
Bakulia | 137 | 18:00 | 131 | 09:00 | Maniknagar | 132 | 03:00 | 125 | 11:00
Banani | 137 | 05:00 | 121 | 10:00 | Matarbari | 125 | 12:00 | 114 | 02:00
Bangabhaban | 132 | 05:00 | 125 | 11:00 | Matuail | 127 | 03:00 | 122 | 11:00
Barapukuria | 138 | 14:00 | 127 | 12:00 | Metrorail_Motijheel | 132 | 03:00 | 125 | 11:00
Barguna | 135 | 06:00 | 132 | 00:00 | Metrorail_Uttara | 132 | 03:00 | 119 | 16:00
Barishal | 132 | 04:00 | 127 | 11:00 | Millgate | 133 | 02:00 | 121 | 16:00
Barishal-230 | 132 | 04:00 | 127 | 13:00 | Mirpur | 132 | 02:00 | 122 | 11:00
Baroaulia | 133 | 00:00 | 129 | 10:00 | Mirzapur | 130 | 04:00 | 124 | 15:00
Baroirhat | 132 | 18:00 | 126 | 10:00 | Mithapukur | 134 | 14:00 | 124 | 12:00
Bashundhara | 137 | 04:00 | 121 | 12:00 | MI_Cement | 130.4 | 05:00 | 122 | 16:00
BashundharaCement | 128 | 17:00 | 124 | 08:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 04:00 | 123 | 19:00 | Mogbazar | 139 | 22:00 | 124 | 10:00
Benapole | 130 | 06:00 | 122 | 13:00 | Mongla | 130 | 09:00 | 122 | 18:30
Bhaluka | 130 | 18:00 | 120 | 11:00 | Motijheel | 132 | 05:00 | 125 | 11:00
Bhandaria | 126 | 09:00 | 115 | 19:00 | Muktagacha | 132 | 06:00 | 122 | 06:00
Bhangura | 133 | 03:00 | 129 | 11:00 | Munshiganj | 126 | 00:00 | 120 | 11:00
Bheramara | 137 | 04:00 | 134 | 12:00 | Muradnagar | 127 | 18:00 | 120 | 11:00
Bheramara(GK) | 136 | 00:00 | 134 | 12:00 | Mymensingh | 132 | 06:00 | 115 | 11:00
Bhulta | 125 | 18:00 | 119 | 11:00 | Naogaon | 130 | 14:00 | 124 | 12:00
Bog-Sherpur | 134 | 14:00 | 128 | 12:00 | Narail | 131 | 05:00 | 124 | 02:00
Bogura | 135 | 14:00 | 129 | 12:00 | Narinda | 132 | 03:00 | 125 | 11:00
Bogura-230 | 135 | 14:00 | 130 | 07:00 | Narshingdi | 130 | 07:00 | 115 | 11:00
Brahmanbaria | 133 | 18:00 | 125 | 10:00 | Natore | 133 | 00:00 | 130 | 12:00
Cantonment | 133 | 04:00 | 123 | 16:00 | Nawabganj | 132 | 04:00 | 123 | 12:00
Chandina | 130 | 18:00 | 124 | 11:00 | Netrakona | 121 | 06:00 | 115 | 00:00
Chandpur | 135 | 23:00 | 130 | 01:00 | New | 134 | 03:00 | 121 | 16:00
Chandraghona | 136 | 18:00 | 132 | 10:00 | Niamatpur | 135 | 09:00 | 132 | 07:00
Chapai | 134 | 09:00 | 130 | 02:00 | Noapara | 133 | 06:00 | 125 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 18:00 | 121 | 11:00 | Pabna | 135 | 04:00 | 131 | 12:00
Chauddagram | 130 | 18:00 | 124 | 11:00 | Palashbari | 129 | 04:00 | 122 | 07:00
Chhatak | 127 | 06:00 | 121 | 19:30 | Panchagarh | 141 | 03:00 | 117 | 10:00
Chowmuhani | 131 | 18:00 | 126 | 10:00 | Patiya | 134 | 14:00 | 129 | 10:00
Chuadanga | 130 | 05:00 | 124 | 12:00 | Patuakhali | 137 | 11:00 | 134 | 00:00
Coxsbazar | 123 | 12:00 | 116 | 00:00 | Payra | 136 | 03:00 | 135 | 00:00
Cumilla(N) | 130 | 18:00 | 126 | 10:00 | PHP | 132 | 18:30 | 125 | 11:00
Cumilla(S) | 130 | 05:00 | 125 | 11:00 | Postogola | 132 | 03:00 | 125 | 12:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 137 | 04:00 | 123 | 10:00
Daudkandi | 125 | 18:00 | 117 | 11:00 | Purbasadipur | 135 | 03:00 | 118 | 12:00
DhakaUniversity | 137 | 02:00 | 124 | 10:00 | Rahanpur | 136 | 14:00 | 133 | 18:00
Dhamrai | 132 | 00:00 | 124 | 10:00 | Rahanpur-400 | 137 | 14:00 | 134 | 07:00
Dhanmondi | 137.5 | 22:00 | 123 | 12:00 | Rahim | 128 | 04:00 | 122 | 12:00
Dohazari | 132 | 14:00 | 126 | 01:00 | Rajbari | 134 | 06:00 | 121 | 20:00
Faridpur | 134 | 03:00 | 130 | 12:00 | Rajendrapur | 132 | 00:00 | 120 | 11:00
Fatullah | 134 | 04:00 | 127 | 11:00 | Rajshahi | 133 | 01:00 | 128 | 12:00
Fenchuganj | 135 | 04:00 | 133 | 18:30 | Rajshahi-230 | 133 | 06:00 | 127 | 13:00
Feni | 132 | 18:00 | 120 | 01:00 | Ramganj | 131 | 18:00 | 126 | 01:00
Ghatail | 128 | 05:00 | 121 | 07:00 | Rampur | 133 | 03:00 | 130 | 09:00
Ghorashal | 135 | 05:00 | 127 | 12:00 | Rampura | 137 | 22:00 | 123 | 10:00
Goalpara | 135 | 04:00 | 127 | 13:00 | Rangamati | 135 | 18:00 | 131 | 10:00
Gollamari | 135 | 06:00 | 129 | 13:00 | Rangpur | 135 | 14:00 | 125 | 08:00
Gopalganj | 134 | 00:00 | 127 | 13:00 | Ruppur | 137 | 04:00 | 134 | 07:00
Gopalganj-400 | 135 | 05:00 | 130 | 14:00 | Saidpur | 134 | 12:00 | 122 | 11:00
Gulshan | 137 | 22:00 | 123 | 12:00 | Satkhira | 132 | 09:00 | 124 | 13:00
Halishahar | 135 | 18:00 | 130 | 09:00 | Satmasjid | 133 | 04:00 | 124 | 12:00
Haripur | 127 | 03:00 | 123 | 11:00 | Savar | 132 | 04:00 | 120 | 11:00
HaripurSBU | 127 | 03:00 | 123 | 11:00 | SevenRings | 136 | 04:00 | 126 | 10:00
Hasnabad | 132 | 03:00 | 125 | 15:00 | ShahCement | 127 | 18:00 | 123 | 11:00
Hathazari | 135 | 09:00 | 132 | 10:00 | Shahjadpur | 135 | 04:00 | 132 | 00:00
Ishurdi | 137 | 03:00 | 134 | 13:00 | Shahjibazar | 135 | 07:00 | 127 | 10:00
Jaldhaka | 133 | 14:00 | 120 | 12:00 | Shahmirpur | 136 | 18:00 | 130 | 10:00
Jamalpur | 130 | 05:00 | 121 | 00:00 | Shariatpur | 132 | 04:00 | 128 | 11:00
Jashore | 133 | 06:00 | 123 | 15:00 | Sherpur | 131 | 06:00 | 117 | 07:00
Jhenaidah | 135 | 06:00 | 125 | 13:00 | Shikalbaha | 124 | 14:00 | 119 | 04:00
Jhenaidah-230 | 135 | 06:00 | 128 | 13:00 | Shikalbaha-230 | 137 | 18:00 | 133 | 05:00
Joydebpur | 132 | 01:00 | 120 | 10:00 | Shitalakhya | 130.5 | 05:00 | 122 | 16:00
Joypurhat | 128 | 14:00 | 122 | 12:00 | Sholosohor | 136 | 18:00 | 132 | 11:00
Juldah | 135 | 18:00 | 130 | 10:00 | Shyampur | 132 | 00:00 | 127 | 12:00
Kabirpur | 134 | 00:00 | 117 | 16:00 | Shyampur-230 | 135 | 06:00 | 127 | 12:00
Kachua | 135 | 18:00 | 130 | 01:00 | Siddhirganj | 136 | 20:00 | 122 | 12:00
Kaliakoir | 135 | 02:00 | 126 | 16:00 | Sirajganj | 131 | 04:00 | 127 | 12:00
Kallyanpur | 134 | 05:00 | 124 | 11:00 | Sonargaon | 125 | 04:00 | 121 | 11:00
Kalurghat | 136 | 18:00 | 131 | 10:00 | Sreemongol | 133 | 07:00 | 127 | 10:00
Kamrangirchar | 133 | 06:00 | 123 | 11:00 | Sreepur | 131 | 04:00 | 124 | 10:00
Kaptai | 137 | 18:00 | 135 | 4:00 | Srinagar | 132 | 03:00 | 123 | 16:00
Kasba | 124 | 03:00 | 118 | 11:00 | SSM | 139 | 23:00 | 132 | 11:00
Kazla | 132 | 05:00 | 125 | 12:00 | Sunamganj | 125 | 11:00 | 119 | 19:00
Keranigonj | 133 | 04:00 | 124 | 12:00 | Sylhet | 130 | 07:00 | 126 | 19:00
Khagrachori | 134 | 18:00 | 130 | 10:00 | Sylhet-132 | 130 | 18:00 | 127 | 00:00
Khulna | 133 | 06:00 | 127 | 13:00 | Tangail | 127 | 12:00 | 122 | 00:00
Khulna(S) | 135 | 06:00 | 129 | 13:00 | Taraganj | 134 | 14:00 | 123 | 12:00
Khulshi | 133 | 18:00 | 128 | 09:00 | Thakurgaon | 137 | 03:00 | 114 | 11:00
Kishoreganj | 126 | 18:00 | 120 | 09:00 | TK | 136 | 18:00 | 132 | 09:00
Kodda | 133 | 02:00 | 118 | 12:00 | Tongi | 134 | 03:00 | 125 | 11:00
KSRM | 134 | 17:00 | 130 | 10:00 | Ullahpara | 133 | 05:00 | 128 | 12:00
Kulaura | 135 | 07:00 | 131 | 18:30 | Ullon | 137 | 22:00 | 123 | 10:00
Kurigram | 133 | 14:00 | 121 | 07:00 | Uttara | 134 | 04:00 | 123 | 10:00
Kushtia | 133 | 05:00 | 129 | 00:00 | UttaraNew | 132 | 03:00 | 119 | 16:00
Laksam | 133 | 18:00 | 128 | 11:00 | Zigatola | 132 | 04:00 | 123 | 12:00
Lakshmipur | 131 | 18:00 | 126 | 11:00
Lalbag | 132 | 04:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division